## 00_JB_Index
KALASIN ENGINEERING ¦ JUNCTION BOX LOOP TEST REGISTER: IS-JB-612
Project Sprint 18K TPA Spray Dryer / Jet Cooker ¦ Location: IS-JB-612 ¦ 1 Equipment = 1 Sheet
TOTAL EQUIPMENT |  | TOTAL ACTIVE CHANNELS |  | DIGITAL INPUT (DI) |  | DIGITAL OUTPUT (DO) |  | ANALOG IN/OUT (AI/AO)
17 Units |  | 17 Channels |  | 15 Pts |  | 0 Pts |  | 2 AI / 0 AO
Item # | Equipment Tag | Equipment Service Description | P&ID Drawing No. | Primary Signal Breakdown | Total Channels | Primary JB Terminal | PLC Rack / Slot | CAD Wiring Typical | Loop Test Status | QA/QC Sign-off & Date
1 | DPT-61310 | Vent filter pressure | 325-01-613-PD-03 | 1x AI | 1 | P4-TBAI2-1(A/B) | C4/C4S6 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
2 | DPT-61312 | Vent filter pressure | 325-01-613-PD-05 | 1x AI | 1 | P4-TBAI2-2(A/B) | C4/C4S6 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
3 | ISV-61303 | Explosion isolation flap valve ISV-61303 | 325-01-613-PD-03 | 1x DI (Solenoid + FB) | 1 | P4-TBDI2-1 | C4/C4S2 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
4 | ISV-61304 | Explosion isolation flap valve ISV-61304 | 325-01-613-PD-05 | 1x DI (Solenoid + FB) | 1 | P4-TBDI2-2 | C4/C4S2 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
5 | LSH-61304 | Big bag level alarm high | 325-01-613-PD-03 | 1x DI | 1 | P4-TBDI2-3 | C4/C4S2 | TYP-DI-01 / SWITCH | READY FOR TEST | Pending Sign-off
6 | LSH-61305 | Big bag level alarm high | 325-01-613-PD-05 | 1x DI | 1 | P4-TBDI2-4 | C4/C4S2 | TYP-DI-01 / SWITCH | READY FOR TEST | Pending Sign-off
7 | LSH-61307 | High Level alarm reject screen | 325-01-613-PD-01 | 1x DI | 1 | P4-TBDI2-5 | C4/C4S2 | TYP-DI-01 / SWITCH | READY FOR TEST | Pending Sign-off
8 | LSH-61312 | Level alarm high | 325-01-613-PD-05 | 1x DI | 1 | P4-TBDI2-6 | C4/C4S2 | TYP-DI-01 / SWITCH | READY FOR TEST | Pending Sign-off
9 | PSE-61302 | Explosion Vent PSE-61302 | 325-01-613-PD-03 | 1x DI | 1 | P4-TBDI2-7 | C4/C4S2 | TYP-IS-01 / BARRIER | READY FOR TEST | Pending Sign-off
10 | PSE-61303 | Explosion Vent PSE-61303 | 325-01-613-PD-05 | 1x DI | 1 | P4-TBDI2-8 | C4/C4S2 | TYP-IS-01 / BARRIER | READY FOR TEST | Pending Sign-off
11 | RV-61301 | IN-8 | - | 1x DI (Solenoid + FB) | 1 | P4-TBDI2-9 | C4/C4S2 | TYP-IS-01 / BARRIER | READY FOR TEST | Pending Sign-off
12 | RV-61304 | IN-9 | - | 1x DI (Solenoid + FB) | 1 | P4-TBDI2-10 | C4/C4S2 | TYP-IS-01 / BARRIER | READY FOR TEST | Pending Sign-off
13 | RV-61305 | IN-10 | - | 1x DI (Solenoid + FB) | 1 | P4-TBDI2-11 | C4/C4S2 | TYP-IS-01 / BARRIER | READY FOR TEST | Pending Sign-off
14 | SC-61301 | IN-11 | - | 1x DI | 1 | P4-TBDI2-12 | C4/C4S2 | TYP-IS-01 / BARRIER | READY FOR TEST | Pending Sign-off
15 | SC-61302 | IN-12 | - | 1x DI | 1 | P4-TBDI2-13 | C4/C4S2 | TYP-IS-01 / BARRIER | READY FOR TEST | Pending Sign-off
16 | ZS-61312 | Position Magnet Door | 325-01-613-PD-01 | 1x DI | 1 | P4-TBDI2-14 | C4/C4S2 | TYP-IS-01 / BARRIER | READY FOR TEST | Pending Sign-off
17 | ZS-61313 | Position Magnet Door | 325-01-613-PD-01 | 1x DI | 1 | P4-TBDI2-15 | C4/C4S2 | TYP-IS-01 / BARRIER | READY FOR TEST | Pending Sign-off

## DPT-61310
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: DPT-61310 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | DPT-61310 |  | P&ID Number: | 325-01-613-PD-03 |  | Junction Box: | IS-JB-612
Service Description: | Vent filter pressure |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Differential Pressure Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Pressure / Diff. Pressure Transmitter (4-20mA AI) [Pins A+B] | AI | DPT-61310_AI_1 | C4/C4S6 Pins 2(A) & 1(B) | P4-TBAI2-1(A/B) | C4S6-2/P4-TBAI2-1(A) (+) / C4S6-1/P4-TBAI2-1(B) (-) | P4-TBAI2-1(A)/C4S6-2 (+) / P4-TBAI2-1(B)/C4S6-1 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | DPT-61310 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | DPT-61310 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | DPT-61310 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## DPT-61312
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: DPT-61312 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | DPT-61312 |  | P&ID Number: | 325-01-613-PD-05 |  | Junction Box: | IS-JB-612
Service Description: | Vent filter pressure |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Differential Pressure Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Pressure / Diff. Pressure Transmitter (4-20mA AI) [Pins A+B] | AI | DPT-61312_AI_1 | C4/C4S6 Pins 4(A) & 3(B) | P4-TBAI2-2(A/B) | C4S6-4/P4-TBAI2-2(A) (+) / C4S6-3/P4-TBAI2-2(B) (-) | P4-TBAI2-2(A)/C4S6-4 (+) / P4-TBAI2-2(B)/C4S6-3 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | DPT-61312 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | DPT-61312 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | DPT-61312 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## ISV-61303
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: ISV-61303 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | ISV-61303 |  | P&ID Number: | 325-01-613-PD-03 |  | Junction Box: | IS-JB-612
Service Description: | Explosion isolation flap valve ISV-61303 |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Position switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - ISV-61303_DI_1 | DI | ISV-61303_DI_1 | C4/C4S2 1 | P4-TBDI2-1 | C4S2-1/P4-TBDI2-1 | P4-TBDI2-1/C4S2-1 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | ISV-61303 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | ISV-61303 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | ISV-61303 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## ISV-61304
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: ISV-61304 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | ISV-61304 |  | P&ID Number: | 325-01-613-PD-05 |  | Junction Box: | IS-JB-612
Service Description: | Explosion isolation flap valve ISV-61304 |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Position switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - ISV-61304_DI_1 | DI | ISV-61304_DI_1 | C4/C4S2 2 | P4-TBDI2-2 | C4S2-2/P4-TBDI2-2 | P4-TBDI2-2/C4S2-2 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | ISV-61304 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | ISV-61304 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | ISV-61304 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## LSH-61304
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: LSH-61304 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | LSH-61304 |  | P&ID Number: | 325-01-613-PD-03 |  | Junction Box: | IS-JB-612
Service Description: | Big bag level alarm high |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Level switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Liquid / Powder Level Switch Trip Status (DI) | DI | LSH-61304_DI_1 | C4/C4S2 3 | P4-TBDI2-3 | C4S2-3/P4-TBDI2-3 | P4-TBDI2-3/C4S2-3 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | LSH-61304 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | LSH-61304 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | LSH-61304 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## LSH-61305
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: LSH-61305 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | LSH-61305 |  | P&ID Number: | 325-01-613-PD-05 |  | Junction Box: | IS-JB-612
Service Description: | Big bag level alarm high |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Level switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Liquid / Powder Level Switch Trip Status (DI) | DI | LSH-61305_DI_1 | C4/C4S2 4 | P4-TBDI2-4 | C4S2-4/P4-TBDI2-4 | P4-TBDI2-4/C4S2-4 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | LSH-61305 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | LSH-61305 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | LSH-61305 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## LSH-61307
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: LSH-61307 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | LSH-61307 |  | P&ID Number: | 325-01-613-PD-01 |  | Junction Box: | IS-JB-612
Service Description: | High Level alarm reject screen |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Level switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Liquid / Powder Level Switch Trip Status (DI) | DI | LSH-61307_DI_1 | C4/C4S2 5 | P4-TBDI2-5 | C4S2-5/P4-TBDI2-5 | P4-TBDI2-5/C4S2-5 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | LSH-61307 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | LSH-61307 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | LSH-61307 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## LSH-61312
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: LSH-61312 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | LSH-61312 |  | P&ID Number: | 325-01-613-PD-05 |  | Junction Box: | IS-JB-612
Service Description: | Level alarm high |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Level switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Liquid / Powder Level Switch Trip Status (DI) | DI | LSH-61312_DI_1 | C4/C4S2 6 | P4-TBDI2-6 | C4S2-6/P4-TBDI2-6 | P4-TBDI2-6/C4S2-6 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | LSH-61312 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | LSH-61312 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | LSH-61312 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PSE-61302
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PSE-61302 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PSE-61302 |  | P&ID Number: | 325-01-613-PD-03 |  | Junction Box: | IS-JB-612
Service Description: | Explosion Vent PSE-61302 |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Position switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Pressure Switch Trip Status (DI) | DI | PSE-61302_DI_1 | C4/C4S2 7 | P4-TBDI2-7 | C4S2-7/P4-TBDI2-7 | P4-TBDI2-7/C4S2-7 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PSE-61302 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PSE-61302 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PSE-61302 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PSE-61303
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PSE-61303 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PSE-61303 |  | P&ID Number: | 325-01-613-PD-05 |  | Junction Box: | IS-JB-612
Service Description: | Explosion Vent PSE-61303 |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Position switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Pressure Switch Trip Status (DI) | DI | PSE-61303_DI_1 | C4/C4S2 8 | P4-TBDI2-8 | C4S2-8/P4-TBDI2-8 | P4-TBDI2-8/C4S2-8 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PSE-61303 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PSE-61303 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PSE-61303 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## RV-61301
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: RV-61301 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | RV-61301 |  | P&ID Number: | 325-01-xxx-PD-xx |  | Junction Box: | IS-JB-612
Service Description: | IN-8 |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - RV-61301_DI_1 | DI | RV-61301_DI_1 | C4/C4S2 9 | P4-TBDI2-9 | C4S2-9/P4-TBDI2-9 | P4-TBDI2-9/C4S2-9 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | RV-61301 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | RV-61301 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | RV-61301 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## RV-61304
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: RV-61304 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | RV-61304 |  | P&ID Number: | 325-01-xxx-PD-xx |  | Junction Box: | IS-JB-612
Service Description: | IN-9 |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - RV-61304_DI_1 | DI | RV-61304_DI_1 | C4/C4S2 10 | P4-TBDI2-10 | C4S2-10/P4-TBDI2-10 | P4-TBDI2-10/C4S2-10 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | RV-61304 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | RV-61304 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | RV-61304 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## RV-61305
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: RV-61305 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | RV-61305 |  | P&ID Number: | 325-01-xxx-PD-xx |  | Junction Box: | IS-JB-612
Service Description: | IN-10 |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - RV-61305_DI_1 | DI | RV-61305_DI_1 | C4/C4S2 11 | P4-TBDI2-11 | C4S2-11/P4-TBDI2-11 | P4-TBDI2-11/C4S2-11 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | RV-61305 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | RV-61305 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | RV-61305 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## SC-61301
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: SC-61301 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | SC-61301 |  | P&ID Number: | 325-01-xxx-PD-xx |  | Junction Box: | IS-JB-612
Service Description: | IN-11 |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - SC-61301_DI_1 | DI | SC-61301_DI_1 | C4/C4S2 12 | P4-TBDI2-12 | C4S2-12/P4-TBDI2-12 | P4-TBDI2-12/C4S2-12 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | SC-61301 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | SC-61301 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | SC-61301 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## SC-61302
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: SC-61302 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | SC-61302 |  | P&ID Number: | 325-01-xxx-PD-xx |  | Junction Box: | IS-JB-612
Service Description: | IN-12 |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - SC-61302_DI_1 | DI | SC-61302_DI_1 | C4/C4S2 13 | P4-TBDI2-13 | C4S2-13/P4-TBDI2-13 | P4-TBDI2-13/C4S2-13 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | SC-61302 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | SC-61302 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | SC-61302 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## ZS-61312
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: ZS-61312 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | ZS-61312 |  | P&ID Number: | 325-01-613-PD-01 |  | Junction Box: | IS-JB-612
Service Description: | Position Magnet Door |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Limit Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - ZS-61312_DI_1 | DI | ZS-61312_DI_1 | C4/C4S2 14 | P4-TBDI2-14 | C4S2-14/P4-TBDI2-14 | P4-TBDI2-14/C4S2-14 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | ZS-61312 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | ZS-61312 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | ZS-61312 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## ZS-61313
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: ZS-61313 ¦ Junction Box: IS-JB-612 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | ZS-61313 |  | P&ID Number: | 325-01-613-PD-01 |  | Junction Box: | IS-JB-612
Service Description: | Position Magnet Door |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Limit Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - ZS-61313_DI_1 | DI | ZS-61313_DI_1 | C4/C4S2 15 | P4-TBDI2-15 | C4S2-15/P4-TBDI2-15 | P4-TBDI2-15/C4S2-15 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | ZS-61313 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | ZS-61313 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | ZS-61313 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run