## 00_JB_Index
KALASIN ENGINEERING ¦ JUNCTION BOX LOOP TEST REGISTER: JB-602
Project Sprint 18K TPA Spray Dryer / Jet Cooker ¦ Location: JB-602 ¦ 1 Equipment = 1 Sheet
TOTAL EQUIPMENT |  | TOTAL ACTIVE CHANNELS |  | DIGITAL INPUT (DI) |  | DIGITAL OUTPUT (DO) |  | ANALOG IN/OUT (AI/AO)
50 Units |  | 57 Channels |  | 23 Pts |  | 3 Pts |  | 29 AI / 2 AO
Item # | Equipment Tag | Equipment Service Description | P&ID Drawing No. | Primary Signal Breakdown | Total Channels | Primary JB Terminal | PLC Rack / Slot | CAD Wiring Typical | Loop Test Status | QA/QC Sign-off & Date
1 | AT-60241 | Dust Analyzer Transmitter for Exhaust Duct (DTEX-22) | 325-01-602-PD-05 | 1x AI | 1 | P2-TBAI2-1(A/B) | C2/C2S10 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
2 | DPT-60203 | Gas Pressure Differential Transmitter for Air Filter (FICA-21) | 325-01-602-PD-03 | 1x AI | 1 | P2-TBAI2-2(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
3 | FT-60202 | Steam feed to Spray dryer | 325-01-602-PD-09 | 1x AI, 1x DI (Flow + Pulse + Pwr) | 2 | P2-TBAI2-3(A/B) | C2/C2S10 | TYP-AI-02 / FLOW | READY FOR TEST | Pending Sign-off
4 | FT-60210 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) | 325-01-602-PD-03 | 2x AI (Flow + Pulse + Pwr) | 2 | P3-TBAI1-10(A/B) | C3/C3S6 | TYP-AI-02 / FLOW | READY FOR TEST | Pending Sign-off
5 | FT-60211 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) | 325-01-602-PD-03 | 2x AI (Flow + Pulse + Pwr) | 2 | P3-TBAI1-11(A/B) | C3/C3S6 | TYP-AI-02 / FLOW | READY FOR TEST | Pending Sign-off
6 | LSH-60251 | Water Level Switch High for Fire Deluge Pipe (FWDP-22) | 325-01-602-PD-04 | 1x DI | 1 | P2-TBDI2-2 | C2/C2S2 | TYP-DI-01 / SWITCH | READY FOR TEST | Pending Sign-off
7 | PSL-60220 | Gas Pressure Switch Low for Spray Chamber (CHAM-21) | 325-01-602-PD-04 | 1x DI | 1 | P2-TBDI2-3 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
8 | PT-60210 | Gas Pressure Transmitter for Hot Air Duct (DTHA-21) | 325-01-602-PD-03 | 1x AI | 1 | P2-TBAI2-4(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
9 | PT-60215 | 15% Polypropylene Glycol Pressure Indicator Transmitter for Heat Recovery Pumping Skid (PUCF-21) | 325-01-602-PD-03 | 1x AI | 1 | P2-TBAI2-5(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
10 | PT-60216 | Gas Pressure Transmitter for Combustion Air Burner Duct (DTCB-21) | 325-01-602-PD-03 | 1x AI | 1 | P2-TBAI2-6(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
11 | PT-60240 | Gas Pressure Transmitter for Bag House Exhaust Duct (DTEX-22) | 325-01-602-PD-05 | 1x AI | 1 | P2-TBAI2-7(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
12 | PT-60241 | Gas Pressure Transmitter for Exhaust Fan (FANE-21) | 325-01-602-PD-05 | 1x AI | 1 | P2-TBAI2-8(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
13 | TSH-60230 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | 325-01-602-PD-04 | 1x DI | 1 | P2-TBDI2-4 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
14 | TSH-60240 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-5 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
15 | TSH-60241A | Surface Heating Temperature switch high for bag house cone (BGHS-21) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-6 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
16 | TSH-60242A | Surface Heating Temperature switch high for bag house cone (BGHS-21) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-7 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
17 | TSH-60243A | Surface Heating Temperature switch high for bag house cone (BGHS-21) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-8 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
18 | TSL-60241B | Surface Heating Temperature switch low for bag house cone (BGHS-21) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-9 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
19 | TSL-60242B | Surface Heating Temperature switch low for bag house cone (BGHS-21) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-10 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
20 | TSL-60243B | Surface Heating Temperature switch low for bag house cone (BGHS-21) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-11 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
21 | TT-60210 | Gas Temperature Element for Hot Air Duct (DTHA-21) | 325-01-602-PD-03 | 1x AI | 1 | P2-TBAI2-9(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
22 | TT-60210A | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | 325-01-602-PD-03 | 1x AI | 1 | P2-TBAI2-10(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
23 | TT-60210B | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | 325-01-602-PD-03 | 1x AI | 1 | P2-TBAI2-11(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
24 | TT-60211 | Gas Temperature Element for Hot Air Duct (DTHA-21) | 325-01-602-PD-03 | 1x AI | 1 | P2-TBAI2-12(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
25 | TT-60212A | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | 325-01-602-PD-03 | 1x AI | 1 | P2-TBAI2-13(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
26 | TT-60212B | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | 325-01-602-PD-03 | 1x AI | 1 | P2-TBAI2-14(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
27 | TT-60214 | Steam Temperature Transmitter for Cold Air Duct (DTCA-23) | 325-01-602-PD-03 | 1x AI | 1 | P2-TBAI2-15(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
28 | TT-60215A | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | 325-01-602-PD-03 | 1x AI | 1 | P2-TBAI2-16(A/B) | C2/C2S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
29 | TT-60215B | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | 325-01-602-PD-03 | 1x AI | 1 | P3-TBAI1-1(A/B) | C3/C3S6 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
30 | TT-60216 | Gas Temperature Transmitter for Combustion Air Burner Duct (DTCB-21) | 325-01-602-PD-03 | 1x AI | 1 | P3-TBAI1-2(A/B) | C3/C3S6 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
31 | TT-60240 | Gas Temperature Transmitter for Exhaust Fan (FANE-21) | 325-01-602-PD-05 | 1x AI | 1 | P3-TBAI1-3(A/B) | C3/C3S6 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
32 | TT-60241A | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | 325-01-602-PD-05 | 1x AI | 1 | P3-TBAI1-4(A/B) | C3/C3S6 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
33 | TT-60241B | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | 325-01-602-PD-05 | 1x AI | 1 | P3-TBAI1-5(A/B) | C3/C3S6 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
34 | TV-60202 | IOUT-1 | - | 1x AO (Solenoid + FB) | 1 | P3-TBAO1-2 | C3/C3S12 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
35 | TV-60214 | Steam Temperature Valve for Pre-Heat Steam Heat Exchanger (HXCH-21) | 325-01-602-PD-03 | 1x AO (Solenoid + FB) | 1 | P3-TBAO1-3 | C3/C3S12 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
36 | VT-60210A | Vibration Transmitter for Main Supply Air Fan (FANS-21) | 325-01-602-PD-03 | 1x AI | 1 | P3-TBAI1-6(A/B) | C3/C3S6 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
37 | VT-60210B | Vibration Transmitter for Main Supply Air Fan (FANS-21) | 325-01-602-PD-03 | 1x AI | 1 | P3-TBAI1-7(A/B) | C3/C3S6 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
38 | VT-60241A | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | 325-01-602-PD-05 | 1x AI | 1 | P3-TBAI1-8(A/B) | C3/C3S6 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
39 | VT-60241B | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | 325-01-602-PD-05 | 1x AI | 1 | P3-TBAI1-9(A/B) | C3/C3S6 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
40 | XA-60240A | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-12 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
41 | XA-60240B | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-13 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
42 | XA-60241A | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-14 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
43 | XA-60241B | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-15 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
44 | XA-60242A | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-16 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
45 | XA-60242B | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-17 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
46 | XA-60243A | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-18 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
47 | XA-60243B | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | 325-01-602-PD-05 | 1x DI | 1 | P2-TBDI2-19 | C2/C2S2 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
48 | XS-60240B | Fan Command for BGHS-21 (Bag House Air Pulsing) | 325-01-602-PD-05 | 1x DO | 1 | P2-TBRL1-17 | C2/C2S6 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
49 | XV-60214 | Steam feed to Spray dryer | 325-01-602-PD-03 | 2x DI, 1x DO (Solenoid + FB) | 3 | P2-TBDI2-20 | C2/C2S2 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
50 | XV-60241 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | 325-01-602-PD-05 | 2x DI, 1x DO (Solenoid + FB) | 3 | P2-TBDI2-22 | C2/C2S2 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off

## AT-60241
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: AT-60241 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | AT-60241 |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Dust Analyzer Transmitter for Exhaust Duct (DTEX-22) |  | Calibrated Range: | 5000 mg |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Dust Analyzer Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Gas / Dust / Quality Analyzer (4-20mA AI) [Pins A+B] | AI | AT-60241_AI_1 | C2/C2S10 Pins 2(A) & 1(B) | P2-TBAI2-1(A/B) | C2S10-2/P2-TBAI2-1(A) (+) / C2S10-1/P2-TBAI2-1(B) (-) | P2-TBAI2-1(A)/C2S10-2 (+) / P2-TBAI2-1(B)/C2S10-1 (-) | White (+ / IN-x), Black (- / i RTN-x)
PWR | Instrument Auxiliary Power Supply (24VDC / 220VAC) | PWR | AT-60241_PWR | CA1 PSU1/2 Redundant Bus | JB-602-TB24V / 0V | CA1-PSU-24V | AT-60241-V+ | Brown (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | AT-60241 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | AT-60241 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | AT-60241 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## DPT-60203
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: DPT-60203 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | DPT-60203 |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Gas Pressure Differential Transmitter for Air Filter (FICA-21) |  | Calibrated Range: | -100 to 500 mBar |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Differential Pressure Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Pressure / Diff. Pressure Transmitter (4-20mA AI) [Pins A+B] | AI | DPT-60203_AI_1 | C2/C2S10 Pins 4(A) & 3(B) | P2-TBAI2-2(A/B) | C2S10-4/P2-TBAI2-2(A) (+) / C2S10-3/P2-TBAI2-2(B) (-) | P2-TBAI2-2(A)/C2S10-4 (+) / P2-TBAI2-2(B)/C2S10-3 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | DPT-60203 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | DPT-60203 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | DPT-60203 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## FT-60202
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: FT-60202 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | FT-60202 |  | P&ID Number: | 325-01-602-PD-09 |  | Junction Box: | JB-602
Service Description: | Steam feed to Spray dryer |  | Calibrated Range: | 0 - 2000 kg/hr |  | Channel Count: | 2 Active Process Channels
Instrument Type: | Vortex Flow Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Flow Rate Measurement (4-20mA AI) [Pins A+B] | AI | FT-60202_AI_1 | C2/C2S10 Pins 6(A) & 5(B) | P2-TBAI2-3(A/B) | C2S10-6/P2-TBAI2-3(A) (+) / C2S10-5/P2-TBAI2-3(B) (-) | P2-TBAI2-3(A)/C2S10-6 (+) / P2-TBAI2-3(B)/C2S10-5 (-) | White (+ / IN-x), Black (- / i RTN-x)
CH-02 | Pulse / High-Speed Batch Counter Input (DI) | DI | FT-60202_DI_1 | C2/C2S2 1 | P2-TBDI2-1 | C2S2-1/P2-TBDI2-1 | P2-TBDI2-1/C2S2-1 | White (Sig), Grey (24VDC)
PWR | Instrument Auxiliary Power Supply (24VDC / 220VAC) | PWR | FT-60202_PWR | CA1 PSU1/2 Redundant Bus | JB-602-TB24V / 0V | CA1-PSU-24V | FT-60202-V+ | Brown (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
4.2 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | FT-60202 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | FT-60202 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | FT-60202 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## FT-60210
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: FT-60210 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | FT-60210 |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) |  | Calibrated Range: | 126000 m3/h |  | Channel Count: | 2 Active Process Channels
Instrument Type: | Thermal Mass Flow Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Flow Rate Measurement (4-20mA AI) [Pins A+B] | AI | FT-60210_AI_1 | C3/C3S6 Pins 22(A) & 21(B) | P3-TBAI1-10(A/B) | C3S6-22/P3-TBAI1-10(A) (+) / C3S6-21/P3-TBAI1-10(B) (-) | P3-TBAI1-10(A)/C3S6-22 (+) / P3-TBAI1-10(B)/C3S6-21 (-) | White (+ / IN-x), Black (- / i RTN-x)
CH-02 | Analog Density / Temperature / Mass (4-20mA AI) [Pins A+B] | AI | FT-60210_AI_2 | C3/C3S6 Pins 26(A) & 25(B) | P3-TBAI1-12(A/B) | C3S6-26/P3-TBAI1-12(A) (+) / C3S6-25/P3-TBAI1-12(B) (-) | P3-TBAI1-12(A)/C3S6-26 (+) / P3-TBAI1-12(B)/C3S6-25 (-) | White (+ / IN-x), Black (- / i RTN-x)
PWR | Instrument Auxiliary Power Supply (24VDC / 220VAC) | PWR | FT-60210_PWR | CA1 PSU1/2 Redundant Bus | JB-602-TB24V / 0V | CA1-PSU-24V | FT-60210-V+ | Brown (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | FT-60210 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | FT-60210 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | FT-60210 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## FT-60211
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: FT-60211 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | FT-60211 |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) |  | Calibrated Range: | 126000 m3/h |  | Channel Count: | 2 Active Process Channels
Instrument Type: | Thermal Mass Flow Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Flow Rate Measurement (4-20mA AI) [Pins A+B] | AI | FT-60211_AI_1 | C3/C3S6 Pins 24(A) & 23(B) | P3-TBAI1-11(A/B) | C3S6-24/P3-TBAI1-11(A) (+) / C3S6-23/P3-TBAI1-11(B) (-) | P3-TBAI1-11(A)/C3S6-24 (+) / P3-TBAI1-11(B)/C3S6-23 (-) | White (+ / IN-x), Black (- / i RTN-x)
CH-02 | Analog Density / Temperature / Mass (4-20mA AI) [Pins A+B] | AI | FT-60211_AI_2 | C3/C3S6 Pins 30(A) & 29(B) | P3-TBAI1-13(A/B) | C3S6-30/P3-TBAI1-13(A) (+) / C3S6-29/P3-TBAI1-13(B) (-) | P3-TBAI1-13(A)/C3S6-30 (+) / P3-TBAI1-13(B)/C3S6-29 (-) | White (+ / IN-x), Black (- / i RTN-x)
PWR | Instrument Auxiliary Power Supply (24VDC / 220VAC) | PWR | FT-60211_PWR | CA1 PSU1/2 Redundant Bus | JB-602-TB24V / 0V | CA1-PSU-24V | FT-60211-V+ | Brown (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | FT-60211 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | FT-60211 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | FT-60211 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## LSH-60251
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: LSH-60251 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | LSH-60251 |  | P&ID Number: | 325-01-602-PD-04 |  | Junction Box: | JB-602
Service Description: | Water Level Switch High for Fire Deluge Pipe (FWDP-22) |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Level switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Liquid / Powder Level Switch Trip Status (DI) | DI | LSH-60251_DI_1 | C2/C2S2 2 | P2-TBDI2-2 | C2S2-2/P2-TBDI2-2 | P2-TBDI2-2/C2S2-2 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | LSH-60251 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | LSH-60251 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | LSH-60251 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PSL-60220
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PSL-60220 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PSL-60220 |  | P&ID Number: | 325-01-602-PD-04 |  | Junction Box: | JB-602
Service Description: | Gas Pressure Switch Low for Spray Chamber (CHAM-21) |  | Calibrated Range: | -0.01 mbar |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Pressure switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Pressure Switch Trip Status (DI) | DI | PSL-60220_DI_1 | C2/C2S2 3 | P2-TBDI2-3 | C2S2-3/P2-TBDI2-3 | P2-TBDI2-3/C2S2-3 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PSL-60220 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PSL-60220 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PSL-60220 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PT-60210
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PT-60210 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PT-60210 |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Gas Pressure Transmitter for Hot Air Duct (DTHA-21) |  | Calibrated Range: | 0 - 0.1 mbar |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Pressure Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Pressure / Diff. Pressure Transmitter (4-20mA AI) [Pins A+B] | AI | PT-60210_AI_1 | C2/C2S10 Pins 8(A) & 7(B) | P2-TBAI2-4(A/B) | C2S10-8/P2-TBAI2-4(A) (+) / C2S10-7/P2-TBAI2-4(B) (-) | P2-TBAI2-4(A)/C2S10-8 (+) / P2-TBAI2-4(B)/C2S10-7 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PT-60210 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PT-60210 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PT-60210 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PT-60215
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PT-60215 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PT-60215 |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | 15% Polypropylene Glycol Pressure Indicator Transmitter for Heat Recovery Pumping Skid (PUCF-21) |  | Calibrated Range: | 0 - 6 bar |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Pressure Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Pressure / Diff. Pressure Transmitter (4-20mA AI) [Pins A+B] | AI | PT-60215_AI_1 | C2/C2S10 Pins 12(A) & 11(B) | P2-TBAI2-5(A/B) | C2S10-12/P2-TBAI2-5(A) (+) / C2S10-11/P2-TBAI2-5(B) (-) | P2-TBAI2-5(A)/C2S10-12 (+) / P2-TBAI2-5(B)/C2S10-11 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PT-60215 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PT-60215 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PT-60215 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PT-60216
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PT-60216 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PT-60216 |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Gas Pressure Transmitter for Combustion Air Burner Duct (DTCB-21) |  | Calibrated Range: | 0 - 100 mbar |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Pressure Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Pressure / Diff. Pressure Transmitter (4-20mA AI) [Pins A+B] | AI | PT-60216_AI_1 | C2/C2S10 Pins 14(A) & 13(B) | P2-TBAI2-6(A/B) | C2S10-14/P2-TBAI2-6(A) (+) / C2S10-13/P2-TBAI2-6(B) (-) | P2-TBAI2-6(A)/C2S10-14 (+) / P2-TBAI2-6(B)/C2S10-13 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PT-60216 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PT-60216 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PT-60216 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PT-60240
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PT-60240 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PT-60240 |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Gas Pressure Transmitter for Bag House Exhaust Duct (DTEX-22) |  | Calibrated Range: | -100 to 200 mbar |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Pressure Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Pressure / Diff. Pressure Transmitter (4-20mA AI) [Pins A+B] | AI | PT-60240_AI_1 | C2/C2S10 Pins 16(A) & 15(B) | P2-TBAI2-7(A/B) | C2S10-16/P2-TBAI2-7(A) (+) / C2S10-15/P2-TBAI2-7(B) (-) | P2-TBAI2-7(A)/C2S10-16 (+) / P2-TBAI2-7(B)/C2S10-15 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PT-60240 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PT-60240 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PT-60240 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PT-60241
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PT-60241 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PT-60241 |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Gas Pressure Transmitter for Exhaust Fan (FANE-21) |  | Calibrated Range: | 0 - 0.1 mbar |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Pressure Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Pressure / Diff. Pressure Transmitter (4-20mA AI) [Pins A+B] | AI | PT-60241_AI_1 | C2/C2S10 Pins 18(A) & 17(B) | P2-TBAI2-8(A/B) | C2S10-18/P2-TBAI2-8(A) (+) / C2S10-17/P2-TBAI2-8(B) (-) | P2-TBAI2-8(A)/C2S10-18 (+) / P2-TBAI2-8(B)/C2S10-17 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PT-60241 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PT-60241 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PT-60241 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TSH-60230
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TSH-60230 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TSH-60230 |  | P&ID Number: | 325-01-602-PD-04 |  | Junction Box: | JB-602
Service Description: | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) |  | Calibrated Range: | 0 - 140 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - TSH-60230_DI_1 | DI | TSH-60230_DI_1 | C2/C2S2 4 | P2-TBDI2-4 | C2S2-4/P2-TBDI2-4 | P2-TBDI2-4/C2S2-4 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TSH-60230 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TSH-60230 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TSH-60230 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TSH-60240
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TSH-60240 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TSH-60240 |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) |  | Calibrated Range: | 0 - 140 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - TSH-60240_DI_1 | DI | TSH-60240_DI_1 | C2/C2S2 5 | P2-TBDI2-5 | C2S2-5/P2-TBDI2-5 | P2-TBDI2-5/C2S2-5 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TSH-60240 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TSH-60240 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TSH-60240 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TSH-60241A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TSH-60241A ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TSH-60241A |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Surface Heating Temperature switch high for bag house cone (BGHS-21) |  | Calibrated Range: | 0 - 100 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - TSH-60241A_DI_1 | DI | TSH-60241A_DI_1 | C2/C2S2 6 | P2-TBDI2-6 | C2S2-6/P2-TBDI2-6 | P2-TBDI2-6/C2S2-6 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TSH-60241A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TSH-60241A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TSH-60241A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TSH-60242A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TSH-60242A ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TSH-60242A |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Surface Heating Temperature switch high for bag house cone (BGHS-21) |  | Calibrated Range: | 0 - 100 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - TSH-60242A_DI_1 | DI | TSH-60242A_DI_1 | C2/C2S2 7 | P2-TBDI2-7 | C2S2-7/P2-TBDI2-7 | P2-TBDI2-7/C2S2-7 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TSH-60242A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TSH-60242A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TSH-60242A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TSH-60243A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TSH-60243A ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TSH-60243A |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Surface Heating Temperature switch high for bag house cone (BGHS-21) |  | Calibrated Range: | 0 - 100 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - TSH-60243A_DI_1 | DI | TSH-60243A_DI_1 | C2/C2S2 8 | P2-TBDI2-8 | C2S2-8/P2-TBDI2-8 | P2-TBDI2-8/C2S2-8 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TSH-60243A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TSH-60243A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TSH-60243A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TSL-60241B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TSL-60241B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TSL-60241B |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Surface Heating Temperature switch low for bag house cone (BGHS-21) |  | Calibrated Range: | 0 - 100 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - TSL-60241B_DI_1 | DI | TSL-60241B_DI_1 | C2/C2S2 9 | P2-TBDI2-9 | C2S2-9/P2-TBDI2-9 | P2-TBDI2-9/C2S2-9 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TSL-60241B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TSL-60241B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TSL-60241B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TSL-60242B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TSL-60242B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TSL-60242B |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Surface Heating Temperature switch low for bag house cone (BGHS-21) |  | Calibrated Range: | 0 - 100 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - TSL-60242B_DI_1 | DI | TSL-60242B_DI_1 | C2/C2S2 10 | P2-TBDI2-10 | C2S2-10/P2-TBDI2-10 | P2-TBDI2-10/C2S2-10 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TSL-60242B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TSL-60242B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TSL-60242B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TSL-60243B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TSL-60243B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TSL-60243B |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Surface Heating Temperature switch low for bag house cone (BGHS-21) |  | Calibrated Range: | 0 - 100 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - TSL-60243B_DI_1 | DI | TSL-60243B_DI_1 | C2/C2S2 11 | P2-TBDI2-11 | C2S2-11/P2-TBDI2-11 | P2-TBDI2-11/C2S2-11 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TSL-60243B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TSL-60243B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TSL-60243B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TT-60210
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TT-60210 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TT-60210 |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Gas Temperature Element for Hot Air Duct (DTHA-21) |  | Calibrated Range: | 0 - 400'°C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Temperature Transmitter (4-20mA AI) [Pins A+B] | AI | TT-60210_AI_1 | C2/C2S10 Pins 20(A) & 19(B) | P2-TBAI2-9(A/B) | C2S10-20/P2-TBAI2-9(A) (+) / C2S10-19/P2-TBAI2-9(B) (-) | P2-TBAI2-9(A)/C2S10-20 (+) / P2-TBAI2-9(B)/C2S10-19 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TT-60210 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TT-60210 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TT-60210 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TT-60210A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TT-60210A ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TT-60210A |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) |  | Calibrated Range: | 0 - 100 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Temperature Transmitter (4-20mA AI) [Pins A+B] | AI | TT-60210A_AI_1 | C2/C2S10 Pins 22(A) & 21(B) | P2-TBAI2-10(A/B) | C2S10-22/P2-TBAI2-10(A) (+) / C2S10-21/P2-TBAI2-10(B) (-) | P2-TBAI2-10(A)/C2S10-22 (+) / P2-TBAI2-10(B)/C2S10-21 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TT-60210A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TT-60210A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TT-60210A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TT-60210B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TT-60210B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TT-60210B |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) |  | Calibrated Range: | 0 - 100 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Temperature Transmitter (4-20mA AI) [Pins A+B] | AI | TT-60210B_AI_1 | C2/C2S10 Pins 24(A) & 23(B) | P2-TBAI2-11(A/B) | C2S10-24/P2-TBAI2-11(A) (+) / C2S10-23/P2-TBAI2-11(B) (-) | P2-TBAI2-11(A)/C2S10-24 (+) / P2-TBAI2-11(B)/C2S10-23 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TT-60210B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TT-60210B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TT-60210B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TT-60211
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TT-60211 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TT-60211 |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Gas Temperature Element for Hot Air Duct (DTHA-21) |  | Calibrated Range: | 0 - 400'°C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Temperature Transmitter (4-20mA AI) [Pins A+B] | AI | TT-60211_AI_1 | C2/C2S10 Pins 26(A) & 25(B) | P2-TBAI2-12(A/B) | C2S10-26/P2-TBAI2-12(A) (+) / C2S10-25/P2-TBAI2-12(B) (-) | P2-TBAI2-12(A)/C2S10-26 (+) / P2-TBAI2-12(B)/C2S10-25 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TT-60211 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TT-60211 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TT-60211 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TT-60212A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TT-60212A ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TT-60212A |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) |  | Calibrated Range: | 0 - 100 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Temperature Transmitter (4-20mA AI) [Pins A+B] | AI | TT-60212A_AI_1 | C2/C2S10 Pins 30(A) & 29(B) | P2-TBAI2-13(A/B) | C2S10-30/P2-TBAI2-13(A) (+) / C2S10-29/P2-TBAI2-13(B) (-) | P2-TBAI2-13(A)/C2S10-30 (+) / P2-TBAI2-13(B)/C2S10-29 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TT-60212A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TT-60212A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TT-60212A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TT-60212B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TT-60212B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TT-60212B |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) |  | Calibrated Range: | 0 - 100 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Temperature Transmitter (4-20mA AI) [Pins A+B] | AI | TT-60212B_AI_1 | C2/C2S10 Pins 32(A) & 31(B) | P2-TBAI2-14(A/B) | C2S10-32/P2-TBAI2-14(A) (+) / C2S10-31/P2-TBAI2-14(B) (-) | P2-TBAI2-14(A)/C2S10-32 (+) / P2-TBAI2-14(B)/C2S10-31 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TT-60212B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TT-60212B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TT-60212B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TT-60214
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TT-60214 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TT-60214 |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Steam Temperature Transmitter for Cold Air Duct (DTCA-23) |  | Calibrated Range: | -10 to 250°C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Temperature Transmitter (4-20mA AI) [Pins A+B] | AI | TT-60214_AI_1 | C2/C2S10 Pins 34(A) & 33(B) | P2-TBAI2-15(A/B) | C2S10-34/P2-TBAI2-15(A) (+) / C2S10-33/P2-TBAI2-15(B) (-) | P2-TBAI2-15(A)/C2S10-34 (+) / P2-TBAI2-15(B)/C2S10-33 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TT-60214 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TT-60214 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TT-60214 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TT-60215A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TT-60215A ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TT-60215A |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) |  | Calibrated Range: | -10 to 150°C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Temperature Transmitter (4-20mA AI) [Pins A+B] | AI | TT-60215A_AI_1 | C2/C2S10 Pins 36(A) & 35(B) | P2-TBAI2-16(A/B) | C2S10-36/P2-TBAI2-16(A) (+) / C2S10-35/P2-TBAI2-16(B) (-) | P2-TBAI2-16(A)/C2S10-36 (+) / P2-TBAI2-16(B)/C2S10-35 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TT-60215A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TT-60215A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TT-60215A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TT-60215B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TT-60215B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TT-60215B |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) |  | Calibrated Range: | -10 to 150°C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Temperature Transmitter (4-20mA AI) [Pins A+B] | AI | TT-60215B_AI_1 | C3/C3S6 Pins 2(A) & 1(B) | P3-TBAI1-1(A/B) | C3S6-2/P3-TBAI1-1(A) (+) / C3S6-1/P3-TBAI1-1(B) (-) | P3-TBAI1-1(A)/C3S6-2 (+) / P3-TBAI1-1(B)/C3S6-1 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TT-60215B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TT-60215B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TT-60215B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TT-60216
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TT-60216 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TT-60216 |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Gas Temperature Transmitter for Combustion Air Burner Duct (DTCB-21) |  | Calibrated Range: | 0 - 200'°C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Temperature Transmitter (4-20mA AI) [Pins A+B] | AI | TT-60216_AI_1 | C3/C3S6 Pins 4(A) & 3(B) | P3-TBAI1-2(A/B) | C3S6-4/P3-TBAI1-2(A) (+) / C3S6-3/P3-TBAI1-2(B) (-) | P3-TBAI1-2(A)/C3S6-4 (+) / P3-TBAI1-2(B)/C3S6-3 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TT-60216 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TT-60216 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TT-60216 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TT-60240
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TT-60240 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TT-60240 |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Gas Temperature Transmitter for Exhaust Fan (FANE-21) |  | Calibrated Range: | 0 - 400'°C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Temperature Transmitter (4-20mA AI) [Pins A+B] | AI | TT-60240_AI_1 | C3/C3S6 Pins 6(A) & 5(B) | P3-TBAI1-3(A/B) | C3S6-6/P3-TBAI1-3(A) (+) / C3S6-5/P3-TBAI1-3(B) (-) | P3-TBAI1-3(A)/C3S6-6 (+) / P3-TBAI1-3(B)/C3S6-5 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TT-60240 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TT-60240 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TT-60240 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TT-60241A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TT-60241A ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TT-60241A |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) |  | Calibrated Range: | 0 - 100 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Temperature Transmitter (4-20mA AI) [Pins A+B] | AI | TT-60241A_AI_1 | C3/C3S6 Pins 8(A) & 7(B) | P3-TBAI1-4(A/B) | C3S6-8/P3-TBAI1-4(A) (+) / C3S6-7/P3-TBAI1-4(B) (-) | P3-TBAI1-4(A)/C3S6-8 (+) / P3-TBAI1-4(B)/C3S6-7 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TT-60241A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TT-60241A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TT-60241A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TT-60241B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TT-60241B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TT-60241B |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) |  | Calibrated Range: | 0 - 100 C |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Temperature Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Temperature Transmitter (4-20mA AI) [Pins A+B] | AI | TT-60241B_AI_1 | C3/C3S6 Pins 12(A) & 11(B) | P3-TBAI1-5(A/B) | C3S6-12/P3-TBAI1-5(A) (+) / C3S6-11/P3-TBAI1-5(B) (-) | P3-TBAI1-5(A)/C3S6-12 (+) / P3-TBAI1-5(B)/C3S6-11 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TT-60241B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TT-60241B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TT-60241B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TV-60202
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TV-60202 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TV-60202 |  | P&ID Number: | 325-01-xxx-PD-xx |  | Junction Box: | JB-602
Service Description: | IOUT-1 |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Output Control Setpoint (4-20mA AO) - TV-60202_AO_1 | AO | TV-60202_AO_1 | C3/C3S12 9 | P3-TBAO1-2 | C3S12-9/P3-TBAO1-2 | P3-TBAO1-2/C3S12-9 | White (+ / IOUT), Black (- / COM)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TV-60202 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TV-60202 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TV-60202 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## TV-60214
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: TV-60214 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | TV-60214 |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Steam Temperature Valve for Pre-Heat Steam Heat Exchanger (HXCH-21) |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Automatic Control valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Output Control Setpoint (4-20mA AO) - TV-60214_AO_1 | AO | TV-60214_AO_1 | C3/C3S12 13 | P3-TBAO1-3 | C3S12-13/P3-TBAO1-3 | P3-TBAO1-3/C3S12-13 | White (+ / IOUT), Black (- / COM)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | TV-60214 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | TV-60214 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | TV-60214 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## VT-60210A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: VT-60210A ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | VT-60210A |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Vibration Transmitter for Main Supply Air Fan (FANS-21) |  | Calibrated Range: | mm/sec |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Vibration Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Input Process Variable (4-20mA AI) - VT-60210A_AI_1 [Pins A+B] | AI | VT-60210A_AI_1 | C3/C3S6 Pins 14(A) & 13(B) | P3-TBAI1-6(A/B) | C3S6-14/P3-TBAI1-6(A) (+) / C3S6-13/P3-TBAI1-6(B) (-) | P3-TBAI1-6(A)/C3S6-14 (+) / P3-TBAI1-6(B)/C3S6-13 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | VT-60210A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | VT-60210A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | VT-60210A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## VT-60210B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: VT-60210B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | VT-60210B |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Vibration Transmitter for Main Supply Air Fan (FANS-21) |  | Calibrated Range: | mm/sec |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Vibration Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Input Process Variable (4-20mA AI) - VT-60210B_AI_1 [Pins A+B] | AI | VT-60210B_AI_1 | C3/C3S6 Pins 16(A) & 15(B) | P3-TBAI1-7(A/B) | C3S6-16/P3-TBAI1-7(A) (+) / C3S6-15/P3-TBAI1-7(B) (-) | P3-TBAI1-7(A)/C3S6-16 (+) / P3-TBAI1-7(B)/C3S6-15 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | VT-60210B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | VT-60210B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | VT-60210B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## VT-60241A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: VT-60241A ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | VT-60241A |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) |  | Calibrated Range: | mm/sec |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Vibration Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Input Process Variable (4-20mA AI) - VT-60241A_AI_1 [Pins A+B] | AI | VT-60241A_AI_1 | C3/C3S6 Pins 18(A) & 17(B) | P3-TBAI1-8(A/B) | C3S6-18/P3-TBAI1-8(A) (+) / C3S6-17/P3-TBAI1-8(B) (-) | P3-TBAI1-8(A)/C3S6-18 (+) / P3-TBAI1-8(B)/C3S6-17 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | VT-60241A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | VT-60241A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | VT-60241A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## VT-60241B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: VT-60241B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | VT-60241B |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) |  | Calibrated Range: | mm/sec |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Vibration Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Input Process Variable (4-20mA AI) - VT-60241B_AI_1 [Pins A+B] | AI | VT-60241B_AI_1 | C3/C3S6 Pins 20(A) & 19(B) | P3-TBAI1-9(A/B) | C3S6-20/P3-TBAI1-9(A) (+) / C3S6-19/P3-TBAI1-9(B) (-) | P3-TBAI1-9(A)/C3S6-20 (+) / P3-TBAI1-9(B)/C3S6-19 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | VT-60241B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | VT-60241B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | VT-60241B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-60240A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-60240A ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-60240A |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-60240A_DI_1 | DI | XA-60240A_DI_1 | C2/C2S2 12 | P2-TBDI2-12 | C2S2-12/P2-TBDI2-12 | P2-TBDI2-12/C2S2-12 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-60240A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-60240A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-60240A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-60240B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-60240B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-60240B |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-60240B_DI_1 | DI | XA-60240B_DI_1 | C2/C2S2 13 | P2-TBDI2-13 | C2S2-13/P2-TBDI2-13 | P2-TBDI2-13/C2S2-13 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-60240B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-60240B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-60240B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-60241A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-60241A ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-60241A |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-60241A_DI_1 | DI | XA-60241A_DI_1 | C2/C2S2 14 | P2-TBDI2-14 | C2S2-14/P2-TBDI2-14 | P2-TBDI2-14/C2S2-14 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-60241A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-60241A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-60241A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-60241B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-60241B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-60241B |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-60241B_DI_1 | DI | XA-60241B_DI_1 | C2/C2S2 15 | P2-TBDI2-15 | C2S2-15/P2-TBDI2-15 | P2-TBDI2-15/C2S2-15 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-60241B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-60241B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-60241B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-60242A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-60242A ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-60242A |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-60242A_DI_1 | DI | XA-60242A_DI_1 | C2/C2S2 16 | P2-TBDI2-16 | C2S2-16/P2-TBDI2-16 | P2-TBDI2-16/C2S2-16 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-60242A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-60242A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-60242A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-60242B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-60242B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-60242B |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-60242B_DI_1 | DI | XA-60242B_DI_1 | C2/C2S2 19 | P2-TBDI2-17 | C2S2-19/P2-TBDI2-17 | P2-TBDI2-17/C2S2-19 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-60242B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-60242B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-60242B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-60243A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-60243A ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-60243A |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-60243A_DI_1 | DI | XA-60243A_DI_1 | C2/C2S2 20 | P2-TBDI2-18 | C2S2-20/P2-TBDI2-18 | P2-TBDI2-18/C2S2-20 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-60243A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-60243A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-60243A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-60243B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-60243B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-60243B |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-60243B_DI_1 | DI | XA-60243B_DI_1 | C2/C2S2 21 | P2-TBDI2-19 | C2S2-21/P2-TBDI2-19 | P2-TBDI2-19/C2S2-21 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-60243B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-60243B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-60243B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XS-60240B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XS-60240B ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XS-60240B |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Fan Command for BGHS-21 (Bag House Air Pulsing) |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Output Command (24VDC DO) - XS-60240B_DO_1 | DO | XS-60240B_DO_1 | C2/C2S6 19 | P2-TBRL1-17 | C2S6-19/P2-TBRL1-17 | P2-TBRL1-17/C2S6-19 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XS-60240B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XS-60240B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XS-60240B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-60214
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-60214 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-60214 |  | P&ID Number: | 325-01-602-PD-03 |  | Junction Box: | JB-602
Service Description: | Steam feed to Spray dryer |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-60214_DI_1 | C2/C2S2 22 | P2-TBDI2-20 | C2S2-22/P2-TBDI2-20 | P2-TBDI2-20/C2S2-22 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-60214_DI_2 | C2/C2S2 23 | P2-TBDI2-21 | C2S2-23/P2-TBDI2-21 | P2-TBDI2-21/C2S2-23 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-60214_DO_1 | C2/C2S6 20 | P2-TBRL1-18 | C2S6-20/P2-TBRL1-18 | P2-TBRL1-18/C2S6-20 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-60214 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-60214 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-60214 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-60241
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-60241 ¦ Junction Box: JB-602 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-60241 |  | P&ID Number: | 325-01-602-PD-05 |  | Junction Box: | JB-602
Service Description: | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | On/Off Valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-60241_DI_1 | C2/C2S2 24 | P2-TBDI2-22 | C2S2-24/P2-TBDI2-22 | P2-TBDI2-22/C2S2-24 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-60241_DI_2 | C2/C2S2 25 | P2-TBDI2-23 | C2S2-25/P2-TBDI2-23 | P2-TBDI2-23/C2S2-25 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-60241_DO_1 | C2/C2S6 21 | P2-TBRL1-19 | C2S6-21/P2-TBRL1-19 | P2-TBRL1-19/C2S6-21 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-60241 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-60241 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-60241 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run