## 00_JB_Index
KALASIN ENGINEERING ¦ JUNCTION BOX LOOP TEST REGISTER: RIO-200
Project Sprint 18K TPA Spray Dryer / Jet Cooker ¦ Location: RIO-200 ¦ 1 Equipment = 1 Sheet
TOTAL EQUIPMENT |  | TOTAL ACTIVE CHANNELS |  | DIGITAL INPUT (DI) |  | DIGITAL OUTPUT (DO) |  | ANALOG IN/OUT (AI/AO)
38 Units |  | 57 Channels |  | 40 Pts |  | 8 Pts |  | 9 AI / 0 AO
Item # | Equipment Tag | Equipment Service Description | P&ID Drawing No. | Primary Signal Breakdown | Total Channels | Primary JB Terminal | PLC Rack / Slot | CAD Wiring Typical | Loop Test Status | QA/QC Sign-off & Date
1 | EXT-BIILER | 2-Wire 4-20mA (A: IN-0 / B: i RTN-0) | - | 1x AI | 1 | P5-TBAI1-1(A/B) | C5/C5S4 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
2 | FS-20201 | IN-0 | - | 1x DI | 1 | P5-TBDI1-1 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
3 | FT-913201 | Flow outlet LPG line | 325-01-913-PD-02 | 2x AI, 1x DI (Flow + Pulse + Pwr) | 3 | P5-TBAI1-2(A/B) | C5/C5S4 | TYP-AI-02 / FLOW | READY FOR TEST | Pending Sign-off
4 | FT-936201 | Process Water | 325-01-930-PD-01 | 1x AI, 1x DI (Flow + Pulse + Pwr) | 2 | P5-TBAI1-4(A/B) | C5/C5S4 | TYP-AI-02 / FLOW | READY FOR TEST | Pending Sign-off
5 | FT-936202 | Process Water | 325-01-930-PD-02 | 1x AI, 1x DI (Flow + Pulse + Pwr) | 2 | P5-TBAI1-5(A/B) | C5/C5S4 | TYP-AI-02 / FLOW | READY FOR TEST | Pending Sign-off
6 | HV-20204 | Slurry Drain line | 325-01-202-PD-01 | 1x DI (Solenoid + FB) | 1 | P5-TBDI1-8 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
7 | HV-20205 | Slurry Drain line | 325-01-202-PD-01 | 1x DI (Solenoid + FB) | 1 | P5-TBDI1-9 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
8 | HV-20206 | Slurry Drain line | 325-01-202-PD-01 | 1x DI (Solenoid + FB) | 1 | P5-TBDI1-10 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
9 | HV-20207 | Slurry Drain line | 325-01-202-PD-01 | 1x DI (Solenoid + FB) | 1 | P5-TBDI1-11 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
10 | HV-20208 | Slurry Drain line | 325-01-202-PD-02 | 1x DI (Solenoid + FB) | 1 | P5-TBDI1-12 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
11 | HV-20209 | Slurry Drain line | 325-01-202-PD-02 | 1x DI (Solenoid + FB) | 1 | P5-TBDI1-13 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
12 | HV-20210 | Slurry Drain line | 325-01-202-PD-02 | 1x DI (Solenoid + FB) | 1 | P5-TBDI1-14 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
13 | LSL-814201 | Low Level alarm | 325-01-814-PD-01 | 1x DI | 1 | P5-TBDI1-5 | C5/C5S1 | TYP-DI-01 / SWITCH | READY FOR TEST | Pending Sign-off
14 | LT-913201 | Level LPG in storage | 325-01-913-PD-01 | 1x AI | 1 | P5-TBAI1-6(A/B) | C5/C5S4 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
15 | PK-913201 | IN-5 | - | 1x DI | 1 | P5-TBDI1-6 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
16 | PK-913202 | IN-6 | - | 1x DI | 1 | P5-TBDI1-7 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
17 | PT-913201 | Pressure outlet LPG line | 325-01-913-PD-02 | 1x AI | 1 | P5-TBAI1-7(A/B) | C5/C5S4 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
18 | XA-80305A | Gas Vaporizer 4 Run Status | 325-01-913-PD-02 | 1x DI | 1 | P5-TBDI1-15 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
19 | XA-80305B | Gas Vaporizer 4 Alarm status | 325-01-913-PD-02 | 1x DI | 1 | P5-TBDI1-16 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
20 | XA-80305C | Gas Vaporizer 4 High Temp Shut-Down status | 325-01-913-PD-02 | 1x DI | 1 | P5-TBDI1-17 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
21 | XA-80305D | Gas Vaporizer 4 Working Temp Shun-Off status | 325-01-913-PD-02 | 1x DI | 1 | P5-TBDI1-18 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
22 | XA-80305E | Gas Vaporizer 4 Low Water Shun-Off status | 325-01-913-PD-02 | 1x DI | 1 | P5-TBDI1-19 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
23 | XA-80305F | IN-19 | - | 1x DI | 1 | P5-TBDI1-20 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
24 | XA-80306A | Gas Vaporizer 5 Run Status | 325-01-913-PD-02 | 1x DI | 1 | P5-TBDI1-21 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
25 | XA-80306B | Gas Vaporizer 5 Alarm status | 325-01-913-PD-02 | 1x DI | 1 | P5-TBDI1-22 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
26 | XA-80306C | Gas Vaporizer 5 High Temp Shut-Down status | 325-01-913-PD-02 | 1x DI | 1 | P5-TBDI1-23 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
27 | XA-80306D | Gas Vaporizer 5 Working Temp Shun-Off status | 325-01-913-PD-02 | 1x DI | 1 | P5-TBDI1-24 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
28 | XA-80306E | Gas Vaporizer 5 Low Water Shun-Off status | 325-01-913-PD-02 | 1x DI | 1 | P5-TBDI1-25 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
29 | XA-80306F | IN-25 | - | 1x DI | 1 | P5-TBDI1-26 | C5/C5S1 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
30 | XA-92201 | LEL gas Buzzer Alarm | 325-01-923-PD-03 | 1x DO | 1 | P5-TBRL1-1 | C5/C5S3 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
31 | XT-92201 | LEL gas analyzer | 325-01-923-PD-03 | 1x AI | 1 | P5-TBAI1-8(A/B) | C5/C5S4 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
32 | XV-20201 | Slurry Preparation Tank 1 | 325-01-202-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P5-TBDI1-27 | C5/C5S1 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
33 | XV-20202 | Slurry Preparation Tank 1 | 325-01-202-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P5-TBDI1-29 | C5/C5S1 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
34 | XV-20203 | Slurry Preparation Tank 1 | 325-01-202-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P5-TBDI1-31 | C5/C5S1 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
35 | XV-20211 | Slurry Preparation Tank 2 | 325-01-202-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P5-TBDI2-1 | C5/C5S2 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
36 | XV-20212 | Slurry Preparation Tank 2 | 325-01-202-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P5-TBDI2-3 | C5/C5S2 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
37 | XV-20213 | Slurry Preparation Tank 2 | 325-01-202-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P5-TBDI2-5 | C5/C5S2 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
38 | XV-913201 | Outlet LPG line | 325-01-913-PD-02 | 1x AI, 2x DI, 1x DO (Solenoid + FB) | 4 | P5-TBAI1-9(A/B) | C5/C5S4 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off

## EXT-BIILER
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: EXT-BIILER ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | EXT-BIILER |  | P&ID Number: | 325-01-xxx-PD-xx |  | Junction Box: | RIO-200
Service Description: | 2-Wire 4-20mA (A: IN-0 / B: i RTN-0) |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Input Process Variable (4-20mA AI) - EXT-BIILER_AI_1 [Pins A+B] | AI | EXT-BIILER_AI_1 | C5/C5S4 Pins 2(A) & 1(B) | P5-TBAI1-1(A/B) | C5S4-2/P5-TBAI1-1(A) (+) / C5S4-1/P5-TBAI1-1(B) (-) | P5-TBAI1-1(A)/C5S4-2 (+) / P5-TBAI1-1(B)/C5S4-1 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | EXT-BIILER SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | EXT-BIILER WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | EXT-BIILER ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## FS-20201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: FS-20201 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | FS-20201 |  | P&ID Number: | 325-01-xxx-PD-xx |  | Junction Box: | RIO-200
Service Description: | IN-0 |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Flow Switch Alarm Status (DI) | DI | FS-20201_DI_1 | C5/C5S1 1 | P5-TBDI1-1 | C5S1-1/P5-TBDI1-1 | P5-TBDI1-1/C5S1-1 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | FS-20201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | FS-20201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | FS-20201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## FT-913201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: FT-913201 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | FT-913201 |  | P&ID Number: | 325-01-913-PD-02 |  | Junction Box: | RIO-200
Service Description: | Flow outlet LPG line |  | Calibrated Range: | 0-1000kg/hr |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Coriolis Flow Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Flow Rate Measurement (4-20mA AI) [Pins A+B] | AI | FT-913201_AI_1 | C5/C5S4 Pins 4(A) & 3(B) | P5-TBAI1-2(A/B) | C5S4-4/P5-TBAI1-2(A) (+) / C5S4-3/P5-TBAI1-2(B) (-) | P5-TBAI1-2(A)/C5S4-4 (+) / P5-TBAI1-2(B)/C5S4-3 (-) | White (+ / IN-x), Black (- / i RTN-x)
CH-02 | Analog Density / Temperature / Mass (4-20mA AI) [Pins A+B] | AI | FT-913201_AI_2 | C5/C5S4 Pins 6(A) & 5(B) | P5-TBAI1-3(A/B) | C5S4-6/P5-TBAI1-3(A) (+) / C5S4-5/P5-TBAI1-3(B) (-) | P5-TBAI1-3(A)/C5S4-6 (+) / P5-TBAI1-3(B)/C5S4-5 (-) | White (+ / IN-x), Black (- / i RTN-x)
CH-03 | Pulse / High-Speed Batch Counter Input (DI) | DI | FT-913201_DI_1 | C5/C5S1 2 | P5-TBDI1-2 | C5S1-2/P5-TBDI1-2 | P5-TBDI1-2/C5S1-2 | White (Sig), Grey (24VDC)
PWR | Instrument Auxiliary Power Supply (24VDC / 220VAC) | PWR | FT-913201_PWR | CA1 PSU1/2 Redundant Bus | RIO-200-TB24V / 0V | CA1-PSU-24V | FT-913201-V+ | Brown (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
4.2 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | FT-913201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | FT-913201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | FT-913201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## FT-936201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: FT-936201 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | FT-936201 |  | P&ID Number: | 325-01-930-PD-01 |  | Junction Box: | RIO-200
Service Description: | Process Water |  | Calibrated Range: | 0-1000kg/m³ |  | Channel Count: | 2 Active Process Channels
Instrument Type: | Magnetic Flow Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Flow Rate Measurement (4-20mA AI) [Pins A+B] | AI | FT-936201_AI_1 | C5/C5S4 Pins 8(A) & 7(B) | P5-TBAI1-4(A/B) | C5S4-8/P5-TBAI1-4(A) (+) / C5S4-7/P5-TBAI1-4(B) (-) | P5-TBAI1-4(A)/C5S4-8 (+) / P5-TBAI1-4(B)/C5S4-7 (-) | White (+ / IN-x), Black (- / i RTN-x)
CH-02 | Pulse / High-Speed Batch Counter Input (DI) | DI | FT-936201_DI_1 | C5/C5S1 3 | P5-TBDI1-3 | C5S1-3/P5-TBDI1-3 | P5-TBDI1-3/C5S1-3 | White (Sig), Grey (24VDC)
PWR | Instrument Auxiliary Power Supply (24VDC / 220VAC) | PWR | FT-936201_PWR | CA1 PSU1/2 Redundant Bus | RIO-200-TB24V / 0V | CA1-PSU-24V | FT-936201-V+ | Brown (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
4.2 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | FT-936201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | FT-936201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | FT-936201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## FT-936202
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: FT-936202 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | FT-936202 |  | P&ID Number: | 325-01-930-PD-02 |  | Junction Box: | RIO-200
Service Description: | Process Water |  | Calibrated Range: | 0 - 20 m3/ hr |  | Channel Count: | 2 Active Process Channels
Instrument Type: | Magnetic Flow Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Flow Rate Measurement (4-20mA AI) [Pins A+B] | AI | FT-936202_AI_1 | C5/C5S4 Pins 12(A) & 11(B) | P5-TBAI1-5(A/B) | C5S4-12/P5-TBAI1-5(A) (+) / C5S4-11/P5-TBAI1-5(B) (-) | P5-TBAI1-5(A)/C5S4-12 (+) / P5-TBAI1-5(B)/C5S4-11 (-) | White (+ / IN-x), Black (- / i RTN-x)
CH-02 | Pulse / High-Speed Batch Counter Input (DI) | DI | FT-936202_DI_1 | C5/C5S1 4 | P5-TBDI1-4 | C5S1-4/P5-TBDI1-4 | P5-TBDI1-4/C5S1-4 | White (Sig), Grey (24VDC)
PWR | Instrument Auxiliary Power Supply (24VDC / 220VAC) | PWR | FT-936202_PWR | CA1 PSU1/2 Redundant Bus | RIO-200-TB24V / 0V | CA1-PSU-24V | FT-936202-V+ | Brown (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
4.2 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | FT-936202 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | FT-936202 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | FT-936202 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## HV-20204
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: HV-20204 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | HV-20204 |  | P&ID Number: | 325-01-202-PD-01 |  | Junction Box: | RIO-200
Service Description: | Slurry Drain line |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Valve With Position Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | HV-20204_DI_1 | C5/C5S1 8 | P5-TBDI1-8 | C5S1-8/P5-TBDI1-8 | P5-TBDI1-8/C5S1-8 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | HV-20204 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | HV-20204 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | HV-20204 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## HV-20205
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: HV-20205 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | HV-20205 |  | P&ID Number: | 325-01-202-PD-01 |  | Junction Box: | RIO-200
Service Description: | Slurry Drain line |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Valve With Position Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | HV-20205_DI_1 | C5/C5S1 9 | P5-TBDI1-9 | C5S1-9/P5-TBDI1-9 | P5-TBDI1-9/C5S1-9 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | HV-20205 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | HV-20205 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | HV-20205 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## HV-20206
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: HV-20206 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | HV-20206 |  | P&ID Number: | 325-01-202-PD-01 |  | Junction Box: | RIO-200
Service Description: | Slurry Drain line |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Valve With Position Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | HV-20206_DI_1 | C5/C5S1 10 | P5-TBDI1-10 | C5S1-10/P5-TBDI1-10 | P5-TBDI1-10/C5S1-10 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | HV-20206 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | HV-20206 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | HV-20206 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## HV-20207
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: HV-20207 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | HV-20207 |  | P&ID Number: | 325-01-202-PD-01 |  | Junction Box: | RIO-200
Service Description: | Slurry Drain line |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Valve With Position Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | HV-20207_DI_1 | C5/C5S1 11 | P5-TBDI1-11 | C5S1-11/P5-TBDI1-11 | P5-TBDI1-11/C5S1-11 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | HV-20207 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | HV-20207 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | HV-20207 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## HV-20208
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: HV-20208 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | HV-20208 |  | P&ID Number: | 325-01-202-PD-02 |  | Junction Box: | RIO-200
Service Description: | Slurry Drain line |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Valve With Position Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | HV-20208_DI_1 | C5/C5S1 12 | P5-TBDI1-12 | C5S1-12/P5-TBDI1-12 | P5-TBDI1-12/C5S1-12 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | HV-20208 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | HV-20208 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | HV-20208 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## HV-20209
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: HV-20209 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | HV-20209 |  | P&ID Number: | 325-01-202-PD-02 |  | Junction Box: | RIO-200
Service Description: | Slurry Drain line |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Valve With Position Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | HV-20209_DI_1 | C5/C5S1 13 | P5-TBDI1-13 | C5S1-13/P5-TBDI1-13 | P5-TBDI1-13/C5S1-13 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | HV-20209 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | HV-20209 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | HV-20209 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## HV-20210
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: HV-20210 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | HV-20210 |  | P&ID Number: | 325-01-202-PD-02 |  | Junction Box: | RIO-200
Service Description: | Slurry Drain line |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Valve With Position Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | HV-20210_DI_1 | C5/C5S1 14 | P5-TBDI1-14 | C5S1-14/P5-TBDI1-14 | P5-TBDI1-14/C5S1-14 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | HV-20210 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | HV-20210 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | HV-20210 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## LSL-814201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: LSL-814201 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | LSL-814201 |  | P&ID Number: | 325-01-814-PD-01 |  | Junction Box: | RIO-200
Service Description: | Low Level alarm |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Liquid / Powder Level Switch Trip Status (DI) | DI | LSL-814201_DI_1 | C5/C5S1 5 | P5-TBDI1-5 | C5S1-5/P5-TBDI1-5 | P5-TBDI1-5/C5S1-5 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | LSL-814201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | LSL-814201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | LSL-814201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## LT-913201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: LT-913201 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | LT-913201 |  | P&ID Number: | 325-01-913-PD-01 |  | Junction Box: | RIO-200
Service Description: | Level LPG in storage |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Level transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Level Transmitter (4-20mA AI) [Pins A+B] | AI | LT-913201_AI_1 | C5/C5S4 Pins 14(A) & 13(B) | P5-TBAI1-6(A/B) | C5S4-14/P5-TBAI1-6(A) (+) / C5S4-13/P5-TBAI1-6(B) (-) | P5-TBAI1-6(A)/C5S4-14 (+) / P5-TBAI1-6(B)/C5S4-13 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | LT-913201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | LT-913201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | LT-913201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PK-913201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PK-913201 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PK-913201 |  | P&ID Number: | 325-01-xxx-PD-xx |  | Junction Box: | RIO-200
Service Description: | IN-5 |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - PK-913201_DI_1 | DI | PK-913201_DI_1 | C5/C5S1 6 | P5-TBDI1-6 | C5S1-6/P5-TBDI1-6 | P5-TBDI1-6/C5S1-6 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PK-913201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PK-913201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PK-913201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PK-913202
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PK-913202 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PK-913202 |  | P&ID Number: | 325-01-xxx-PD-xx |  | Junction Box: | RIO-200
Service Description: | IN-6 |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - PK-913202_DI_1 | DI | PK-913202_DI_1 | C5/C5S1 7 | P5-TBDI1-7 | C5S1-7/P5-TBDI1-7 | P5-TBDI1-7/C5S1-7 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PK-913202 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PK-913202 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PK-913202 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PT-913201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PT-913201 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PT-913201 |  | P&ID Number: | 325-01-913-PD-02 |  | Junction Box: | RIO-200
Service Description: | Pressure outlet LPG line |  | Calibrated Range: | 0 - 10 barg |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Pressure Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Pressure / Diff. Pressure Transmitter (4-20mA AI) [Pins A+B] | AI | PT-913201_AI_1 | C5/C5S4 Pins 16(A) & 15(B) | P5-TBAI1-7(A/B) | C5S4-16/P5-TBAI1-7(A) (+) / C5S4-15/P5-TBAI1-7(B) (-) | P5-TBAI1-7(A)/C5S4-16 (+) / P5-TBAI1-7(B)/C5S4-15 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PT-913201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PT-913201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PT-913201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-80305A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-80305A ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-80305A |  | P&ID Number: | 325-01-913-PD-02 |  | Junction Box: | RIO-200
Service Description: | Gas Vaporizer 4 Run Status |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Gas vaporizer Ready |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-80305A_DI_1 | DI | XA-80305A_DI_1 | C5/C5S1 15 | P5-TBDI1-15 | C5S1-15/P5-TBDI1-15 | P5-TBDI1-15/C5S1-15 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-80305A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-80305A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-80305A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-80305B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-80305B ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-80305B |  | P&ID Number: | 325-01-913-PD-02 |  | Junction Box: | RIO-200
Service Description: | Gas Vaporizer 4 Alarm status |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Gas vaporizer Run |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-80305B_DI_1 | DI | XA-80305B_DI_1 | C5/C5S1 16 | P5-TBDI1-16 | C5S1-16/P5-TBDI1-16 | P5-TBDI1-16/C5S1-16 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-80305B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-80305B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-80305B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-80305C
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-80305C ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-80305C |  | P&ID Number: | 325-01-913-PD-02 |  | Junction Box: | RIO-200
Service Description: | Gas Vaporizer 4 High Temp Shut-Down status |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Gas vaporizer Failed |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-80305C_DI_1 | DI | XA-80305C_DI_1 | C5/C5S1 19 | P5-TBDI1-17 | C5S1-19/P5-TBDI1-17 | P5-TBDI1-17/C5S1-19 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-80305C SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-80305C WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-80305C ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-80305D
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-80305D ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-80305D |  | P&ID Number: | 325-01-913-PD-02 |  | Junction Box: | RIO-200
Service Description: | Gas Vaporizer 4 Working Temp Shun-Off status |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Gas vaporizer Overheated |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-80305D_DI_1 | DI | XA-80305D_DI_1 | C5/C5S1 20 | P5-TBDI1-18 | C5S1-20/P5-TBDI1-18 | P5-TBDI1-18/C5S1-20 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-80305D SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-80305D WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-80305D ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-80305E
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-80305E ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-80305E |  | P&ID Number: | 325-01-913-PD-02 |  | Junction Box: | RIO-200
Service Description: | Gas Vaporizer 4 Low Water Shun-Off status |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Gas vaporizer Excessive flow tripped |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-80305E_DI_1 | DI | XA-80305E_DI_1 | C5/C5S1 21 | P5-TBDI1-19 | C5S1-21/P5-TBDI1-19 | P5-TBDI1-19/C5S1-21 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-80305E SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-80305E WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-80305E ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-80305F
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-80305F ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-80305F |  | P&ID Number: | 325-01-xxx-PD-xx |  | Junction Box: | RIO-200
Service Description: | IN-19 |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-80305F_DI_1 | DI | XA-80305F_DI_1 | C5/C5S1 22 | P5-TBDI1-20 | C5S1-22/P5-TBDI1-20 | P5-TBDI1-20/C5S1-22 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-80305F SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-80305F WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-80305F ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-80306A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-80306A ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-80306A |  | P&ID Number: | 325-01-913-PD-02 |  | Junction Box: | RIO-200
Service Description: | Gas Vaporizer 5 Run Status |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Gas vaporizer Ready |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-80306A_DI_1 | DI | XA-80306A_DI_1 | C5/C5S1 23 | P5-TBDI1-21 | C5S1-23/P5-TBDI1-21 | P5-TBDI1-21/C5S1-23 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-80306A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-80306A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-80306A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-80306B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-80306B ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-80306B |  | P&ID Number: | 325-01-913-PD-02 |  | Junction Box: | RIO-200
Service Description: | Gas Vaporizer 5 Alarm status |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Gas vaporizer Run |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-80306B_DI_1 | DI | XA-80306B_DI_1 | C5/C5S1 24 | P5-TBDI1-22 | C5S1-24/P5-TBDI1-22 | P5-TBDI1-22/C5S1-24 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-80306B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-80306B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-80306B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-80306C
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-80306C ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-80306C |  | P&ID Number: | 325-01-913-PD-02 |  | Junction Box: | RIO-200
Service Description: | Gas Vaporizer 5 High Temp Shut-Down status |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Gas vaporizer Failed |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-80306C_DI_1 | DI | XA-80306C_DI_1 | C5/C5S1 25 | P5-TBDI1-23 | C5S1-25/P5-TBDI1-23 | P5-TBDI1-23/C5S1-25 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-80306C SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-80306C WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-80306C ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-80306D
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-80306D ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-80306D |  | P&ID Number: | 325-01-913-PD-02 |  | Junction Box: | RIO-200
Service Description: | Gas Vaporizer 5 Working Temp Shun-Off status |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Gas vaporizer Overheated |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-80306D_DI_1 | DI | XA-80306D_DI_1 | C5/C5S1 26 | P5-TBDI1-24 | C5S1-26/P5-TBDI1-24 | P5-TBDI1-24/C5S1-26 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-80306D SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-80306D WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-80306D ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-80306E
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-80306E ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-80306E |  | P&ID Number: | 325-01-913-PD-02 |  | Junction Box: | RIO-200
Service Description: | Gas Vaporizer 5 Low Water Shun-Off status |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Gas vaporizer Excessive flow tripped |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-80306E_DI_1 | DI | XA-80306E_DI_1 | C5/C5S1 27 | P5-TBDI1-25 | C5S1-27/P5-TBDI1-25 | P5-TBDI1-25/C5S1-27 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-80306E SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-80306E WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-80306E ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-80306F
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-80306F ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-80306F |  | P&ID Number: | 325-01-xxx-PD-xx |  | Junction Box: | RIO-200
Service Description: | IN-25 |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Field Process Equipment |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Input Status Contact (24VDC DI) - XA-80306F_DI_1 | DI | XA-80306F_DI_1 | C5/C5S1 28 | P5-TBDI1-26 | C5S1-28/P5-TBDI1-26 | P5-TBDI1-26/C5S1-28 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-80306F SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-80306F WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-80306F ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XA-92201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XA-92201 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XA-92201 |  | P&ID Number: | 325-01-923-PD-03 |  | Junction Box: | RIO-200
Service Description: | LEL gas Buzzer Alarm |  | Calibrated Range: | 0-10%LEL |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Gas detector |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Discrete Output Command (24VDC DO) - XA-92201_DO_1 | DO | XA-92201_DO_1 | C5/C5S3 1 | P5-TBRL1-1 | C5S3-1/P5-TBRL1-1 | P5-TBRL1-1/C5S3-1 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XA-92201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XA-92201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XA-92201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XT-92201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XT-92201 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XT-92201 |  | P&ID Number: | 325-01-923-PD-03 |  | Junction Box: | RIO-200
Service Description: | LEL gas analyzer |  | Calibrated Range: | 0-10%LEL |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Gas detector |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Input Process Variable (4-20mA AI) - XT-92201_AI_1 [Pins A+B] | AI | XT-92201_AI_1 | C5/C5S4 Pins 18(A) & 17(B) | P5-TBAI1-8(A/B) | C5S4-18/P5-TBAI1-8(A) (+) / C5S4-17/P5-TBAI1-8(B) (-) | P5-TBAI1-8(A)/C5S4-18 (+) / P5-TBAI1-8(B)/C5S4-17 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XT-92201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XT-92201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XT-92201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-20201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-20201 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-20201 |  | P&ID Number: | 325-01-202-PD-01 |  | Junction Box: | RIO-200
Service Description: | Slurry Preparation Tank 1 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-20201_DI_1 | C5/C5S1 29 | P5-TBDI1-27 | C5S1-29/P5-TBDI1-27 | P5-TBDI1-27/C5S1-29 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-20201_DI_2 | C5/C5S1 30 | P5-TBDI1-28 | C5S1-30/P5-TBDI1-28 | P5-TBDI1-28/C5S1-30 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-20201_DO_1 | C5/C5S3 2 | P5-TBRL1-2 | C5S3-2/P5-TBRL1-2 | P5-TBRL1-2/C5S3-2 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-20201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-20201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-20201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-20202
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-20202 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-20202 |  | P&ID Number: | 325-01-202-PD-01 |  | Junction Box: | RIO-200
Service Description: | Slurry Preparation Tank 1 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-20202_DI_1 | C5/C5S1 31 | P5-TBDI1-29 | C5S1-31/P5-TBDI1-29 | P5-TBDI1-29/C5S1-31 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-20202_DI_2 | C5/C5S1 32 | P5-TBDI1-30 | C5S1-32/P5-TBDI1-30 | P5-TBDI1-30/C5S1-32 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-20202_DO_1 | C5/C5S3 3 | P5-TBRL1-3 | C5S3-3/P5-TBRL1-3 | P5-TBRL1-3/C5S3-3 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-20202 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-20202 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-20202 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-20203
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-20203 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-20203 |  | P&ID Number: | 325-01-202-PD-01 |  | Junction Box: | RIO-200
Service Description: | Slurry Preparation Tank 1 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-20203_DI_1 | C5/C5S1 33 | P5-TBDI1-31 | C5S1-33/P5-TBDI1-31 | P5-TBDI1-31/C5S1-33 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-20203_DI_2 | C5/C5S1 34 | P5-TBDI1-32 | C5S1-34/P5-TBDI1-32 | P5-TBDI1-32/C5S1-34 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-20203_DO_1 | C5/C5S3 4 | P5-TBRL1-4 | C5S3-4/P5-TBRL1-4 | P5-TBRL1-4/C5S3-4 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-20203 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-20203 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-20203 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-20211
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-20211 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-20211 |  | P&ID Number: | 325-01-202-PD-01 |  | Junction Box: | RIO-200
Service Description: | Slurry Preparation Tank 2 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-20211_DI_1 | C5/C5S2 1 | P5-TBDI2-1 | C5S2-1/P5-TBDI2-1 | P5-TBDI2-1/C5S2-1 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-20211_DI_2 | C5/C5S2 2 | P5-TBDI2-2 | C5S2-2/P5-TBDI2-2 | P5-TBDI2-2/C5S2-2 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-20211_DO_1 | C5/C5S3 5 | P5-TBRL1-5 | C5S3-5/P5-TBRL1-5 | P5-TBRL1-5/C5S3-5 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-20211 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-20211 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-20211 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-20212
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-20212 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-20212 |  | P&ID Number: | 325-01-202-PD-01 |  | Junction Box: | RIO-200
Service Description: | Slurry Preparation Tank 2 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-20212_DI_1 | C5/C5S2 3 | P5-TBDI2-3 | C5S2-3/P5-TBDI2-3 | P5-TBDI2-3/C5S2-3 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-20212_DI_2 | C5/C5S2 4 | P5-TBDI2-4 | C5S2-4/P5-TBDI2-4 | P5-TBDI2-4/C5S2-4 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-20212_DO_1 | C5/C5S3 6 | P5-TBRL1-6 | C5S3-6/P5-TBRL1-6 | P5-TBRL1-6/C5S3-6 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-20212 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-20212 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-20212 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-20213
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-20213 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-20213 |  | P&ID Number: | 325-01-202-PD-01 |  | Junction Box: | RIO-200
Service Description: | Slurry Preparation Tank 2 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-20213_DI_1 | C5/C5S2 5 | P5-TBDI2-5 | C5S2-5/P5-TBDI2-5 | P5-TBDI2-5/C5S2-5 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-20213_DI_2 | C5/C5S2 6 | P5-TBDI2-6 | C5S2-6/P5-TBDI2-6 | P5-TBDI2-6/C5S2-6 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-20213_DO_1 | C5/C5S3 7 | P5-TBRL1-7 | C5S3-7/P5-TBRL1-7 | P5-TBRL1-7/C5S3-7 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-20213 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-20213 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-20213 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-913201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-913201 ¦ Junction Box: RIO-200 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-913201 |  | P&ID Number: | 325-01-913-PD-02 |  | Junction Box: | RIO-200
Service Description: | Outlet LPG line |  | Calibrated Range: | On-Off |  | Channel Count: | 4 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Input Process Variable (4-20mA AI) - XV-913201_AI_1 [Pins A+B] | AI | XV-913201_AI_1 | C5/C5S4 Pins 20(A) & 19(B) | P5-TBAI1-9(A/B) | C5S4-20/P5-TBAI1-9(A) (+) / C5S4-19/P5-TBAI1-9(B) (-) | P5-TBAI1-9(A)/C5S4-20 (+) / P5-TBAI1-9(B)/C5S4-19 (-) | White (+ / IN-x), Black (- / i RTN-x)
CH-02 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-913201_DI_1 | C5/C5S2 7 | P5-TBDI2-7 | C5S2-7/P5-TBDI2-7 | P5-TBDI2-7/C5S2-7 | White (Sig), Grey (24VDC)
CH-03 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-913201_DI_1 | C5/C5S2 8 | P5-TBDI2-8 | C5S2-8/P5-TBDI2-8 | P5-TBDI2-8/C5S2-8 | White (Sig), Grey (24VDC)
CH-04 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-913201_DO_1 | C5/C5S3 8 | P5-TBRL1-8 | C5S3-8/P5-TBRL1-8 | P5-TBRL1-8/C5S3-8 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
4.2 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-913201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-913201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-913201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run