## 00_Executive_Summary
KALASIN ENGINEERING ¦ xCIP-1545 AUTOMATION SYSTEM (Ref: x2608003)
MASTER INSTRUMENT LOOP TESTING PLAN, PROCEDURE & COMMISSIONING SCHEDULE — SPRINT 18K TPA SPRAY DRYER / JET COOKER
TOTAL INSTRUMENT LOOPS |  | COLD LOOP INSPECTION |  | HOT LOOP CALIBRATION |  | COMMISSIONING SCHEDULE |  | STANDARD COMPLIANCE |  | PUNCHLIST TRACKING
560 Loops |  | 100% Verified |  | 5-Point Simulation |  | 4 Weeks (20 Days) |  | IEC 62381 / ISA |  | Cat A & B System
Master Client Schedule Rev 3.6a |  | Continuity, Megger 500VDC, Polarity |  | 0%, 25%, 50%, 75%, 100% Range |  | Mobilization to Client Handover |  | Field Instrument Loop Check Standard |  | 100% Pre-commissioning Sign-off
1. LOOP TESTING SCOPE & SUBSYSTEM WORK BREAKDOWN
Subsystem / Plant Area | Target Field Enclosures | Associated PLC Rack | Total Loops | Discrete DI/DO | Analog AI/AO | Hazardous Area Zone | Primary Test Protocol | Estimated Duration | Scheduled Window | Responsible Team Lead | Witness / QA/QC | Status
Jet Cooker Infeed & Pre-Treatment | JB-401 (Floor 2F) | Chassis C1 (Panel P1) | 96 | 74 | 22 | Safe Area | Cold + 4-20mA Flow/Press Sim | 3 Working Days | Week 1 (Day 3–5) | Lead Inst. Eng (Kalasin) | Ingredion QA/QC | READY FOR EXECUTION
Jet Cooker Thermal Cooking Skid | JB-402 (Floor 2F) | Chassis C2 (Panel P2) | 48 | 33 | 15 | Safe Area | Temp RTD + Steam PRV Stroke | 2 Working Days | Week 2 (Day 6–7) | Senior Comm. Eng | Ingredion QA/QC | READY FOR EXECUTION
Spray Dryer Base & Powder Discharge | JB-601 (Floor 1F) | Chassis C1 (Panel P1) | 61 | 45 | 16 | Safe Area | Rotary Valve + Pressure Trans | 2 Working Days | Week 2 (Day 8–9) | Lead Inst. Eng (Kalasin) | Ingredion QA/QC | READY FOR EXECUTION
Spray Dryer Cyclone & Exhaust Section | JB-602 (Floor 3F) | Chassis C2 (Panel P2) | 86 | 26 | 60 | Safe Area | Diff Pressure DP + Temp RTDs | 3 Working Days | Week 2 (Day 9–10) | Senior Comm. Eng | Ingredion QA/QC | READY FOR EXECUTION
Spray Dryer Direct Burner & Air Heater | JB-606 (Floor 6F) | Chassis C3 (Panel P3) | 9 | 5 | 4 | Classified / Burner | Combustible Gas + Thermal Flow | 1 Working Day | Week 3 (Day 11) | Lead Inst. Eng (Kalasin) | Burner Specialist | READY FOR EXECUTION
Spray Dryer Main Mid-Tower Section | JB-607, JB-608 (4F) | Chassis C2 & C3 (P2/P3) | 179 | 121 | 58 | Dust Zone 22 (Ext) | High-Density Transmitters & Valves | 4 Working Days | Week 3 (Day 12–14) | Lead Inst. Eng (Kalasin) | Ingredion QA/QC | READY FOR EXECUTION
Spray Dryer Upper Tower & Atomizer | JB-612 (Floor 6/8F) | Chassis C4 (Panel P4) | 40 | 32 | 8 | Dust Zone 21/22 | Atomizer Speed + Vent Pressure | 2 Working Days | Week 3 (Day 14–15) | Senior Comm. Eng | Ingredion QA/QC | READY FOR EXECUTION
Packing Tower Feed & Silo Discharge | JB-618 (Packing) | Chassis C3 (Panel P3) | 29 | 21 | 8 | Dust Zone 22 | Powder Silo Fork + Sieve DI | 2 Working Days | Week 4 (Day 16–17) | Lead Inst. Eng (Kalasin) | Ingredion QA/QC | READY FOR EXECUTION
Hazardous Area Intrinsically Safe Loops | IS-JB-603/608/612/618 | Chassis C4 (P4 IS) | 99 | 50 | 49 | ATEX Zone 1/21 (Ex ia) | P&F IS Barrier Insulation & Loop Check | 3 Working Days | Week 4 (Day 17–18) | Ex-Certified Inspector | TUV / Client Safety | READY FOR EXECUTION
Slurry Preparation Outbuilding | RIO-200 (Slurry 2F) | Chassis C5 (RIO-200) | 66 | 48 | 18 | Safe Area | 1Gbps DLR Ring + Slurry pH/Mass Flow | 2 Working Days | Week 4 (Day 18–19) | Senior Comm. Eng | Ingredion QA/QC | READY FOR EXECUTION
Integrated Interlocks & Handover | CA1 Central MCP | Master Chassis C1-C5 | 560 | 334 | 226 | Central Control | Full ESD Trip & SCADA Graphic Verification | 2 Working Days | Week 4 (Day 19–20) | Project Commissioning Mgr | Ingredion Project Mgr | PLANNED
2. REQUIRED TEST INSTRUMENTS, CALIBRATORS & COMMISSIONING TOOL SPECIFICATIONS
Item # | Equipment Description | Manufacturer & Model | Calibration Parameter | Operating Range | Accuracy / Tolerance | Valid Calibration Certificate | Calibration Expiry Date | Dedicated Testing Purpose | Quantity Required | Serial Number | Certification Agency | Status
1 | Precision Documenting Process Calibrator | Fluke 754 | 4-20mA, Volts, RTD, TC, HART | -10 to 55 mA / 0-30V / Pt100 | ±0.01% of Reading | ISO/IEC 17025 Certified | 31-DEC-2026 | Analog 4-20mA 5-Point Loop Simulation & HART Config | 2 Units | FLK-754-98421 | NIST / Thai Metrology | CERTIFIED ACTIVE
2 | Precision Digital Pressure Calibrator | Druck DPI 611 | Gauge & Differential Pressure | -1 to 20 bar (Hydraulic/Pneu) | ±0.0185% FS | ISO/IEC 17025 Certified | 15-NOV-2026 | Pressure & Differential Transmitter Calibration Check | 1 Unit | DRK-611-34901 | Baker Hughes Cal Lab | CERTIFIED ACTIVE
3 | True RMS Digital Industrial Multimeter | Fluke 87V | AC/DC Volts, Amps, Resistance, Continuity | 0 - 1000V DC / 0 - 20A / 50MΩ | ±0.05% Accuracy | Factory Calibrated | 28-FEB-2027 | Cold continuity check, 24VDC loop power verification | 3 Units | FLK-87V-11204 | Fluke Service Center | CERTIFIED ACTIVE
4 | High-Voltage Insulation Resistance Tester | Megger MIT410/2 | Insulation Resistance @ 250V/500VDC | 10 kΩ to 100 GΩ | ±2% ±2 digits | Annual Certified | 15-JAN-2027 | Pre-power cable insulation & shield isolation (>20MΩ) | 2 Units | MEG-410-88319 | Megger Calibration Lab | CERTIFIED ACTIVE
5 | Pneumatic Hand Test Pump w/ Vernier | Ralston Instruments AP-002 | Pneumatic Air Pressure / Vacuum | 0 to 300 psi (20 bar) | Fine Vernier 0.01 psi | Traceable Reference | 31-DEC-2026 | Field Pressure Transmitter 5-point mechanical test | 2 Units | RAL-AP-55201 | Ralston Metrology | CERTIFIED ACTIVE
6 | Industrial 2-Way VHF/UHF Radios | Motorola Mototrbo DP4801e | Intrinsically Safe ATEX Comms | 136 - 174 MHz | ATEX Gas/Dust Certified | Radio License Compliant | Permanent | Direct Field-to-Control Room voice coordination | 6 Units | MOT-DP-4801-SET | NBTC Thailand | INSPECTED ACTIVE

## 01_Loop_Test_Procedure
KALASIN ENGINEERING ¦ STANDARD OPERATING PROCEDURE (SOP) — INSTRUMENT LOOP TESTING
Standardized Loop Check Protocol in Accordance with IEC 62381 (Factory & Site Acceptance Testing of Automation Systems)
Stage # | Testing Activity / Protocol Step | Detailed Standard Operating Procedure (SOP) | Pass / Acceptance Criteria | Responsible Personnel | Verifying Document / Record | QA/QC Hold Point
STAGE 0 | Pre-Testing Prerequisite & Safety LOTO | 1. Verify that all field piping, hydrotests, electrical tray routing and mechanical terminations are complete. 2. Obtain valid Work Permit (Hot/Cold Work) and apply Lockout/Tagout (LOTO) on pneumatic headers and high-voltage power feeds. 3. Verify calibration validity of Fluke 754 calibrators and Megger instruments. 4. Establish dedicated radio communication between Field Lead and Control Room SCADA Operator. | Approved Work Permit, zero residual hazardous energy, test calibrator valid certificates on file. | Commissioning Lead & Safety Officer | Work Permit + Equipment Cal Certs | HOLD POINT (Mandatory Sign-off)
STAGE 1 | Phase 1: Cold Loop Inspection & Cable Testing | 1. Perform visual inspection of instrument mounting, cable gland sealing, tag plate correctness, and drain plugs. 2. Verify cable core identification against marshaling wiring drawings (C1S4-19/P1-TBDI1-17). 3. Disconnect transmitter and I/O card terminals before insulation testing to prevent card damage. 4. Perform Megger test @ 500VDC: Core-to-Core and Core-to-Shield/Ground for minimum 60 seconds. 5. Check cable shield continuity and ensure single-point grounding at Central Cabinet CA1 / IS barrier bar only. | Insulation resistance > 20 MΩ @ 500VDC. Shield grounded at Cabinet side ONLY (no double-grounding). Continuity resistance < 2 Ω. | Instrument Technician & QC Inspector | Cold Loop Check Sheet (Sheet 03) | WITNESS POINT
STAGE 2 | Phase 2: Hot Loop Check & Power-Up | 1. Reconnect field wiring to marshaling terminals and transmitter terminals. 2. Energize 24VDC power supply circuit breaker in Control Cabinet CA1. 3. Measure DC voltage across instrument terminals using Fluke 87V. 4. Measure quiescent current draw and confirm proper polarity (positive to + / return to -). 5. In intrinsically safe (IS) loops, verify Pepperl+Fuchs IS barrier output voltage and barrier grounding. | Terminal voltage within 21.6V to 26.4VDC. Quiescent current: 3.8 to 4.2 mA for analog 2-wire. No tripped fuses or circuit breaker faults. | Senior Commissioning Engineer | Hot Loop Power-Up Record | REVIEW POINT
STAGE 3 | Phase 3: 5-Point Analog Loop Calibration Check (AI/AO) | 1. Connect Fluke 754 precision calibrator in mA simulation mode at transmitter field terminals. 2. Inject current ascending: 0% (4.00 mA), 25% (8.00 mA), 50% (12.00 mA), 75% (16.00 mA), 100% (20.00 mA). 3. Record Raw PLC counts (0..32767 for 1756-IF16) and SCADA HMI graphical display reading in engineering units. 4. Repeat descending check: 100% -> 75% -> 50% -> 25% -> 0% to evaluate hysteresis. 5. Verify HART digital communication and tag configuration using HART communicator. | Max error ≤ ±0.5% of calibrated span across all 5 test points. Zero and span linearity verified. SCADA matches field simulation exactly. | Lead Instrument Engineer & SCADA Engineer | 5-Point Calibration Record (Sheet 03) | HOLD POINT (Client Witness)
STAGE 4 | Phase 4: Discrete Digital Loop (DI) & Limit Switch Check | 1. For proximity / limit switches (HV-40201, XV feedback): manually trip lever to Open and Closed positions. 2. For level forks (FTM51 / FTL51B): simulate tuning fork immersion / vibration damping. 3. For pressure switches (PTC31B) and flow switches (FSL): simulate trip pressure / paddle movement. 4. Observe LED status indicator on 1756-IB32 card and verify tag status change (0 -> 1) on SCADA screen. 5. Check debounce time filter (standard 10ms) and verify alarm banner appearance. | 100% state change fidelity (Open=1, Close=0 or fail-safe logic). Card LED and SCADA display update within <100ms. No contact chatter. | Instrument Technician & SCADA Operator | Discrete Test Log Sheet | WITNESS POINT
STAGE 5 | Phase 5: Digital Output (DO) & Solenoid Valve Actuation | 1. Verify pneumatic air supply header pressure (minimum 5.5 to 6.0 bar stable). 2. Issue Manual DO command (Force or HMI manual toggle) from SCADA workstation. 3. Verify 1756-OB32 channel output energizes 24VDC interposing relay / solenoid valve coil. 4. Confirm physical actuator stroke movement and measure open/close stroke travel time with stopwatch. 5. Verify that limit switch position feedback (ZSO / ZSC) returns to PLC and changes valve symbol color on SCADA. | Full valve travel stroke without sticking or pneumatic leakage. Stroke time within vendor datasheet specs (<3 sec for ball valves). SCADA graphic updates from Red to Green. | Commissioning Lead & Mechanical Tech | Valve Actuation Test Protocol | WITNESS POINT
STAGE 6 | Phase 6: Control Valve (AO/AI) Modulation & Positioner Stroke | 1. Supply regulated instrument air (4.0 to 6.0 bar) to Samson Type 3241 / Trovis 3730-1 positioner. 2. Command AO from SCADA at 0%, 25%, 50%, 75%, 100% and descending. 3. Measure physical valve travel scale indicator and compare against 4-20mA position transmitter feedback. 4. Test fail-safe action: simulate power loss and air supply disconnection; confirm valve drives to fail position (Fail-Closed FC or Fail-Open FO). 5. Check valve seat tightness and seat leakage shut-off class. | Travel error ≤ ±1.0% of full stroke. Hysteresis ≤ 0.5%. Fail-safe spring return drives to fail-safe position in <2.0 seconds. | Valve Specialist & Lead Inst Engineer | Control Valve Calibration Certificate | HOLD POINT (Client Witness)
STAGE 7 | Phase 7: Alarm, Trip & Safety Interlock Verification | 1. Inject process values beyond configured alarm setpoints: Low (L), High (H), Low-Low (LL), High-High (HH). 2. Confirm audible horn annunciator, alarm banner flashing, and historical alarm log timestamp. 3. Verify automated safety shutdown interlocks (e.g. Cyclone High Temp -> Trip Burner Gas Solenoid). 4. Confirm that latched emergency shutdown (ESD) alarms require manual operator reset. 5. Verify First-Out alarm discrimination logic. | 100% interlock trip action verified. ESD valve de-energization confirmed. Correct alarm priority colors (Red=Emergency, Yellow=Warning). | Lead Process Automation Engineer & Client Rep | Safety Interlock Matrix Sign-off | HOLD POINT (Mandatory Sign-off)
STAGE 8 | Phase 8: Punchlist Management & Final Acceptance Handover | 1. Classify any defects: Category A (Must fix prior to start-up) or Category B (Minor, rectifiable during operation). 2. Record punchlist item with clear tag ID, responsible contractor, and target completion date. 3. Affix tamper-evident waterproof green 'LOOP CHECK PASSED' calibration tag onto field instrument. 4. Compile signed loop test sheets, calibration records, and ITP documentation into Master Handover Binder. 5. Obtain formal tripartite sign-off: Contractor Commissioning Lead, Client Inspector, and Project QA/QC Manager. | Zero Category A punchlist items remaining. All Category B items agreed with sign-off. Green Loop Pass tag affixed to instrument. | Project Commissioning Manager & Client PM | Master Handover Certificate | FINAL ACCEPTANCE MILESTONE

## 02_Master_Testing_Schedule
KALASIN ENGINEERING ¦ MASTER COMMISSIONING & LOOP TESTING EXECUTION SCHEDULE
4-Week Comprehensive Day-by-Day (Days 1 to 20) Gantt Timeline Across All Plant Subsystems & Field Junction Boxes
TASK IDENTIFICATION & WORK BREAKDOWN |  |  |  |  | WEEK 1: MOBILIZATION & JET COOKER |  |  |  |  | WEEK 2: SPRAY DRYER LOWER & MID |  |  |  |  | WEEK 3: UPPER TOWER & IS ZONES |  |  |  |  | WEEK 4: SLURRY RIO & SYSTEM HANDOVER
Task ID | Activity / Loop Testing Scope Description | Target Area / JB | Duration | Lead | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | D9 | D10 | D11 | D12 | D13 | D14 | D15 | D16 | D17 | D18 | D19 | D20
T-01 | Mobilization, Safety Induction, LOTO & Calibrator Certification | Site-wide | 2 Days | Lead | █ | █
T-02 | Control Cabinet CA1 Power-up & DLR Network Health Check | CA1 MCP | 1 Day | Comm |  | █
T-03 | JB-401 Jet Cooker Infeed Cold Loop Check & Megger Testing | JB-401 (2F) | 2 Days | Inst-1 |  |  | █ | █
T-04 | JB-401 Jet Cooker Hot Loop 5-Pt Calibration & Discrete Check | JB-401 (2F) | 2 Days | Inst-1 |  |  |  | █ | █
T-05 | JB-402 Jet Cooker Skid Cold Loop & Hot Loop Testing | JB-402 (2F) | 2 Days | Inst-2 | [5 empty] | █ | █
T-06 | Jet Cooker Steam PRV & Samson Control Valve Stroke Check | Jet Cooker | 1 Day | Valve | [6 empty] | █
T-07 | MILESTONE 1: Jet Cooker Skid Loop Test Handover Sign-off | Skid 2F | Milestone | PM/QC | [6 empty] | ★
T-08 | JB-601 Spray Dryer Base Floor 1F Cold & Hot Loop Tests | JB-601 (1F) | 2 Days | Inst-1 | [7 empty] | █ | █
T-09 | JB-602 Cyclone & Exhaust Floor 3F Cold & Hot Loop Tests | JB-602 (3F) | 2 Days | Inst-2 | [8 empty] | █ | █
T-10 | JB-606 Direct Air Heater Burner Loop Checking | JB-606 (6F) | 1 Day | Inst-1 | [10 empty] | █
T-11 | JB-607 Mid-Tower Main Deck High-Density Loop Testing (Part 1) | JB-607 (4F) | 2 Days | Inst-1 | [10 empty] | █ | █
T-12 | JB-607 Mid-Tower Main Deck High-Density Loop Testing (Part 2) | JB-607 (4F) | 2 Days | Inst-2 | [12 empty] | █ | █
T-13 | JB-608 Auxiliary Deck Sight Glass & Level Testing | JB-608 (4F) | 1 Day | Inst-1 | [13 empty] | █
T-14 | JB-612 Upper Tower & Atomizer 6F/8F Loop Check | JB-612 (6/8F) | 2 Days | Inst-2 | [13 empty] | █ | █
T-15 | MILESTONE 2: Spray Dryer Tower Loop Test Handover Sign-off | Dryer Tower | Milestone | PM/QC | [14 empty] | ★
T-16 | JB-618 Packing Tower & Silos Cold & Hot Loop Tests | JB-618 | 2 Days | Inst-1 | [15 empty] | █ | █
T-17 | IS-JB-603 & IS-JB-608 Intrinsically Safe Ex ia Loop Check | IS JBs (Ex) | 2 Days | Ex-Lead | [15 empty] | █ | █
T-18 | IS-JB-612 & IS-JB-618 Intrinsically Safe Ex ia Loop Check | IS JBs (Ex) | 2 Days | Ex-Lead | [16 empty] | █ | █
T-19 | RIO-200 Slurry Outbuilding Remote Station Loop Check | RIO-200 (2F) | 2 Days | Inst-2 | [17 empty] | █ | █
T-20 | Integrated System Safety Interlocks & ESD Trip Simulation | CA1 / Plant | 2 Days | Auto | [18 empty] | █ | █
T-21 | Category A & B Punchlist Clearance & Pre-start Rectification | Site-wide | 1 Day | Team | [19 empty] | █
T-22 | FINAL MILESTONE: Master Loop Check Protocol Tripartite Handover | Client MCP | Final | Tripartite | [19 empty] | ★

## 03_Loop_Test_Master_List
KALASIN ENGINEERING ¦ MASTER INSTRUMENT LOOP TESTING & CALIBRATION VERIFICATION SCHEDULE
Point-by-Point Field Loop Check Record (Rev. 3.6a Master) Cross-Referenced with CAD Loop Typical Diagrams (DWG/DXF)
Item # | Active Tag No. | Legacy Tag | P&ID No. | Instrument Service Description | Instrument Type / Name | Signal Type | Calibrated Range | CAD Typical ID | CAD Strip Type | CAD DWG Reference | Field Junction Box | Terminal Block ID | PLC Rack / Slot | Wire Tag (PLC Side) | Wire Tag (Terminal Side) | PLC Tag Name | Cold Continuity (<2Ω) | Cold Megger (>20MΩ) | Hot Power (24VDC) | Calibration 0% (4mA) | Calibration 50% (12mA) | Calibration 100% (20mA) | Stroke / Trip Response | Testing Status | QA/QC Sign-off & Date
1 | AT-60241 | - | 325-01-602-PD-05 | Dust Analyzer Transmitter for Exhaust Duct (DTEX-22) | Dust Analyzer Transmitter | 4 - 20 mA | 5000 mg | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBAI2-1(B) | C2/C2S10 | C2S10-1/P2-TBAI2-1(B) | P2-TBAI2-1(B)/C2S10-1 | AT-60241_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
2 | DPT-60201 | DPT-60901 | 325-01-602-PD-09 | Steam filter pressure | Differential Pressure Transmitter | 4 - 20 mA | 0-1 barg | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-606 | P3-TBAI1-15(B) | C3/C3S6 | C3S6-33/P3-TBAI1-15(B) | P3-TBAI1-15(B)/C3S6-33 | DPT-60201_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
3 | DPT-61301 | - | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | 4 - 20 mA | - | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-618 | P4-TBAI2-5(B) | C4/C4S6 | C4S6-11/P4-TBAI2-5(B) | P4-TBAI2-5(B)/C4S6-11 | DPT-61301_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
4 | DPT-61302 | - | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | 4 - 20 mA | - | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-618 | P4-TBAI2-6(B) | C4/C4S6 | C4S6-13/P4-TBAI2-6(B) | P4-TBAI2-6(B)/C4S6-13 | DPT-61302_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
5 | DPT-61310 | - | 325-01-613-PD-03 | Vent filter pressure | Differential Pressure Transmitter | 4 - 20 mA | - | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-612 | P4-TBAI2-1(B) | C4/C4S6 | C4S6-1/P4-TBAI2-1(B) | P4-TBAI2-1(B)/C4S6-1 | DPT-61310_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
6 | DPT-61312 | - | 325-01-613-PD-05 | Vent filter pressure | Differential Pressure Transmitter | 4 - 20 mA | - | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-612 | P4-TBAI2-2(B) | C4/C4S6 | C4S6-3/P4-TBAI2-2(B) | P4-TBAI2-2(B)/C4S6-3 | DPT-61312_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
7 | DPT-60202 | - | 325-01-602-PD-08 | Gas Pressure Differential Transmitter for Air Filter (FICA-31) | Differential Pressure Transmitter | 4 - 20 mA | -100 to 500 mBar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-601 | P1-TBAI2-2(B) | C1/C1S11 | C1S11-3/P1-TBAI2-2(B) | P1-TBAI2-2(B)/C1S11-3 | DPT-60202_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
8 | DPT-60203 | - | 325-01-602-PD-03 | Gas Pressure Differential Transmitter for Air Filter (FICA-21) | Differential Pressure Transmitter | 4 - 20 mA | -100 to 500 mBar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBAI2-2(B) | C2/C2S10 | C2S10-3/P2-TBAI2-2(B) | P2-TBAI2-2(B)/C2S10-3 | DPT-60203_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
9 | FSL-20201 |  | 325-01-202-PD-01 | Slurry low flow | Flow Switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
10 | FSL-40201 |  | 325-01-402-PD-01 | Slurry low flow | Flow Switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI1-17 | C1/C1S4 | C1S4-19/P1-TBDI1-17 | P1-TBDI1-17/C1S4-19 | FSL-40201_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
11 | FSL-40202 |  | 325-01-402-PD-01 | Slurry low flow | Flow Switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI1-18 | C1/C1S4 | C1S4-20/P1-TBDI1-18 | P1-TBDI1-18/C1S4-20 | FSL-40202_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
12 | FS-40204 |  | 325-01-402-PD-01 | Jet Cooker | Flow Switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-1 | C2/C2S1 | C2S1-1/P2-TBDI1-1 | P2-TBDI1-1/C2S1-1 | FS-40204_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
13 | FS-40205 |  | 325-01-402-PD-02 | Jet Cooker | Flow Switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-2 | C2/C2S1 | C2S1-2/P2-TBDI1-2 | P2-TBDI1-2/C2S1-2 | FS-40205_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
14 | FT-40201 | - | 325-01-402-PD-02 | Slurry flowrate & density check transfer line | Coriolis Flow Transmitter | 4 - 20 mA,Pulse | 0-15 m³/hr | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI1-19 | C1/C1S4 | C1S4-21/P1-TBDI1-19 | P1-TBDI1-19/C1S4-21 | FT-40201_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
15 | FT-40202 | - | 325-01-402-PD-02 | Feed Slurry Flow Transmitter for Pipe (PIPE) | Magnetic Flow Transmitter | 4 - 20 mA,Pulse | 0 to 8,000 m³/hr | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-401 | P1-TBDI1-20 | C1/C1S4 | C1S4-22/P1-TBDI1-20 | P1-TBDI1-20/C1S4-22 | FT-40202_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
16 | FT-40221 |  | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter | 4 - 20 mA,Pulse | 0-6 m³/hr | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-3 | C2/C2S1 | C2S1-3/P2-TBDI1-3 | P2-TBDI1-3/C2S1-3 | FT-40221_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
17 | FT-40222 |  | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter | 4 - 20 mA,Pulse | 0-850 kg/hr | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-4 | C2/C2S1 | C2S1-4/P2-TBDI1-4 | P2-TBDI1-4/C2S1-4 | FT-40222_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
18 | FT-60221 | - | 325-01-602-PD-04 | Cool air Flow | Thermal Mass Flow Transmitter | 4 - 20 mA | 2500 m3/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-2(B) | C3/C3S7 | C3S7-3/P3-TBAI2-2(B) | P3-TBAI2-2(B)/C3S7-3 | FT-60221_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
19 | FT-60201 | - | 325-01-602-PD-08 | Gas Flow Transmitter for Cooling Conveying Cold Air Duct (DTCA-32) | Thermal Mass Flow Transmitter | 4 - 20 mA | 70000 m3/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-601 | P1-TBAI2-3(B) | C1/C1S11 | C1S11-5/P1-TBAI2-3(B) | P1-TBAI2-3(B)/C1S11-5 | FT-60201_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
20 | FT-60210 | - | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) | Thermal Mass Flow Transmitter | 4 - 20 mA | 126000 m3/h | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | JB-602 | P3-TBAI1-10(B) | C3/C3S6 | C3S6-21/P3-TBAI1-10(B) | P3-TBAI1-10(B)/C3S6-21 | FT-60210_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
21 | FT-60211 | - | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) | Thermal Mass Flow Transmitter | 4 - 20 mA | 126000 m3/h | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | JB-602 | P3-TBAI1-11(B) | C3/C3S6 | C3S6-23/P3-TBAI1-11(B) | P3-TBAI1-11(B)/C3S6-23 | FT-60211_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
22 | FT-60261FA | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #1 (AMTV-11A) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-3(B) | C3/C3S7 | C3S7-5/P3-TBAI2-3(B) | P3-TBAI2-3(B)/C3S7-5 | FT-60261FA_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
23 | FT-60261FB | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #2 (AMTV-11A) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-4(B) | C3/C3S7 | C3S7-7/P3-TBAI2-4(B) | P3-TBAI2-4(B)/C3S7-7 | FT-60261FB_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
24 | FT-60261FC | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #3 (AMTV-11A) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-5(B) | C3/C3S7 | C3S7-11/P3-TBAI2-5(B) | P3-TBAI2-5(B)/C3S7-11 | FT-60261FC_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
25 | FT-60261FD | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #4 (AMTV-11A) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-6(B) | C3/C3S7 | C3S7-13/P3-TBAI2-6(B) | P3-TBAI2-6(B)/C3S7-13 | FT-60261FD_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
26 | FT-60262FE | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #5 (AMTV-11B) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-7(B) | C3/C3S7 | C3S7-15/P3-TBAI2-7(B) | P3-TBAI2-7(B)/C3S7-15 | FT-60262FE_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
27 | FT-60262FF | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #6 (AMTV-11B) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-8(B) | C3/C3S7 | C3S7-17/P3-TBAI2-8(B) | P3-TBAI2-8(B)/C3S7-17 | FT-60262FF_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
28 | FT-60262FG | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #7 (AMTV-11B) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-9(B) | C3/C3S7 | C3S7-19/P3-TBAI2-9(B) | P3-TBAI2-9(B)/C3S7-19 | FT-60262FG_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
29 | FT-60262FH | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #8 (AMTV-11B) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-10(B) | C3/C3S7 | C3S7-21/P3-TBAI2-10(B) | P3-TBAI2-10(B)/C3S7-21 | FT-60262FH_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
30 | FT-60263FJ | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #9 (AMTV-11C) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-11(B) | C3/C3S7 | C3S7-23/P3-TBAI2-11(B) | P3-TBAI2-11(B)/C3S7-23 | FT-60263FJ_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
31 | FT-60263FK | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #10 (AMTV-11C) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-12(B) | C3/C3S7 | C3S7-25/P3-TBAI2-12(B) | P3-TBAI2-12(B)/C3S7-25 | FT-60263FK_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
32 | FT-60263FL | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #11 (AMTV-11C) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-13(B) | C3/C3S7 | C3S7-29/P3-TBAI2-13(B) | P3-TBAI2-13(B)/C3S7-29 | FT-60263FL_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
33 | FT-60263FM | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #12 (AMTV-11C) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-14(B) | C3/C3S7 | C3S7-31/P3-TBAI2-14(B) | P3-TBAI2-14(B)/C3S7-31 | FT-60263FM_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
34 | FT-60264FN | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #13 (AMTV-11D) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-15(B) | C3/C3S7 | C3S7-33/P3-TBAI2-15(B) | P3-TBAI2-15(B)/C3S7-33 | FT-60264FN_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
35 | FT-60264FP | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #14 (AMTV-11D) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-16(B) | C3/C3S7 | C3S7-35/P3-TBAI2-16(B) | P3-TBAI2-16(B)/C3S7-35 | FT-60264FP_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
36 | FT-60264FQ | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #15 (AMTV-11D) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI3-1(B) | C3/C3S8 | C3S8-1/P3-TBAI3-1(B) | P3-TBAI3-1(B)/C3S8-1 | FT-60264FQ_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
37 | FT-60264FR | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #16 (AMTV-11D) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI3-2(B) | C3/C3S8 | C3S8-3/P3-TBAI3-2(B) | P3-TBAI3-2(B)/C3S8-3 | FT-60264FR_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
38 | FT-61307 | - | 325-01-613-PD-04 | Compressed air Flow | Thermal Mass Flow Transmitter | 4 - 20 mA | 0 - 1000 m3/hr | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-601 | P1-TBAI2-5(B) | C1/C1S11 | C1S11-11/P1-TBAI2-5(B) | P1-TBAI2-5(B)/C1S11-11 | FT-61307_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
39 | FT-60203 | FT-60901 | 325-01-602-PD-09 | Culinary steam feed to Spray dryer | Vortex Flow Transmitter | 4 - 20 mA | 0 - 7000 kg/hr | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-606 | P3-TBDI1-17 | C3/C3S1 | C3S1-19/P3-TBDI1-17 | P3-TBDI1-17/C3S1-19 | FT-60203_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
40 | FT-60202 | FT-60902 | 325-01-602-PD-09 | Steam feed to Spray dryer | Vortex Flow Transmitter | 4 - 20 mA | 0 - 2000 kg/hr | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBDI2-1 | C2/C2S2 | C2S2-1/P2-TBDI2-1 | P2-TBDI2-1/C2S2-1 | FT-60202_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
41 | FT-60204 | FT-61101 | 325-01-602-PD-10 | Compressed air Flow | Thermal Mass Flow Transmitter | 4 - 20 mA | 0 - 1000 m3/hr | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-601 | P1-TBAI2-4(B) | C1/C1S11 | C1S11-7/P1-TBAI2-4(B) | P1-TBAI2-4(B)/C1S11-7 | FT-60204_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
42 | FT-936201 | FT-90301 | 325-01-930-PD-01 | Process Water | Magnetic Flow Transmitter | 4 - 20 mA,Pulse | 0-1000kg/m³ | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | RIO-200 | P5-TBDI1-3 | C5/C5S1 | C5S1-3/P5-TBDI1-3 | P5-TBDI1-3/C5S1-3 | FT-936201_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
43 | FT-936202 | FT-93001 | 325-01-930-PD-02 | Process Water | Magnetic Flow Transmitter | 4 - 20 mA,Pulse | 0 - 20 m3/ hr | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | RIO-200 | P5-TBDI1-4 | C5/C5S1 | C5S1-4/P5-TBDI1-4 | P5-TBDI1-4/C5S1-4 | FT-936202_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
44 | HS-61307A | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
45 | HS-61307B | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
46 | HS-61307C | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
47 | HS-61307D | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
48 | HS-61307E | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
49 | HS-61307F | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
50 | HS-61307G | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
51 | HS-61307H | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
52 | HS-61307I | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
53 | HS-61307J | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
54 | HS-61307K | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
55 | HS-61307L | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
56 | HS-61307M | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
57 | HS-61307N | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
58 | HS-61307O | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
59 | HS-61307P | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
60 | HS-61307Q | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
61 | HS-61307R | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
62 | HV-40203 | HV-4106 | 325-01-402-PD-01 | Slurry Drain tank TS-40201 | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI1-23 | C1/C1S4 | C1S4-25/P1-TBDI1-23 | P1-TBDI1-23/C1S4-25 | HV-40203_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
63 | HV-40201 | HV-4108 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI1-21 | C1/C1S4 | C1S4-23/P1-TBDI1-21 | P1-TBDI1-21/C1S4-23 | HV-40201_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
64 | HV-40204 | HV-4126 | 325-01-402-PD-01 | Slurry Drain tank TS-40202 | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI1-24 | C1/C1S4 | C1S4-26/P1-TBDI1-24 | P1-TBDI1-24/C1S4-26 | HV-40204_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
65 | HV-40202 | HV-4128 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI1-22 | C1/C1S4 | C1S4-24/P1-TBDI1-22 | P1-TBDI1-22/C1S4-24 | HV-40202_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
66 | HV-40206 | HV-4208 | 325-01-402-PD-01 | Slurry Drain tank TS-40203 | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI1-26 | C1/C1S4 | C1S4-28/P1-TBDI1-26 | P1-TBDI1-26/C1S4-28 | HV-40206_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
67 | HV-40205 | HV-4210 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI1-25 | C1/C1S4 | C1S4-27/P1-TBDI1-25 | P1-TBDI1-25/C1S4-27 | HV-40205_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
68 | HV-40207 |  | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-5 | C2/C2S1 | C2S1-5/P2-TBDI1-5 | P2-TBDI1-5/C2S1-5 | HV-40207_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
69 | HV-40208 |  | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-6 | C2/C2S1 | C2S1-6/P2-TBDI1-6 | P2-TBDI1-6/C2S1-6 | HV-40208_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
70 | LSH-60230 | - | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-21) | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-603 | P4-TBDI1-4 | C4/C4S1 | C4S1-4/P4-TBDI1-4 | P4-TBDI1-4/C4S1-4 | LSH-60230_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
71 | LSH-60231 | - | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-22) | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-603 | P4-TBDI1-5 | C4/C4S1 | C4S1-5/P4-TBDI1-5 | P4-TBDI1-5/C4S1-5 | LSH-60231_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
72 | LSH-60240 | - | 325-01-602-PD-05 | Powder Level Switch High for Bag House (BGHS-21) | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-603 | P4-TBDI1-6 | C4/C4S1 | C4S1-6/P4-TBDI1-6 | P4-TBDI1-6/C4S1-6 | LSH-60240_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
73 | LSH-60250 | - | 325-01-602-PD-05 | Water Level Switch High for Fire Deluge Pipe (FWDP-21) | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-606 | P3-TBDI1-18 | C3/C3S1 | C3S1-20/P3-TBDI1-18 | P3-TBDI1-18/C3S1-20 | LSH-60250_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
74 | LSH-60251 | - | 325-01-602-PD-04 | Water Level Switch High for Fire Deluge Pipe (FWDP-22) | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-2 | C2/C2S2 | C2S2-2/P2-TBDI2-2 | P2-TBDI2-2/C2S2-2 | LSH-60251_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
75 | LSL-60201 | LSL-61101 | 325-01-602-PD-11 | Level low switch | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI3-19 | C1/C1S6 | C1S6-21/P1-TBDI3-19 | P1-TBDI3-19/C1S6-21 | LSL-60201_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
76 | LSH-61301 | - | 325-01-613-PD-01 | Level alarm high | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-618 | P4-TBDI3-2 | C4/C4S3 | C4S3-2/P4-TBDI3-2 | P4-TBDI3-2/C4S3-2 | LSH-61301_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
77 | LSL-61302 | - | 325-01-613-PD-01 | Level alarm low | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-618 | P4-TBDI3-6 | C4/C4S3 | C4S3-6/P4-TBDI3-6 | P4-TBDI3-6/C4S3-6 | LSL-61302_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
78 | LS-61303 | - | 325-01-613-PD-01 | Level switch | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-618 | P3-TBDI3-5 | C3/C3S3 | C3S3-5/P3-TBDI3-5 | P3-TBDI3-5/C3S3-5 | LS-61303_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
79 | LSH-61304 | - | 325-01-613-PD-03 | Big bag level alarm high | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-612 | P4-TBDI2-3 | C4/C4S2 | C4S2-3/P4-TBDI2-3 | P4-TBDI2-3/C4S2-3 | LSH-61304_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
80 | LSH-61305 | - | 325-01-613-PD-05 | Big bag level alarm high | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-612 | P4-TBDI2-4 | C4/C4S2 | C4S2-4/P4-TBDI2-4 | P4-TBDI2-4/C4S2-4 | LSH-61305_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
81 | LSH-61306 | - | 325-01-613-PD-01 | Level alarm high | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-618 | P4-TBDI3-4 | C4/C4S3 | C4S3-4/P4-TBDI3-4 | P4-TBDI3-4/C4S3-4 | LSH-61306_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
82 | LSH-61307 |  | 325-01-613-PD-01 | High Level alarm reject screen | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-612 | P4-TBDI2-5 | C4/C4S2 | C4S2-5/P4-TBDI2-5 | P4-TBDI2-5/C4S2-5 | LSH-61307_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
83 | LSH-61308 |  | 325-01-613-PD-01 | High Level alarm Cooling cyclone | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-618 | P4-TBDI3-5 | C4/C4S3 | C4S3-5/P4-TBDI3-5 | P4-TBDI3-5/C4S3-5 | LSH-61308_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
84 | LSH-61312 | - | 325-01-613-PD-05 | Level alarm high | Level switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-612 | P4-TBDI2-6 | C4/C4S2 | C4S2-6/P4-TBDI2-6 | P4-TBDI2-6/C4S2-6 | LSH-61312_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
85 | LSL-814201 | LSL-81001 | 325-01-814-PD-01 | Low Level alarm |  | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-5 | C5/C5S1 | C5S1-5/P5-TBDI1-5 | P5-TBDI1-5/C5S1-5 | LSL-814201_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
86 | LT-40201 | LT-40101 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 1 | Level transmitter | 4 - 20 mA | 0 - 10 m. | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-401 | P1-TBAI1-5(B) | C1/C1S10 | C1S10-11/P1-TBAI1-5(B) | P1-TBAI1-5(B)/C1S10-11 | LT-40201_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
87 | LT-40202 | LT-40102 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 2 | Level transmitter | 4 - 20 mA | 0 - 10 m. | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-401 | P1-TBAI1-6(B) | C1/C1S10 | C1S10-13/P1-TBAI1-6(B) | P1-TBAI1-6(B)/C1S10-13 | LT-40202_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
88 | LT-40203 | LT-40201 | 325-01-402-PD-02 | Level transmitter in Spray dryer infeed tank | Level transmitter | 4 - 20 mA | 0 - 10 m. | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-401 | P1-TBAI1-4(B) | C1/C1S10 | C1S10-7/P1-TBAI1-4(B) | P1-TBAI1-4(B)/C1S10-7 | LT-40203_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
89 | LT-61301 | - | 325-01-613-PD-01 | Level powder in silo | Level transmitter | 4 - 20 mA | - | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-618 | P4-TBAI2-7(B) | C4/C4S6 | C4S6-15/P4-TBAI2-7(B) | P4-TBAI2-7(B)/C4S6-15 | LT-61301_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
90 | pHT-40201 | pHT-40101 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 1 | pH Analyzer | 4 - 20 mA | 0-14 | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-401 | P1-TBAI1-7(B) | C1/C1S10 | C1S10-15/P1-TBAI1-7(B) | P1-TBAI1-7(B)/C1S10-15 | pHT-40201_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
91 | pHT-40202 | pHT-40102 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 2 | pH Analyzer | 4 - 20 mA | 0-14 | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-401 | P1-TBAI1-8(B) | C1/C1S10 | C1S10-17/P1-TBAI1-8(B) | P1-TBAI1-8(B)/C1S10-17 | pHT-40202_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
92 | PSL-60220 | - | 325-01-602-PD-04 | Gas Pressure Switch Low for Spray Chamber (CHAM-21) | Pressure switch | Dry Contact | -0.01 mbar | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-3 | C2/C2S2 | C2S2-3/P2-TBDI2-3 | P2-TBDI2-3/C2S2-3 | PSL-60220_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
93 | PSL-61301 |  | 325-01-613-PD-01 | Pressure alarm low | Pressure switch | Dry Contact | 0.3-0.7barg | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-618 | P3-TBDI3-6 | C3/C3S3 | C3S3-6/P3-TBDI3-6 | P3-TBDI3-6/C3S3-6 | PSL-61301_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
94 | PSL-61302 | - | 325-01-613-PD-01 | Pressure alarm low | Pressure switch | Dry Contact | 40 mbarg | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-618 | P3-TBDI3-7 | C3/C3S3 | C3S3-7/P3-TBDI3-7 | P3-TBDI3-7/C3S3-7 | PSL-61302_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
95 | PSL-61305 | - | 325-01-613-PD-03 | Pressure alarm low | Pressure switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBDI2-1 | C3/C3S2 | C3S2-1/P3-TBDI2-1 | P3-TBDI2-1/C3S2-1 | PSL-61305_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
96 | PSL-61306 | - | 325-01-613-PD-05 | Pressure alarm low | Pressure switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBDI2-2 | C3/C3S2 | C3S2-2/P3-TBDI2-2 | P3-TBDI2-2/C3S2-2 | PSL-61306_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
97 | PSL-61311 | - | 325-01-613-PD-04 | Pressure alarm low | Pressure switch | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-618 | P3-TBDI3-8 | C3/C3S3 | C3S3-8/P3-TBDI3-8 | P3-TBDI3-8/C3S3-8 | PSL-61311_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
98 | PT-40201 | - | 325-01-402-PD-02 | Pressure Transmitter for Inlet Filter Strainer (FSTR-11) | Pressure Transmitter | 4 - 20 mA | -100 to 500 mBar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-401 | P1-TBAI1-9(B) | C1/C1S10 | C1S10-19/P1-TBAI1-9(B) | P1-TBAI1-9(B)/C1S10-19 | PT-40201_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
99 | PT-40202 | - | 325-01-402-PD-02 | Feed Slurry Pressure Transmitter for Pipe (PIPE) | Pressure Transmitter | 4 - 20 mA | 0 - 10'barg | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-401 | P1-TBAI1-10(B) | C1/C1S10 | C1S10-21/P1-TBAI1-10(B) | P1-TBAI1-10(B)/C1S10-21 | PT-40202_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
100 | PT-40222 |  | 325-01-402-PD-02 | Jet Cooker | Pressure Transmitter | 4 - 20 mA | 0 - 12'barg | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-402 | P2-TBAI1-5(B) | C2/C2S9 | C2S9-11/P2-TBAI1-5(B) | P2-TBAI1-5(B)/C2S9-11 | PT-40222_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
101 | PT-60201 | - | 325-01-602-PD-02 | Steam feed to Spray dryer | Pressure Transmitter | 4 - 20 mA | 0 - 20 bar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI3-3(B) | C3/C3S8 | C3S8-5/P3-TBAI3-3(B) | P3-TBAI3-3(B)/C3S8-5 | PT-60201_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
102 | PT-60202 | - | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter | 4 - 20 mA | 0 to 500 bar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-401 | P1-TBAI1-11(B) | C1/C1S10 | C1S10-23/P1-TBAI1-11(B) | P1-TBAI1-11(B)/C1S10-23 | PT-60202_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
103 | PT-60203 | - | 325-01-602-PD-08 | Gas Pressure Transmitter for Cool Air Duct (DTCA-32) | Pressure Transmitter | 4 - 20 mA | 0 - 0.1 mbar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-601 | P1-TBAI2-6(B) | C1/C1S11 | C1S11-13/P1-TBAI2-6(B) | P1-TBAI2-6(B)/C1S11-13 | PT-60203_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
104 | PT-60210 | - | 325-01-602-PD-03 | Gas Pressure Transmitter for Hot Air Duct (DTHA-21) | Pressure Transmitter | 4 - 20 mA | 0 - 0.1 mbar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBAI2-4(B) | C2/C2S10 | C2S10-7/P2-TBAI2-4(B) | P2-TBAI2-4(B)/C2S10-7 | PT-60210_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
105 | PT-60215 | - | 325-01-602-PD-03 | 15% Polypropylene Glycol Pressure Indicator Transmitter for Heat Recovery Pumping Skid (PUCF-21) | Pressure Transmitter | 4 - 20 mA | 0 - 6 bar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBAI2-5(B) | C2/C2S10 | C2S10-11/P2-TBAI2-5(B) | P2-TBAI2-5(B)/C2S10-11 | PT-60215_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
106 | PT-60216 | - | 325-01-602-PD-03 | Gas Pressure Transmitter for Combustion Air Burner Duct (DTCB-21) | Pressure Transmitter | 4 - 20 mA | 0 - 100 mbar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBAI2-6(B) | C2/C2S10 | C2S10-13/P2-TBAI2-6(B) | P2-TBAI2-6(B)/C2S10-13 | PT-60216_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
107 | PT-60220 | - | 325-01-602-PD-04 | Gas Pressure Transmitter for Chamber (CHAM-21) | Pressure Transmitter | 4 - 20 mA | -100 - 100 mbar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-608 | P4-TBAI1-9(B) | C4/C4S5 | C4S5-19/P4-TBAI1-9(B) | P4-TBAI1-9(B)/C4S5-19 | PT-60220_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
108 | PT-60221 | - | 325-01-602-PD-04 | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25) | Pressure Transmitter | 4 - 20 mA | 0 - 0.1 mbar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI3-5(B) | C3/C3S8 | C3S8-11/P3-TBAI3-5(B) | P3-TBAI3-5(B)/C3S8-11 | PT-60221_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
109 | PT-60230 | - | 325-01-602-PD-04 | Gas Pressure Transmitter for Conveying Duct (DTCO-21) | Pressure Transmitter | 4 - 20 mA | 0 - 0.1 mbar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-603 | P4-TBAI1-1(B) | C4/C4S5 | C4S5-1/P4-TBAI1-1(B) | P4-TBAI1-1(B)/C4S5-1 | PT-60230_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
110 | PT-60231 | - | 325-01-602-PD-04 | Gas Pressure Transmitter for Cyclone Exhaust Duct (DTCE-21) | Pressure Transmitter | 4 - 20 mA | -100 to 200 mbar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-603 | P4-TBAI1-2(B) | C4/C4S5 | C4S5-3/P4-TBAI1-2(B) | P4-TBAI1-2(B)/C4S5-3 | PT-60231_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
111 | PT-60240 | - | 325-01-602-PD-05 | Gas Pressure Transmitter for Bag House Exhaust Duct (DTEX-22) | Pressure Transmitter | 4 - 20 mA | -100 to 200 mbar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBAI2-7(B) | C2/C2S10 | C2S10-15/P2-TBAI2-7(B) | P2-TBAI2-7(B)/C2S10-15 | PT-60240_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
112 | PT-60241 | - | 325-01-602-PD-05 | Gas Pressure Transmitter for Exhaust Fan (FANE-21) | Pressure Transmitter | 4 - 20 mA | 0 - 0.1 mbar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBAI2-8(B) | C2/C2S10 | C2S10-17/P2-TBAI2-8(B) | P2-TBAI2-8(B)/C2S10-17 | PT-60241_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
113 | PT-60204 | PT-61101 | 325-01-602-PD-10 | Pressure transmitter | Pressure Transmitter | 4 - 20 mA | 0 - 10 barg | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-601 | P1-TBAI2-7(B) | C1/C1S11 | C1S11-15/P1-TBAI2-7(B) | P1-TBAI2-7(B)/C1S11-15 | PT-60204_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
114 | PT-61301 | - | 325-01-613-PD-01 | Pressure in silo | Pressure Transmitter | 4 - 20 mA | 0 - 1 barg | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-618 | P4-TBAI2-8(B) | C4/C4S6 | C4S6-17/P4-TBAI2-8(B) | P4-TBAI2-8(B)/C4S6-17 | PT-61301_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
115 | PT-61302 | - | 325-01-613-PD-03 | Pressure in vacuum line | Pressure Transmitter | 4 - 20 mA | -100 - 100 mbarg | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-612 | P3-TBAI4-9(B) | C3/C3S9 | C3S9-19/P3-TBAI4-9(B) | P3-TBAI4-9(B)/C3S9-19 | PT-61302_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
116 | PT-61303 | - | 325-01-613-PD-01 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) | Pressure Transmitter | 4 - 20 mA | -100 to 200 mbar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-618 | P3-TBAI4-1(B) | C3/C3S9 | C3S9-1/P3-TBAI4-1(B) | P3-TBAI4-1(B)/C3S9-1 | PT-61303_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
117 | PT-61304 | - | 325-01-613-PD-01 | Gas Pressure Transmitter for Storage Bin Cyclone Inlet Duct (CYCL-31) | Pressure Transmitter | 4 - 20 mA | -100 to 200 mbar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-618 | P4-TBAI2-10(B) | C4/C4S6 | C4S6-21/P4-TBAI2-10(B) | P4-TBAI2-10(B)/C4S6-21 | PT-61304_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
118 | PT-61305 | - | 325-01-613-PD-01 | Gas Pressure Transmitter for Exhaust Duct (DTEX-31) | Pressure Transmitter | 4 - 20 mA | -100 to 200 mbar | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-618 | P4-TBAI2-11(B) | C4/C4S6 | C4S6-23/P4-TBAI2-11(B) | P4-TBAI2-11(B)/C4S6-23 | PT-61305_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
119 | PT-61309 | - | 325-01-613-PD-04 | Pressure transmitter | Pressure Transmitter | 4 - 20 mA | 0 - 10 barg | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-612 | P3-TBAI4-10(B) | C3/C3S9 | C3S9-21/P3-TBAI4-10(B) | P3-TBAI4-10(B)/C3S9-21 | PT-61309_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
120 | PCV-60201 | PV-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic Control valve | 4 - 20 mA | 0 - 100% | TYP-AO-01 | TBAO | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAO1-4 | C3/C3S12 | C3S12-19/P3-TBAO1-4 | P3-TBAO1-4/C3S12-19 | PV-60201_AO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
121 | SV-40201 | SV-40101 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 1 | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBRL1-25 | C1/C1S8 | C1S8-27/P1-TBRL1-25 | P1-TBRL1-25/C1S8-27 | SV-40201_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
122 | SV-40202 | SV-40102 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 2 | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBRL1-26 | C1/C1S8 | C1S8-28/P1-TBRL1-26 | P1-TBRL1-26/C1S8-28 | SV-40202_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
123 | SV-40203 | SV-40103 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 1 | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBRL1-27 | C1/C1S8 | C1S8-29/P1-TBRL1-27 | P1-TBRL1-27/C1S8-29 | SV-40203_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
124 | SV-40204 | SV-40104 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 2 | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBRL1-28 | C1/C1S8 | C1S8-30/P1-TBRL1-28 | P1-TBRL1-28/C1S8-30 | SV-40204_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
125 | SV-60220 | - | 325-01-602-PD-04 | PA On/Off Valve for Chamber PSE purge air (CHAM-21) | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-606 | P3-TBRL1-9 | C3/C3S4 | C3S4-9/P3-TBRL1-9 | P3-TBRL1-9/C3S4-9 | SV-60220_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
126 | SV-60230 | - | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 27 (CYCL-21) | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBRL2-19 | C1/C1S9 | C1S9-21/P1-TBRL2-19 | P1-TBRL2-19/C1S9-21 | SV-60230_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
127 | SV-60231 | - | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 28 (CYCL-22) | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBRL2-22 | C1/C1S9 | C1S9-24/P1-TBRL2-22 | P1-TBRL2-22/C1S9-24 | SV-60231_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
128 | SV-60240A | - | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29A (BGHS-21) | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBRL2-21 | C1/C1S9 | C1S9-23/P1-TBRL2-21 | P1-TBRL2-21/C1S9-23 | SV-60240A_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
129 | SV-60240B | - | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29B (BGHS-21) | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBRL2-23 | C1/C1S9 | C1S9-25/P1-TBRL2-23 | P1-TBRL2-23/C1S9-25 | SV-60240B_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
130 | SV-60240C | - | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29C (BGHS-21) | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBRL2-24 | C1/C1S9 | C1S9-26/P1-TBRL2-24 | P1-TBRL2-24/C1S9-26 | SV-60240C_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
131 | SV-61301 | - | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-618 | P3-TBRL2-3 | C3/C3S5 | C3S5-3/P3-TBRL2-3 | P3-TBRL2-3/C3S5-3 | SV-61301_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
132 | SV-61302 | - | 325-01-613-PD-01 | Air service | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-618 | P3-TBRL2-4 | C3/C3S5 | C3S5-4/P3-TBRL2-4 | P3-TBRL2-4/C3S5-4 | SV-61302_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
132 | SV-61306 |  | 325-01-613-PD-01 | Air service | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-618 | P3-TBRL2-8 | C3/C3S5 | C3S5-8/P3-TBRL2-8 | P3-TBRL2-8/C3S5-8 | SV-61306_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
133 | SV-61303 | - | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-618 | P3-TBRL2-5 | C3/C3S5 | C3S5-5/P3-TBRL2-5 | P3-TBRL2-5/C3S5-5 | SV-61303_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
134 | SV-61305 | - | 325-01-613-PD-01 | Air service | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-618 | P3-TBRL2-7 | C3/C3S5 | C3S5-7/P3-TBRL2-7 | P3-TBRL2-7/C3S5-7 | SV-61305_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
135 | SV-61308 | - | 325-01-613-PD-03 | Timer compress air pluse solenoid valve | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBRL1-20 | C3/C3S4 | C3S4-22/P3-TBRL1-20 | P3-TBRL1-20/C3S4-22 | SV-61308_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
136 | SV-61309 | - | 325-01-613-PD-03 | Air service | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBRL1-21 | C3/C3S4 | C3S4-23/P3-TBRL1-21 | P3-TBRL1-21/C3S4-23 | SV-61309_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
137 | SV-61310 | - | 325-01-613-PD-05 | Timer compress air pluse solenoid valve | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBRL1-22 | C3/C3S4 | C3S4-24/P3-TBRL1-22 | P3-TBRL1-22/C3S4-24 | SV-61310_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
138 | SV-61311 | - | 325-01-613-PD-05 | Air service | Solenoid valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBRL1-23 | C3/C3S4 | C3S4-25/P3-TBRL1-23 | P3-TBRL1-23/C3S4-25 | SV-61311_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
139 | TSH-60230 | - | 325-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | Temperature Switch | Dry Contact | 0 - 140 C | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-4 | C2/C2S2 | C2S2-4/P2-TBDI2-4 | P2-TBDI2-4/C2S2-4 | TSH-60230_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
140 | TSH-60240 | - | 325-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | Temperature Switch | Dry Contact | 0 - 140 C | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-5 | C2/C2S2 | C2S2-5/P2-TBDI2-5 | P2-TBDI2-5/C2S2-5 | TSH-60240_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
141 | TT-40221 |  | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter | 4 - 20 mA | 0 - 120 C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-402 | P2-TBAI1-6(B) | C2/C2S9 | C2S9-13/P2-TBAI1-6(B) | P2-TBAI1-6(B)/C2S9-13 | TT-40221_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
142 | TT-40222 |  | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter | 4 - 20 mA | 0 - 200 C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-402 | P2-TBAI1-7(B) | C2/C2S9 | C2S9-15/P2-TBAI1-7(B) | P2-TBAI1-7(B)/C2S9-15 | TT-40222_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
143 | TT-60201 | - | 325-01-602-PD-02 | Steam feed to Spray dryer | Temperature Transmitter | 4 - 20 mA | 0 - 300 C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI3-8(B) | C3/C3S8 | C3S8-17/P3-TBAI3-8(B) | P3-TBAI3-8(B)/C3S8-17 | TT-60201_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
144 | TT-60210 | - | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBAI2-9(B) | C2/C2S10 | C2S10-19/P2-TBAI2-9(B) | P2-TBAI2-9(B)/C2S10-19 | TT-60210_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
145 | TT-60210A | TT-60212A | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter | 4 - 20 mA | 0 - 100 C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBAI2-10(B) | C2/C2S10 | C2S10-21/P2-TBAI2-10(B) | P2-TBAI2-10(B)/C2S10-21 | TT-60210A_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
146 | TT-60210B | TT-60212B | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter | 4 - 20 mA | 0 - 100 C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBAI2-11(B) | C2/C2S10 | C2S10-23/P2-TBAI2-11(B) | P2-TBAI2-11(B)/C2S10-23 | TT-60210B_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
147 | TT-60211 | - | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBAI2-12(B) | C2/C2S10 | C2S10-25/P2-TBAI2-12(B) | P2-TBAI2-12(B)/C2S10-25 | TT-60211_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
148 | TT-60214 | - | 325-01-602-PD-03 | Steam Temperature Transmitter for Cold Air Duct (DTCA-23) | Temperature Transmitter | 4 - 20 mA | -10 to 250°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBAI2-15(B) | C2/C2S10 | C2S10-33/P2-TBAI2-15(B) | P2-TBAI2-15(B)/C2S10-33 | TT-60214_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
149 | TT-60215A | - | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter | 4 - 20 mA | -10 to 150°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P2-TBAI2-16(B) | C2/C2S10 | C2S10-35/P2-TBAI2-16(B) | P2-TBAI2-16(B)/C2S10-35 | TT-60215A_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
150 | TT-60215B | - | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter | 4 - 20 mA | -10 to 150°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P3-TBAI1-1(B) | C3/C3S6 | C3S6-1/P3-TBAI1-1(B) | P3-TBAI1-1(B)/C3S6-1 | TT-60215B_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
151 | TT-60216 | - | 325-01-602-PD-03 | Gas Temperature Transmitter for Combustion Air Burner Duct (DTCB-21) | Temperature Transmitter | 4 - 20 mA | 0 - 200'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P3-TBAI1-2(B) | C3/C3S6 | C3S6-3/P3-TBAI1-2(B) | P3-TBAI1-2(B)/C3S6-3 | TT-60216_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
152 | TT-60220 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-608 | P4-TBAI1-10(B) | C4/C4S5 | C4S5-21/P4-TBAI1-10(B) | P4-TBAI1-10(B)/C4S5-21 | TT-60220_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
153 | TT-60221 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-608 | P4-TBAI1-11(B) | C4/C4S5 | C4S5-23/P4-TBAI1-11(B) | P4-TBAI1-11(B)/C4S5-23 | TT-60221_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
154 | TT-60222 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-608 | P4-TBAI1-12(B) | C4/C4S5 | C4S5-25/P4-TBAI1-12(B) | P4-TBAI1-12(B)/C4S5-25 | TT-60222_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
155 | TT-60223 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-608 | P4-TBAI1-13(B) | C4/C4S5 | C4S5-29/P4-TBAI1-13(B) | P4-TBAI1-13(B)/C4S5-29 | TT-60223_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
156 | TT-60224 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-603 | P4-TBAI1-3(B) | C4/C4S5 | C4S5-5/P4-TBAI1-3(B) | P4-TBAI1-3(B)/C4S5-5 | TT-60224_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
157 | TT-60225 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-603 | P4-TBAI1-4(B) | C4/C4S5 | C4S5-7/P4-TBAI1-4(B) | P4-TBAI1-4(B)/C4S5-7 | TT-60225_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
158 | TT-60226 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-603 | P4-TBAI1-5(B) | C4/C4S5 | C4S5-11/P4-TBAI1-5(B) | P4-TBAI1-5(B)/C4S5-11 | TT-60226_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
159 | TT-60227 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-603 | P4-TBAI1-6(B) | C4/C4S5 | C4S5-13/P4-TBAI1-6(B) | P4-TBAI1-6(B)/C4S5-13 | TT-60227_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
160 | TT-60230 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Conveying Duct (DTCO-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-603 | P4-TBAI1-7(B) | C4/C4S5 | C4S5-15/P4-TBAI1-7(B) | P4-TBAI1-7(B)/C4S5-15 | TT-60230_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
161 | TT-60240 | - | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Fan (FANE-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P3-TBAI1-3(B) | C3/C3S6 | C3S6-5/P3-TBAI1-3(B) | P3-TBAI1-3(B)/C3S6-5 | TT-60240_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
162 | TT-60241A | - | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter | 4 - 20 mA | 0 - 100 C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P3-TBAI1-4(B) | C3/C3S6 | C3S6-7/P3-TBAI1-4(B) | P3-TBAI1-4(B)/C3S6-7 | TT-60241A_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
163 | TT-60241B | - | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter | 4 - 20 mA | 0 - 100 C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P3-TBAI1-5(B) | C3/C3S6 | C3S6-11/P3-TBAI1-5(B) | P3-TBAI1-5(B)/C3S6-11 | TT-60241B_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
164 | TT-60245 | - | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Stack (DTXS-21) | Temperature Transmitter | 4 - 20 mA | -10 to 150°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-608 | P3-TBAI3-16(B) | C3/C3S8 | C3S8-35/P3-TBAI3-16(B) | P3-TBAI3-16(B)/C3S8-35 | TT-60245_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
165 | TT-60202 | TT-60702 | 325-01-602-PD-07 | Compress air temp to camera | Temperature Transmitter | 4 - 20 mA | 0 - 40 C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI3-9(B) | C3/C3S8 | C3S8-19/P3-TBAI3-9(B) | P3-TBAI3-9(B)/C3S8-19 | TT-60202_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
166 | TT-61301 | - | 325-01-613-PD-01 | Gas Temperature Transmitter for Cold Air Duct (DTCA-32) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-618 | P4-TBAI2-12(B) | C4/C4S6 | C4S6-25/P4-TBAI2-12(B) | P4-TBAI2-12(B)/C4S6-25 | TT-61301_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
167 | TT-61302 | - | 325-01-613-PD-01 | Gas and Powder Temperature Transmitter for Cooling Cyclone (CYCL-31) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-618 | P4-TBAI2-13(B) | C4/C4S6 | C4S6-29/P4-TBAI2-13(B) | P4-TBAI2-13(B)/C4S6-29 | TT-61302_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
168 | TCV-40222 |  | 325-01-402-PD-02 | Jet Cooker | Automatic Control valve | 4 - 20 mA | 0 - 100% | TYP-AO-01 | TBAO | LOOP DIAGRAM WRING.dwg | JB-402 | P3-TBAO1-1 | C3/C3S12 | C3S12-3/P3-TBAO1-1 | P3-TBAO1-1/C3S12-3 | TCV-40222_AO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
169 | TCV-60214 | TV-60214 | 325-01-602-PD-03 | Steam Temperature Valve for Pre-Heat Steam Heat Exchanger (HXCH-21) | Automatic Control valve | 4 - 20 mA | 0 - 100% | TYP-AO-01 | TBAO | LOOP DIAGRAM WRING.dwg | JB-602 | P3-TBAO1-3 | C3/C3S12 | C3S12-13/P3-TBAO1-3 | P3-TBAO1-3/C3S12-13 | TV-60214_AO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
170 | TCV-60202 | TV-60702 | 325-01-602-PD-07 | Chiller water control valve | 3-way Control valve | 4 - 20 mA | 0 - 100% | TYP-AO-01 | TBAO | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
171 | VT-60210A | - | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter | 4 - 20 mA | mm/sec | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P3-TBAI1-6(B) | C3/C3S6 | C3S6-13/P3-TBAI1-6(B) | P3-TBAI1-6(B)/C3S6-13 | VT-60210A_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
172 | VT-60210B | - | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter | 4 - 20 mA | mm/sec | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P3-TBAI1-7(B) | C3/C3S6 | C3S6-15/P3-TBAI1-7(B) | P3-TBAI1-7(B)/C3S6-15 | VT-60210B_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
173 | VT-60241A | - | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter | 4 - 20 mA | mm/sec | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P3-TBAI1-8(B) | C3/C3S6 | C3S6-17/P3-TBAI1-8(B) | P3-TBAI1-8(B)/C3S6-17 | VT-60241A_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
174 | VT-60241B | - | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter | 4 - 20 mA | mm/sec | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-602 | P3-TBAI1-9(B) | C3/C3S6 | C3S6-19/P3-TBAI1-9(B) | P3-TBAI1-9(B)/C3S6-19 | VT-60241B_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
175 | XT-60201 | XT-60301 | 325-01-402-PD-03 | LEL gas analyzer | Gas detector | 4 - 20 mA | 0-10%LEL | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | IS-JB-608 | P4-TBAI1-14(B) | C4/C4S5 | C4S5-31/P4-TBAI1-14(B) | P4-TBAI1-14(B)/C4S5-31 | XT-60201_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
176 | XA-60201 | XA-60301 | 325-01-402-PD-03 | LEL gas Buzzer Alarm | Gas detector | 4 - 20 mA | 0-10%LEL | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | IS-JB-608 | P4-TBRL1-9 | C4/C4S4 | C4S4-9/P4-TBRL1-9 | P4-TBRL1-9/C4S4-9 | XA-60201_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
177 | XT-92201 | - | 325-01-923-PD-03 | LEL gas analyzer | Gas detector | 4 - 20 mA | 0-10%LEL | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | RIO-200 | P5-TBAI1-8(B) | C5/C5S4 | C5S4-17/P5-TBAI1-8(B) | P5-TBAI1-8(B)/C5S4-17 | XT-92201_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
178 | XA-92201 | - | 325-01-923-PD-03 | LEL gas Buzzer Alarm | Gas detector | 4 - 20 mA | 0-10%LEL | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBRL1-1 | C5/C5S3 | C5S3-1/P5-TBRL1-1 | P5-TBRL1-1/C5S3-1 | XA-92201_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
179 | XV-40201A | XV-40101A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI1-27 | C1/C1S4 | C1S4-29/P1-TBDI1-27 | P1-TBDI1-27/C1S4-29 | XV-40201A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
180 | XV-40201B | XV-40101B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI1-29 | C1/C1S4 | C1S4-31/P1-TBDI1-29 | P1-TBDI1-29/C1S4-31 | XV-40201B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
181 | XV-40201C | XV-40101C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI1-31 | C1/C1S4 | C1S4-33/P1-TBDI1-31 | P1-TBDI1-31/C1S4-33 | XV-40201C_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
182 | XV-40201D | XV-40101D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-1 | C1/C1S5 | C1S5-1/P1-TBDI2-1 | P1-TBDI2-1/C1S5-1 | XV-40201D_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
183 | XV-40201E | XV-40101E | 325-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-3 | C1/C1S5 | C1S5-3/P1-TBDI2-3 | P1-TBDI2-3/C1S5-3 | XV-40201E_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
184 | XV-40201F | XV-40101F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-5 | C1/C1S5 | C1S5-5/P1-TBDI2-5 | P1-TBDI2-5/C1S5-5 | XV-40201F_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
185 | XV-40201G | XV-40101G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-7 | C1/C1S5 | C1S5-7/P1-TBDI2-7 | P1-TBDI2-7/C1S5-7 | XV-40201G_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
186 | XV-40201H | XV-40101H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-9 | C1/C1S5 | C1S5-9/P1-TBDI2-9 | P1-TBDI2-9/C1S5-9 | XV-40201H_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
187 | XV-40202A | XV-40102A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-11 | C1/C1S5 | C1S5-11/P1-TBDI2-11 | P1-TBDI2-11/C1S5-11 | XV-40202A_DI_2 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
188 | XV-40202B | XV-40102B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-12 | C1/C1S5 | C1S5-12/P1-TBDI2-12 | P1-TBDI2-12/C1S5-12 | XV-40202B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
189 | XV-40202C | XV-40102C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-14 | C1/C1S5 | C1S5-14/P1-TBDI2-14 | P1-TBDI2-14/C1S5-14 | XV-40202C_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
190 | XV-40202D | XV-40102D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-16 | C1/C1S5 | C1S5-16/P1-TBDI2-16 | P1-TBDI2-16/C1S5-16 | XV-40202D_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
191 | XV-40202E | XV-40102E | 325-01-402-PD-01 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-18 | C1/C1S5 | C1S5-20/P1-TBDI2-18 | P1-TBDI2-18/C1S5-20 | XV-40202E_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
192 | XV-40202F | XV-40102F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-21 | C1/C1S5 | C1S5-23/P1-TBDI2-21 | P1-TBDI2-21/C1S5-23 | XV-40202F_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
193 | XV-40202G | XV-40102G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-23 | C1/C1S5 | C1S5-25/P1-TBDI2-23 | P1-TBDI2-23/C1S5-25 | XV-40202G_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
194 | XV-40202H | XV-40102H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-25 | C1/C1S5 | C1S5-27/P1-TBDI2-25 | P1-TBDI2-25/C1S5-27 | XV-40202H_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
195 | XV-40203B | XV-40201B | 325-01-402-PD-02 | Slurry feed-out Spray dryer infeed tank | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-27 | C1/C1S5 | C1S5-29/P1-TBDI2-27 | P1-TBDI2-27/C1S5-29 | XV-40203B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
196 | XV-40203C | XV-40201C | 325-01-402-PD-02 | Water washing line outlet Spray dryer infeed tank | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-29 | C1/C1S5 | C1S5-31/P1-TBDI2-29 | P1-TBDI2-29/C1S5-31 | XV-40203C_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
197 | XV-40203D | XV-40201D | 325-01-402-PD-02 | CIP water washing Spray dryer infeed tank | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI2-31 | C1/C1S5 | C1S5-33/P1-TBDI2-31 | P1-TBDI2-31/C1S5-33 | XV-40203D_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
198 | XV-40203E | XV-40201E | 325-01-402-PD-02 | CIP hight pressure water washing Spray dryer infeed tank | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-401 | P1-TBDI3-1 | C1/C1S6 | C1S6-1/P1-TBDI3-1 | P1-TBDI3-1/C1S6-1 | XV-40203E_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
199 | XV-40203F |  | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-7 | C2/C2S1 | C2S1-7/P2-TBDI1-7 | P2-TBDI1-7/C2S1-7 | XV-40203F_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
200 | XV-40204B |  | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-9 | C2/C2S1 | C2S1-9/P2-TBDI1-9 | P2-TBDI1-9/C2S1-9 | XV-40204B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
201 | XV-40204C |  | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-11 | C2/C2S1 | C2S1-11/P2-TBDI1-11 | P2-TBDI1-11/C2S1-11 | XV-40204C_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
202 | XV-40205A |  | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-13 | C2/C2S1 | C2S1-13/P2-TBDI1-13 | P2-TBDI1-13/C2S1-13 | XV-40205A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
203 | XV-40205B |  | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-15 | C2/C2S1 | C2S1-15/P2-TBDI1-15 | P2-TBDI1-15/C2S1-15 | XV-40205B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
204 | XV-40205C |  | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-17 | C2/C2S1 | C2S1-19/P2-TBDI1-17 | P2-TBDI1-17/C2S1-19 | XV-40205C_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
205 | XV-40205D |  | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-19 | C2/C2S1 | C2S1-21/P2-TBDI1-19 | P2-TBDI1-19/C2S1-21 | XV-40205D_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
206 | XV-40205F |  | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-21 | C2/C2S1 | C2S1-23/P2-TBDI1-21 | P2-TBDI1-21/C2S1-23 | XV-40205F_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
207 | XV-40222 |  | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-402 | P2-TBDI1-23 | C2/C2S1 | C2S1-25/P2-TBDI1-23 | P2-TBDI1-23/C2S1-25 | XV-40222_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
208 | XV-60201 | - | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-17 | C2/C2S3 | C2S3-19/P2-TBDI3-17 | P2-TBDI3-17/C2S3-19 | XV-60201_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
209 | XV-60251 | - | 325-01-602-PD-01 | Liquid On/Off Valve for Drain Pipe (PIPE) | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBRL2-26 | C1/C1S9 | C1S9-28/P1-TBRL2-26 | P1-TBRL2-26/C1S9-28 | XV-60251_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
210 | XV-60214 | XV-60301 | 325-01-602-PD-03 | Steam feed to Spray dryer | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-20 | C2/C2S2 | C2S2-22/P2-TBDI2-20 | P2-TBDI2-20/C2S2-22 | XV-60214_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
211 | XV-60202 | XV-61101 | 325-01-602-PD-11 | High Pressure Water On/Off Valve for Drain Pipe | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-14 | C1/C1S7 | C1S7-14/P1-TBDI4-14 | P1-TBDI4-14/C1S7-14 | XV-60202_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
212 | XV-61301 | HV-61301 | 325-01-613-PD-01 | Product feed-out Packing silo | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-618 | P3-TBDI3-11 | C3/C3S3 | C3S3-11/P3-TBDI3-11 | P3-TBDI3-11/C3S3-11 | XV-61301_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
213 | XV-61302 | - | 325-01-613-PD-02 | Dust collector feed vent | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBDI2-14 | C3/C3S2 | C3S2-14/P3-TBDI2-14 | P3-TBDI2-14/C3S2-14 | XV-61302_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
214 | XV-61303 | - | 325-01-613-PD-02 | Dust collector feed from packer | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBDI2-16 | C3/C3S2 | C3S2-16/P3-TBDI2-16 | P3-TBDI2-16/C3S2-16 | XV-61303_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
215 | DV-61301 |  | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61301 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-618 | P3-TBDI3-1 | C3/C3S3 | C3S3-1/P3-TBDI3-1 | P3-TBDI3-1/C3S3-1 | DV-61301_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
216 | DV-61302 |  | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61302 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-618 | P3-TBDI3-3 | C3/C3S3 | C3S3-3/P3-TBDI3-3 | P3-TBDI3-3/C3S3-3 | DV-61302_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
217 | ZS-60201A | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-608 | P4-TBDI1-17 | C4/C4S1 | C4S1-19/P4-TBDI1-17 | P4-TBDI1-17/C4S1-19 | ZS-60201A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
218 | ZS-60201B | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-608 | P4-TBDI1-18 | C4/C4S1 | C4S1-20/P4-TBDI1-18 | P4-TBDI1-18/C4S1-20 | ZS-60201B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
219 | ZS-60201C | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-603 | P4-TBDI1-9 | C4/C4S1 | C4S1-9/P4-TBDI1-9 | P4-TBDI1-9/C4S1-9 | ZS-60201C_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
220 | ZS-60201D | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-603 | P4-TBDI1-10 | C4/C4S1 | C4S1-10/P4-TBDI1-10 | P4-TBDI1-10/C4S1-10 | ZS-60201D_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
221 | ZS-60201E | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-603 | P4-TBDI1-11 | C4/C4S1 | C4S1-11/P4-TBDI1-11 | P4-TBDI1-11/C4S1-11 | ZS-60201E_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
222 | ZS-60229 |  | 325-01-602-PD-04 | Limit Switch for CY-60230 (Door Service) | Limit Switch | Switch PNP | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-603 | P4-TBDI1-12 | C4/C4S1 | C4S1-12/P4-TBDI1-12 | P4-TBDI1-12/C4S1-12 | ZS-60229_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
223 | ZS-60230 |  | 325-01-602-PD-04 | Limit Switch for CY-60231 (Door Service) | Limit Switch | Switch PNP | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-603 | P4-TBDI1-13 | C4/C4S1 | C4S1-13/P4-TBDI1-13 | P4-TBDI1-13/C4S1-13 | ZS-60230_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
224 | ZS-60231A | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Spectacle Inserted) | Limit Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-603 | P4-TBDI1-14 | C4/C4S1 | C4S1-14/P4-TBDI1-14 | P4-TBDI1-14/C4S1-14 | ZS-60231A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
225 | ZS-60231B | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Blind Inserted) | Limit Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-603 | P4-TBDI1-15 | C4/C4S1 | C4S1-15/P4-TBDI1-15 | P4-TBDI1-15/C4S1-15 | ZS-60231B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
226 | ZS-60231C | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Spool Inserted) | Limit Switch | Switch PNP | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-608 | P4-TBDI1-19 | C4/C4S1 | C4S1-21/P4-TBDI1-19 | P4-TBDI1-19/C4S1-21 | ZS-60231C_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
227 | ZS-60231D | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Blind Inserted) | Limit Switch | Switch PNP | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-608 | P4-TBDI1-20 | C4/C4S1 | C4S1-22/P4-TBDI1-20 | P4-TBDI1-20/C4S1-22 | ZS-60231D_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
228 | ZS-60231E | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Spool Inserted) | Limit Switch | Switch PNP | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-608 | P4-TBDI1-21 | C4/C4S1 | C4S1-23/P4-TBDI1-21 | P4-TBDI1-21/C4S1-23 | ZS-60231E_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
229 | ZS-60231F | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Blind Inserted) | Limit Switch | Switch PNP | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-608 | P4-TBDI1-22 | C4/C4S1 | C4S1-24/P4-TBDI1-22 | P4-TBDI1-22/C4S1-24 | ZS-60231F_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
230 | ZS-60240 |  | 325-01-602-PD-05 | Limit Switch for FA-60240 (Door Service) | Limit Switch | Switch PNP | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-608 | P4-TBDI1-23 | C4/C4S1 | C4S1-25/P4-TBDI1-23 | P4-TBDI1-23/C4S1-25 | ZS-60240_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
231 | ZS-61310 | - | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-618 | P4-TBDI3-12 | C4/C4S3 | C4S3-12/P4-TBDI3-12 | P4-TBDI3-12/C4S3-12 | ZS-61310_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
232 | ZS-61311 | - | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-618 | P4-TBDI3-13 | C4/C4S3 | C4S3-13/P4-TBDI3-13 | P4-TBDI3-13/C4S3-13 | ZS-61311_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
233 | ZS-61312 | - | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-612 | P4-TBDI2-14 | C4/C4S2 | C4S2-14/P4-TBDI2-14 | P4-TBDI2-14/C4S2-14 | ZS-61312_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
234 | ZS-61313 | - | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-612 | P4-TBDI2-15 | C4/C4S2 | C4S2-15/P4-TBDI2-15 | P4-TBDI2-15/C4S2-15 | ZS-61313_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
235 |  | - | - | Lototo-01 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
236 |  | - | - | Lototo-02 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
237 |  | - | - | Lototo-03 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
238 |  | - | - | Lototo-04 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
239 |  | - | - | Lototo-05 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
240 |  | - | - | Lototo-06 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
241 |  | - | - | Lototo-07 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
242 |  | - | - | Lototo-08 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
243 |  | - | - | Lototo-09 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
244 |  | - | - | Lototo-10 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
245 |  | - | - | Lototo-11 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
246 |  | - | - | Lototo-12 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
246 | ES-60201 |  | - | Emergency stop activated @ Spray Nozzle 7th Floor | E-Stop Swtich | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
246 | ES-60202 |  | - | Emergency stop activated @ Sight glass 6th Floor | E-Stop Swtich | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI3-17 | C1/C1S6 | C1S6-19/P1-TBDI3-17 | P1-TBDI3-17/C1S6-19 | ES-60202_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
246 | ES-60203 |  | - | Emergency stop activated @ Control Room | E-Stop Swtich | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
246 | ES-61301 |  | - | Emergency stop activated @ SC-61301,SC-61302 | E-Stop Swtich | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
247 | DEDERT SUPPLY EQUIPMENT | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
248 | FT-60207 | FT-60701 | 325-01-602-PD-07 | Instr. Air Flow Transmitter for Camera #4 (ACAM-21) | Flow Transmitter | 4 - 20 mA | - | TYP-AI-02 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI2-1(B) | C3/C3S7 | C3S7-1/P3-TBAI2-1(B) | P3-TBAI2-1(B)/C3S7-1 | FT-60207_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
249 | PT-60207 | PT-60701 | 325-01-602-PD-07 | Instr. Air Pressure Transmitter for Camera #4 (ACAM-21) | Pressure Transmitter | 4 - 20 mA | - | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI3-4(B) | C3/C3S8 | C3S8-7/P3-TBAI3-4(B) | P3-TBAI3-4(B)/C3S8-7 | PT-60207_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
250 | XV-60240D | SV-60240D | 325-01-602-PD-05 | PA On/Off Valve for Bag House Tank Valve (BGHS-21) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-18 | C1/C1S7 | C1S7-20/P1-TBDI4-18 | P1-TBDI4-18/C1S7-20 | XV-60240D_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
251 | SV-60207 | SV-60701 | 325-01-602-PD-07 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) | On/Off Valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-9 | C2/C2S3 | C2S3-9/P2-TBDI3-9 | P2-TBDI3-9/C2S3-9 | SV-60207_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
252 | SV-60201 | - | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) | On/Off Valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI3-20 | C1/C1S6 | C1S6-22/P1-TBDI3-20 | P1-TBDI3-20/C1S6-22 | SV-60201_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
| SSL-60201 |  | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-21) | Low Speed Switch | Switch PNP | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
| ZS-60201 |  | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-21/ RV-60201) Casing Closed | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
253 | SV-60202 | - | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) | On/Off Valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI3-22 | C1/C1S6 | C1S6-24/P1-TBDI3-22 | P1-TBDI3-22/C1S6-24 | SV-60202_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
| SSL-60202 |  | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-22) | Low Speed Switch | Switch PNP | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
| ZS-60202 |  | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-22/ RV-60202) Casing Closed | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
254 | SV-60203 | - | 325-01-602-PD-08 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) | On/Off Valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI3-24 | C1/C1S6 | C1S6-26/P1-TBDI3-24 | P1-TBDI3-24/C1S6-26 | SV-60203_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
| SSL-60203 |  | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-23) | Low Speed Switch | Switch PNP | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
| ZS-60203 |  | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-23/ RV-60203) Casing Closed | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
255 | SV-61304 | - | 325-01-613-PD-01 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) | On/Off Valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-618 | P3-TBDI3-9 | C3/C3S3 | C3S3-9/P3-TBDI3-9 | P3-TBDI3-9/C3S3-9 | SV-61304_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
| SSL-61304 |  | 325-01-613-PD-01 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-31) | Low Speed Switch | Switch PNP | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
| ZS-61304 |  | 325-01-613-PD-01 | Position - Rotary Valve (RVAL-31/ RV-61304) Casing Closed | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
256 | TT-60207 | TT-60701 | 325-01-602-PD-07 | Instr. Air Temperature Transmitter for Air Manifold - Camera #4 (ACAM-21) | Temperature Transmitter | 4 - 20 mA | - | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI3-10(B) | C3/C3S8 | C3S8-21/P3-TBAI3-10(B) | P3-TBAI3-10(B)/C3S8-21 | TT-60207_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
257 | XV-60261FA | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-25 | C2/C2S3 | C2S3-27/P2-TBDI3-25 | P2-TBDI3-25/C2S3-27 | XV-60261FA_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
258 | XV-60261FB | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-29 | C2/C2S3 | C2S3-31/P2-TBDI3-29 | P2-TBDI3-29/C2S3-31 | XV-60261FB_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
259 | XV-60261FC | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-1 | C2/C2S4 | C2S4-1/P2-TBDI4-1 | P2-TBDI4-1/C2S4-1 | XV-60261FC_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
260 | XV-60261FD | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-5 | C2/C2S4 | C2S4-5/P2-TBDI4-5 | P2-TBDI4-5/C2S4-5 | XV-60261FD_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
261 | XV-60261SA | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-9 | C2/C2S4 | C2S4-9/P2-TBDI4-9 | P2-TBDI4-9/C2S4-9 | XV-60261SA_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
262 | XV-60261SB | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-11 | C2/C2S4 | C2S4-11/P2-TBDI4-11 | P2-TBDI4-11/C2S4-11 | XV-60261SB_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
263 | XV-60261SC | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-13 | C2/C2S4 | C2S4-13/P2-TBDI4-13 | P2-TBDI4-13/C2S4-13 | XV-60261SC_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
264 | XV-60261SD | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-15 | C2/C2S4 | C2S4-15/P2-TBDI4-15 | P2-TBDI4-15/C2S4-15 | XV-60261SD_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
265 | XV-60262FE | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-19 | C2/C2S4 | C2S4-21/P2-TBDI4-19 | P2-TBDI4-19/C2S4-21 | XV-60262FE_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
266 | XV-60262FF | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-21 | C2/C2S4 | C2S4-23/P2-TBDI4-21 | P2-TBDI4-21/C2S4-23 | XV-60262FF_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
267 | XV-60262FG | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-23 | C2/C2S4 | C2S4-25/P2-TBDI4-23 | P2-TBDI4-23/C2S4-25 | XV-60262FG_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
268 | XV-60262FH | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-25 | C2/C2S4 | C2S4-27/P2-TBDI4-25 | P2-TBDI4-25/C2S4-27 | XV-60262FH_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
269 | XV-60262SE | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-27 | C2/C2S4 | C2S4-29/P2-TBDI4-27 | P2-TBDI4-27/C2S4-29 | XV-60262SE_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
270 | XV-60262SF | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-29 | C2/C2S4 | C2S4-31/P2-TBDI4-29 | P2-TBDI4-29/C2S4-31 | XV-60262SF_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
271 | XV-60262SG | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-31 | C2/C2S4 | C2S4-33/P2-TBDI4-31 | P2-TBDI4-31/C2S4-33 | XV-60262SG_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
272 | XV-60262SH | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI5-1 | C2/C2S5 | C2S5-1/P2-TBDI5-1 | P2-TBDI5-1/C2S5-1 | XV-60262SH_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
273 | XV-60263FJ | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI5-5 | C2/C2S5 | C2S5-5/P2-TBDI5-5 | P2-TBDI5-5/C2S5-5 | XV-60263FJ_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
274 | XV-60263FK | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI5-7 | C2/C2S5 | C2S5-7/P2-TBDI5-7 | P2-TBDI5-7/C2S5-7 | XV-60263FK_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
275 | XV-60263FL | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI5-9 | C2/C2S5 | C2S5-9/P2-TBDI5-9 | P2-TBDI5-9/C2S5-9 | XV-60263FL_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
276 | XV-60263FM | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI5-11 | C2/C2S5 | C2S5-11/P2-TBDI5-11 | P2-TBDI5-11/C2S5-11 | XV-60263FM_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
277 | XV-60263SJ | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI5-13 | C2/C2S5 | C2S5-13/P2-TBDI5-13 | P2-TBDI5-13/C2S5-13 | XV-60263SJ_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
278 | XV-60263SK | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI5-15 | C2/C2S5 | C2S5-15/P2-TBDI5-15 | P2-TBDI5-15/C2S5-15 | XV-60263SK_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
279 | XV-60263SL | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI5-17 | C2/C2S5 | C2S5-19/P2-TBDI5-17 | P2-TBDI5-17/C2S5-19 | XV-60263SL_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
280 | XV-60263SM | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI5-19 | C2/C2S5 | C2S5-21/P2-TBDI5-19 | P2-TBDI5-19/C2S5-21 | XV-60263SM_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
281 | XV-60264FN | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-13 | C2/C2S3 | C2S3-13/P2-TBDI3-13 | P2-TBDI3-13/C2S3-13 | XV-60264FN_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
282 | XV-60264FP | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-15 | C2/C2S3 | C2S3-15/P2-TBDI3-15 | P2-TBDI3-15/C2S3-15 | XV-60264FP_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
283 | XV-60264FQ | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-19 | C2/C2S3 | C2S3-21/P2-TBDI3-19 | P2-TBDI3-19/C2S3-21 | XV-60264FQ_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
284 | XV-60264FR | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-23 | C2/C2S3 | C2S3-25/P2-TBDI3-23 | P2-TBDI3-23/C2S3-25 | XV-60264FR_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
285 | XV-60264SN | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-27 | C2/C2S3 | C2S3-29/P2-TBDI3-27 | P2-TBDI3-27/C2S3-29 | XV-60264SN_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
286 | XV-60264SP | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-31 | C2/C2S3 | C2S3-33/P2-TBDI3-31 | P2-TBDI3-31/C2S3-33 | XV-60264SP_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
287 | XV-60264SQ | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-3 | C2/C2S4 | C2S4-3/P2-TBDI4-3 | P2-TBDI4-3/C2S4-3 | XV-60264SQ_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
288 | XV-60264SR | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI4-7 | C2/C2S4 | C2S4-7/P2-TBDI4-7 | P2-TBDI4-7/C2S4-7 | XV-60264SR_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
289 | XV-60261DA |  | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11A | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
290 | XV-60262DE |  | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11B | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
291 | XV-60263DN |  | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11C | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
292 | XV-60264DJ |  | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11D | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
293 | XV-60241 | - | 325-01-602-PD-05 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-22 | C2/C2S2 | C2S2-24/P2-TBDI2-22 | P2-TBDI2-22/C2S2-24 | XV-60241_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
294 | XV-60240 | - | 325-01-602-PD-08 | Powder On/Off Valve for Diverter Valve (DVTR-21) | On/Off Valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
295 | Machine Equipment Supply | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
296 | PSE-61300 | - | 325-01-613-PD-01 | Explosion Vent PSE-61300 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-618 | P4-TBDI3-7 | C4/C4S3 | C4S3-7/P4-TBDI3-7 | P4-TBDI3-7/C4S3-7 | PSE-61300_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
297 | PSE-61301 | - | 325-01-613-PD-01 | Explosion Vent PSE-61301 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-618 | P4-TBDI3-8 | C4/C4S3 | C4S3-8/P4-TBDI3-8 | P4-TBDI3-8/C4S3-8 | PSE-61301_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
298 | ISV-61302 | - | 325-01-613-PD-01 | Explosion isolation flap valve ISV-61302 | Position switch | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
299 | PSE-61302 | - | 325-01-613-PD-03 | Explosion Vent PSE-61302 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-612 | P4-TBDI2-7 | C4/C4S2 | C4S2-7/P4-TBDI2-7 | P4-TBDI2-7/C4S2-7 | PSE-61302_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
300 | PSE-61303 | - | 325-01-613-PD-05 | Explosion Vent PSE-61303 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-612 | P4-TBDI2-8 | C4/C4S2 | C4S2-8/P4-TBDI2-8 | P4-TBDI2-8/C4S2-8 | PSE-61303_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
301 | PSE-61304 | - | 325-01-613-PD-01 | Explosion Vent PSE-61304 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-618 | P4-TBDI3-9 | C4/C4S3 | C4S3-9/P4-TBDI3-9 | P4-TBDI3-9/C4S3-9 | PSE-61304_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
302 | ZS-61306 | PSV-61301A | 325-01-613-PD-01 | Position Brether Valve High Pressure PSV-61301 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-618 | P4-TBDI3-10 | C4/C4S3 | C4S3-10/P4-TBDI3-10 | P4-TBDI3-10/C4S3-10 | PSV-61301A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
303 | ZS-61307 | PSV-61301B | 325-01-613-PD-01 | Position Brether Valve Vacuum Pressure PSV-61301 | Position switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | IS-JB-618 | P4-TBDI3-11 | C4/C4S3 | C4S3-11/P4-TBDI3-11 | P4-TBDI3-11/C4S3-11 | PSV-61301B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
304 | ISV-61303 | - | 325-01-613-PD-03 | Explosion isolation flap valve ISV-61303 | Position switch | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | IS-JB-612 | P4-TBDI2-1 | C4/C4S2 | C4S2-1/P4-TBDI2-1 | P4-TBDI2-1/C4S2-1 | ISV-61303_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
305 | ISV-61304 | - | 325-01-613-PD-05 | Explosion isolation flap valve ISV-61304 | Position switch | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | IS-JB-612 | P4-TBDI2-2 | C4/C4S2 | C4S2-2/P4-TBDI2-2 | P4-TBDI2-2/C4S2-2 | ISV-61304_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
306 | MCC ROOM | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
307 | AT-40201 | ATY-40101 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40201 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | IS-JB-603 | P4-TBDI1-1 | C4/C4S1 | C4S1-1/P4-TBDI1-1 | P4-TBDI1-1/C4S1-1 | AT-40201_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
308 | AT-40202 | ATY-40102 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40202 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | IS-JB-603 | P4-TBDI1-2 | C4/C4S1 | C4S1-2/P4-TBDI1-2 | P4-TBDI1-2/C4S1-2 | AT-40202_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
309 | AT-40203 | ATY-40201 | 325-01-402-PD-02 | Start / Stop Command for VSD AT-40203 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | IS-JB-603 | P4-TBDI1-3 | C4/C4S1 | C4S1-3/P4-TBDI1-3 | P4-TBDI1-3/C4S1-3 | AT-40203_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
310 | BF-60210 | BFY-60210 | 325-01-602-PD-03 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
311 | BF-60211 | BFY-60211 | 325-01-602-PD-03 | Start / Stop Command for VSD FANC-21 (Combustion Fan) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
312 | BF-60240 | BFY-60240 | 325-01-602-PD-05 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
313 | BF-60220 | BFY-60220 | 325-01-602-PD-04 | Start / Stop Command for VSD FANS-22 (Cooling Fan) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
314 | BF-60206 | BFY-60206 | 325-01-602-PD-08 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
315 | BF-61301 | BFY-61301 | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
316 | BF-61302 | BFY-61302 | 325-01-613-PD-05 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
317 | BF-61303 | BFY-61303 | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
318 | BLM-61302 | - | 325-01-613-PD-01 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | เปลี่ยนไปจ่ายเป็น Power Feeder | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
319 | PD-60202B | PCM-60205-B | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Oil Pump ) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
320 | PD-60202C | PCM-60205-C | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 1 ) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
321 | PD-60202D | PCM-60205-D | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 2 ) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
322 | PD-60202E | PCM-60205-E | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Main motor Fan ) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
323 | PC-40203 | PCY-40201 | 325-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
324 | PC-40201 | PCY-40101 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40201 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
325 | PC-40202 | PCY-40102 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40202 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
326 | PD-40204 |  | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40204 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
327 | PD-40205 |  | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40205 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
328 | PD-60202A | PCY-60205-A | 325-01-602-PD-01 | Start / Stop Command for VSD PUPD-11 (Positive Displacement Pump ) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
329 | PCY-60215 | - | 325-01-602-PD-03 | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
330 | BL-61301 | PVM-61301 | 325-01-613-PD-03 | Start / Stop Command for FVNR PV-61301 (Vacuum Cleaning Fan) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | JB-612 | P3-TBDI2-3 | C3/C3S2 | C3S2-3/P3-TBDI2-3 | P3-TBDI2-3/C3S2-3 | PVM-61301_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
331 | RVM-60201 | - | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
332 | RVM-60202 | - | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
333 | RVM-60203 | - | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
334 | RVM-60204 | - | 325-01-602-PD-08 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
335 | RVM-61301 | - | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61301 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
336 | RVM-61302 | - | 325-01-613-PD-03 | Start / Stop Command for FVNR RV-61302 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
337 | RVM-61303 | - | 325-01-613-PD-05 | Start / Stop Command for FVNR RV-61303 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
338 | RVM-61304 | - | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61304 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
339 | RVM-61305 | - | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61305 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
340 | SCM-61301 | - | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61301 (Sifter ) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
341 | SCM-61302 | - | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61302 (Sifter ) |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
342 | B&B Packing | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
343 | XA-61301A | - | 325-01-613-PD-02 | Request filter plant (Fugitive) | Request filter plant | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBDI2-5 | C3/C3S2 | C3S2-5/P3-TBDI2-5 | P3-TBDI2-5/C3S2-5 | XA-61301A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
344 | XA-61301B | - | 325-01-613-PD-02 | Request material transport | Request material transport | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBDI2-6 | C3/C3S2 | C3S2-6/P3-TBDI2-6 | P3-TBDI2-6/C3S2-6 | XA-61301B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
345 | XA-61301C | - | 325-01-613-PD-02 | Request belt plant | Request belt plant | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBDI2-7 | C3/C3S2 | C3S2-7/P3-TBDI2-7 | P3-TBDI2-7/C3S2-7 | XA-61301C_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
346 | XA-61301D | - | 325-01-613-PD-02 | Machine in operation | Machine in operation | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBDI2-8 | C3/C3S2 | C3S2-8/P3-TBDI2-8 | P3-TBDI2-8/C3S2-8 | XA-61301D_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
347 | XA-61301E | - | 325-01-613-PD-02 | General Fault | General Fault | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBDI2-9 | C3/C3S2 | C3S2-9/P3-TBDI2-9 | P3-TBDI2-9/C3S2-9 | XA-61301E_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
348 | XA-61301F | - | 325-01-613-PD-02 | Machine is ready | Machine is ready | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBDI2-10 | C3/C3S2 | C3S2-10/P3-TBDI2-10 | P3-TBDI2-10/C3S2-10 | XA-61301F_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
349 | XA-61301G | - | 325-01-613-PD-02 | Emergency stop activated | Emergency stop activated | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBDI2-11 | C3/C3S2 | C3S2-11/P3-TBDI2-11 | P3-TBDI2-11/C3S2-11 | XA-61301G_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
350 | XA-61301H | - | 325-01-613-PD-02 | Silo minimum | Silo minimum | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBDI2-12 | C3/C3S2 | C3S2-12/P3-TBDI2-12 | P3-TBDI2-12/C3S2-12 | XA-61301H_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
351 | XA-61301J | - | 325-01-613-PD-02 | Silo maximum | Silo maximum | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBDI2-13 | C3/C3S2 | C3S2-13/P3-TBDI2-13 | P3-TBDI2-13/C3S2-13 | XA-61301J_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
352 | XS-61301A | - | 325-01-613-PD-02 | Filter plant in operation | Filter plant in operation | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBRL1-24 | C3/C3S4 | C3S4-26/P3-TBRL1-24 | P3-TBRL1-24/C3S4-26 | XS-61301A_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
353 | XS-61301B | - | 325-01-613-PD-02 | Material transport in operation | Material transport in operation | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBRL1-25 | C3/C3S4 | C3S4-27/P3-TBRL1-25 | P3-TBRL1-25/C3S4-27 | XS-61301B_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
354 | XS-61301C | - | 325-01-613-PD-02 | Belt plant in operation | Belt plant in operation | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBRL1-26 | C3/C3S4 | C3S4-28/P3-TBRL1-26 | P3-TBRL1-26/C3S4-28 | XS-61301C_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
355 | XS-61301D | - | 325-01-613-PD-02 | Sequence Stop | Sequence Stop | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBRL1-27 | C3/C3S4 | C3S4-29/P3-TBRL1-27 | P3-TBRL1-27/C3S4-29 | XS-61301D_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
356 | XS-61301E | - | 325-01-613-PD-02 | Status from Customer Emergency stop | Status from Customer Emergency stop | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBRL1-28 | C3/C3S4 | C3S4-30/P3-TBRL1-28 | P3-TBRL1-28/C3S4-30 | XS-61301E_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
357 | XS-61301F | - | 325-01-613-PD-02 | Operation Release | Operation Release | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-612 | P3-TBRL1-29 | C3/C3S4 | C3S4-31/P3-TBRL1-29 | P3-TBRL1-29/C3S4-31 | XS-61301F_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
358 |  | - | 325-01-613-PD-02 | Spare |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
359 |  | - | 325-01-613-PD-02 | Spare |  | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
360 |  | - | 325-01-613-PD-02 | Spare |  | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
361 |  | - | 325-01-613-PD-02 | Communication Signal |  | Communication Signal | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
362 | Boiler | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
363 | XA-92201B |  | 325-01-922-PD-03 | Boiler common alarm |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
363 | XA-92201C |  | 325-01-922-PD-03 | Boiler Trip |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
363 | XA-92212B |  | 325-01-922-PD-03 | Burner Trip |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
363 | XL-92201B |  | 325-01-922-PD-03 | Boiler Operate |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
363 | XL-92201C |  | 325-01-922-PD-03 | Remote Setpoint Activated |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
363 | ZL-92201 |  | 325-01-922-PD-03 | Remote Setpoint Status |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
363 |  | - | 325-01-922-PD-03 | Communication Signal |  | Communication Signal | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
| Bin Vent Filter (FA-61301) | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
363 | XA-FA-61301A |  | 325-01-613-PD-01 | Start / Stop Command for FA-61301 |  | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
364 | XA-FA-61301B |  | 325-01-613-PD-01 | Compress air low (Spare) |  | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
365 | XS-FA-61301 |  | 325-01-613-PD-01 | Alarm 1 |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
| Fugitive Dust Filter (FA-61310) | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
363 | XA-FA-61310A |  | 325-01-613-PD-01 | Start / Stop Command for FA-61310 |  | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
364 | XA-FA-61310B |  | 325-01-613-PD-01 | Compress air low (Spare) |  | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
365 | XS-FA-61310 |  | 325-01-613-PD-01 | Alarm 1 |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
| Vacuum Cleaner Filter (FA-61311) | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
363 | XA-FA-61311A |  | 325-01-613-PD-03 | Start / Stop Command for FA-61311 |  | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
364 | XA-FA-61311B |  | 325-01-613-PD-03 | Compress air low (Spare) |  | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
365 | XS-FA-61311 |  | 325-01-613-PD-03 | Alarm 1 |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
| Local Exhaust Ventilation Filter (FA-61312) | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
363 | XA-FA-61312A |  | 325-01-613-PD-05 | Start / Stop Command for FA-61311 |  | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
364 | XA-FA-61312B |  | 325-01-613-PD-05 | Compress air low (Spare) |  | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
365 | XS-FA-61312 |  | 325-01-613-PD-05 | Alarm 1 |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
362 | Bag Filter Control Panel (FA-60240) | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
363 | XS-60240A | - | 325-01-602-PD-05 | Start / Stop Command for BGHS-21 (Bag House Air Pulsing) |  | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
364 | XS-60240B | - | 325-01-602-PD-05 | Fan Command for BGHS-21 (Bag House Air Pulsing) |  | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBRL1-17 | C2/C2S6 | C2S6-19/P2-TBRL1-17 | P2-TBRL1-17/C2S6-19 | XS-60240B_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
365 | XA-60240A | - | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-12 | C2/C2S2 | C2S2-12/P2-TBDI2-12 | P2-TBDI2-12/C2S2-12 | XA-60240A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
366 | XA-60240B | - | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-13 | C2/C2S2 | C2S2-13/P2-TBDI2-13 | P2-TBDI2-13/C2S2-13 | XA-60240B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
367 | DPI-60240 | - | 325-01-602-PD-05 | Gas Pressure Differntial Pressure (Bag House Air Pulsing) |  | 4 - 20 mA | - | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-601 | P1-TBAI2-1(B) | C1/C1S11 | C1S11-1/P1-TBAI2-1(B) | P1-TBAI2-1(B)/C1S11-1 | DPI-60240_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
368 | HTRE-21 Heater Control Panel (TRACING) | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
369 | XS-60241A | - | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
370 | XA-60241A | - | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-14 | C2/C2S2 | C2S2-14/P2-TBDI2-14 | P2-TBDI2-14/C2S2-14 | XA-60241A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
371 | XA-60241B | - | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-15 | C2/C2S2 | C2S2-15/P2-TBDI2-15 | P2-TBDI2-15/C2S2-15 | XA-60241B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
372 | TSH-60241A | - | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | 0 - 100 C | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-6 | C2/C2S2 | C2S2-6/P2-TBDI2-6 | P2-TBDI2-6/C2S2-6 | TSH-60241A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
373 | TSL-60241B | - | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | 0 - 100 C | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-9 | C2/C2S2 | C2S2-9/P2-TBDI2-9 | P2-TBDI2-9/C2S2-9 | TSL-60241B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
374 | HTRE-22 Heater Control Panel (TRACING) | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
375 | XS-60242A | - | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
376 | XA-60242A | - | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-16 | C2/C2S2 | C2S2-16/P2-TBDI2-16 | P2-TBDI2-16/C2S2-16 | XA-60242A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
377 | XA-60242B | - | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-17 | C2/C2S2 | C2S2-19/P2-TBDI2-17 | P2-TBDI2-17/C2S2-19 | XA-60242B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
378 | TSH-60242A | - | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | 0 - 100 C | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-7 | C2/C2S2 | C2S2-7/P2-TBDI2-7 | P2-TBDI2-7/C2S2-7 | TSH-60242A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
379 | TSL-60242B | - | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | 0 - 100 C | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-10 | C2/C2S2 | C2S2-10/P2-TBDI2-10 | P2-TBDI2-10/C2S2-10 | TSL-60242B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
380 | HTRE-23 Heater Control Panel (TRACING) | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
381 | XS-60243A | - | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
382 | XA-60243A | - | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-18 | C2/C2S2 | C2S2-20/P2-TBDI2-18 | P2-TBDI2-18/C2S2-20 | XA-60243A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
383 | XA-60243B | - | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-19 | C2/C2S2 | C2S2-21/P2-TBDI2-19 | P2-TBDI2-19/C2S2-21 | XA-60243B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
384 | TSH-60243A | - | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | 0 - 100 C | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-8 | C2/C2S2 | C2S2-8/P2-TBDI2-8 | P2-TBDI2-8/C2S2-8 | TSH-60243A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
385 | TSL-60243B | - | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | 0 - 100 C | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-11 | C2/C2S2 | C2S2-11/P2-TBDI2-11 | P2-TBDI2-11/C2S2-11 | TSL-60243B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
386 | Air Heater Burner Control Panel (PK-60210) | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
387 | XA-FH-60210A | - | 325-01-602-PD-06 | BMS PANEL POWER ON for AHTR-21 |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-1 | C2/C2S3 | C2S3-1/P2-TBDI3-1 | P2-TBDI3-1/C2S3-1 | XA-FH-60210A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
388 | XA-FH-60210B | - | 325-01-602-PD-06 | BMS Burner High Fire Purge for AHTR-21 |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-2 | C2/C2S3 | C2S3-2/P2-TBDI3-2 | P2-TBDI3-2/C2S3-2 | XA-FH-60210B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
389 | XA-FH-60210C | - | 325-01-602-PD-06 | BMS Burner On for AHTR-21 |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-3 | C2/C2S3 | C2S3-3/P2-TBDI3-3 | P2-TBDI3-3/C2S3-3 | XA-FH-60210C_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
390 | XA-FH-60210D | - | 325-01-602-PD-06 | BMS BMS Lockout for AHTR-21 |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-4 | C2/C2S3 | C2S3-4/P2-TBDI3-4 | P2-TBDI3-4/C2S3-4 | XA-FH-60210D_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
391 | XA-FH-60210E | - | 325-01-602-PD-06 | BMS Remote Modet for AHTR-21 |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBDI3-5 | C2/C2S3 | C2S3-5/P2-TBDI3-5 | P2-TBDI3-5/C2S3-5 | XA-FH-60210E_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
392 | XS-FH-60210A | - | 325-01-602-PD-06 | Burner Remote Start for AHTR-21 |  | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
393 | XS-FH-60210B | - | 325-01-602-PD-06 | Dryer Interlocks for AHTR-21 |  | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
394 | XS-FH-60210C | - | 325-01-602-PD-06 | Remote Reset for AHTR-21 |  | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBRL2-2 | C2/C2S7 | C2S7-2/P2-TBRL2-2 | P2-TBRL2-2/C2S7-2 | XS-FH-60210C_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
395 | XS-FH-60210D | - | 325-01-602-PD-06 | Spare |  | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-607 | P2-TBRL2-3 | C2/C2S7 | C2S7-3/P2-TBRL2-3 | P2-TBRL2-3/C2S7-3 | XS-FH-60210D_DO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
396 | XS-FH-60210E |  | 325-01-602-PD-06 | Exhaust fan run status BF-60240 |  | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
397 | XS-FH-60210F |  | 325-01-602-PD-06 | Supply fan run status BF-60210 |  | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
398 | XS-FH-60210G |  | 325-01-602-PD-06 | Combusion fan run status BF-60211 |  | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
399 | TI-FH-60210 | - | 325-01-602-PD-06 | Gas Burner Firing Rate Temp Signal |  | 4 - 20 mA | On-Off | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI3-7(B) | C3/C3S8 | C3S8-15/P3-TBAI3-7(B) | P3-TBAI3-7(B)/C3S8-15 | TI-FH-60210_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
400 | UY-FH-60210A | - | 325-01-602-PD-06 | Comb fan VFD Speed Control |  | 4 - 20 mA | On-Off | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAI3-11(B) | C3/C3S8 | C3S8-23/P3-TBAI3-11(B) | P3-TBAI3-11(B)/C3S8-23 | UY-FH-60210A_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
401 | UY-FH-60210B | - | 325-01-602-PD-06 | Demand Signal |  | 4 - 20 mA | On-Off | TYP-AO-01 | TBAO | LOOP DIAGRAM WRING.dwg | JB-607 | P3-TBAO1-5 | C3/C3S12 | C3S12-4/P3-TBAO1-5 | P3-TBAO1-5/C3S12-4 | UY-FH-60210B_AO_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
402 | COM-FH-60210B | - | 325-01-602-PD-06 | Communication Signal |  | Modbus RTU | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
403 | TE-60212 | - | - | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Element | T/C Type K | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel(HCP) | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
404 | DPHL-60230 | - | - | Gas Pressure Differntial Switch Low for Exhaust Fan (FANE-21) | Pressure Differntial Switch Low | Dry Contact | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel(HCP) | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
405 | DPSL-60211 | - | - | Gas Pressure Differential Switch Low for Combustion Fan (FANC-21) | Pressure Differential Switch Low | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | AHTR Control Panel(HCP) | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
406 | FCV-60211B | - | - | Gas Flow Control Damper (Valve) for Burner Combustion Air Duct (DTCB-21) | Flow Control Damper (Valve) | Internal wiring | - | TYP-AO-01 | TBAO | LOOP DIAGRAM WRING.dwg | AHTR Control Panel(HCP) | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
407 | ZT-60211B | - | - | Gas Position Transmitter for Combustion Air Damper Actuator (DTCB-21) | Position Transmitter | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel(HCP) | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
408 | ZSL-60211B | - | - | Gas Position Switch Low for Combustion Air Damper Actuator (DTCB-21) | Position Switch Low | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel(HCP) | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
409 | ZSH-60211B | - | - | Gas Position Switch High for Combustion Air Damper Actuator (DTCB-21) | Position Switch High | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel(HCP) | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
410 | VJ-01 (24VDC) | - | - | Valve train J-BOX | Control Box | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel(HCP) | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
411 | VJ-01 (220VAC) | - | - | Valve train J-BOX | Control Box | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel(HCP) | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
412 | UJ-01 (24VDC) | - | - | Valve train J-BOX | Control Box | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel(HCP) | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
413 | UJ-01 (220VAC) | - | - | Valve train J-BOX | Control Box | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel(HCP) | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
414 | PV-60210A | - | - | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | Internal wiring | - | TYP-AO-01 | TBAO | LOOP DIAGRAM WRING.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
415 | PV-60210B | - | - | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | Internal wiring | - | TYP-AO-01 | TBAO | LOOP DIAGRAM WRING.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
416 | DPT-60210 | - | - | Gas Pressure Differential Switch Low for Main Supply Air Fan (FANS-21) | Pressure Differential Switch Low | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
417 | DPSL-60210B | - | - | Gas Pressure Differential Switch Low for Air Heater (AHTR-21) | Pressure Differential Switch Low | Internal wiring | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
418 | DPSH-60210C | - | - | Gas Pressure Differential Switch High for Air Heater (AHTR-21) | Pressure Differential Switch High | Internal wiring | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
419 | BE-60210A | - | - | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
420 | BE-60210B | - | - | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
421 | IX-60210A | - | - | Gas Ignition Transformer for Air Heater (AHTR-21) | Ignition Transformer | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
422 | FCV-60210A | - | - | Gas Flow Control Valve for Air Heater Gas Train (GTRN-21) | Flow Control Valve | Internal wiring | - | TYP-AO-01 | TBAO | LOOP DIAGRAM WRING.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
423 | ZSL-60210A | - | - | Gas Position Switch Low for Air Heater Gas Train (GTRN-21) | Position Switch Low | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
424 | ZT-60210A | - | - | Gas Position Transmitter for Air Heater Gas Train (GTRN-21) | Position Transmitter | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
425 | PSH-60210 | - | - | Gas Pressure Switch High for Air Heater Gas Train (GTRN-21) | Pressure Switch High | Internal wiring | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
426 | BV-60210B | - | - | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
427 | ZSO-60210B | - | - | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | Internal wiring | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
428 | ZSC-60210B | - | - | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | Internal wiring | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
429 | VV-60210 | - | - | Gas Venting Valve (main gas) for Air Heater Gas Train (GTRN-21) | Venting Valve (main gas) | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
430 | ZSO-60210C | - | - | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | Internal wiring | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
431 | ZSC-60210C | - | - | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | Internal wiring | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
432 | PSL-60210 | - | - | Gas Pressure Switch Low for Air Heater Gas Train (GTRN-21) | Pressure Switch Low | Internal wiring | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
433 | BV-60210A | - | - | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | Internal wiring | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
434 | ZSO-60210A | - | - | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | Internal wiring | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
435 | ZSC-60210A | - | - | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | Internal wiring | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | AHTR Control Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
436 | High Pressure Pump (PD-60202) | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
437 | XS-60202 | ES-60202 | 325-01-602-PD-01 | E-Stop for PUPD-11 (Positive Displacement Pump ) | E-Stop | Dry Contact | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI3-17 | C1/C1S6 | C1S6-19/P1-TBDI3-17 | P1-TBDI3-17/C1S6-19 | ES-60202_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
438 | XA-60202 |  | 325-01-602-PD-01 | High Oil Pressure Alarm | Lamp | 24 VDC energized | - | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
439 | PT-60202 | PT-60205 | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter | 4 - 20 mA | - | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-401 | P1-TBAI1-11(B) | C1/C1S10 | C1S10-23/P1-TBAI1-11(B) | P1-TBAI1-11(B)/C1S10-23 | PT-60202_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
440 | FS-60202 | FS-60205 | 325-01-602-PD-01 | Cooling Water Return Flow Switch for Positive Displacement Pump (PUPD-11) | Flow Switch | - | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI3-18 | C1/C1S6 | C1S6-20/P1-TBDI3-18 | P1-TBDI3-18/C1S6-20 | FS-60205_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
441 | XS-60205 | - | 325-01-602-PD-01 | Start / Stop Command for PUPD-11 (Positive Displacement Pump ) | Start / Stop Command | - | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
442 | VS-60202 | VS-60205 | 325-01-602-PD-01 | Vibration Gear Box Vibration Switch for Switch Vibration for PUPD-11 (PUPD-11) | Vibration Switch | 4 - 20 mA | - | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | JB-601 | P1-TBDI3-26 | C1/C1S6 | C1S6-28/P1-TBDI3-26 | P1-TBDI3-26/C1S6-28 | VS-60205_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
443 | XV-60202A | XV-60205A | 325-01-602-PD-01 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) | On/Off Valve | 24 VDC energized | - | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-16 | C1/C1S7 | C1S7-16/P1-TBDI4-16 | P1-TBDI4-16/C1S7-16 | XV-60205A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
444 | PS-60202 |  | 325-01-602-PD-01 | Oil Pressure Switch for Positive Displacement Pump (PUPD-11) | Flow Switch | - | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
445 | TT-60202A |  | 325-01-602-PD-01 | Temperature for Positive Displacement Pump (PUPD-11) | TC / Temperature Transmitter | - | - | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
446 | TT-60202B |  | 325-01-602-PD-01 | Temperature for Positive Displacement Pump (PUPD-11) | TC / Temperature Transmitter | - | - | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
447 | YA-60205 | - | 325-01-602-PD-01 | Fault Command |  | - | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | JB-601 | P1-TBDI4-22 | C1/C1S7 | C1S7-24/P1-TBDI4-22 | P1-TBDI4-22/C1S7-24 | YA-60205_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
448 | YI-60205 | - | 325-01-602-PD-01 | Run Command |  | - | - | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | JB-601 | P1-TBDI4-23 | C1/C1S7 | C1S7-25/P1-TBDI4-23 | P1-TBDI4-23/C1S7-25 | YI-60205_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
449 | Suppression Panel | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
450 | PSH-61301 | - | 325-01-613-PD-01 | Gas and Powder Pressure Switch High for Storage Bin Cyclone Inlet Duct (####-##) | Pressure Switch High | - | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | Suppression Sys. Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
451 | PSH-60220 | - | 325-01-602-PD-04 | Gas Pressure Switch High for Spray Chamber (CHAM-21) | Pressure Switch High | - | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | Suppression Sys. Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
452 | PSH-60230 | - | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-21) | Pressure Switch High | - | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | Suppression Sys. Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
453 | PSH-60231 | - | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-22) | Pressure Switch High | - | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | Suppression Sys. Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
454 | PSH-60224 | - | 325-01-602-PD-05 | Gas and Powder Pressure Switch High for Bag House (BGHS-21) | Pressure Switch High | - | - | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | Suppression Sys. Panel | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | PACKAGE LOCAL | Pending Sign-off
455 | XA-60202A | - | 325-01-602-PD-08 | General Alarm Emergency Stop Actuation for XSUP-5601 (Supression Panel) | General Alarm Emergency Stop Actuation | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-1 | C1/C1S7 | C1S7-1/P1-TBDI4-1 | P1-TBDI4-1/C1S7-1 | XA-60202A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
456 | XA-60202B | - | 325-01-602-PD-08 | General Fault Controlled Stop for XSUP-5601 (Supression Panel) | General Fault Controlled Stop | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-2 | C1/C1S7 | C1S7-2/P1-TBDI4-2 | P1-TBDI4-2/C1S7-2 | XA-60202B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
457 | XA-60202C | - | 325-01-602-PD-08 | General Armed Status Indicator for XSUP-5601 (Supression Panel) | General Armed Status Indicator | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-3 | C1/C1S7 | C1S7-3/P1-TBDI4-3 | P1-TBDI4-3/C1S7-3 | XA-60202C_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
458 | XA-60202D | - | 325-01-602-PD-08 | Power Fault Status Indicator for XSUP-5601 (Supression Panel) | Power Fault Status Indicator | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-4 | C1/C1S7 | C1S7-4/P1-TBDI4-4 | P1-TBDI4-4/C1S7-4 | XA-60202D_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
459 | XA-60202E | - | 325-01-602-PD-08 | Dryer CHAM-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | Dryer CHAM-21 Emergency Stop Actuation | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-5 | C1/C1S7 | C1S7-5/P1-TBDI4-5 | P1-TBDI4-5/C1S7-5 | XA-60202E_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
460 | XA-60202F | - | 325-01-602-PD-08 | CHAM-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CHAM-21 Controlled Stop Trouble (No Protection) | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-6 | C1/C1S7 | C1S7-6/P1-TBDI4-6 | P1-TBDI4-6/C1S7-6 | XA-60202F_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
461 | XA-60202G | - | 325-01-602-PD-08 | CYCL-21/22 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-21/22 Emergency Stop Actuation | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-7 | C1/C1S7 | C1S7-7/P1-TBDI4-7 | P1-TBDI4-7/C1S7-7 | XA-60202G_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
462 | XA-60202H | - | 325-01-602-PD-08 | CYCL-21/22 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-21/22 Controlled Stop Trouble (No Protection) | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-8 | C1/C1S7 | C1S7-8/P1-TBDI4-8 | P1-TBDI4-8/C1S7-8 | XA-60202H_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
463 | XA-60202J | - | 325-01-602-PD-08 | BGHS-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | BGHS-21 Emergency Stop Actuation | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-10 | C1/C1S7 | C1S7-10/P1-TBDI4-10 | P1-TBDI4-10/C1S7-10 | XA-60202J_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
464 | XA-60202K | - | 325-01-602-PD-08 | BGHS-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | BGHS-21 Controlled Stop Trouble (No Protection) | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-11 | C1/C1S7 | C1S7-11/P1-TBDI4-11 | P1-TBDI4-11/C1S7-11 | XA-60202K_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
465 | XA-60202L | - | 325-01-602-PD-08 | CYCL-31 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-31 Emergency Stop Actuation | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-12 | C1/C1S7 | C1S7-12/P1-TBDI4-12 | P1-TBDI4-12/C1S7-12 | XA-60202L_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
466 | XA-60202M | - | 325-01-602-PD-08 | CYCL-31 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-31 Controlled Stop Trouble (No Protection) | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-13 | C1/C1S7 | C1S7-13/P1-TBDI4-13 | P1-TBDI4-13/C1S7-13 | XA-60202M_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
467 | Fire Deluge PK-60221 | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
468 | XA-60221A | XA-60261 | 325-01-602-PD-04 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Fire Deluge Fault (No Protection) | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-606 | P3-TBDI1-19 | C3/C3S1 | C3S1-21/P3-TBDI1-19 | P3-TBDI1-19/C3S1-21 | XA-60261_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
469 | XA-60221B | XA-60262 | 325-01-602-PD-04 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Fire Deluge Alarm (Deluge Activated) | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-606 | P3-TBDI1-20 | C3/C3S1 | C3S1-22/P3-TBDI1-20 | P3-TBDI1-20/C3S1-22 | XA-60262_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
470 | XS-60221 | XS-60260 | 325-01-602-PD-04 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
139 | TSH-60230 |  | 325-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | Temperature Switch | Dry Contact | 0 - 140 C | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-4 | C2/C2S2 | C2S2-4/P2-TBDI2-4 | P2-TBDI2-4/C2S2-4 | TSH-60230_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
471 | Fire Deluge PK-60222 | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
472 | XA-60222A |  | 325-01-602-PD-05 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Fire Deluge Fault (No Protection) | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
473 | XA-60222B |  | 325-01-602-PD-05 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Fire Deluge Alarm (Deluge Activated) | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
474 | XS-60222 |  | 325-01-602-PD-05 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
| XV-60240D |  | 325-01-602-PD-05 | Drain Valve |  | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | JB-601 | P1-TBDI4-18 | C1/C1S7 | C1S7-20/P1-TBDI4-18 | P1-TBDI4-18/C1S7-20 | XV-60240D_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
140 | TSH-60240 |  | 325-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | Temperature Switch | Dry Contact | 0 - 140 C | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | JB-602 | P2-TBDI2-5 | C2/C2S2 | C2S2-5/P2-TBDI2-5 | P2-TBDI2-5/C2S2-5 | TSH-60240_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
475 | Keaser Air Blower | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
476 | XS-61302 |  | 325-01-613-PD-01 | Start / Stop Command for Bin Aerator Blower | Start / Stop Command | Dry Contact | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
477 | XA-61302A |  | 325-01-613-PD-01 | Operational / Running status |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
478 | XA-61302B |  | 325-01-613-PD-01 | Local / Remote status |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
479 | XA-61302C |  | 325-01-613-PD-01 | Fault / Trip condition |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
480 | XA-61302D |  | 325-01-613-PD-01 | Warning condition |  | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | PLC | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
481 | REMOTE I-O Area-200 | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
482 | HV-20204 | HV-2022 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-8 | C5/C5S1 | C5S1-8/P5-TBDI1-8 | P5-TBDI1-8/C5S1-8 | HV-20204_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
483 | HV-20205 | HV-2024 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-9 | C5/C5S1 | C5S1-9/P5-TBDI1-9 | P5-TBDI1-9/C5S1-9 | HV-20205_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
484 | HV-20206 | HV-2026 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-10 | C5/C5S1 | C5S1-10/P5-TBDI1-10 | P5-TBDI1-10/C5S1-10 | HV-20206_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
485 | HV-20207 | HV-2030 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-11 | C5/C5S1 | C5S1-11/P5-TBDI1-11 | P5-TBDI1-11/C5S1-11 | HV-20207_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
486 | HV-20208 | HV-2032 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-12 | C5/C5S1 | C5S1-12/P5-TBDI1-12 | P5-TBDI1-12/C5S1-12 | HV-20208_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
487 | HV-20209 | HV-2035 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-13 | C5/C5S1 | C5S1-13/P5-TBDI1-13 | P5-TBDI1-13/C5S1-13 | HV-20209_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
488 | HV-20210 | HV-2038 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-14 | C5/C5S1 | C5S1-14/P5-TBDI1-14 | P5-TBDI1-14/C5S1-14 | HV-20210_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
489 | XV-20201 | - | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-27 | C5/C5S1 | C5S1-29/P5-TBDI1-27 | P5-TBDI1-27/C5S1-29 | XV-20201_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
490 | XV-20202 | - | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-29 | C5/C5S1 | C5S1-31/P5-TBDI1-29 | P5-TBDI1-29/C5S1-31 | XV-20202_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
491 | XV-20203 | - | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-31 | C5/C5S1 | C5S1-33/P5-TBDI1-31 | P5-TBDI1-31/C5S1-33 | XV-20203_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
492 | XV-20211 | - | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI2-1 | C5/C5S2 | C5S2-1/P5-TBDI2-1 | P5-TBDI2-1/C5S2-1 | XV-20211_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
493 | XV-20212 | - | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI2-3 | C5/C5S2 | C5S2-3/P5-TBDI2-3 | P5-TBDI2-3/C5S2-3 | XV-20212_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
494 | XV-20213 | - | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI2-5 | C5/C5S2 | C5S2-5/P5-TBDI2-5 | P5-TBDI2-5/C5S2-5 | XV-20213_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
495 | LS-814201 | LS-81001 | 325-01-814-PD-01 | Level alarm low | Level switch | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
496 | PC-20201 | PCM-2030 | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2030 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | RIO-200 | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
497 | PCM-2031 | - | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2031 | ยกเลิก | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | RIO-200 | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
498 | PC-814201 | PCY-81001 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81001 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | RIO-200 | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
499 | PC-814202 | PCY-81002 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81002 |  | 24 VDC energized | On-Off | TYP-GEN-01 | TBCI | LOOP DIAGRAM WRING.dwg | RIO-200 | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
500 | LPG Station | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
501 | FT-913201 | FT-80301 | 325-01-913-PD-02 | Flow outlet LPG line | Coriolis Flow Transmitter | 4 - 20 mA,Pulse | 0-1000kg/hr | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-2 | C5/C5S1 | C5S1-2/P5-TBDI1-2 | P5-TBDI1-2/C5S1-2 | FT-913201_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
502 | LT-913201 | LT-80301 | 325-01-913-PD-01 | Level LPG in storage | Level transmitter | 4 - 20 mA | - | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | RIO-200 | P5-TBAI1-6(B) | C5/C5S4 | C5S4-13/P5-TBAI1-6(B) | P5-TBAI1-6(B)/C5S4-13 | LT-913201_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
503 | PT-913201 | PT-80302 | 325-01-913-PD-02 | Pressure outlet LPG line | Pressure Transmitter | 4 - 20 mA | 0 - 10 barg | TYP-AI-01 | TBAI | LOOP DIAGRAM WRING.dwg | RIO-200 | P5-TBAI1-7(B) | C5/C5S4 | C5S4-15/P5-TBAI1-7(B) | P5-TBAI1-7(B)/C5S4-15 | PT-913201_AI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
504 | XV-913201 |  | 325-01-913-PD-02 | Outlet LPG line | Automatic on/off valve | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI2-7 | C5/C5S2 | C5S2-7/P5-TBDI2-7 | P5-TBDI2-7/C5S2-7 | XV-913201_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
505 | Gas Vaporizer 4 | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
506 | XA-913201A | XA-80305A | 325-01-913-PD-02 | Gas Vaporizer 4 Run Status | Gas vaporizer Ready | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-15 | C5/C5S1 | C5S1-15/P5-TBDI1-15 | P5-TBDI1-15/C5S1-15 | XA-80305A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
507 | XA-913201B | XA-80305B | 325-01-913-PD-02 | Gas Vaporizer 4 Alarm status | Gas vaporizer Run | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-16 | C5/C5S1 | C5S1-16/P5-TBDI1-16 | P5-TBDI1-16/C5S1-16 | XA-80305B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
508 | XA-913201C | XA-80305C | 325-01-913-PD-02 | Gas Vaporizer 4 High Temp Shut-Down status | Gas vaporizer Failed | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-17 | C5/C5S1 | C5S1-19/P5-TBDI1-17 | P5-TBDI1-17/C5S1-19 | XA-80305C_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
509 | XA-913201D | XA-80305D | 325-01-913-PD-02 | Gas Vaporizer 4 Working Temp Shun-Off status | Gas vaporizer Overheated | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-18 | C5/C5S1 | C5S1-20/P5-TBDI1-18 | P5-TBDI1-18/C5S1-20 | XA-80305D_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
510 | XA-913201E | XA-80305E | 325-01-913-PD-02 | Gas Vaporizer 4 Low Water Shun-Off status | Gas vaporizer Excessive flow tripped | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-19 | C5/C5S1 | C5S1-21/P5-TBDI1-19 | P5-TBDI1-19/C5S1-21 | XA-80305E_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
512 | XS-913201A | XS-80305A | 325-01-913-PD-02 | Start Command for Gas Vaporizer 4 | Start Command | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | RIO-200 | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
512 | XS-913201B | XS-80305B | 325-01-913-PD-02 | Stop Command for Gas Vaporizer 4 | Stop Command | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | RIO-200 | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
513 | Gas Vaporizer 5 | - | - |  |  | - | - | TYP-MECH | N/A | Standard Mechanical Typical | Local Dial | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | MECHANICAL | Pending Sign-off
514 | XA-913202A | XA-80306A | 325-01-913-PD-02 | Gas Vaporizer 5 Run Status | Gas vaporizer Ready | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-21 | C5/C5S1 | C5S1-23/P5-TBDI1-21 | P5-TBDI1-21/C5S1-23 | XA-80306A_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
515 | XA-913202B | XA-80306B | 325-01-913-PD-02 | Gas Vaporizer 5 Alarm status | Gas vaporizer Run | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-22 | C5/C5S1 | C5S1-24/P5-TBDI1-22 | P5-TBDI1-22/C5S1-24 | XA-80306B_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
516 | XA-913202C | XA-80306C | 325-01-913-PD-02 | Gas Vaporizer 5 High Temp Shut-Down status | Gas vaporizer Failed | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-23 | C5/C5S1 | C5S1-25/P5-TBDI1-23 | P5-TBDI1-23/C5S1-25 | XA-80306C_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
517 | XA-913202D | XA-80306D | 325-01-913-PD-02 | Gas Vaporizer 5 Working Temp Shun-Off status | Gas vaporizer Overheated | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-24 | C5/C5S1 | C5S1-26/P5-TBDI1-24 | P5-TBDI1-24/C5S1-26 | XA-80306D_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
518 | XA-913202E | XA-80306E | 325-01-913-PD-02 | Gas Vaporizer 5 Low Water Shun-Off status | Gas vaporizer Excessive flow tripped | Dry Contact | On-Off | TYP-DI-01 | TBDI | PANEL WIRING DIAGRAM.dwg | RIO-200 | P5-TBDI1-25 | C5/C5S1 | C5S1-27/P5-TBDI1-25 | P5-TBDI1-25/C5S1-27 | XA-80306E_DI_1 | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | READY FOR TEST | Pending Sign-off
519 | XS-913202A | XS-80306A | 325-01-913-PD-02 | Start Command for Gas Vaporizer 5 | Start Command | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | RIO-200 | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off
520 | XS-913202B | XS-80306B | 325-01-913-PD-02 | Stop Command for Gas Vaporizer 5 | Stop Command | 24 VDC energized | On-Off | TYP-DO-01 | TBDO | PANEL WIRING DIAGRAM.dwg | RIO-200 | - | - | - | - | - | [ ] Pass | ____ MΩ | [ ] 24V | ____ mA | ____ mA | ____ mA | [ ] Pass | RESERVE ALLOC | Pending Sign-off

## 04_ITP_Inspection_Plan
KALASIN ENGINEERING ¦ INSPECTION & TEST PLAN (ITP) — INSTRUMENTATION & CONTROL SYSTEMS
Quality Assurance & Control Verification Matrix (H = Hold Point, W = Witness Point, R = Review of Records)
Item # | Activity / Inspection Description | Reference Standard / Spec | Acceptance Criteria | Verifying Document | Contractor (Kalasin) | Client (Ingredion) | Third Party / TUV | Milestone Stage
1 | Receiving Inspection of Field Instruments & Transmitters | Project Instrument Datasheets | Damage-free, correct model, serial no., tag plate | Material Receiving Report (MRR) | H (Perform) | W (Witness) | R (Review) | Pre-Installation
2 | Cable Tray, Conduit & Field Gland Integrity Inspection | IEC 60079-14 / NEC 500 | Proper earthing, fire stops, Ex d/e rated glands | Cable Installation Record | H (Perform) | W (Witness) | R (Review) | Pre-Commissioning
3 | Field Instrument Mechanical Mounting & Impulse Piping | P&ID / Hook-up Drawings | Vibration-free, correct slopes, 5-valve manifolds tight | Mechanical Completion Cert | H (Perform) | W (Witness) | R (Review) | Pre-Commissioning
4 | Cable Continuity & Insulation Resistance (Megger Test) | IEC 62381 Clause 5.2 | Core-Core & Core-Earth > 20 MΩ @ 500VDC | Cold Loop Check Sheet | H (Perform) | W (Witness) | R (Review) | Loop Test Phase 1
5 | Shield Single-Point Earthing & Barrier Ground Bar | ISA-RP60.8 / IEC 60079-11 | Single-point earth at CA1 only. IS ground < 1.0 Ω | Earthing Test Certificate | H (Perform) | H (Hold) | W (Witness) | Loop Test Phase 1
6 | Hot Loop 24VDC Power Verification & Polarity Check | ControlLogix Wiring Diagram | Voltage 24VDC ±10%. Correct polarity without shorts | Power-Up Inspection Log | H (Perform) | R (Review) | R (Review) | Loop Test Phase 2
7 | Analog Transmitter 5-Point Calibration Simulation (AI) | IEC 62381 Clause 5.3 | Accuracy ≤ ±0.5% span at 0, 25, 50, 75, 100% | Loop Calibration Record | H (Perform) | W (Witness) | R (Review) | Loop Test Phase 3
8 | Control Valve Modulation Stroke & Fail-Safe Test (AO) | ISA-75.05 / IEC 60534 | Stroke error ≤ 1.0%. Fail-safe action < 2 sec | Valve Stroke Test Sheet | H (Perform) | H (Hold) | R (Review) | Loop Test Phase 4
9 | Discrete Limit Switch & Solenoid Valve Function Check | P&ID & Logic Diagram | 100% position switch fidelity & travel time < 3 sec | Discrete Check Sheet | H (Perform) | W (Witness) | R (Review) | Loop Test Phase 4
10 | Safety Interlock Trip & Emergency Shutdown (ESD) Test | Process Cause & Effect Matrix | 100% trip execution, alarm banner flashing, horn | Safety Trip Protocol | H (Perform) | H (Hold) | H (Hold) | Loop Test Phase 5
11 | SCADA Graphic HMI Representation & Alarm Logging | SCADA Architecture Spec | Real-time updates, engineering units, alarm logs | HMI Verification Log | H (Perform) | W (Witness) | R (Review) | Loop Test Phase 5
12 | Punchlist Clearance (Category A Zero-Defect Handover) | Contract Commissioning Spec | Zero Category A items. Cat B clearance schedule agreed | Punchlist Clearance Form | H (Perform) | H (Hold) | R (Review) | Final Handover

## 05_Loop_Test_Form_Template
KALASIN ENGINEERING ¦ INSTRUMENT LOOP CHECK CERTIFICATE
PROJECT: SPRINT 18K TPA SPRAY DRYER / JET COOKER ¦ CLIENT: INGREDION (THAILAND) CO., LTD.
Tag Number: | FT-40201 | P&ID Number: | 325-01-402-PD-02 | Service Desc: | Slurry Infeed Mass Flow Transmitter
Signal Type: | 4 - 20 mA HART | Calibrated Range: | 0 - 15,000 kg/hr | Eng. Units: | kg/hr
Junction Box: | JB-401 (Floor 2F) | Marshaling TB: | P1-TBDI1-19 | PLC Channel: | Chassis C1 / Slot 4 / Pin 21
PLC Tag Name: | FT-40201_AI_1 | Manufacturer: | Endress+Hauser | Model Series: | Promass F 300 / 83F Coriolis
TEST EQUIPMENT & CALIBRATOR TRACEABILITY
Equipment Type | Manufacturer / Model | Serial Number | Calibration Expiry Date | Accuracy | Cal Certificate #
Documenting Process Calibrator | Fluke 754 | FLK-754-98421 | 31-DEC-2026 | ±0.01% Reading | NIST-2026-98102
5-POINT ANALOG LOOP SIMULATION & CALIBRATION RESULTS
Test Point (%) | Input Signal (mA) | Expected Value (EU) | Field Meas (mA) | SCADA Reading (EU) | PLC Raw Counts | Error (% Span) | Result (Pass/Fail)
0.0 % (Zero) | 4.00 mA | 0.0 kg/hr | 4.001 mA | 0.0 kg/hr | 0 counts | +0.01 % | PASS
25.0 % (Quarter) | 8.00 mA | 3,750.0 kg/hr | 8.002 mA | 3,751.2 kg/hr | 8192 counts | +0.02 % | PASS
50.0 % (Mid-scale) | 12.00 mA | 7,500.0 kg/hr | 11.998 mA | 7,498.5 kg/hr | 16384 counts | -0.01 % | PASS
75.0 % (Three-Quarter) | 16.00 mA | 11,250.0 kg/hr | 16.003 mA | 11,252.1 kg/hr | 24576 counts | +0.03 % | PASS
100.0 % (Full Span) | 20.00 mA | 15,000.0 kg/hr | 19.997 mA | 14,996.8 kg/hr | 32767 counts | -0.02 % | PASS
TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Title | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag Affixed
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | Ready for Wet Commissioning
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared for Operation

## 06_CAD_Loop_Wiring_Reference
KALASIN ENGINEERING ¦ CAD INSTRUMENT LOOP DIAGRAM & PANEL WIRING SPECIFICATION
Application of LOOP DIAGRAM WRING.dwg & PANEL WIRING DIAGRAM.dwg (DWG & DXF) to Project Sprint 18K TPA
1. CAD SOURCE DRAWINGS & DXF CONVERSION MASTER AUDIT
Drawing Filename | File Format | File Size | Modelspace Entities | Text Annotations | Block Definitions | Conversion Tool | Engineering Application Scope
LOOP DIAGRAM WRING.dwg | AutoCAD DWG (v2018) | 2.05 MB | 48,670 entities | 18,638 texts | 1,138 blocks | Native Client Source | Field-to-Marshalling 3-Zone Loop Typicals (AI, AO, DI, DO, IS)
LOOP DIAGRAM WRING.dxf | AutoCAD DXF (ASCII) | 28.37 MB | 48,670 entities | 18,638 texts | 1,138 blocks | dwg2dxf (GNU LibreDWG) | Fully Parsable Open CAD Format / ezdxf Programmatic Automation
PANEL WIRING DIAGRAM.dwg | AutoCAD DWG (v2018) | 4.53 MB | 22,994 entities | 9,462 texts | 1,107 blocks | Native Client Source | Marshalling CA1 & RIO-200 Internal Wiring, Fuses, Diode Redundancy
PANEL WIRING DIAGRAM.dxf | AutoCAD DXF (ASCII) | 100.82 MB | 22,994 entities | 9,462 texts | 1,107 blocks | dwg2dxf (GNU LibreDWG) | Full High-Resolution Vector Export for Electrical CAD Integration
2. 3-ZONE INSTRUMENT WIRING ARCHITECTURE & TERMINAL DESIGNATIONS
Physical Zone | CAD Drawing Block / Column | Terminal Prefix | Terminal Model / Spec | Wire Color Standard | Core / Pair Tagging | Shield Treatment Philosophy | Inspection Checkpoint
Zone 1: FIELD | FIELD column (Transmitter, Valve, Switch) | Terminals 1(+), 2(-), PE | M20 / 0.5-inch NPT Ex-d/Ex-e Gland | White (+), Black (-) | Branch 1Px0.75mm² or 1Px1.5mm² | CUTBACK & TAPE (Floating, isolated from instrument housing) | Verify cable gland IP66/67, seal, O-ring, and floating shield
Zone 2: JUNCTION BOX | JUNCTION BOX column (JB-401..618, IS-JB) | TBAI, TBAO, TBDI, TBDO, TBCI | Weidmüller WDU 2.5 / Phoenix UK | White (+), Black (-) | PR 1..PR 24 (Pair numbers marked) | SH Feedthrough (Isolated rail, NOT bonded to JB enclosure frame) | Check terminal torque 0.6Nm, wire ferrules, trunk gland earthing
Zone 3: MARSHALLING | CONTROL ROOM column (Cabinet CA1 / RIO-200) | TBDAI, TBDAO, TBDDI, TBDDO | WSI 6-LD (0.5A Fuse) / Disconnect | White (+), Black (-), Red/Blue | Multi-pair 24Px0.75mm² Re-2Y(st)-Yv | IE Instrument Earth (Single-Point Star bonded to Clean Earth Pit) | Verify fuse rating (0.5A fast), disconnect knife closed, IE <1.0Ω
Zone 3: PLC I/O RACK | 1756 ControlLogix / 1794 FLEX I/O | RTB Terminal (Chassis C1..C5) | 1756-TBCH / 1794-TB3 Removable TB | Grey (DC+), Blue (DC-), White (Sig) | Pre-formed wiring harness to CA1 | Internal chassis backplane isolated ground | Verify card LED active, channel OK, tag scaled in ControlLogix
3. MASTER CAD TYPICAL LOOP WIRING CONFIGURATIONS & COMMISSIONING PROCEDURES
CAD Typical ID | Instrument Loop Category | Sample Project Tags | Terminal Strip | Signal Standard | Power Source | Commissioning Cold Check | Commissioning Hot / Calibration Check
TYP-AI-01 | 2-Wire Loop Powered Analog Transmitter | PT-10080, LT-10081, TT-10085, PDT-60101 | TBAI.xx | 4-20mA DC (2-Wire) | 24VDC from CA1 Marshalling | Megger core-to-earth >20MΩ @ 500VDC, continuity <2.0Ω | Inject 4, 8, 12, 16, 20 mA via Fluke 789 at field terminals; verify ControlLogix tag scaling ±0.2%
TYP-AI-02 | 4-Wire Active Powered Analog Transmitter | FT-102900, FT-102901, FT-106003, DT-106004 | TBAI.xx | 4-20mA DC (Active Output) | 220VAC / 24VDC Aux Power | Megger power and signal cores separately >20MΩ | Power up instrument; measure 24VDC/220VAC; simulate 0-100% flow from local transmitter menu; check SCADA
TYP-AO-01 | 4-20mA SMART Control Valve Positioner | FCV-102900-1, FCV-102901-1, FCV-106003-1 | TBAO.xx | 4-20mA Command + Travel FB | 4-20mA loop powered positioner | Loop resistance check (typ. 250-450Ω), air supply 5.5 bar | Force 4, 8, 12, 16, 20 mA from ControlLogix; verify 0, 25, 50, 75, 100% physical stroke and limit switches
TYP-DI-01 | Discrete Status / Limit / Level Switch | LSH-60101, LSL-60102, ZSO-102900, ZSC-102900 | TBDI.xx | 24VDC Interrogation Contact | 24VDC Wetting Voltage from CA1 | Contact open = ∞ MΩ, contact closed = <2.0Ω | Verify 24VDC at field contact; actuate switch manually; verify PLC card LED on/off and HMI alarm latching
TYP-DO-01 | Solenoid Valve / Interposing Relay Drive | XV-102900, SOV-102901, SV-60101, PMP-40101 | TBDO.xx | 24VDC Switched Output | 24VDC from 1756-OB32 / Omron Relay | Coil resistance check (typ. 30-120Ω), diode polarity check | Command DO bit from ControlLogix; verify interposing relay pull-in, 24VDC at solenoid, pneumatic actuation
TYP-IS-01 | Intrinsically Safe Ex Loop (Hazardous Area) | Loops landed in IS-JB-603, 608, 612, 618 | TB-IS.xx (Blue) | Ex-ia / Ex-ib Certified Loop | Galvanic Isolator (MTL / P+F) in CA1 | Verify blue trunk cable, isolated shield, clearance >50mm | Measure barrier output Voc, Isc; verify entity parameter matching (Ca > C_cable + C_inst, La > L_cable + L_inst)
4. MARSHALLING CABINET (CA1) INTERNAL ARRANGEMENT & 24VDC POWER SYSTEM
Subsystem Component | Specification / Model in DWG | Location in CA1 | Redundancy / Protection Mechanism | Testing & Verification Requirement
Primary Power Supplies (PSU1 & PSU2) | Phoenix Contact Quint Power 24VDC / 40A | Cabinet Base DIN Rail (Left & Right) | N+1 Active Redundancy via Diode Decoupling Module | Simulate AC supply failure on PSU1; verify seamless 24VDC transfer without PLC dip
Branch Circuit Fuses | Weidmüller WSI 6-LD / WDU 2.5 with 0.5A fast fuse | Marshalling Terminal Rails TBX204..TBX207 | Individual channel fuse isolation with blown-fuse LED | Measure loop voltage drop across fuse holder (<0.1VDC); verify fuse LED indicator
Dual Earthing Busbars | PE (Protective Earth) & IE (Instrument Earth) | Cabinet Bottom Isolated Copper Bars (PE=Direct, IE=Isolated) | Single-Point Grounding architecture prevents ground loop hum | Measure resistance between IE bar and clean earth pit (<1.0Ω); check IE-to-PE isolation (>10MΩ)
Internal Wire Ducting | Slotted PVC Trunking 40x100mm & 70x100mm | Vertical & Horizontal Cabinet Wireways | Physical segregation between 24VDC signal and 220VAC power | Inspect 50mm separation between IS blue ducts and non-IS grey ducts; 50% fill factor
PLC Remote I/O Adapters | 1794-AENTR / 1756-EN2TR Dual Port EtherNet/IP | Chassis Mounting Plates | Device Level Ring (DLR) fault-tolerant network topology | Perform network ring break test; verify zero packet loss to central ControlLogix processor