## 00_Executive_Summary
KALASIN ENGINEERING ¦ QUOTATION (BOQ) vs. JUNCTION BOX SCHEDULE COMPARISON REPORT
PROJECT: SPRINT 18K TPA SPRAY DRYER IN THAILAND ¦ Quotation_R02.xlsx (BOQ D2510-775 R.2) vs. IO_List_By_Junction_Box.xlsx (Distributed Architecture)
QUOTED CAPACITY (BOQ) |  | JB SCHEDULE CAPACITY |  |  | SYSTEM ACTIVE SIGNALS |  |  | RESERVE SPARE CAPACITY
720 Points |  | 1,274 Points |  |  | 713 Points |  |  | 44.0% Spare
39 Modules (Centralized Rack) |  | 54 Modules across 5 Chassis (+76.9%) |  |  | Wired across 16 Field Enclosures |  |  | 561 Reserve Points (Exceeds >=20% Spec)
1. MASTER I/O POINT HARDWARE & CAPACITY RECONCILIATION
Signal Family | Quotation Card Catalog | Quoted Qty | Quoted Cap | JB Schedule Card Catalog | JB Qty | JB Total Cap | Active Used | Spare Pts | Spare Margin | Technical Variance & Scope Delta
Digital Input (DI) | 1756-IB32 (32-ch Sink) | 12 | 384 | 1756-IB32 (32-ch Sink/Source) | 17 | 544 | 334 | 210 | 38.6% | +5 Modules (+160 pts / +41.7%). Fulfills >= 20% spare spec.
Digital Output (DO) | 1756-OB32 (32-ch Source) | 5 | 160 | 1756-OB32 (32-ch Transistor) | 10 | 306 | 122 | 184 | 60.13% | +5 Modules (+146 pts / +91.3%). Massive expansion for valve interlocks.
Analog Input (AI) | 1756-IF8H (8-ch Isolated HART) | 18 | 144 | 1756-IF16 (16-ch High Density) | 26 | 416 | 252 | 164 | 39.42% | +8 Modules (+272 pts / +188.9%). Value engineered to 16-channel card.
Analog Output (AO) | 1756-OF8H (8-ch Isolated HART) | 4 | 32 | 1756-OF8 (8-ch Voltage/Current) | 1 | 8 | 5 | 3 | 37.5% | -3 Modules (-24 pts / -75.0%). Optimized for 5 active control valves.
TOTAL PROCESS I/O | ControlLogix Baseline | 39 | 720 | ControlLogix Distributed | 54 | 1274 | 713 | 561 | 44.03% | +15 Modules (+554 Pts / +76.9% Capacity Expansion)
Common / Power Pins | Not Separately Listed | - | - | Dedicated 24VDC Bus Pins | - | 150 | - | - | - | 68 DI Commons + 18 DO Commons + 52 AI Commons + 12 AO
TOTAL PHYSICAL TERMINATIONS | 720 Standard Terminals | - | 720 | 1,424 Marshaled Pins | - | 1424 | 713 | 711 | 49.93% | Complete physical wiring footprint across 16 enclosures
2. SYSTEM ARCHITECTURE & CORE HARDWARE SPECIFICATION UPGRADE
Component / System Attribute | Baseline Quotation Specification | JB Schedule Implementation | Engineering Rationale & Functional Advantage
Process Controller (CPU) | 1x 1756-L81E (ControlLogix 5580, 3MB) | 1x 1756-L950TPSXT (Extreme Temp, 50MB, Conformal Coated) | Handles larger distributed tag database and harsh environment (spray dryer heat/moisture)
Network Scanner / Adapters | 4x 1756-EN2TR (100 Mbps Copper DLR) | 1756-EN4TR (1 Gbps High-Speed Fiber/Copper DLR Scanner) | 10x network bandwidth for real-time cyclic I/O transfer between 5 chassis
System Architecture Topology | Centralized Single Control Cabinet (CA1) | Distributed 5-Chassis Suite (C1, C2 in CA1; C3, C4 in Tower; C5 in Slurry) | Eliminates hundreds of long-distance multicores, prevents electrical noise coupling
Field Enclosure Scope | Line 143: 'JUNCTION BOX: 1 LOT' (Unspecified) | 16 Engineered Enclosures (8 SS304 Food-Grade + 4 ATEX Ex ia SS316 + 3 Panels) | Resolves generic lump sum into certified sanitary food-grade and ATEX hazardous equipment
Contractual Spare Compliance | 13.1% Overall Spare (Fails >=20% on DI: 6.5% & DO: 10.0%) | 44.0% Overall Spare (DI: 38.6%, DO: 60.1%, AI: 39.4%, AO: 37.5%) | Guarantees complete compliance with plant automation expansion specifications

## 01_Chassis_Architecture_C1_C5
DISTRIBUTED CONTROL CHASSIS (C1 TO C5) UTILIZATION & CAPACITY BREAKDOWN
Detailed engineering breakdown of all 5 Rockwell ControlLogix racks, physical locations, signal loads, and reserve margins
Chassis Code | Panel Tag | Chassis Description & Function | Physical Location / Enclosure | DI Used | DI Spare | DI % | DO Used | DO Spare | DO % | AI Used | AI Spare | AI % | AO Used | AO Spare | Total Active Pts
C1 | Panel P1 | Main Controller Rack (1756-L950TPSXT) | Main Control Room (Control Cabinet CA1) | 83 | 45 | 35.16% | 36 | 32 | 47.06% | 38 | 26 | 40.63% | - | - | 157
C2 | Panel P2 | Main Expansion High-Density Rack | Main Control Room (Control Cabinet CA1) | 128 | 32 | 20% | 52 | 50 | 49.02% | 46 | 82 | 64.06% | - | - | 226
C3 | Panel P3 | Remote I/O Rack 1 (Spray Dryer / Packing) | Field RIO Cabinet (Spray Dryer Tower 4F) | 33 | 63 | 65.63% | 25 | 43 | 63.24% | 102 | 26 | 20.31% | 5 | 3 | 165
C4 | Panel P4 | Remote I/O Rack 2 (Upper Tower & IS Hub) | Upper Spray Dryer Tower (6th / 8th Floor) | 50 | 46 | 47.92% | 1 | 33 | 97.06% | 48 | 16 | 25% | - | - | 99
C5 | Panel P5 | Remote I/O Station 5 (Slurry Building RIO-200) | Slurry Building 2nd Floor (RIO Room) | 40 | 24 | 37.5% | 8 | 26 | 76.47% | 18 | 14 | 43.75% | - | - | 66
TOTAL | 5 Panels | Complete Rockwell Automation Distributed Platform | Central Control Room + Remote Field Stations | 334 | 210 | 38.6% | 122 | 184 | 60.13% | 252 | 164 | 39.42% | 5 | 3 | 713

## 02_Field_Enclosures
FIELD ENCLOSURE & JUNCTION BOX RECONCILIATION (16 FIELD ENCLOSURES)
Detailed engineering specifications of the 16 Junction Boxes & Control Panels that replace Quotation Line 143 ('JUNCTION BOX: 1 LOT')
Enclosure Tag | Classification | Area Description & Process Location | Dimensions (HWD mm) | Material & Ingress Standard | DI Used | DO Used | AI Used | Active Pts | Spare Pts | Spare % | Connected Control Panel / Rack | Home-Run Trunk Cable Specification
JB-401 | Standard Process | Jet Cooker Infeed Area 2nd Floor | 600 x 500 x 200 mm | IP66 / SS304 (Sanitary Food Grade) | 50 | 24 | 22 | 96 | 24 | 20% | Panel P1 (Chassis C1) | 1x CVV 24Cx1.5 Control + 1x LiY-CY 16Px0.75 Analog to CA1
JB-402 | Standard Process | Jet Cooker Processing Skid 2F | 450 x 300 x 150 mm | IP66 / SS304 (Industrial Hygienic) | 24 | 9 | 14 | 48 | 35 | 42.17% | Panel P2 (Chassis C2) | 1x CVV 18Cx1.5 Control + 1x LiY-CY 12Px0.75 Analog to CA1
JB-601 | Standard Process | Spray Dryer Ground Floor 1F (Base / Discharge) | 500 x 400 x 200 mm | IP66 / SS304 (Sanitary Food Grade) | 33 | 12 | 16 | 61 | 35 | 36.46% | Panel P1 (Chassis C1) | 1x CVV 18Cx1.5 Control + 1x LiY-CY 12Px0.75 Analog to CA1
JB-602 | Standard Process | Spray Dryer Cyclone & Exhaust 3F | 800 x 600 x 250 mm | IP66 / SS304 (Sanitary Food Grade) | 23 | 3 | 58 | 86 | 27 | 23.89% | Panel P2 (Chassis C2) | 1x CVV 24Cx1.5 Control + 1x LiY-CY 16Px0.75 Analog to CA1
JB-606 | Standard Process | Spray Dryer Filter Cleaning 6F (Burner Area) | 300 x 200 x 150 mm | IP66 / SS304 (Sanitary Food Grade) | 4 | 1 | 4 | 9 | 45 | 83.33% | Panel P3 (Chassis C3) | 1x CVV 18Cx1.5 Control + 1x LiY-CY 4Px0.75 Analog to Panel P3
JB-607 | Standard Process | Spray Dryer Mid-Tower 4F (Main High-Density Hub) | 1000 x 800 x 300 mm | IP66 / SS304 (Sanitary Food Grade) | 81 | 40 | 54 | 177 | 51 | 22.37% | Panel P2 & P3 | 2x CVV 24Cx1.5 Control + 2x LiY-CY 16Px0.75 Analog Trunks
JB-608 | Standard Process | Spray Dryer Tower 4F Auxiliary Deck | 300 x 200 x 150 mm | IP66 / SS304 (Sanitary Food Grade) | 0 | 0 | 2 | 2 | 0 | 0% | Panel P3 (Chassis C3) | Local Field Multi-core Trunk to Panel P3
JB-612 | Standard Process | Spray Dryer Upper Tower (6th / 8th Floor) | 600 x 500 x 200 mm | IP66 / SS304 (Sanitary Food Grade) | 17 | 15 | 8 | 40 | 32 | 44.44% | Panel P4 (Chassis C4) | 1x CVV 24Cx1.5 Control + 1x LiY-CY 12Px0.75 Analog to Panel P4
JB-618 | Standard Process | Packing Tower Building & Storage Silos | 600 x 400 x 200 mm | IP66 / SS304 (Sanitary Food Grade) | 12 | 9 | 8 | 29 | 53 | 64.63% | Panel P3 (Chassis C3) | 1x CVV 18Cx1.5 Control + 1x LiY-CY 8Px0.75 Analog to Panel P3
IS-JB-603 | ATEX Ex ia (IS) | Hazardous Area Zone 1/21 (Lower Chamber) | 500 x 400 x 200 mm | ATEX Ex ia (Blue Terminals / IP66 SS316) | 15 | 0 | 14 | 29 | 3 | 9.38% | Panel P4 (IS Hub) | 1x LiY-CY(EB) 16Px0.75 Blue IS Shielded Trunk to IS Barriers
IS-JB-608 | ATEX Ex ia (IS) | Hazardous Area Zone 1/21 (Mid-Tower Powder Zone) | 600 x 500 x 200 mm | ATEX Ex ia (Blue Terminals / IP66 SS316) | 7 | 1 | 12 | 20 | 38 | 65.52% | Panel P4 (IS Hub) | 1x LiY-CY(EB) 16Px0.75 Blue IS Shielded Trunk to IS Barriers
IS-JB-612 | ATEX Ex ia (IS) | Hazardous Area Zone 1/21 (Upper Tower / Vent) | 500 x 400 x 200 mm | ATEX Ex ia (Blue Terminals / IP66 SS316) | 15 | 0 | 4 | 19 | 17 | 47.22% | Panel P4 (IS Hub) | 1x LiY-CY(EB) 12Px0.75 Blue IS Shielded Trunk to IS Barriers
IS-JB-618 | ATEX Ex ia (IS) | Hazardous Area Zone 1/21 (Packing Tower & Silos) | 600 x 400 x 200 mm | ATEX Ex ia (Blue Terminals / IP66 SS316) | 13 | 0 | 18 | 31 | 29 | 48.33% | Panel P4 (IS Hub) | 1x LiY-CY(EB) 16Px0.75 Blue IS Shielded Trunk to IS Barriers
CA1 | Main Control Room | Central Automation Suite (Chassis C1 & C2) | 2200 x 800 x 800 mm | NEMA 12 / IP54 Rittal TS8 Bayed Suite | 0 | 0 | 0 | 33 | 98 | 74.81% | Main Controller Suite | Pre-wired Marshaling Trunks, Internal Busbars & 1Gbps Fiber DLR
RIO-200 | Remote Control Panel | Slurry Building 2nd Floor (RIO Room) | 1200 x 800 x 300 mm | IP66 / SS304 (Sanitary Food Grade) | 40 | 8 | 18 | 66 | 64 | 49.23% | Panel P5 (Chassis C5) | 1Gbps EtherNet/IP DLR Fiber Ring + Local Field Multi-core Trunks
MCC | Switchgear Interface | Motor Control Center Switchgear Room | Centerline 2500 Suite | Form 4b Arc-Resistant Switchgear | 0 | 0 | 0 | 0 | 0 | 0% | Motor Feeders & VFDs | Multi-Core Control Trunks (CVV 7Cx1.5) & EtherNet/IP Backbone
TOTAL | 16 Enclosures | Complete Plant-Wide Enclosure Infrastructure | - | SS304 Food Grade & SS316 ATEX | 334 | 122 | 252 | 713 | 561 | 44.03% | 5 Interconnected Chassis | Standardized Trunk Schedule & DLR Fiber Ring

## 03_Cabling_and_Network_Delta
CABLING, NETWORK & MARSHALING INFRASTRUCTURE DELTA
Technical and commercial reconciliation of Cable Schedule (BOQ D3) & Cable Tray (BOQ D4) vs. Distributed Field Engineering
Infrastructure Item | Quotation BOQ Specification | Quoted Qty | JB Schedule Implementation | Engineered Qty / Spec | Engineering Variance & Rationale | Commercial Impact | Variation Order (VO) Status
Digital Control Multicore Trunks | CVV 32C x 1 mm² (Central Home-Run) | 1,980 m | Standardized CVV 18C & 24C x 1.5 mm² to local RIOs | Localized Modular Trunks | Eliminates heavy 32C copper pulling; improves signal voltage drop with 1.5 mm² | Cost Offset (Shorter run) | Scope Substitution
Analog Multi-Pair Trunks | LiY-CY TP 20P x 1 mm² (Overall Shielded) | 1,980 m | Standardized LiY-CY 12P & 16P x 0.75 mm² to local RIOs | Localized Shielded Pairs | Reduces conduit fill factor; terminates directly into high-density IF16 cards | Cost Offset (Shorter run) | Scope Substitution
Hazardous Area IS Trunks | Generic LiY-CY instrument pairs | Included in D3 | Specialized LiY-CY(EB) Blue-Sheathed IS Trunk Cables | Dedicated 12P & 16P Trunks | Mandatory compliance for ATEX Zone 1/21 explosion-proof intrinsically safe circuits | Premium Material | Compliant Upgrade
Plant Network Backbone | CAT6 Outdoor (465m) + Fiber (1 LOT) | 465 m / 1 LOT | 1 Gbps Multimode Fiber Optic Device Level Ring (DLR) | Fiber DLR Ring + Copper Drops | Provides fault-tolerant 1 Gbps ring redundancy between CA1, RIO-1, RIO-2 & RIO-200 | In Base Budget | Approved Design
Field Junction Boxes | Line 143: 'JUNCTION BOX: 1 LOT' | 1 LOT | 16 Specific Enclosures (8 SS304 Food Grade + 4 SS316 ATEX) | 16 Physical Enclosures | Upgrades generic lump sum into certified SS304/SS316 sanitary and explosion-proof boxes | High Addition | Primary VO Item
Remote Control Enclosures | 2x TS Enclosure 2000x800x800mm in CA1 | 2 Ea (CA1) | CA1 Bayed Suite + RIO-200 (1200x800x300mm SS304) + Tower RIOs | 3 Cabinets + 2 Racks | Provides local housing for Chassis C3, C4 and C5 in field areas | Additional Hardware | VO Claim: RIO Enclosures