## 00_Executive_Summary
KALASIN ENGINEERING ¦ COMPREHENSIVE I/O POINT & SCOPE COMPARISON REPORT
PROJECT: SPRINT 18K TPA SPRAY DRYER IN THAILAND ¦ Quotation Ref: BOQ No. D2510-775 R.2 (Quotation_R02.xlsx) vs. Instrument I-O List Rev.3.6a (02 OCT 2026)
QUOTED HARDWARE CAPACITY |  |  | REV.3.6a PROCESS I/O DEMAND |  |  | TOTAL SPARE CHANNELS |  |  | 20% SPARE SPEC COMPLIANCE
720 Channels |  |  | 626 Points |  |  | +94 Points (13.1%) |  |  | DEFICIT ON DI & DO
384 DI ¦ 160 DO ¦ 144 AI ¦ 32 AO (1756 CLX) |  |  | 359 DI ¦ 144 DO ¦ 118 AI ¦ 5 AO (+40 Bus = 666) |  |  | Overall Hardwired Process Spare Capacity |  |  | DI: 6.5% spare ¦ DO: 10.0% spare (Requires VO)
1. MASTER I/O POINT COMPARISON & CONTRACTUAL SPARE MARGIN ANALYSIS (DI, DO, AI, AO)
Signal Family | Hardware Card Catalog | Quoted Qty (Mod) | Quoted Cap (Pts) | Rev.3.6a Demand (Pts) | Main PLC Demand | RIO-200 Demand | Local Panels / MCC | Spare Points (Pts) | Spare Margin (%) | Target Spec | Contractual Status (20% Spec)
Digital Input (DI) | 1756-IB32 (32-ch 24VDC Sink) | 12 | 384 | 359 | 317 | 35 | 7 | 25 | 6.51% | >= 20.0% | DEFICIT (-13.5% vs 20% spec)
Digital Output (DO) | 1756-OB32 (32-ch 24VDC Source) | 5 | 160 | 144 | 131 | 13 | 0 | 16 | 10% | >= 20.0% | DEFICIT (-10.0% vs 20% spec)
Analog Input (AI) | 1756-IF8H (8-ch Isolated HART) | 18 | 144 | 118 | 114 | 4 | 0 | 26 | 18.06% | >= 20.0% | SLIGHT DEFICIT (-1.9% vs 20%)
Analog Output (AO) | 1756-OF8H (8-ch Isolated HART) | 4 | 32 | 5 | 5 | 0 | 0 | 27 | 84.38% | >= 20.0% | COMPLIANT (+64.4% spare)
TOTAL PROCESS I/O | Rockwell ControlLogix 5580 | 39 | 720 | 626 | 567 | 52 | 7 | 94 | 13.06% | >= 20.0% | SYSTEM DEFICIT (13.1% vs 20%)
Communication Bus (EtherNet/IP) | 1756-EN2TR DLR Scanner | 4 | Network | 40 | 37 | 3 | 0 | - | - | N/A | BUS INTEGRATED (37 Main + 3 RIO)
2. INTRINSIC SAFETY (IS) BARRIERS & AMPLIFIERS COMPARISON (HAZARDOUS AREA SCOPE)
Protection Device Description | Quotation Line Item | Quoted Qty (Ea) | Quoted Total Cost (THB) | Rev.3.6a Hazardous Area Demand | Protection Standard | Spare Units (Ea) | Spare Margin (%) | Contractual Status
Safety Barrier For AI/AO Signal | D1 - Line 34 | 27 | 170100 | 22 AI Transmitters (Ex ic / Ex ia) | Ex ic / Ex ia (P&F Isolated) | 5 | 18.52% | COMPLIANT (Healthy Spare)
Switch Amplifier For DI/DO Signal | D1 - Line 35 | 62 | 581560 | 29 DI Signals + 2 DO Valves | Ex ic NAMUR / Dry Contact | 31 | 50% | COMPLIANT (50.0% Spare)
3. CRITICAL ENGINEERING FINDINGS & VARIATION ORDER (VO) RECOMMENDATIONS
Finding 1: Digital Input (DI) Spare Deficit |  |  | Quoted DI capacity is 384 pts. Rev.3.6a demands 359 pts, leaving only 25 spare points (6.51%). This is far below the mandatory 20.0% spare specification (which would require >= 77 spare points, i.e., at least 436 points capacity).
Finding 2: Digital Output (DO) Spare Deficit |  |  | Quoted DO capacity is 160 pts. Rev.3.6a demands 144 pts, leaving only 16 spare points (10.00%). This is also below the 20.0% spare specification (which would require >= 32 spare points, i.e., at least 176 points capacity).
Finding 3: Main PLC Only Spare Status |  |  | If RIO-200 (52 points) is treated as a separate dedicated field enclosure, the Central MCP Cabinet spare becomes 17.4% for DI and 18.1% for DO. Still marginally under 20%.
Finding 4: Major Field Scope Expansions (VO Candidates) |  |  | Field instruments expanded significantly: +3 Coriolis Mass Flowmeters (FT-40201, FT-40221, FT-40222), +2 Gas Detectors, +15 Pneumatic Automated Valves, +8 Temperature Switches, and +5 Level Switches compared to BOQ D2.
Recommendation: Recommended Hardware Addition for VO |  |  | To achieve >= 20.0% spare compliance across all families: (1) Add 3x 1756-IB32 modules (+96 DI) -> Total DI: 480 pts (33.7% spare); (2) Add 1x 1756-OB32 module (+32 DO) -> Total DO: 192 pts (25.0% spare). Total hardware addition = 4 cards.

## 01_IO_Detailed_Breakdown
I/O POINT DETAILED DISTRIBUTION & EXCEL FORMULA AUDIT
Breakdown by Physical Destination, Subsystem Enclosure, and Technical Analysis of Rev.3.6a Row 578 Formula Discrepancy
1. I/O BREAKDOWN BY SIGNAL DESTINATION (MAIN PLC vs. RIO-200 vs. LOCAL PANELS)
Signal Destination ('Signal to') | Primary Enclosure / Location | DI (Pts) | DO (Pts) | AI (Pts) | AO (Pts) | Hardwired Process Total | Bus (Pts) | Total w/ Bus | Active Tags | Architecture & Cabling Notes
PLC | Main Control Cabinet CA1 (Control Room) | 317 | 131 | 114 | 5 | 567 | 37 | 604 | 429 | Primary central control system via 16 Field Junction Boxes
RIO-200 | Remote I/O Cabinet RIO-200 (Slurry Bldg 2F) | 35 | 13 | 4 | 0 | 52 | 3 | 55 | 36 | Slurry preparation, LPG station, & gas vaporizer package
Heat Control Panel (HTRE-21) | Local Electric Heater Control Panel HTRE-21 | 2 | 0 | 0 | 0 | 2 | 0 | 2 | 2 | Tracing heater power on/trip interlock status to local panel
Heat Control Panel (HTRE-22) | Local Electric Heater Control Panel HTRE-22 | 2 | 0 | 0 | 0 | 2 | 0 | 2 | 2 | Tracing heater power on/trip interlock status to local panel
Heat Control Panel (HTRE-23) | Local Electric Heater Control Panel HTRE-23 | 2 | 0 | 0 | 0 | 2 | 0 | 2 | 2 | Tracing heater power on/trip interlock status to local panel
Hard Wired to MCC FANE-21 | Motor Control Center Switchgear Room | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | Direct hardwired interlock to exhaust fan starter
TOTAL ALL ACTIVE FIELD SIGNALS | Complete Rev.3.6a Field Scope | 359 | 144 | 118 | 5 | 626 | 40 | 666 | 471 | Matches full verified instrument schedule
2. TECHNICAL AUDIT: REV.3.6a ROW 578 EXCEL FORMULA vs. TRUE ACTIVE ROW COUNT
Comparison Metric | DI (Col H) | DO (Col G) | AI (Col J) | AO (Col I) | Process I/O Total | Bus (Col K) | Grand Total | Discrepancy Status / Cause | Engineering Significance | Resolution
Rev.3.6a Row 578 Excel Formula Value | 324 | 132 | 117 | 5 | 578 | - | 578 | Omitted 48 points across 4 separate line blocks | Misrepresents true skid I/O requirement | Update formula to SUM(G12:G571)
True Actual Row Count (Rows 12 to 571) | 359 | 144 | 118 | 5 | 626 | 40 | 666 | Verified complete sum of all physical field items | True engineering baseline for hardware sizing | Confirmed accurate baseline
Formula Under-counting Variance (Delta) | 35 | 12 | 1 | 0 | 48 | 40 | 88 | +35 DI, +12 DO, +1 AI, +40 Bus omitted from sum | Hardware would be under-dimensioned by 48 pts | Must size hardware for 626 pts minimum
3. DETAILS OF ROW BLOCKS OMITTED FROM REV.3.6a ROW 578 FORMULA
Omitted Row Range | Subsystem / Package Description | Omitted DI | Omitted DO | Omitted AI | Omitted AO | Omitted Bus | Key Tags / Item Names | P&ID / Package Reference | Reason for Formula Omission | Hardware Impact
Rows 398 - 409 | Fugitive, Vacuum & Exhaust Dust Filters (FA-61310/11/12) | 3 | 3 | 0 | 0 | 0 | FA-61310, FA-61311, FA-61312 Start/Stop & Alarms | Bag Filter Vendor Skid | Skipped when inserting filter sub-rows | Requires 3 DI + 3 DO channels
Row 415 | Bag House Air Pulsing DP Transmitter | 0 | 0 | 1 | 0 | 0 | DPI-60240 (Bag House Air Pulsing) | 325-01-602-PD-05 | Formula jumped from 414 to 417 | Requires 1 AI channel
Rows 503 - 514 | Explosion Suppression System Panel (XSUP-5601) | 12 | 0 | 0 | 0 | 0 | XA-60202A through XA-60202M (Arm, Trip, Fault) | Safety Skid Package | Formula jumped from 496 to 533 | Requires 12 DI safety channels
Rows 516 - 523 | Fire Deluge Skids (PK-60221 & PK-60222) | 4 | 2 | 0 | 0 | 0 | XA-60261/62 (Deluge Fault & Alarm), XS-60260 Start | Fire Protection Skid | Formula jumped from 496 to 533 | Requires 4 DI + 2 DO channels
Rows 527 - 531 | Kaeser Bin Aerator Blower Package | 4 | 1 | 0 | 0 | 0 | Start/Stop, Run Status, Local/Remote, Fault, Warning | Pneumatic Conveying Package | Formula jumped from 496 to 533 | Requires 4 DI + 1 DO channels
Row 563 | Gas Vaporizer 4 Stop Command | 0 | 1 | 0 | 0 | 0 | XS-80305B (Stop Command Gas Vaporizer 4) | 325-01-913-PD-02 | Typo in range: 557:562 stopped at Start cmd | Requires 1 DO channel
TOTAL OMITTED SIGNALS | Sum of all signals missing from formula | 23 | 7 | 1 | 0 | 0 | 48 Process Pts Total | - | Manual multi-range Excel formula error | Crucial to capture in hardware sizing

## 02_Field_Instrument_Comparison
FIELD INSTRUMENT SCOPE COMPARISON: BOQ ITEM D2 vs. REV.3.6a INSTRUMENT SCHEDULE
Detailed Item-by-Item Scope Reconciliation between Quotation BOQ (D2510-775 R.2) and Latest Field Engineering Tag List
BOQ Line Item | Instrument Family / Category | Quotation Item Description | Quoted Qty | Unit | Rev.3.6a Count | Variance (Delta) | Scope Status | Identified Tags / Equipment Model in Rev.3.6a | Process Function & Location | Variation Order (VO) Commercial Impact
D2 - 83 | ANALYZER | PH ANALYZER | 2 | Ea | 2 | 0 | EXACT MATCH | pHT-40201, pHT-40202 | Slurry feed pH monitoring | In base contract
D2 - 84 | ANALYZER | DUST ANALYZER | 1 | Ea | 1 | 0 | EXACT MATCH | AT-60241 (DTEX-22) | Exhaust duct emission compliance | In base contract
D2 - 85 | ANALYZER | GAS ANALYZER / DETECTOR | 2 | Ea | 4 | 2 | ADDED (+2) | XT-60201, XT-92201, GD-913201, GD-913202 | LPG area & burner hazardous gas detection | VO Claim: +2 Gas Detectors
D2 - 87 | FLOW METER | ROTA METER | 5 | Ea | 5 | 0 | EXACT MATCH | Local direct-reading rotameters | Purge water & seal flush lines | In base contract
D2 - 90-92 | FLOW TRANSMITTER | MAGNETIC FLOW (2", 3", 4") | 3 | Ea | 3 | 0 | EXACT MATCH | FT-40202 (3"), FT-936201 (4"), FT-936202 (2") | Process water & slurry metering | In base contract
D2 - 94-95 | FLOW TRANSMITTER | VORTEX FLOW (4", 6") | 2 | Ea | 2 | 0 | EXACT MATCH | FT-60202 (6"), FT-60203 (4") | High-pressure culinary & plant steam | In base contract
D2 - 96 | FLOW TRANSMITTER | TURBINE FLOW 4" | 1 | Ea | 1 | 0 | EXACT MATCH | FT-60204 | Plant auxiliary fuel/air line | In base contract
D2 - 97 | FLOW TRANSMITTER | THERMAL MASS FLOW | 6 | Ea | 6 | 0 | EXACT MATCH | FT-60201, FT-60210, FT-60211, FT-60221, FT-61307, FT-60204 | Compressed air & combustion gas headers | In base contract
D2 - 98 | FLOW TRANSMITTER | ULTRA-SONIC FLOW | 16 | Ea | 16 | 0 | EXACT MATCH | FT-60261FA..FD, FT-60262FE..FH, FT-60263FJ..FM, FT-60264FN..FR | Cooling water & spray nozzle manifolds | In base contract
D2 - 99 | FLOW TRANSMITTER | CORIOLIS MASS FLOW 2" | 1 | Ea | 4 | 3 | ADDED (+3) | FT-40201 (2"), FT-40221 (2"), FT-40222 (2"), FT-913201 | Precision slurry feed & LPG mass delivery | VO Claim: +3 High-Value Coriolis
D2 - 100 | LEVEL SWITCH | LEVEL SWITCH (Vibrating Fork) | 12 | Ea | 17 | 5 | ADDED (+5) | LSH-61301/03/06/08, LSL-61302/07/09, LS-814201.. | Bin overflow prevention & sump alarms | VO Claim: +5 Level Switches
D2 - 102 | LEVEL TRANSMITTER | DIFFERENTIAL PRESSURE TYPE | 4 | Ea | 4 | 0 | EXACT MATCH | LT-40201, LT-40202, LT-40203, LT-61301 | Slurry preparation & storage tanks | In base contract
D2 - 103 | LEVEL TRANSMITTER | RADAR TYPE LEVEL TRANSMITTER | 1 | Ea | 1 | 0 | EXACT MATCH | LT-913201 (LPG Storage Tank) | Non-contact radar level for bulk storage | In base contract
D2 - 104 | PRESSURE SWITCH | PRESSURE SWITCH | 1 | Ea | 16 | 15 | ADDED (+15) | PSH-60220/24/30/31, PSH-61301, PSL-60210.. | Suppression skid & burner safety interlocks | VO Claim: +15 Pressure Switches
D2 - 106 | PRESSURE TRANSMITTER | GAUGE PRESSURE TRANSMITTER | 21 | Ea | 25 | 4 | ADDED (+4) | PT-60201..PT-60225, PT-913201 | Air header, steam header, chamber pressure | VO Claim: +4 Pressure Transmitters
D2 - 107 | PRESSURE TRANSMITTER | DIFFERENTIAL PRESSURE TRANSMITTER | 8 | Ea | 8 | 0 | EXACT MATCH | DPT-60201..DPT-60203, DPT-61301..DPT-61312 | Steam filter, vent filter, air filter delta-P | In base contract
D2 - 108 | PRESSURE GAUGE | LOCAL PRESSURE GAUGE | 40 | Ea | 40 | 0 | EXACT MATCH | Local bourdon tube indicators (Non-PLC) | Field mechanical gauge stations | In base contract
D2 - 109 | PRESSURE REGULATOR | SELF-OPERATING PRESSURE REGULATOR | 21 | Ea | 21 | 0 | EXACT MATCH | Field pneumatic regulators (Non-PLC) | Instrument air supply lines | In base contract
D2 - 111-113 | CONTROL VALVE | PNEUMATIC CONTROL VALVE (4-20mA) | 3 | Ea | 5 | 2 | ADDED (+2) | PV-60201, TV-60214, TV-60701, TCV-40222, FCV-60210A | High-temp exhaust bypass & slurry modulating | VO Claim: +2 Modulating Control Valves
D2 - 115-126 | ON/OFF VALVE | PNEUMATIC VALVES (Ball/BF/Gate) | 33 | Ea | 48 | 15 | ADDED (+15) | XV-20201..XV-20213, XV-40201A..H, XV-61301.. | Slurry tank isolating, cip routing, bin gate | VO Claim: +15 Automated On/Off Valves
D2 - 128-129 | SOLENOID VALVE | SOLENOID VALVE (1/2", 3/4") | 21 | Ea | 19 | -2 | REDUCED (-2) | SV-40201..SV-40204, Solenoid manifolds | Air piloting & local purge valves | Minor scope consolidation
D2 - 131-134 | VALVE W/ SWITCH | VALVE WITH POSITION SWITCH | 13 | Ea | 15 | 2 | ADDED (+2) | HV-20204..HV-20210, HV-40201..HV-40203 | Manual drain valves with open/close feedback | VO Claim: +2 Switch Valves
D2 - 136 | TEMP TRANSMITTER | PROCESS TEMPERATURE TRANSMITTER | 21 | Ea | 28 | 7 | ADDED (+7) | TT-40201..TT-40210, TT-60201..TT-60235 | Chamber inlet/outlet, air heater, cyclones | VO Claim: +7 Temp Transmitters
D2 - 137 | TEMP TRANSMITTER | BEARING TEMPERATURE TRANSMITTER | 4 | Ea | 4 | 0 | EXACT MATCH | TT-60210A/B (Combustion Fan), TT-60241A/B (Exhaust Fan) | Heavy fan motor bearing protection | In base contract
D2 - 138 | TEMP SWITCH | TEMPERATURE SWITCH | 2 | Ea | 10 | 8 | ADDED (+8) | TSH-60230/40, TSH/L-60241A/B, TSH/L-60242A/B.. | Duct thermal run-away trip interlocks | VO Claim: +8 Temp Switches
D2 - 139 | TEMP GAUGE | LOCAL BIMETAL TEMPERATURE GAUGE | 3 | Ea | 3 | 0 | EXACT MATCH | Local dial thermometers (Non-PLC) | Field pipe thermal indication | In base contract
D2 - 140 | LIMIT SWITCH | MECHANICAL / PROX LIMIT SWITCH | 11 | Ea | 18 | 7 | ADDED (+7) | ZSO/ZSC valve feedback & access door switches | Dryer hatch interlocks & slide gates | VO Claim: +7 Limit Switches
D2 - 141 | VIBRATION TX | VIBRATION TRANSMITTER | 4 | Ea | 4 | 0 | EXACT MATCH | VT-60210A/B, VT-60241A/B (Fans FANE-21 & FANE-22) | Exhaust & combustion fan vibration monitor | In base contract
D2 - 142 | HAND SWITCH BOX | FIELD HAND SWITCH BOX | 18 | Ea | 18 | 0 | EXACT MATCH | HS-61307A through HS-61307R (18 units) | Local operator start/stop stations | In base contract
D2 - 144 | LOCAL PANEL | MACHINE LOCAL PANEL | 4 | Ea | 4 | 0 | EXACT MATCH | LCP-01..LCP-04 (Burner, Deluge, Suppression, Baghouse) | Local package interface panels | In base contract

## 03_Rev3.6a_Full_IO_Schedule
REV.3.6a FULL VERIFIED INSTRUMENT & I/O SCHEDULE (COMPLETE 560 LINE REGISTER)
Complete signal register extracted from Instrument I-O List Rev.3.6a.xlsx with PLC signal allocation, cable type, and hazardous area rating
Line # | Item # | Tag No. (Old) | New Tag No. | P&ID No. | Description | Instrument Name | DO | DI | AO | AI | Bus | Signal Type | Signal To | Range | Function | Cable Type | Protection
1 | 1 | AT-60241 | AT-60241 | 325-01-602-PD-05 | Dust Analyzer Transmitter for Exhaust Duct (DTEX-22) | Dust Analyzer Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 5000 mg | 0 - 100% |  | -
2 | 2 | DPT-60901 | DPT-60201 | 325-01-602-PD-09 | Steam filter pressure | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0-1 barg | 0 - 100% |  | -
3 | 3 | DPT-61301 | DPT-61301 | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 500 mBar./0 - 100% |  | Ex t/d
4 | 4 | DPT-61302 | DPT-61302 | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 500 mBar./0 - 100% |  | Ex t/d
5 | 5 | DPT-61310 | DPT-61310 | 325-01-613-PD-03 | Vent filter pressure | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 0-250 mbarg / 0 - 100% |  | Ex t/d
6 | 6 | DPT-61312 | DPT-61312 | 325-01-613-PD-05 | Vent filter pressure | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 0-250 mbarg / 0 - 100% |  | Ex t/d
7 | 7 | DPT-60202 | DPT-60202 | 325-01-602-PD-08 | Gas Pressure Differential Transmitter for Air Filter (FICA-31) | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 500 mBar | 0 to1000 |  | -
8 | 8 | DPT-60203 | DPT-60203 | 325-01-602-PD-03 | Gas Pressure Differential Transmitter for Air Filter (FICA-21) | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 500 mBar | 0-100 mbarg / 0 - 100% |  | -
9 | 9 |  | FSL-20201 | 325-01-202-PD-01 | Slurry low flow | Flow Switch | - | 1 | - | - | - | Dry Contact | PLC |  | n/a |  | -
10 | 10 |  | FSL-40201 | 325-01-402-PD-01 | Slurry low flow | Flow Switch | - | 1 | - | - | - | Dry Contact | PLC |  | n/a |  | -
11 | 11 |  | FSL-40202 | 325-01-402-PD-01 | Slurry low flow | Flow Switch | - | 1 | - | - | - | Dry Contact | PLC |  | n/a |  | -
12 | 12 |  | FS-40204 | 325-01-402-PD-01 | Jet Cooker | Flow Switch | - | 1 | - | - | - | Dry Contact | PLC |  | n/a |  | -
13 | 13 |  | FS-40205 | 325-01-402-PD-02 | Jet Cooker | Flow Switch | - | 1 | - | - | - | Dry Contact | PLC |  | n/a |  | -
14 | 14 | FT-40201 | FT-40201 | 325-01-402-PD-02 | Slurry flowrate & density check transfer line | Coriolis Flow Transmitter | - | 1 | - | 2 | - | 4 - 20 mA,Pulse | PLC | 0-15 m³/hr | Flow rate |  | -
15 | 15 | FT-40202 | FT-40202 | 325-01-402-PD-02 | Feed Slurry Flow Transmitter for Pipe (PIPE) | Magnetic Flow Transmitter | - | 1 | - | 1 | - | 4 - 20 mA,Pulse | PLC | 0 to 8,000 m³/hr | 0 - 100% |  | -
16 | 16 |  | FT-40221 | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter | - | 1 | - | 2 | - | 4 - 20 mA,Pulse | PLC | 0-6 m³/hr | Flow rate |  | -
17 | 17 |  | FT-40222 | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter | - | 1 | - | 2 | - | 4 - 20 mA,Pulse | PLC | 0-850 kg/hr | Flow rate |  | -
18 | 18 | FT-60221 | FT-60221 | 325-01-602-PD-04 | Cool air Flow | Thermal Mass Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 2500 m3/h | n/a |  | -
19 | 19 | FT-60201 | FT-60201 | 325-01-602-PD-08 | Gas Flow Transmitter for Cooling Conveying Cold Air Duct (DTCA-32) | Thermal Mass Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 70000 m3/h | 0 - 100% |  | -
20 | 20 | FT-60210 | FT-60210 | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) | Thermal Mass Flow Transmitter | - | - | - | 2 | - | 4 - 20 mA | PLC | 126000 m3/h | 0 - 100% |  | -
21 | 21 | FT-60211 | FT-60211 | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) | Thermal Mass Flow Transmitter | - | - | - | 2 | - | 4 - 20 mA | PLC | 126000 m3/h | 0 - 100% |  | -
22 | 22 | FT-60261FA | FT-60261FA | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #1 (AMTV-11A) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
23 | 23 | FT-60261FB | FT-60261FB | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #2 (AMTV-11A) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
24 | 24 | FT-60261FC | FT-60261FC | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #3 (AMTV-11A) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
25 | 25 | FT-60261FD | FT-60261FD | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #4 (AMTV-11A) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
26 | 26 | FT-60262FE | FT-60262FE | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #5 (AMTV-11B) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
27 | 27 | FT-60262FF | FT-60262FF | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #6 (AMTV-11B) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
28 | 28 | FT-60262FG | FT-60262FG | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #7 (AMTV-11B) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
29 | 29 | FT-60262FH | FT-60262FH | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #8 (AMTV-11B) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
30 | 30 | FT-60263FJ | FT-60263FJ | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #9 (AMTV-11C) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
31 | 31 | FT-60263FK | FT-60263FK | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #10 (AMTV-11C) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
32 | 32 | FT-60263FL | FT-60263FL | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #11 (AMTV-11C) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
33 | 33 | FT-60263FM | FT-60263FM | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #12 (AMTV-11C) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
34 | 34 | FT-60264FN | FT-60264FN | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #13 (AMTV-11D) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
35 | 35 | FT-60264FP | FT-60264FP | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #14 (AMTV-11D) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
36 | 36 | FT-60264FQ | FT-60264FQ | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #15 (AMTV-11D) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
37 | 37 | FT-60264FR | FT-60264FR | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #16 (AMTV-11D) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | -
38 | 38 | FT-61307 | FT-61307 | 325-01-613-PD-04 | Compressed air Flow | Thermal Mass Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 1000 m3/hr | 0 - 100% |  | -
39 | 39 | FT-60901 | FT-60203 | 325-01-602-PD-09 | Culinary steam feed to Spray dryer | Vortex Flow Transmitter | - | 1 | - | 1 | - | 4 - 20 mA | PLC | 0 - 7000 kg/hr | 0 - 100% |  | -
40 | 40 | FT-60902 | FT-60202 | 325-01-602-PD-09 | Steam feed to Spray dryer | Vortex Flow Transmitter | - | 1 | - | 1 | - | 4 - 20 mA | PLC | 0 - 2000 kg/hr | 0 - 100% |  | -
41 | 41 | FT-61101 | FT-60204 | 325-01-602-PD-10 | Compressed air Flow | Thermal Mass Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 1000 m3/hr | 0 - 100% |  | -
42 | 42 | FT-90301 | FT-936201 | 325-01-930-PD-01 | Process Water | Magnetic Flow Transmitter | - | 1 | - | 1 | - | 4 - 20 mA,Pulse | PLC | 0-1000kg/m³ | Flow rate |  | -
43 | 43 | FT-93001 | FT-936202 | 325-01-930-PD-02 | Process Water | Magnetic Flow Transmitter | - | 1 | - | 1 | - | 4 - 20 mA,Pulse | PLC | 0 - 20 m3/ hr | 0 - 100% |  | -
44 | 44 | HS-61307A | HS-61307A | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | 2 | - | - | - | Dry Contact | PLC |  |  |  | Ex d
45 | 45 | HS-61307B | HS-61307B | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
46 | 46 | HS-61307C | HS-61307C | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
47 | 47 | HS-61307D | HS-61307D | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
48 | 48 | HS-61307E | HS-61307E | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
49 | 49 | HS-61307F | HS-61307F | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
50 | 50 | HS-61307G | HS-61307G | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
51 | 51 | HS-61307H | HS-61307H | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
52 | 52 | HS-61307I | HS-61307I | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
53 | 53 | HS-61307J | HS-61307J | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
54 | 54 | HS-61307K | HS-61307K | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
55 | 55 | HS-61307L | HS-61307L | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
56 | 56 | HS-61307M | HS-61307M | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
57 | 57 | HS-61307N | HS-61307N | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
58 | 58 | HS-61307O | HS-61307O | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
59 | 59 | HS-61307P | HS-61307P | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
60 | 60 | HS-61307Q | HS-61307Q | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
61 | 61 | HS-61307R | HS-61307R | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | - | - | - | - | Dry Contact | PLC |  |  |  | Ex d
62 | 62 | HV-4106 | HV-40203 | 325-01-402-PD-01 | Slurry Drain tank TS-40201 | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | -
63 | 63 | HV-4108 | HV-40201 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | -
64 | 64 | HV-4126 | HV-40204 | 325-01-402-PD-01 | Slurry Drain tank TS-40202 | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | -
65 | 65 | HV-4128 | HV-40202 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | -
66 | 66 | HV-4208 | HV-40206 | 325-01-402-PD-01 | Slurry Drain tank TS-40203 | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | -
67 | 67 | HV-4210 | HV-40205 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | -
68 | 68 |  | HV-40207 | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | -
69 | 69 |  | HV-40208 | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | -
70 | 70 | LSH-60230 | LSH-60230 | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-21) | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " high" / Overfill |  | Ex t/d
71 | 71 | LSH-60231 | LSH-60231 | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-22) | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " high" / Overfill |  | Ex t/d
72 | 72 | LSH-60240 | LSH-60240 | 325-01-602-PD-05 | Powder Level Switch High for Bag House (BGHS-21) | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " high" / Overfill |  | Ex t/d
73 | 73 | LSH-60250 | LSH-60250 | 325-01-602-PD-05 | Water Level Switch High for Fire Deluge Pipe (FWDP-21) | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " high" / Overfill |  | -
74 | 74 | LSH-60251 | LSH-60251 | 325-01-602-PD-04 | Water Level Switch High for Fire Deluge Pipe (FWDP-22) | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " high" / Overfill |  | -
75 | 75 | LSL-61101 | LSL-60201 | 325-01-602-PD-11 | Level low switch | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " Low " / Run dry protection |  | -
76 | 76 | LSH-61301 | LSH-61301 | 325-01-613-PD-01 | Level alarm high | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " Full " / Overfill |  | Ex t/d
77 | 77 | LSL-61302 | LSL-61302 | 325-01-613-PD-01 | Level alarm low | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " Low " / Overfill |  | Ex t/d
78 | 78 | LS-61303 | LS-61303 | 325-01-613-PD-01 | Level switch | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " high" / Overfill |  | Ex t/d
79 | 79 | LSH-61304 | LSH-61304 | 325-01-613-PD-03 | Big bag level alarm high | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill |  | Ex t/d
80 | 80 | LSH-61305 | LSH-61305 | 325-01-613-PD-05 | Big bag level alarm high | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill |  | Ex t/d
81 | 81 | LSH-61306 | LSH-61306 | 325-01-613-PD-01 | Level alarm high | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill |  | Ex t/d
82 | 82 |  | LSH-61307 | 325-01-613-PD-01 | High Level alarm reject screen | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill |  | Ex t/d
83 | 83 |  | LSH-61308 | 325-01-613-PD-01 | High Level alarm Cooling cyclone | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill |  | Ex t/d
84 | 84 | LSH-61312 | LSH-61312 | 325-01-613-PD-05 | Level alarm high | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill |  | Ex t/d
85 | 85 | LSL-81001 | LSL-814201 | 325-01-814-PD-01 | Low Level alarm |  | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " Low " / Overfill |  | Ex t/d
86 | 86 | LT-40101 | LT-40201 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 1 | Level transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 m. | 0 - 100% |  | -
87 | 87 | LT-40102 | LT-40202 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 2 | Level transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 m. | 0 - 100% |  | -
88 | 88 | LT-40201 | LT-40203 | 325-01-402-PD-02 | Level transmitter in Spray dryer infeed tank | Level transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 m. | 0 - 100% |  | -
89 | 89 | LT-61301 | LT-61301 | 325-01-613-PD-01 | Level powder in silo | Level transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 0 - 100% |  | Ex ia
90 | 90 | pHT-40101 | pHT-40201 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 1 | pH Analyzer | - | 1 | - | 1 | - | 4 - 20 mA | PLC | 0-14 | 0 - 100% |  | -
91 | 91 | pHT-40102 | pHT-40202 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 2 | pH Analyzer | - | 1 | - | 1 | - | 4 - 20 mA | PLC | 0-14 | 0 - 100% |  | -
92 | 92 | PSL-60220 | PSL-60220 | 325-01-602-PD-04 | Gas Pressure Switch Low for Spray Chamber (CHAM-21) | Pressure switch | - | 1 | - | - | - | Dry Contact | Hard Wired to MCC FANE-21 | -0.01 mbar | 0 to (- 20,000) Pa |  | -
93 | 93 |  | PSL-61301 | 325-01-613-PD-01 | Pressure alarm low | Pressure switch | - | 1 | - | - | - | Dry Contact | PLC | 0.3-0.7barg | 1 barg / Under pressure |  | -
94 | 94 | PSL-61302 | PSL-61302 | 325-01-613-PD-01 | Pressure alarm low | Pressure switch | - | 1 | - | - | - | Dry Contact | PLC | 40 mbarg | 1 barg / Under pressure |  | -
95 | 95 | PSL-61305 | PSL-61305 | 325-01-613-PD-03 | Pressure alarm low | Pressure switch | - | 1 | - | - | - | Dry Contact | PLC |  | 1 barg / Under pressure |  | -
96 | 96 | PSL-61306 | PSL-61306 | 325-01-613-PD-05 | Pressure alarm low | Pressure switch | - | 1 | - | - | - | Dry Contact | PLC |  | 1 barg / Under pressure |  | -
97 | 97 | PSL-61311 | PSL-61311 | 325-01-613-PD-04 | Pressure alarm low | Pressure switch | - | 1 | - | - | - | Dry Contact | PLC |  | 1 barg / Under pressure |  | -
98 | 98 | PT-40201 | PT-40201 | 325-01-402-PD-02 | Pressure Transmitter for Inlet Filter Strainer (FSTR-11) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 500 mBar | 0-250 mbarg / 0 - 100% |  | -
99 | 99 | PT-40202 | PT-40202 | 325-01-402-PD-02 | Feed Slurry Pressure Transmitter for Pipe (PIPE) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10'barg | 0 to 500 |  | -
100 | 100 |  | PT-40222 | 325-01-402-PD-02 | Jet Cooker | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 12'barg | 0 to 500 |  | -
101 | 101 | PT-60201 | PT-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 20 bar | Control Pressure |  | -
102 | 102 | PT-60202 |  | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 500 bar | 0-100% |  | -
103 | 103 | PT-60203 | PT-60203 | 325-01-602-PD-08 | Gas Pressure Transmitter for Cool Air Duct (DTCA-32) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% |  | -
104 | 104 | PT-60210 | PT-60210 | 325-01-602-PD-03 | Gas Pressure Transmitter for Hot Air Duct (DTHA-21) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% |  | -
105 | 105 | PT-60215 | PT-60215 | 325-01-602-PD-03 | 15% Polypropylene Glycol Pressure Indicator Transmitter for Heat Recovery Pumping Skid (PUCF-21) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 6 bar | 0-100% |  | -
106 | 106 | PT-60216 | PT-60216 | 325-01-602-PD-03 | Gas Pressure Transmitter for Combustion Air Burner Duct (DTCB-21) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 100 mbar | 0-100% |  | -
107 | 107 | PT-60220 | PT-60220 | 325-01-602-PD-04 | Gas Pressure Transmitter for Chamber (CHAM-21) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 - 100 mbar | 0-100% |  | Ex ic
108 | 108 | PT-60221 | PT-60221 | 325-01-602-PD-04 | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% |  | -
109 | 109 | PT-60230 | PT-60230 | 325-01-602-PD-04 | Gas Pressure Transmitter for Conveying Duct (DTCO-21) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% |  | Ex ic
110 | 110 | PT-60231 | PT-60231 | 325-01-602-PD-04 | Gas Pressure Transmitter for Cyclone Exhaust Duct (DTCE-21) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% |  | Ex ic
111 | 111 | PT-60240 | PT-60240 | 325-01-602-PD-05 | Gas Pressure Transmitter for Bag House Exhaust Duct (DTEX-22) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% |  | -
112 | 112 | PT-60241 | PT-60241 | 325-01-602-PD-05 | Gas Pressure Transmitter for Exhaust Fan (FANE-21) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% |  | -
113 | 113 | PT-61101 | PT-60204 | 325-01-602-PD-10 | Pressure transmitter | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 barg | 0-100% |  | -
114 | 114 | PT-61301 | PT-61301 | 325-01-613-PD-01 | Pressure in silo | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 1 barg | 0-100% |  | Ex ic
115 | 115 | PT-61302 | PT-61302 | 325-01-613-PD-03 | Pressure in vacuum line | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 - 100 mbarg | 0-100% |  | -
116 | 116 | PT-61303 | PT-61303 | 325-01-613-PD-01 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% |  | Ex ic
117 | 117 | PT-61304 | PT-61304 | 325-01-613-PD-01 | Gas Pressure Transmitter for Storage Bin Cyclone Inlet Duct (CYCL-31) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% |  | Ex ic
118 | 118 | PT-61305 | PT-61305 | 325-01-613-PD-01 | Gas Pressure Transmitter for Exhaust Duct (DTEX-31) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% |  | Ex ic
119 | 119 | PT-61309 | PT-61309 | 325-01-613-PD-04 | Pressure transmitter | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 barg | 0 - 8 barg / 0-100% |  | -
120 | 120 | PV-60201 | PCV-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic Control valve | - | - | 1 | - | - | 4 - 20 mA | PLC | 0 - 100% | Position O/C./0 - 100% |  | -
121 | 121 | SV-40101 | SV-40201 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 1 | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
122 | 122 | SV-40102 | SV-40202 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 2 | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
123 | 123 | SV-40103 | SV-40203 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 1 | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
124 | 124 | SV-40104 | SV-40204 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 2 | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
125 | 125 | SV-60220 | SV-60220 | 325-01-602-PD-04 | PA On/Off Valve for Chamber PSE purge air (CHAM-21) | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
126 | 126 | SV-60230 | SV-60230 | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 27 (CYCL-21) | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
127 | 127 | SV-60231 | SV-60231 | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 28 (CYCL-22) | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
128 | 128 | SV-60240A | SV-60240A | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29A (BGHS-21) | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
129 | 129 | SV-60240B | SV-60240B | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29B (BGHS-21) | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
130 | 130 | SV-60240C | SV-60240C | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29C (BGHS-21) | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
131 | 131 | SV-61301 | SV-61301 | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve | - | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
132 | 132 | SV-61302 | SV-61302 | 325-01-613-PD-01 | Air service | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
133 | 132 |  | SV-61306 | 325-01-613-PD-01 | Air service | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
134 | 133 | SV-61303 | SV-61303 | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve | - | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
135 | 134 | SV-61305 | SV-61305 | 325-01-613-PD-01 | Air service | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
136 | 135 | SV-61308 | SV-61308 | 325-01-613-PD-03 | Timer compress air pluse solenoid valve | Solenoid valve | - | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
137 | 136 | SV-61309 | SV-61309 | 325-01-613-PD-03 | Air service | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
138 | 137 | SV-61310 | SV-61310 | 325-01-613-PD-05 | Timer compress air pluse solenoid valve | Solenoid valve | - | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
139 | 138 | SV-61311 | SV-61311 | 325-01-613-PD-05 | Air service | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
140 | 139 | TSH-60230 | TSH-60230 | 325-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | Temperature Switch | - | 1 | - | - | - | Dry Contact | PLC | 0 - 140 C | 140 |  | Ex d
141 | 140 | TSH-60240 | TSH-60240 | 325-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | Temperature Switch | - | 1 | - | - | - | Dry Contact | PLC | 0 - 140 C | 140 |  | Ex d
142 | 141 |  | TT-40221 | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 120 C | 0 - 300 C |  | -
143 | 142 |  | TT-40222 | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 200 C | 0 - 300 C |  | -
144 | 143 | TT-60201 | TT-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 300 C | 0 - 300 C |  | -
145 | 144 | TT-60210 | TT-60210 | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | -
146 | 145 | TT-60212A | TT-60210A | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 100 C | 0 to 150 |  | -
147 | 146 | TT-60212B | TT-60210B | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 100 C | 0 to 150 |  | -
148 | 147 | TT-60211 | TT-60211 | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | -
149 | 148 | TT-60214 | TT-60214 | 325-01-602-PD-03 | Steam Temperature Transmitter for Cold Air Duct (DTCA-23) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -10 to 250°C | -10 to 250 |  | -
150 | 149 | TT-60215A | TT-60215A | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -10 to 150°C | -10 to 150 |  | -
151 | 150 | TT-60215B | TT-60215B | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -10 to 150°C | -10 to 150 |  | -
152 | 151 | TT-60216 | TT-60216 | 325-01-602-PD-03 | Gas Temperature Transmitter for Combustion Air Burner Duct (DTCB-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 200'°C | 0 to 200 |  | -
153 | 152 | TT-60220 | TT-60220 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic
154 | 153 | TT-60221 | TT-60221 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic
155 | 154 | TT-60222 | TT-60222 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic
156 | 155 | TT-60223 | TT-60223 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic
157 | 156 | TT-60224 | TT-60224 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic
158 | 157 | TT-60225 | TT-60225 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic
159 | 158 | TT-60226 | TT-60226 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic
160 | 159 | TT-60227 | TT-60227 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic
161 | 160 | TT-60230 | TT-60230 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Conveying Duct (DTCO-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic
162 | 161 | TT-60240 | TT-60240 | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Fan (FANE-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | -
163 | 162 | TT-60241A | TT-60241A | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 100 C | 0 to 150 |  | -
164 | 163 | TT-60241B | TT-60241B | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 100 C | 0 to 150 |  | -
165 | 164 | TT-60245 | TT-60245 | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Stack (DTXS-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -10 to 150°C | -10 to 150 |  | -
166 | 165 | TT-60702 | TT-60202 | 325-01-602-PD-07 | Compress air temp to camera | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 40 C | Control Temperature |  | -
167 | 166 | TT-61301 | TT-61301 | 325-01-613-PD-01 | Gas Temperature Transmitter for Cold Air Duct (DTCA-32) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic
168 | 167 | TT-61302 | TT-61302 | 325-01-613-PD-01 | Gas and Powder Temperature Transmitter for Cooling Cyclone (CYCL-31) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic
169 | 168 |  | TCV-40222 | 325-01-402-PD-02 | Jet Cooker | Automatic Control valve | - | - | 1 | - | - | 4 - 20 mA | PLC | 0 - 100% | Command |  | -
170 | 169 | TV-60214 | TCV-60214 | 325-01-602-PD-03 | Steam Temperature Valve for Pre-Heat Steam Heat Exchanger (HXCH-21) | Automatic Control valve | - | - | 1 | - | - | 4 - 20 mA | PLC | 0 - 100% | Command |  | -
171 | 170 | TV-60702 | TCV-60202 | 325-01-602-PD-07 | Chiller water control valve | 3-way Control valve | - | - | 1 | - | - | 4 - 20 mA | PLC | 0 - 100% | Position O/C./0 - 100% |  | -
172 | 171 | VT-60210A | VT-60210A | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | mm/sec | 0 to 15 |  | -
173 | 172 | VT-60210B | VT-60210B | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | mm/sec | 0 to 15 |  | -
174 | 173 | VT-60241A | VT-60241A | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | mm/sec | 0 to 15 |  | -
175 | 174 | VT-60241B | VT-60241B | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | mm/sec | 0 to 15 |  | -
176 | 175 | XT-60301 | XT-60201 | 325-01-402-PD-03 | LEL gas analyzer | Gas detector | - | - | - | 1 | - | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% |  | Ex ic
177 | 176 | XA-60301 | XA-60201 | 325-01-402-PD-03 | LEL gas Buzzer Alarm | Gas detector | 1 | - | - | - | - | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% |  | Ex ic
178 | 177 | XT-92201 | XT-92201 | 325-01-923-PD-03 | LEL gas analyzer | Gas detector | - | - | - | 1 | - | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% |  | Ex ic
179 | 178 | XA-92201 | XA-92201 | 325-01-923-PD-03 | LEL gas Buzzer Alarm | Gas detector | 1 | - | - | - | - | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% |  | Ex ic
180 | 179 | XV-40101A | XV-40201A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
181 | 180 | XV-40101B | XV-40201B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
182 | 181 | XV-40101C | XV-40201C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
183 | 182 | XV-40101D | XV-40201D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
184 | 183 | XV-40101E | XV-40201E | 325-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
185 | 184 | XV-40101F | XV-40201F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
186 | 185 | XV-40101G | XV-40201G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
187 | 186 | XV-40101H | XV-40201H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
188 | 187 | XV-40102A | XV-40202A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
189 | 188 | XV-40102B | XV-40202B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
190 | 189 | XV-40102C | XV-40202C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
191 | 190 | XV-40102D | XV-40202D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
192 | 191 | XV-40102E | XV-40202E | 325-01-402-PD-01 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
193 | 192 | XV-40102F | XV-40202F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
194 | 193 | XV-40102G | XV-40202G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
195 | 194 | XV-40102H | XV-40202H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
196 | 195 | XV-40201B | XV-40203B | 325-01-402-PD-02 | Slurry feed-out Spray dryer infeed tank | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
197 | 196 | XV-40201C | XV-40203C | 325-01-402-PD-02 | Water washing line outlet Spray dryer infeed tank | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
198 | 197 | XV-40201D | XV-40203D | 325-01-402-PD-02 | CIP water washing Spray dryer infeed tank | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
199 | 198 | XV-40201E | XV-40203E | 325-01-402-PD-02 | CIP hight pressure water washing Spray dryer infeed tank | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
200 | 199 |  | XV-40203F | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
201 | 200 |  | XV-40204B | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
202 | 201 |  | XV-40204C | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
203 | 202 |  | XV-40205A | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
204 | 203 |  | XV-40205B | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
205 | 204 |  | XV-40205C | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
206 | 205 |  | XV-40205D | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
207 | 206 |  | XV-40205F | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
208 | 207 |  | XV-40222 | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
209 | 208 | XV-60201 | XV-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
210 | 209 | XV-60251 | XV-60251 | 325-01-602-PD-01 | Liquid On/Off Valve for Drain Pipe (PIPE) | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
211 | 210 | XV-60301 | XV-60214 | 325-01-602-PD-03 | Steam feed to Spray dryer | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
212 | 211 | XV-61101 | XV-60202 | 325-01-602-PD-11 | High Pressure Water On/Off Valve for Drain Pipe | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | -
213 | 212 | HV-61301 | XV-61301 | 325-01-613-PD-01 | Product feed-out Packing silo | Automatic on/off valve | - | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | Ex d
214 | 213 | XV-61302 | XV-61302 | 325-01-613-PD-02 | Dust collector feed vent | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | Ex d
215 | 214 | XV-61303 | XV-61303 | 325-01-613-PD-02 | Dust collector feed from packer | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | Ex d
216 | 215 |  | DV-61301 | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61301 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | Ex d
217 | 216 |  | DV-61302 | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61302 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | Ex d
218 | 217 | ZS-60201A | ZS-60201A | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic
219 | 218 | ZS-60201B | ZS-60201B | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic
220 | 219 | ZS-60201C | ZS-60201C | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic
221 | 220 | ZS-60201D | ZS-60201D | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic
222 | 221 | ZS-60201E | ZS-60201E | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic
223 | 222 |  | ZS-60229 | 325-01-602-PD-04 | Limit Switch for CY-60230 (Door Service) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic
224 | 223 |  | ZS-60230 | 325-01-602-PD-04 | Limit Switch for CY-60231 (Door Service) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic
225 | 224 | ZS-60231A | ZS-60231A | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Spectacle Inserted) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic
226 | 225 | ZS-60231B | ZS-60231B | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Blind Inserted) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic
227 | 226 | ZS-60231C | ZS-60231C | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Spool Inserted) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic
228 | 227 | ZS-60231D | ZS-60231D | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Blind Inserted) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic
229 | 228 | ZS-60231E | ZS-60231E | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Spool Inserted) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic
230 | 229 | ZS-60231F | ZS-60231F | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Blind Inserted) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic
231 | 230 |  | ZS-60240 | 325-01-602-PD-05 | Limit Switch for FA-60240 (Door Service) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic
232 | 231 | ZS-61310 | ZS-61310 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic
233 | 232 | ZS-61311 | ZS-61311 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic
234 | 233 | ZS-61312 | ZS-61312 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic
235 | 234 | ZS-61313 | ZS-61313 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic
236 | 235 |  |  |  | Lototo-01 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
237 | 236 |  |  |  | Lototo-02 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
238 | 237 |  |  |  | Lototo-03 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
239 | 238 |  |  |  | Lototo-04 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
240 | 239 |  |  |  | Lototo-05 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
241 | 240 |  |  |  | Lototo-06 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
242 | 241 |  |  |  | Lototo-07 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
243 | 242 |  |  |  | Lototo-08 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
244 | 243 |  |  |  | Lototo-09 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
245 | 244 |  |  |  | Lototo-10 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
246 | 245 |  |  |  | Lototo-11 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
247 | 246 |  |  |  | Lototo-12 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
248 | 246 |  | ES-60201 |  | Emergency stop activated @ Spray Nozzle 7th Floor | E-Stop Swtich | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
249 | 246 |  | ES-60202 |  | Emergency stop activated @ Sight glass 6th Floor | E-Stop Swtich | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
250 | 246 |  | ES-60203 |  | Emergency stop activated @ Control Room | E-Stop Swtich | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
251 | 246 |  | ES-61301 |  | Emergency stop activated @ SC-61301,SC-61302 | E-Stop Swtich | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
252 | 247 | DEDERT SUPPLY EQUIPMENT |  |  |  |  | - | - | - | - | -
253 | 248 | FT-60701 | FT-60207 | 325-01-602-PD-07 | Instr. Air Flow Transmitter for Camera #4 (ACAM-21) | Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC
254 | 249 | PT-60701 | PT-60207 | 325-01-602-PD-07 | Instr. Air Pressure Transmitter for Camera #4 (ACAM-21) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC
255 | 250 | SV-60240D | XV-60240D | 325-01-602-PD-05 | PA On/Off Valve for Bag House Tank Valve (BGHS-21) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off
256 | 251 | SV-60701 | SV-60207 | 325-01-602-PD-07 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) | On/Off Valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off
257 | 252 | SV-60201 | SV-60201 | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) | On/Off Valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off
258 |  |  | SSL-60201 | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-21) | Low Speed Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off
259 |  |  | ZS-60201 | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-21/ RV-60201) Casing Closed | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off
260 | 253 | SV-60202 | SV-60202 | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off
261 |  |  | SSL-60202 | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-22) | Low Speed Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off
262 |  |  | ZS-60202 | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-22/ RV-60202) Casing Closed | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off
263 | 254 | SV-60203 | SV-60203 | 325-01-602-PD-08 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off
264 |  |  | SSL-60203 | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-23) | Low Speed Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off
265 |  |  | ZS-60203 | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-23/ RV-60203) Casing Closed | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off
266 | 255 | SV-61304 | SV-61304 | 325-01-613-PD-01 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off
267 |  |  | SSL-61304 | 325-01-613-PD-01 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-31) | Low Speed Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off
268 |  |  | ZS-61304 | 325-01-613-PD-01 | Position - Rotary Valve (RVAL-31/ RV-61304) Casing Closed | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off
269 | 256 | TT-60701 | TT-60207 | 325-01-602-PD-07 | Instr. Air Temperature Transmitter for Air Manifold - Camera #4 (ACAM-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC
270 | 257 | XV-60261FA | XV-60261FA | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
271 | 258 | XV-60261FB | XV-60261FB | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
272 | 259 | XV-60261FC | XV-60261FC | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
273 | 260 | XV-60261FD | XV-60261FD | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
274 | 261 | XV-60261SA | XV-60261SA | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
275 | 262 | XV-60261SB | XV-60261SB | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
276 | 263 | XV-60261SC | XV-60261SC | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
277 | 264 | XV-60261SD | XV-60261SD | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
278 | 265 | XV-60262FE | XV-60262FE | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
279 | 266 | XV-60262FF | XV-60262FF | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
280 | 267 | XV-60262FG | XV-60262FG | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
281 | 268 | XV-60262FH | XV-60262FH | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
282 | 269 | XV-60262SE | XV-60262SE | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
283 | 270 | XV-60262SF | XV-60262SF | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
284 | 271 | XV-60262SG | XV-60262SG | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
285 | 272 | XV-60262SH | XV-60262SH | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
286 | 273 | XV-60263FJ | XV-60263FJ | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
287 | 274 | XV-60263FK | XV-60263FK | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
288 | 275 | XV-60263FL | XV-60263FL | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
289 | 276 | XV-60263FM | XV-60263FM | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
290 | 277 | XV-60263SJ | XV-60263SJ | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
291 | 278 | XV-60263SK | XV-60263SK | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
292 | 279 | XV-60263SL | XV-60263SL | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
293 | 280 | XV-60263SM | XV-60263SM | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
294 | 281 | XV-60264FN | XV-60264FN | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
295 | 282 | XV-60264FP | XV-60264FP | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
296 | 283 | XV-60264FQ | XV-60264FQ | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
297 | 284 | XV-60264FR | XV-60264FR | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
298 | 285 | XV-60264SN | XV-60264SN | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
299 | 286 | XV-60264SP | XV-60264SP | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
300 | 287 | XV-60264SQ | XV-60264SQ | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
301 | 288 | XV-60264SR | XV-60264SR | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
302 | 289 |  | XV-60261DA | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11A | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
303 | 290 |  | XV-60262DE | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11B | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
304 | 291 |  | XV-60263DN | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11C | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
305 | 292 |  | XV-60264DJ | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11D | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
306 | 293 | XV-60241 | XV-60241 | 325-01-602-PD-05 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off
307 | 294 | XV-60240 | XV-60240 | 325-01-602-PD-08 | Powder On/Off Valve for Diverter Valve (DVTR-21) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off
308 | 295 | Machine Equipment Supply |  |  |  |  | - | - | - | - | -
309 | 296 | PSE-61300 | PSE-61300 | 325-01-613-PD-01 | Explosion Vent PSE-61300 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic
310 | 297 | PSE-61301 | PSE-61301 | 325-01-613-PD-01 | Explosion Vent PSE-61301 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic
311 | 298 | ISV-61302 | ISV-61302 | 325-01-613-PD-01 | Explosion isolation flap valve ISV-61302 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic
312 | 299 | PSE-61302 | PSE-61302 | 325-01-613-PD-03 | Explosion Vent PSE-61302 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic
313 | 300 | PSE-61303 | PSE-61303 | 325-01-613-PD-05 | Explosion Vent PSE-61303 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic
314 | 301 | PSE-61304 | PSE-61304 | 325-01-613-PD-01 | Explosion Vent PSE-61304 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic
315 | 302 | PSV-61301A | ZS-61306 | 325-01-613-PD-01 | Position Brether Valve High Pressure PSV-61301 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic
316 | 303 | PSV-61301B | ZS-61307 | 325-01-613-PD-01 | Position Brether Valve Vacuum Pressure PSV-61301 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic
317 | 304 | ISV-61303 | ISV-61303 | 325-01-613-PD-03 | Explosion isolation flap valve ISV-61303 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic
318 | 305 | ISV-61304 | ISV-61304 | 325-01-613-PD-05 | Explosion isolation flap valve ISV-61304 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic
319 | 306 | MCC ROOM |  |  |  |  | - | - | - | - | -
320 | 307 | ATY-40101 | AT-40201 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40201 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
321 | 308 | ATY-40102 | AT-40202 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40202 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
322 | 309 | ATY-40201 | AT-40203 | 325-01-402-PD-02 | Start / Stop Command for VSD AT-40203 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
323 | 310 | BFY-60210 | BF-60210 | 325-01-602-PD-03 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
324 | 311 | BFY-60211 | BF-60211 | 325-01-602-PD-03 | Start / Stop Command for VSD FANC-21 (Combustion Fan) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
325 | 312 | BFY-60240 | BF-60240 | 325-01-602-PD-05 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
326 | 313 | BFY-60220 | BF-60220 | 325-01-602-PD-04 | Start / Stop Command for VSD FANS-22 (Cooling Fan) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
327 | 314 | BFY-60206 | BF-60206 | 325-01-602-PD-08 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
328 | 315 | BFY-61301 | BF-61301 | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
329 | 316 | BFY-61302 | BF-61302 | 325-01-613-PD-05 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
330 | 317 | BFY-61303 | BF-61303 | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
331 | 318 | BLM-61302 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | เปลี่ยนไปจ่ายเป็น Power Feeder | - | - | - | - | - | 24 VDC energized | PLC | On-Off
332 | 319 | PCM-60205-B | PD-60202B | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Oil Pump ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
333 | 320 | PCM-60205-C | PD-60202C | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 1 ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
334 | 321 | PCM-60205-D | PD-60202D | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 2 ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
335 | 322 | PCM-60205-E | PD-60202E | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Main motor Fan ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
336 | 323 | PCY-40201 | PC-40203 | 325-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
337 | 324 | PCY-40101 | PC-40201 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40201 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
338 | 325 | PCY-40102 | PC-40202 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40202 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
339 | 326 |  | PD-40204 | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40204 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off |  |  | -
340 | 327 |  | PD-40205 | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40205 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off |  |  | -
341 | 328 | PCY-60205-A | PD-60202A | 325-01-602-PD-01 | Start / Stop Command for VSD PUPD-11 (Positive Displacement Pump ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
342 | 329 | PCY-60215 |  | 325-01-602-PD-03 | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
343 | 330 | PVM-61301 | BL-61301 | 325-01-613-PD-03 | Start / Stop Command for FVNR PV-61301 (Vacuum Cleaning Fan) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
344 | 331 | RVM-60201 |  | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
345 | 332 | RVM-60202 |  | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
346 | 333 | RVM-60203 |  | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
347 | 334 | RVM-60204 |  | 325-01-602-PD-08 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
348 | 335 | RVM-61301 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61301 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
349 | 336 | RVM-61302 |  | 325-01-613-PD-03 | Start / Stop Command for FVNR RV-61302 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
350 | 337 | RVM-61303 |  | 325-01-613-PD-05 | Start / Stop Command for FVNR RV-61303 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
351 | 338 | RVM-61304 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61304 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
352 | 339 | RVM-61305 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61305 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
353 | 340 | SCM-61301 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61301 (Sifter ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
354 | 341 | SCM-61302 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61302 (Sifter ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
355 | 342 | B&B Packing |  |  |  |  | - | - | - | - | -
356 | 343 | XA-61301A | XA-61301A | 325-01-613-PD-02 | Request filter plant (Fugitive) | Request filter plant | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
357 | 344 | XA-61301B | XA-61301B | 325-01-613-PD-02 | Request material transport | Request material transport | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
358 | 345 | XA-61301C | XA-61301C | 325-01-613-PD-02 | Request belt plant | Request belt plant | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
359 | 346 | XA-61301D | XA-61301D | 325-01-613-PD-02 | Machine in operation | Machine in operation | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
360 | 347 | XA-61301E | XA-61301E | 325-01-613-PD-02 | General Fault | General Fault | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
361 | 348 | XA-61301F | XA-61301F | 325-01-613-PD-02 | Machine is ready | Machine is ready | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
362 | 349 | XA-61301G | XA-61301G | 325-01-613-PD-02 | Emergency stop activated | Emergency stop activated | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
363 | 350 | XA-61301H | XA-61301H | 325-01-613-PD-02 | Silo minimum | Silo minimum | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
364 | 351 | XA-61301J | XA-61301J | 325-01-613-PD-02 | Silo maximum | Silo maximum | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
365 | 352 | XS-61301A | XS-61301A | 325-01-613-PD-02 | Filter plant in operation | Filter plant in operation | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
366 | 353 | XS-61301B | XS-61301B | 325-01-613-PD-02 | Material transport in operation | Material transport in operation | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
367 | 354 | XS-61301C | XS-61301C | 325-01-613-PD-02 | Belt plant in operation | Belt plant in operation | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
368 | 355 | XS-61301D | XS-61301D | 325-01-613-PD-02 | Sequence Stop | Sequence Stop | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
369 | 356 | XS-61301E | XS-61301E | 325-01-613-PD-02 | Status from Customer Emergency stop | Status from Customer Emergency stop | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
370 | 357 | XS-61301F | XS-61301F | 325-01-613-PD-02 | Operation Release | Operation Release | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
371 | 358 |  |  | 325-01-613-PD-02 | Spare |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
372 | 359 |  |  | 325-01-613-PD-02 | Spare |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
373 | 360 |  |  | 325-01-613-PD-02 | Spare |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
374 | 361 |  |  | 325-01-613-PD-02 | Communication Signal |  | - | - | - | - | 1 | Communication Signal | PLC | On-Off |  |  | -
375 | 362 | Boiler |  |  |  |  | - | - | - | - | -
376 | 363 |  | XA-92201B | 325-01-922-PD-03 | Boiler common alarm |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
377 | 363 |  | XA-92201C | 325-01-922-PD-03 | Boiler Trip |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
378 | 363 |  | XA-92212B | 325-01-922-PD-03 | Burner Trip |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
379 | 363 |  | XL-92201B | 325-01-922-PD-03 | Boiler Operate |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
380 | 363 |  | XL-92201C | 325-01-922-PD-03 | Remote Setpoint Activated |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
381 | 363 |  | ZL-92201 | 325-01-922-PD-03 | Remote Setpoint Status |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
382 | 363 |  |  | 325-01-922-PD-03 | Communication Signal |  | - | - | - | - | 1 | Communication Signal | PLC | On-Off |  |  | -
383 |  | Bin Vent Filter (FA-61301) |  |  |  |  | - | - | - | - | -
384 | 363 |  | XA-FA-61301A | 325-01-613-PD-01 | Start / Stop Command for FA-61301 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | -
385 | 364 |  | XA-FA-61301B | 325-01-613-PD-01 | Compress air low (Spare) |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | -
386 | 365 |  | XS-FA-61301 | 325-01-613-PD-01 | Alarm 1 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
387 |  | Fugitive Dust Filter (FA-61310) |  |  |  |  | - | - | - | - | -
388 | 363 |  | XA-FA-61310A | 325-01-613-PD-01 | Start / Stop Command for FA-61310 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | -
389 | 364 |  | XA-FA-61310B | 325-01-613-PD-01 | Compress air low (Spare) |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | -
390 | 365 |  | XS-FA-61310 | 325-01-613-PD-01 | Alarm 1 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
391 |  | Vacuum Cleaner Filter (FA-61311) |  |  |  |  | - | - | - | - | -
392 | 363 |  | XA-FA-61311A | 325-01-613-PD-03 | Start / Stop Command for FA-61311 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | -
393 | 364 |  | XA-FA-61311B | 325-01-613-PD-03 | Compress air low (Spare) |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | -
394 | 365 |  | XS-FA-61311 | 325-01-613-PD-03 | Alarm 1 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
395 |  | Local Exhaust Ventilation Filter (FA-61312) |  |  |  |  | - | - | - | - | -
396 | 363 |  | XA-FA-61312A | 325-01-613-PD-05 | Start / Stop Command for FA-61311 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | -
397 | 364 |  | XA-FA-61312B | 325-01-613-PD-05 | Compress air low (Spare) |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | -
398 | 365 |  | XS-FA-61312 | 325-01-613-PD-05 | Alarm 1 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
399 | 362 | Bag Filter Control Panel (FA-60240) |  |  |  |  | - | - | - | - | -
400 | 363 | XS-60240A | XS-60240A | 325-01-602-PD-05 | Start / Stop Command for BGHS-21 (Bag House Air Pulsing) |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
401 | 364 | XS-60240B | XS-60240B | 325-01-602-PD-05 | Fan Command for BGHS-21 (Bag House Air Pulsing) |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
402 | 365 | XA-60240A | XA-60240A | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
403 | 366 | XA-60240B | XA-60240B | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
404 | 367 | DPI-60240 |  | 325-01-602-PD-05 | Gas Pressure Differntial Pressure (Bag House Air Pulsing) |  | - | - | - | 1 | - | 4 - 20 mA | PLC |  |  |  | -
405 | 368 | HTRE-21 Heater Control Panel (TRACING) |  |  |  |  | - | - | - | - | -
406 | 369 | XS-60241A | XS-60241A | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
407 | 370 | XA-60241A | XA-60241A | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
408 | 371 | XA-60241B | XA-60241B | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
409 | 372 | TSH-60241A | TSH-60241A | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | - | 1 | - | - | - | Dry Contact | Heat Control Panel (HTRE-21) | 0 - 100 C | 140 |  | Ex d
410 | 373 | TSL-60241B | TSL-60241B | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | - | 1 | - | - | - | Dry Contact | Heat Control Panel (HTRE-21) | 0 - 100 C | 140 |  | Ex d
411 | 374 | HTRE-22 Heater Control Panel (TRACING) |  |  |  |  | - | - | - | - | -
412 | 375 | XS-60242A | XS-60242A | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
413 | 376 | XA-60242A | XA-60242A | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
414 | 377 | XA-60242B | XA-60242B | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
415 | 378 | TSH-60242A | TSH-60242A | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | - | 1 | - | - | - | Dry Contact | Heat Control Panel (HTRE-22) | 0 - 100 C | 140 |  | Ex d
416 | 379 | TSL-60242B | TSL-60242B | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | - | 1 | - | - | - | Dry Contact | Heat Control Panel (HTRE-22) | 0 - 100 C | 140 |  | Ex d
417 | 380 | HTRE-23 Heater Control Panel (TRACING) |  |  |  |  | - | - | - | - | -
418 | 381 | XS-60243A | XS-60243A | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
419 | 382 | XA-60243A | XA-60243A | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
420 | 383 | XA-60243B | XA-60243B | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
421 | 384 | TSH-60243A | TSH-60243A | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | - | 1 | - | - | - | Dry Contact | Heat Control Panel (HTRE-23) | 0 - 100 C | 140 |  | Ex d
422 | 385 | TSL-60243B | TSL-60243B | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | - | 1 | - | - | - | Dry Contact | Heat Control Panel (HTRE-23) | 0 - 100 C | 140 |  | Ex d
423 | 386 | Air Heater Burner Control Panel (PK-60210) |  |  |  |  | - | - | - | - | -
424 | 387 | XA-FH-60210A | XA-FH-60210A | 325-01-602-PD-06 | BMS PANEL POWER ON for AHTR-21 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
425 | 388 | XA-FH-60210B | XA-FH-60210B | 325-01-602-PD-06 | BMS Burner High Fire Purge for AHTR-21 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
426 | 389 | XA-FH-60210C | XA-FH-60210C | 325-01-602-PD-06 | BMS Burner On for AHTR-21 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
427 | 390 | XA-FH-60210D | XA-FH-60210D | 325-01-602-PD-06 | BMS BMS Lockout for AHTR-21 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
428 | 391 | XA-FH-60210E | XA-FH-60210E | 325-01-602-PD-06 | BMS Remote Modet for AHTR-21 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | -
429 | 392 | XS-FH-60210A | XS-FH-60210A | 325-01-602-PD-06 | Burner Remote Start for AHTR-21 |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
430 | 393 | XS-FH-60210B | XS-FH-60210B | 325-01-602-PD-06 | Dryer Interlocks for AHTR-21 |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
431 | 394 | XS-FH-60210C | XS-FH-60210C | 325-01-602-PD-06 | Remote Reset for AHTR-21 |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
432 | 395 | XS-FH-60210D | XS-FH-60210D | 325-01-602-PD-06 | Spare |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | -
433 | 396 |  | XS-FH-60210E | 325-01-602-PD-06 | Exhaust fan run status BF-60240 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | -
434 | 397 |  | XS-FH-60210F | 325-01-602-PD-06 | Supply fan run status BF-60210 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | -
435 | 398 |  | XS-FH-60210G | 325-01-602-PD-06 | Combusion fan run status BF-60211 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | -
436 | 399 | TI-FH-60210 | TI-FH-60210 | 325-01-602-PD-06 | Gas Burner Firing Rate Temp Signal |  | - | - | - | 1 | - | 4 - 20 mA | PLC | On-Off |  |  | -
437 | 400 | UY-FH-60210A | UY-FH-60210A | 325-01-602-PD-06 | Comb fan VFD Speed Control |  | - | - | - | 1 | - | 4 - 20 mA | PLC | On-Off |  |  | -
438 | 401 | UY-FH-60210B | UY-FH-60210B | 325-01-602-PD-06 | Demand Signal |  | - | - | 1 | - | - | 4 - 20 mA | PLC | On-Off |  |  | -
439 | 402 | COM-FH-60210B | COM-FH-60210B | 325-01-602-PD-06 | Communication Signal |  | - | - | - | - | 1 | Modbus RTU | PLC |  |  |  | -
440 | 403 | TE-60212 | TE-60212 |  | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Element | - | - | - | - | - | T/C Type K | AHTR Control Panel(HCP) |  |  |  | -
441 | 404 | DPHL-60230 | DPHL-60230 |  | Gas Pressure Differntial Switch Low for Exhaust Fan (FANE-21) | Pressure Differntial Switch Low | - | - | - | - | - | Dry Contact | AHTR Control Panel(HCP) |  |  |  | -
442 | 405 | DPSL-60211 | DPSL-60211 |  | Gas Pressure Differential Switch Low for Combustion Fan (FANC-21) | Pressure Differential Switch Low | - | - | - | - | - | Dry Contact | AHTR Control Panel(HCP) |  |  |  | -
443 | 406 | FCV-60211B | FCV-60211B |  | Gas Flow Control Damper (Valve) for Burner Combustion Air Duct (DTCB-21) | Flow Control Damper (Valve) | - | - | - | - | - | Internal wiring | AHTR Control Panel(HCP) |  |  |  | -
444 | 407 | ZT-60211B | ZT-60211B |  | Gas Position Transmitter for Combustion Air Damper Actuator (DTCB-21) | Position Transmitter | - | - | - | - | - | Internal wiring | AHTR Control Panel(HCP) |  |  |  | -
445 | 408 | ZSL-60211B | ZSL-60211B |  | Gas Position Switch Low for Combustion Air Damper Actuator (DTCB-21) | Position Switch Low | - | - | - | - | - | Internal wiring | AHTR Control Panel(HCP) |  |  |  | -
446 | 409 | ZSH-60211B | ZSH-60211B |  | Gas Position Switch High for Combustion Air Damper Actuator (DTCB-21) | Position Switch High | - | - | - | - | - | Internal wiring | AHTR Control Panel(HCP) |  |  |  | -
447 | 410 | VJ-01 (24VDC) | VJ-01 (24VDC) |  | Valve train J-BOX | Control Box | - | - | - | - | - | Internal wiring | AHTR Control Panel(HCP) |  |  |  | -
448 | 411 | VJ-01 (220VAC) | VJ-01 (220VAC) |  | Valve train J-BOX | Control Box | - | - | - | - | - | Internal wiring | AHTR Control Panel(HCP) |  |  |  | -
449 | 412 | UJ-01 (24VDC) | UJ-01 (24VDC) |  | Valve train J-BOX | Control Box | - | - | - | - | - | Internal wiring | AHTR Control Panel(HCP) |  |  |  | -
450 | 413 | UJ-01 (220VAC) | UJ-01 (220VAC) |  | Valve train J-BOX | Control Box | - | - | - | - | - | Internal wiring | AHTR Control Panel(HCP) |  |  |  | -
451 | 414 | PV-60210A | PV-60210A |  | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | - | - | - | - | - | Internal wiring | AHTR Control Panel
452 | 415 | PV-60210B | PV-60210B |  | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | - | - | - | - | - | Internal wiring | AHTR Control Panel
453 | 416 | DPT-60210 | DPT-60210 |  | Gas Pressure Differential Switch Low for Main Supply Air Fan (FANS-21) | Pressure Differential Switch Low | - | - | - | - | - | Internal wiring | AHTR Control Panel
454 | 417 | DPSL-60210B | DPSL-60210B |  | Gas Pressure Differential Switch Low for Air Heater (AHTR-21) | Pressure Differential Switch Low | - | - | - | - | - | Internal wiring | AHTR Control Panel
455 | 418 | DPSH-60210C | DPSH-60210C |  | Gas Pressure Differential Switch High for Air Heater (AHTR-21) | Pressure Differential Switch High | - | - | - | - | - | Internal wiring | AHTR Control Panel
456 | 419 | BE-60210A | BE-60210A |  | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | - | - | - | - | - | Internal wiring | AHTR Control Panel
457 | 420 | BE-60210B | BE-60210B |  | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | - | - | - | - | - | Internal wiring | AHTR Control Panel
458 | 421 | IX-60210A | IX-60210A |  | Gas Ignition Transformer for Air Heater (AHTR-21) | Ignition Transformer | - | - | - | - | - | Internal wiring | AHTR Control Panel
459 | 422 | FCV-60210A | FCV-60210A |  | Gas Flow Control Valve for Air Heater Gas Train (GTRN-21) | Flow Control Valve | - | - | - | - | - | Internal wiring | AHTR Control Panel
460 | 423 | ZSL-60210A | ZSL-60210A |  | Gas Position Switch Low for Air Heater Gas Train (GTRN-21) | Position Switch Low | - | - | - | - | - | Internal wiring | AHTR Control Panel
461 | 424 | ZT-60210A | ZT-60210A |  | Gas Position Transmitter for Air Heater Gas Train (GTRN-21) | Position Transmitter | - | - | - | - | - | Internal wiring | AHTR Control Panel
462 | 425 | PSH-60210 | PSH-60210 |  | Gas Pressure Switch High for Air Heater Gas Train (GTRN-21) | Pressure Switch High | - | - | - | - | - | Internal wiring | AHTR Control Panel
463 | 426 | BV-60210B | BV-60210B |  | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | - | - | - | - | - | Internal wiring | AHTR Control Panel
464 | 427 | ZSO-60210B | ZSO-60210B |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | - | - | - | - | - | Internal wiring | AHTR Control Panel
465 | 428 | ZSC-60210B | ZSC-60210B |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | - | - | - | - | - | Internal wiring | AHTR Control Panel
466 | 429 | VV-60210 | VV-60210 |  | Gas Venting Valve (main gas) for Air Heater Gas Train (GTRN-21) | Venting Valve (main gas) | - | - | - | - | - | Internal wiring | AHTR Control Panel
467 | 430 | ZSO-60210C | ZSO-60210C |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | - | - | - | - | - | Internal wiring | AHTR Control Panel
468 | 431 | ZSC-60210C | ZSC-60210C |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | - | - | - | - | - | Internal wiring | AHTR Control Panel
469 | 432 | PSL-60210 | PSL-60210 |  | Gas Pressure Switch Low for Air Heater Gas Train (GTRN-21) | Pressure Switch Low | - | - | - | - | - | Internal wiring | AHTR Control Panel
470 | 433 | BV-60210A | BV-60210A |  | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | - | - | - | - | - | Internal wiring | AHTR Control Panel
471 | 434 | ZSO-60210A | ZSO-60210A |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | - | - | - | - | - | Internal wiring | AHTR Control Panel
472 | 435 | ZSC-60210A | ZSC-60210A |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | - | - | - | - | - | Internal wiring | AHTR Control Panel
473 | 436 | High Pressure Pump (PD-60202) |  |  |  |  | - | - | - | - | -
474 | 437 | ES-60202 | XS-60202 | 325-01-602-PD-01 | E-Stop for PUPD-11 (Positive Displacement Pump ) | E-Stop | - | 1 | - | - | - | Dry Contact | PLC |  | n/a |  | -
475 | 438 |  | XA-60202 | 325-01-602-PD-01 | High Oil Pressure Alarm | Lamp | 1 | - | - | - | - | 24 VDC energized | PLC |  | n/a |  | -
476 | 439 | PT-60205 | PT-60202 | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC
477 | 440 | FS-60205 | FS-60202 | 325-01-602-PD-01 | Cooling Water Return Flow Switch for Positive Displacement Pump (PUPD-11) | Flow Switch | - | 1 | - | - | - |  | PLC |  |  |  | -
478 | 441 | XS-60205 | XS-60205 | 325-01-602-PD-01 | Start / Stop Command for PUPD-11 (Positive Displacement Pump ) | Start / Stop Command | - | - | - | - | - |  | PLC
479 | 442 | VS-60205 | VS-60202 | 325-01-602-PD-01 | Vibration Gear Box Vibration Switch for Switch Vibration for PUPD-11 (PUPD-11) | Vibration Switch | - | - | - | 1 | - | 4 - 20 mA | PLC
480 | 443 | XV-60205A | XV-60202A | 325-01-602-PD-01 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) | On/Off Valve | 1 | - | - | - | - | 24 VDC energized | PLC |  | Energized " Open" / Position O/C
481 | 444 |  | PS-60202 | 325-01-602-PD-01 | Oil Pressure Switch for Positive Displacement Pump (PUPD-11) | Flow Switch | - | 1 | - | - | - |  | PLC |  |  |  | -
482 | 445 |  | TT-60202A | 325-01-602-PD-01 | Temperature for Positive Displacement Pump (PUPD-11) | TC / Temperature Transmitter | - | - | - | 1 | - |  | PLC |  |  |  | -
483 | 446 |  | TT-60202B | 325-01-602-PD-01 | Temperature for Positive Displacement Pump (PUPD-11) | TC / Temperature Transmitter | - | - | - | 1 | - |  | PLC |  |  |  | -
484 | 447 | YA-60205 | YA-60205 | 325-01-602-PD-01 | Fault Command |  | - | - | - | - | - |  | PLC
485 | 448 | YI-60205 | YI-60205 | 325-01-602-PD-01 | Run Command |  | - | - | - | - | - |  | PLC
486 | 449 | Suppression Panel |  |  |  |  | - | - | - | - | -
487 | 450 | PSH-61301 | PSH-61301 | 325-01-613-PD-01 | Gas and Powder Pressure Switch High for Storage Bin Cyclone Inlet Duct (####-##) | Pressure Switch High | - | - | - | - | - |  | Suppression Sys. Panel
488 | 451 | PSH-60220 | PSH-60220 | 325-01-602-PD-04 | Gas Pressure Switch High for Spray Chamber (CHAM-21) | Pressure Switch High | - | - | - | - | - |  | Suppression Sys. Panel
489 | 452 | PSH-60230 | PSH-60230 | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-21) | Pressure Switch High | - | - | - | - | - |  | Suppression Sys. Panel
490 | 453 | PSH-60231 | PSH-60231 | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-22) | Pressure Switch High | - | - | - | - | - |  | Suppression Sys. Panel
491 | 454 | PSH-60224 | PSH-60224 | 325-01-602-PD-05 | Gas and Powder Pressure Switch High for Bag House (BGHS-21) | Pressure Switch High | - | - | - | - | - |  | Suppression Sys. Panel
492 | 455 | XA-60202A | XA-60202A | 325-01-602-PD-08 | General Alarm Emergency Stop Actuation for XSUP-5601 (Supression Panel) | General Alarm Emergency Stop Actuation | - | 1 | - | - | - | Dry Contact | PLC | On-Off
493 | 456 | XA-60202B | XA-60202B | 325-01-602-PD-08 | General Fault Controlled Stop for XSUP-5601 (Supression Panel) | General Fault Controlled Stop | - | 1 | - | - | - | Dry Contact | PLC | On-Off
494 | 457 | XA-60202C | XA-60202C | 325-01-602-PD-08 | General Armed Status Indicator for XSUP-5601 (Supression Panel) | General Armed Status Indicator | - | 1 | - | - | - | Dry Contact | PLC | On-Off
495 | 458 | XA-60202D | XA-60202D | 325-01-602-PD-08 | Power Fault Status Indicator for XSUP-5601 (Supression Panel) | Power Fault Status Indicator | - | 1 | - | - | - | Dry Contact | PLC | On-Off
496 | 459 | XA-60202E | XA-60202E | 325-01-602-PD-08 | Dryer CHAM-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | Dryer CHAM-21 Emergency Stop Actuation | - | 1 | - | - | - | Dry Contact | PLC | On-Off
497 | 460 | XA-60202F | XA-60202F | 325-01-602-PD-08 | CHAM-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CHAM-21 Controlled Stop Trouble (No Protection) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
498 | 461 | XA-60202G | XA-60202G | 325-01-602-PD-08 | CYCL-21/22 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-21/22 Emergency Stop Actuation | - | 1 | - | - | - | Dry Contact | PLC | On-Off
499 | 462 | XA-60202H | XA-60202H | 325-01-602-PD-08 | CYCL-21/22 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-21/22 Controlled Stop Trouble (No Protection) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
500 | 463 | XA-60202J | XA-60202J | 325-01-602-PD-08 | BGHS-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | BGHS-21 Emergency Stop Actuation | - | 1 | - | - | - | Dry Contact | PLC | On-Off
501 | 464 | XA-60202K | XA-60202K | 325-01-602-PD-08 | BGHS-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | BGHS-21 Controlled Stop Trouble (No Protection) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
502 | 465 | XA-60202L | XA-60202L | 325-01-602-PD-08 | CYCL-31 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-31 Emergency Stop Actuation | - | 1 | - | - | - | Dry Contact | PLC | On-Off
503 | 466 | XA-60202M | XA-60202M | 325-01-602-PD-08 | CYCL-31 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-31 Controlled Stop Trouble (No Protection) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
504 | 467 | Fire Deluge PK-60221 |  |  |  |  | - | - | - | - | -
505 | 468 | XA-60261 | XA-60221A | 325-01-602-PD-04 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Fire Deluge Fault (No Protection) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
506 | 469 | XA-60262 | XA-60221B | 325-01-602-PD-04 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Fire Deluge Alarm (Deluge Activated) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
507 | 470 | XS-60260 | XS-60221 | 325-01-602-PD-04 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off
508 | 139 |  | TSH-60230 | 325-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | Temperature Switch | - | - | - | - | - | Dry Contact | Fire Deluge Control Panel | 0 - 140 C | 140
509 | 471 | Fire Deluge PK-60222 |  |  |  |  | - | - | - | - | -
510 | 472 |  | XA-60222A | 325-01-602-PD-05 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Fire Deluge Fault (No Protection) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
511 | 473 |  | XA-60222B | 325-01-602-PD-05 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Fire Deluge Alarm (Deluge Activated) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
512 | 474 |  | XS-60222 | 325-01-602-PD-05 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off
513 |  |  | XV-60240D | 325-01-602-PD-05 | Drain Valve |  | - | 1 | - | - | - | 24 VDC energized | PLC | On-Off
514 | 140 |  | TSH-60240 | 325-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | Temperature Switch | - | - | - | - | - | Dry Contact | Fire Deluge Control Panel | 0 - 140 C | 140
515 | 475 | Keaser Air Blower |  |  |  |  | - | - | - | - | -
516 | 476 |  | XS-61302 | 325-01-613-PD-01 | Start / Stop Command for Bin Aerator Blower | Start / Stop Command | 1 | - | - | - | - | Dry Contact | PLC | On-Off
517 | 477 |  | XA-61302A | 325-01-613-PD-01 | Operational / Running status |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off
518 | 478 |  | XA-61302B | 325-01-613-PD-01 | Local / Remote status |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off
519 | 479 |  | XA-61302C | 325-01-613-PD-01 | Fault / Trip condition |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off
520 | 480 |  | XA-61302D | 325-01-613-PD-01 | Warning condition |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off
521 | 481 | REMOTE I-O Area-200 |  |  |  |  | - | - | - | - | -
522 | 482 | HV-2022 | HV-20204 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | -
523 | 483 | HV-2024 | HV-20205 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | -
524 | 484 | HV-2026 | HV-20206 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | -
525 | 485 | HV-2030 | HV-20207 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | -
526 | 486 | HV-2032 | HV-20208 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | -
527 | 487 | HV-2035 | HV-20209 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | -
528 | 488 | HV-2038 | HV-20210 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | -
529 | 489 | XV-20201 | XV-20201 | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d
530 | 490 | XV-20202 | XV-20202 | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d
531 | 491 | XV-20203 | XV-20203 | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d
532 | 492 | XV-20211 | XV-20211 | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d
533 | 493 | XV-20212 | XV-20212 | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d
534 | 494 | XV-20213 | XV-20213 | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d
535 | 495 | LS-81001 | LS-814201 | 325-01-814-PD-01 | Level alarm low | Level switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Nondetected " Empty " / Overfill |  | Ex ic
536 | 496 | PCM-2030 | PC-20201 | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2030 |  | - | - | - | - | 1 | 24 VDC energized | RIO-200 | On-Off
537 | 497 | PCM-2031 |  | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2031 | ยกเลิก | 2 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off
538 | 498 | PCY-81001 | PC-814201 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81001 |  | - | - | - | - | 1 | 24 VDC energized | RIO-200 | On-Off
539 | 499 | PCY-81002 | PC-814202 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81002 |  | - | - | - | - | 1 | 24 VDC energized | RIO-200 | On-Off
540 | 500 | LPG Station |  |  |  |  | - | - | - | - | -
541 | 501 | FT-80301 | FT-913201 | 325-01-913-PD-02 | Flow outlet LPG line | Coriolis Flow Transmitter | - | 1 | - | 2 | - | 4 - 20 mA,Pulse | RIO-200 | 0-1000kg/hr | Flow rate |  | Ex d
542 | 502 | LT-80301 | LT-913201 | 325-01-913-PD-01 | Level LPG in storage | Level transmitter | - | - | - | 1 | - | 4 - 20 mA | RIO-200 |  | 0 - 100% |  | Ex ia
543 | 503 | PT-80302 | PT-913201 | 325-01-913-PD-02 | Pressure outlet LPG line | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | RIO-200 | 0 - 10 barg | 0 - 8 barg / 0-100% |  | Ex d
544 | 504 |  | XV-913201 | 325-01-913-PD-02 | Outlet LPG line | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d
545 | 505 | Gas Vaporizer 4 |  |  |  |  | - | - | - | - | -
546 | 506 | XA-80305A | XA-913201A | 325-01-913-PD-02 | Gas Vaporizer 4 Run Status | Gas vaporizer Ready | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | -
547 | 507 | XA-80305B | XA-913201B | 325-01-913-PD-02 | Gas Vaporizer 4 Alarm status | Gas vaporizer Run | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | -
548 | 508 | XA-80305C | XA-913201C | 325-01-913-PD-02 | Gas Vaporizer 4 High Temp Shut-Down status | Gas vaporizer Failed | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | -
549 | 509 | XA-80305D | XA-913201D | 325-01-913-PD-02 | Gas Vaporizer 4 Working Temp Shun-Off status | Gas vaporizer Overheated | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | -
550 | 510 | XA-80305E | XA-913201E | 325-01-913-PD-02 | Gas Vaporizer 4 Low Water Shun-Off status | Gas vaporizer Excessive flow tripped | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | -
551 | 512 | XS-80305A | XS-913201A | 325-01-913-PD-02 | Start Command for Gas Vaporizer 4 | Start Command | 1 | - | - | - | - | 24 VDC energized | RIO-200 | On-Off |  |  | -
552 | 512 | XS-80305B | XS-913201B | 325-01-913-PD-02 | Stop Command for Gas Vaporizer 4 | Stop Command | 1 | - | - | - | - | 24 VDC energized | RIO-200 | On-Off |  |  | -
553 | 513 | Gas Vaporizer 5 |  |  |  |  | - | - | - | - | -
554 | 514 | XA-80306A | XA-913202A | 325-01-913-PD-02 | Gas Vaporizer 5 Run Status | Gas vaporizer Ready | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | -
555 | 515 | XA-80306B | XA-913202B | 325-01-913-PD-02 | Gas Vaporizer 5 Alarm status | Gas vaporizer Run | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | -
556 | 516 | XA-80306C | XA-913202C | 325-01-913-PD-02 | Gas Vaporizer 5 High Temp Shut-Down status | Gas vaporizer Failed | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | -
557 | 517 | XA-80306D | XA-913202D | 325-01-913-PD-02 | Gas Vaporizer 5 Working Temp Shun-Off status | Gas vaporizer Overheated | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | -
558 | 518 | XA-80306E | XA-913202E | 325-01-913-PD-02 | Gas Vaporizer 5 Low Water Shun-Off status | Gas vaporizer Excessive flow tripped | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | -
559 | 519 | XS-80306A | XS-913202A | 325-01-913-PD-02 | Start Command for Gas Vaporizer 5 | Start Command | 1 | - | - | - | - | 24 VDC energized | RIO-200 | On-Off |  |  | -
560 | 520 | XS-80306B | XS-913202B | 325-01-913-PD-02 | Stop Command for Gas Vaporizer 5 | Stop Command | 1 | - | - | - | - | 24 VDC energized | RIO-200 | On-Off |  |  | -