## JB-401_IO_List
KALASIN ENGINEERING — DESTINATION: JB-401 (INFEED AREA 2ND FLOOR JUNCTION BOX)
Location: Infeed Processing 2nd Floor ¦ Enclosure: 800 x 600 x 250 mm (Standard Industrial (IP66 / SS304)) ¦ Total I/O: 112 (AI: 16 ¦ DI: 64 ¦ DO: 32) ¦ Active: 85, Spare: 27 (24.1%) | [16 empty] | ⬅ Return to Destination Index
DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE) | [6 empty] | SIGNAL SPECIFICATION |  |  | SOURCE SPECIFICATION (PLC RACK / CHASSIS / SLOT / CARD PIN / ePLAN WIRE TAG)
Dest Enclosure | Location / Area | Floor / Zone | Field Terminal Block | Term Pin | Instrument Tag | Instrument Description | I/O Type | Signal Spec | Point Status | Point Ref ID | Chassis | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | FSL-40201 | Flow Switch | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P16 | C1 | 3 | 16 | 17 | 1756-IB32 | FSL-40201_DI_1 | Pin 17 | C1S3:17/C1S03-X2:17
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | FSL-40202 | Flow Switch | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P17 | C1 | 3 | 17 | 18 | 1756-IB32 | FSL-40202_DI_1 | Pin 18 | C1S3:18/C1S03-X2:18
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | FT-40201 | Coriolis Flow Transmitter | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P18 | C1 | 3 | 18 | 19 | 1756-IB32 | FT-40201_DI_1 | Pin 19 | C1S3:19/C1S03-X2:19
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | FT-40202 | Magnetic Flow Transmitter | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P19 | C1 | 3 | 19 | 20 | 1756-IB32 | FT-40202_DI_1 | Pin 20 | C1S3:20/C1S03-X2:20
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40201 | Manual Valve With Position Switch | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P20 | C1 | 3 | 20 | 21 | 1756-IB32 | HV-40201_DI_1 | Pin 21 | C1S3:21/C1S03-X2:21
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40202 | Manual Valve With Position Switch | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P21 | C1 | 3 | 21 | 22 | 1756-IB32 | HV-40202_DI_1 | Pin 22 | C1S3:22/C1S03-X2:22
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40203 | Manual Valve With Position Switch | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P22 | C1 | 3 | 22 | 23 | 1756-IB32 | HV-40203_DI_1 | Pin 23 | C1S3:23/C1S03-X2:23
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40204 | Manual Valve With Position Switch | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P23 | C1 | 3 | 23 | 24 | 1756-IB32 | HV-40204_DI_1 | Pin 24 | C1S3:24/C1S03-X2:24
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | HV-40205 | Manual Valve With Position Switch | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P24 | C1 | 3 | 24 | 25 | 1756-IB32 | HV-40205_DI_1 | Pin 25 | C1S3:25/C1S03-X2:25
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | HV-40206 | Manual Valve With Position Switch | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P25 | C1 | 3 | 25 | 26 | 1756-IB32 | HV-40206_DI_1 | Pin 26 | C1S3:26/C1S03-X2:26
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201A |  | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P26 | C1 | 3 | 26 | 27 | 1756-IB32 | XV-40201A_DI_1 | Pin 27 | C1S3:27/C1S03-X2:27
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201A |  | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P27 | C1 | 3 | 27 | 28 | 1756-IB32 | XV-40201A_DI_2 | Pin 28 | C1S3:28/C1S03-X2:28
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201B |  | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P28 | C1 | 3 | 28 | 29 | 1756-IB32 | XV-40201B_DI_1 | Pin 29 | C1S3:29/C1S03-X2:29
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201B |  | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P29 | C1 | 3 | 29 | 30 | 1756-IB32 | XV-40201B_DI_2 | Pin 30 | C1S3:30/C1S03-X2:30
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201C |  | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P30 | C1 | 3 | 30 | 31 | 1756-IB32 | XV-40201C_DI_1 | Pin 31 | C1S3:31/C1S03-X2:31
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201C |  | DI | 24VDC Dry Contact | ACTIVE | C1-S03-P31 | C1 | 3 | 31 | 32 | 1756-IB32 | XV-40201C_DI_2 | Pin 32 | C1S3:32/C1S03-X2:32
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201D |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P00 | C1 | 4 | 0 | 1 | 1756-IB32 | XV-40201D_DI_1 | Pin 1 | C1S4:1/TBDI1:1A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201D |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P01 | C1 | 4 | 1 | 2 | 1756-IB32 | XV-40201D_DI_2 | Pin 2 | C1S4:2/TBDI1:2A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201E |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P02 | C1 | 4 | 2 | 3 | 1756-IB32 | XV-40201E_DI_1 | Pin 3 | C1S4:3/TBDI1:3A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201E |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P03 | C1 | 4 | 3 | 4 | 1756-IB32 | XV-40201E_DI_2 | Pin 4 | C1S4:4/TBDI1:4A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201F |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P04 | C1 | 4 | 4 | 5 | 1756-IB32 | XV-40201F_DI_1 | Pin 5 | C1S4:5/TBDI1:5A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201F |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P05 | C1 | 4 | 5 | 6 | 1756-IB32 | XV-40201F_DI_2 | Pin 6 | C1S4:6/TBDI1:6A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201G |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P06 | C1 | 4 | 6 | 7 | 1756-IB32 | XV-40201G_DI_1 | Pin 7 | C1S4:7/TBDI1:7A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201G |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P07 | C1 | 4 | 7 | 8 | 1756-IB32 | XV-40201G_DI_2 | Pin 8 | C1S4:8/TBDI1:8A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201H |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P08 | C1 | 4 | 8 | 9 | 1756-IB32 | XV-40201H_DI_1 | Pin 9 | C1S4:9/TBDI1:9A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201H |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P09 | C1 | 4 | 9 | 10 | 1756-IB32 | XV-40201H_DI_2 | Pin 10 | C1S4:10/TBDI1:10A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202A |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P11 | C1 | 4 | 11 | 12 | 1756-IB32 | XV-40202A_DI_2 | Pin 12 | C1S4:12/TBDI1:12A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202B |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P12 | C1 | 4 | 12 | 13 | 1756-IB32 | XV-40202B_DI_1 | Pin 13 | C1S4:13/TBDI1:13A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202B |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P13 | C1 | 4 | 13 | 14 | 1756-IB32 | XV-40202B_DI_2 | Pin 14 | C1S4:14/TBDI1:14A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202C |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P14 | C1 | 4 | 14 | 15 | 1756-IB32 | XV-40202C_DI_1 | Pin 15 | C1S4:15/TBDI1:15A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202C |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P15 | C1 | 4 | 15 | 16 | 1756-IB32 | XV-40202C_DI_2 | Pin 16 | C1S4:16/TBDI1:16A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202D |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P16 | C1 | 4 | 16 | 17 | 1756-IB32 | XV-40202D_DI_1 | Pin 17 | C1S4:17/C1S04-X2:17
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202D |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P17 | C1 | 4 | 17 | 18 | 1756-IB32 | XV-40202D_DI_2 | Pin 18 | C1S4:18/C1S04-X2:18
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202E |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P18 | C1 | 4 | 18 | 19 | 1756-IB32 | XV-40202E_DI_1 | Pin 19 | C1S4:19/TBDI1:17A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202A |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P19 | C1 | 4 | 19 | 20 | 1756-IB32 | XV-40202A_DI_1 | Pin 20 | C1S4:20/TBDI1:18A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202E |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P19 | C1 | 4 | 19 | 20 | 1756-IB32 | XV-40202E_DI_2 | Pin 20 | C1S4:20/TBDI1:18A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202F |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P20 | C1 | 4 | 20 | 21 | 1756-IB32 | XV-40202F_DI_1 | Pin 21 | C1S4:21/TBDI1:19A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202F |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P21 | C1 | 4 | 21 | 22 | 1756-IB32 | XV-40202F_DI_2 | Pin 22 | C1S4:22/TBDI1:20A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202G |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P22 | C1 | 4 | 22 | 23 | 1756-IB32 | XV-40202G_DI_1 | Pin 23 | C1S4:23/TBDI1:21A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202G |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P23 | C1 | 4 | 23 | 24 | 1756-IB32 | XV-40202G_DI_2 | Pin 24 | C1S4:24/TBDI1:22A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202H |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P24 | C1 | 4 | 24 | 25 | 1756-IB32 | XV-40202H_DI_1 | Pin 25 | C1S4:25/TBDI1:23A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202H |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P25 | C1 | 4 | 25 | 26 | 1756-IB32 | XV-40202H_DI_2 | Pin 26 | C1S4:26/TBDI1:24A
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203B |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P26 | C1 | 4 | 26 | 27 | 1756-IB32 | XV-40203B_DI_1 | Pin 27 | C1S4:27/TBDI1:25A
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203B |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P27 | C1 | 4 | 27 | 28 | 1756-IB32 | XV-40203B_DI_2 | Pin 28 | C1S4:28/TBDI1:26A
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203C |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P28 | C1 | 4 | 28 | 29 | 1756-IB32 | XV-40203C_DI_1 | Pin 29 | C1S4:29/TBDI1:27A
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203C |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P29 | C1 | 4 | 29 | 30 | 1756-IB32 | XV-40203C_DI_2 | Pin 30 | C1S4:30/TBDI1:28A
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203D |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P30 | C1 | 4 | 30 | 31 | 1756-IB32 | XV-40203D_DI_1 | Pin 31 | C1S4:31/TBDI1:29A
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203D |  | DI | 24VDC Dry Contact | ACTIVE | C1-S04-P31 | C1 | 4 | 31 | 32 | 1756-IB32 | XV-40203D_DI_2 | Pin 32 | C1S4:32/TBDI1:30A
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S05-X1 | - | XV-40203E |  | DI | 24VDC Dry Contact | ACTIVE | C1-S05-P00 | C1 | 5 | 0 | 1 | 1756-IB32 | XV-40203E_DI_1 | Pin 1 | C1S5:1/TBDI2:1A
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S05-X1 | - | XV-40203E |  | DI | 24VDC Dry Contact | ACTIVE | C1-S05-P01 | C1 | 5 | 1 | 2 | 1756-IB32 | XV-40203E_DI_2 | Pin 2 | C1S5:2/TBDI2:2A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P02 | C1 | 5 | 2 | 3 | 1756-IB32 | Spare_DI_0 | Pin 3 | C1S5:3/TBDI2:3A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P03 | C1 | 5 | 3 | 4 | 1756-IB32 | Spare_DI_0 | Pin 4 | C1S5:4/TBDI2:4A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P04 | C1 | 5 | 4 | 5 | 1756-IB32 | Spare_DI_0 | Pin 5 | C1S5:5/TBDI2:5A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P05 | C1 | 5 | 5 | 6 | 1756-IB32 | Spare_DI_0 | Pin 6 | C1S5:6/TBDI2:6A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P06 | C1 | 5 | 6 | 7 | 1756-IB32 | Spare_DI_0 | Pin 7 | C1S5:7/TBDI2:7A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P07 | C1 | 5 | 7 | 8 | 1756-IB32 | Spare_DI_0 | Pin 8 | C1S5:8/TBDI2:8A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P08 | C1 | 5 | 8 | 9 | 1756-IB32 | Spare_DI_0 | Pin 9 | C1S5:9/TBDI2:9A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P09 | C1 | 5 | 9 | 10 | 1756-IB32 | Spare_DI_0 | Pin 10 | C1S5:10/TBDI2:10A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P10 | C1 | 5 | 10 | 11 | 1756-IB32 | Spare_DI_0 | Pin 11 | C1S5:11/TBDI2:11A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P11 | C1 | 5 | 11 | 12 | 1756-IB32 | Spare_DI_0 | Pin 12 | C1S5:12/TBDI2:12A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P12 | C1 | 5 | 12 | 13 | 1756-IB32 | Spare_DI_0 | Pin 13 | C1S5:13/TBDI2:13A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P13 | C1 | 5 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C1S5:14/TBDI2:14A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P14 | C1 | 5 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C1S5:15/TBDI2:15A
JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C1-S05-P15 | C1 | 5 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C1S5:16/TBDI2:16A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202E |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P16 | C1 | 7 | 16 | 17 | 1756-OB32 | XV-40202E_DO_1 | Pin 17 | C1S7:17/C1S07-X2:17
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202F |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P17 | C1 | 7 | 17 | 18 | 1756-OB32 | XV-40202F_DO_1 | Pin 18 | C1S7:18/C1S07-X2:18
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202G |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P18 | C1 | 7 | 18 | 19 | 1756-OB32 | XV-40202G_DO_1 | Pin 19 | C1S7:19/TBDI4:17A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202H |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P19 | C1 | 7 | 19 | 20 | 1756-OB32 | XV-40202H_DO_1 | Pin 20 | C1S7:20/TBDI4:18A
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203B |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P20 | C1 | 7 | 20 | 21 | 1756-OB32 | XV-40203B_DO_1 | Pin 21 | C1S7:21/TBDI4:19A
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203C |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P21 | C1 | 7 | 21 | 22 | 1756-OB32 | XV-40203C_DO_1 | Pin 22 | C1S7:22/TBDI4:20A
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203D |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P22 | C1 | 7 | 22 | 23 | 1756-OB32 | XV-40203D_DO_1 | Pin 23 | C1S7:23/TBDI4:21A
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203E |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P23 | C1 | 7 | 23 | 24 | 1756-OB32 | XV-40203E_DO_1 | Pin 24 | C1S7:24/TBDI4:22A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40201 |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P24 | C1 | 7 | 24 | 25 | 1756-OB32 | SV-40201_DO_1 | Pin 25 | C1S7:25/TBDI4:23A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40202 |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P25 | C1 | 7 | 25 | 26 | 1756-OB32 | SV-40202_DO_1 | Pin 26 | C1S7:26/TBDI4:24A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40203 |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P26 | C1 | 7 | 26 | 27 | 1756-OB32 | SV-40203_DO_1 | Pin 27 | C1S7:27/TBDI4:25A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40204 |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P27 | C1 | 7 | 27 | 28 | 1756-OB32 | SV-40204_DO_1 | Pin 28 | C1S7:28/TBDI4:26A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201A |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P28 | C1 | 7 | 28 | 29 | 1756-OB32 | XV-40201A_DO_1 | Pin 29 | C1S7:29/TBDI4:27A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201B |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P29 | C1 | 7 | 29 | 30 | 1756-OB32 | XV-40201B_DO_1 | Pin 30 | C1S7:30/TBDI4:28A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201C |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P30 | C1 | 7 | 30 | 31 | 1756-OB32 | XV-40201C_DO_1 | Pin 31 | C1S7:31/TBDI4:29A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201D |  | DO | 24VDC Sourcing | ACTIVE | C1-S07-P31 | C1 | 7 | 31 | 32 | 1756-OB32 | XV-40201D_DO_1 | Pin 32 | C1S7:32/TBDI4:30A
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201E |  | DO | 24VDC Sourcing | ACTIVE | C1-S08-P00 | C1 | 8 | 0 | 1 | 1756-OB32 | XV-40201E_DO_1 | Pin 1 | C1S8:1/RL.1:A1
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201F |  | DO | 24VDC Sourcing | ACTIVE | C1-S08-P01 | C1 | 8 | 1 | 2 | 1756-OB32 | XV-40201F_DO_1 | Pin 2 | C1S8:2/RL.2:A1
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201G |  | DO | 24VDC Sourcing | ACTIVE | C1-S08-P02 | C1 | 8 | 2 | 3 | 1756-OB32 | XV-40201G_DO_1 | Pin 3 | C1S8:3/RL.3:A1
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201H |  | DO | 24VDC Sourcing | ACTIVE | C1-S08-P03 | C1 | 8 | 3 | 4 | 1756-OB32 | XV-40201H_DO_1 | Pin 4 | C1S8:4/RL.4:A1
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202A |  | DO | 24VDC Sourcing | ACTIVE | C1-S08-P04 | C1 | 8 | 4 | 5 | 1756-OB32 | XV-40202A_DO_1 | Pin 5 | C1S8:5/RL.5:A1
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202B |  | DO | 24VDC Sourcing | ACTIVE | C1-S08-P05 | C1 | 8 | 5 | 6 | 1756-OB32 | XV-40202B_DO_1 | Pin 6 | C1S8:6/RL.6:A1
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202C |  | DO | 24VDC Sourcing | ACTIVE | C1-S08-P06 | C1 | 8 | 6 | 7 | 1756-OB32 | XV-40202C_DO_1 | Pin 7 | C1S8:7/RL.7:A1
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202D |  | DO | 24VDC Sourcing | ACTIVE | C1-S08-P07 | C1 | 8 | 7 | 8 | 1756-OB32 | XV-40202D_DO_1 | Pin 8 | C1S8:8/RL.8:A1
JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C1-S08-P08 | C1 | 8 | 8 | 9 | 1756-OB32 | Spare_DO_0 | Pin 9 | C1S8:9/RL.9:A1
JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C1-S08-P09 | C1 | 8 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C1S8:10/RL.10:A1
JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C1-S08-P10 | C1 | 8 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C1S8:11/RL.11:A1
JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C1-S08-P11 | C1 | 8 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C1S8:12/RL.12:A1
JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C1-S08-P12 | C1 | 8 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C1S8:13/RL.13:A1
JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C1-S08-P13 | C1 | 8 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C1S8:14/RL.14:A1
JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C1-S08-P14 | C1 | 8 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C1S8:15/RL.15:A1
JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C1-S08-P15 | C1 | 8 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C1S8:16/RL.16:A1
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | FT-40201 | Coriolis Flow Transmitter | AI | 4-20mA HART | ACTIVE | C1-S09-P00 | C1 | 9 | 0 | 1 | 1756-IF16 | FT-40201_AI_1 | Pin 1 | C1S9:1/RL.33:A1
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | FT-40201 | Coriolis Flow Transmitter | AI | 4-20mA HART | ACTIVE | C1-S09-P01 | C1 | 9 | 1 | 2 | 1756-IF16 | FT-40201_AI_2 | Pin 2 | C1S9:2/RL.34:A1
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | FT-40202 | Magnetic Flow Transmitter | AI | 4-20mA HART | ACTIVE | C1-S09-P02 | C1 | 9 | 2 | 3 | 1756-IF16 | FT-40202_AI_1 | Pin 3 | C1S9:3/RL.35:A1
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | LT-40203 | Level Transmitter | AI | 4-20mA HART | ACTIVE | C1-S09-P03 | C1 | 9 | 3 | 4 | 1756-IF16 | LT-40203_AI_1 | Pin 4 | C1S9:4/RL.36:A1
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | LT-40201 | Level Transmitter | AI | 4-20mA HART | ACTIVE | C1-S09-P04 | C1 | 9 | 4 | 5 | 1756-IF16 | LT-40201_AI_1 | Pin 5 | C1S9:5/RL.37:A1
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | LT-40202 | Level Transmitter | AI | 4-20mA HART | ACTIVE | C1-S09-P05 | C1 | 9 | 5 | 6 | 1756-IF16 | LT-40202_AI_1 | Pin 6 | C1S9:6/RL.38:A1
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | pHT-40201 | PH Transmitter | AI | 4-20mA HART | ACTIVE | C1-S09-P06 | C1 | 9 | 6 | 7 | 1756-IF16 | pHT-40201_AI_1 | Pin 7 | C1S9:7/RL.39:A1
JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | pHT-40202 | PH Transmitter | AI | 4-20mA HART | ACTIVE | C1-S09-P07 | C1 | 9 | 7 | 8 | 1756-IF16 | pHT-40202_AI_1 | Pin 8 | C1S9:8/RL.40:A1
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | PT-40201 | Pressure Transmitter | AI | 4-20mA HART | ACTIVE | C1-S09-P08 | C1 | 9 | 8 | 9 | 1756-IF16 | PT-40201_AI_1 | Pin 9 | C1S9:9/RL.41:A1
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | PT-40202 | Pressure Transmitter | AI | 4-20mA HART | ACTIVE | C1-S09-P09 | C1 | 9 | 9 | 10 | 1756-IF16 | PT-40202_AI_1 | Pin 10 | C1S9:10/RL.42:A1
JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | PT-60202 | Pressure Transmitter | AI | 4-20mA HART | ACTIVE | C1-S09-P10 | C1 | 9 | 10 | 11 | 1756-IF16 | PT-60202_AI_1 | Pin 11 | C1S9:11/RL.43:A1
JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | AI | 4-20mA HART | SPARE | C1-S09-P11 | C1 | 9 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C1S9:12/RL.44:A1
JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | AI | 4-20mA HART | SPARE | C1-S09-P12 | C1 | 9 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C1S9:13/RL.45:A1
JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | AI | 4-20mA HART | SPARE | C1-S09-P13 | C1 | 9 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C1S9:14/RL.46:A1
JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | AI | 4-20mA HART | SPARE | C1-S09-P14 | C1 | 9 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C1S9:15/RL.47:A1
JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | AI | 4-20mA HART | SPARE | C1-S09-P15 | C1 | 9 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C1S9:16/RL.48:A1