## 00_JB_Index
KALASIN ENGINEERING ¦ JUNCTION BOX LOOP TEST REGISTER: JB-401
Project Sprint 18K TPA Spray Dryer / Jet Cooker ¦ Location: JB-401 ¦ 1 Equipment = 1 Sheet
TOTAL EQUIPMENT |  | TOTAL ACTIVE CHANNELS |  | DIGITAL INPUT (DI) |  | DIGITAL OUTPUT (DO) |  | ANALOG IN/OUT (AI/AO)
42 Units |  | 85 Channels |  | 50 Pts |  | 24 Pts |  | 11 AI / 0 AO
Item # | Equipment Tag | Equipment Service Description | P&ID Drawing No. | Primary Signal Breakdown | Total Channels | Primary JB Terminal | PLC Rack / Slot | CAD Wiring Typical | Loop Test Status | QA/QC Sign-off & Date
1 | FSL-40201 | Slurry low flow | 325-01-402-PD-01 | 1x DI | 1 | P1-TBDI1-17 | C1/C1S4 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
2 | FSL-40202 | Slurry low flow | 325-01-402-PD-01 | 1x DI | 1 | P1-TBDI1-18 | C1/C1S4 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
3 | FT-40201 | Slurry flowrate & density check transfer line | 325-01-402-PD-02 | 2x AI, 1x DI (Flow + Pulse + Pwr) | 3 | P1-TBAI1-1(A/B) | C1/C1S10 | TYP-AI-02 / FLOW | READY FOR TEST | Pending Sign-off
4 | FT-40202 | Feed Slurry Flow Transmitter for Pipe (PIPE) | 325-01-402-PD-02 | 1x AI, 1x DI (Flow + Pulse + Pwr) | 2 | P1-TBAI1-3(A/B) | C1/C1S10 | TYP-AI-02 / FLOW | READY FOR TEST | Pending Sign-off
5 | HV-40201 | Slurry Drain line | 325-01-402-PD-01 | 1x DI (Solenoid + FB) | 1 | P1-TBDI1-21 | C1/C1S4 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
6 | HV-40202 | Slurry Drain line | 325-01-402-PD-01 | 1x DI (Solenoid + FB) | 1 | P1-TBDI1-22 | C1/C1S4 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
7 | HV-40203 | Slurry Drain tank TS-40201 | 325-01-402-PD-01 | 1x DI (Solenoid + FB) | 1 | P1-TBDI1-23 | C1/C1S4 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
8 | HV-40204 | Slurry Drain tank TS-40202 | 325-01-402-PD-01 | 1x DI (Solenoid + FB) | 1 | P1-TBDI1-24 | C1/C1S4 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
9 | HV-40205 | Slurry Drain line | 325-01-402-PD-01 | 1x DI (Solenoid + FB) | 1 | P1-TBDI1-25 | C1/C1S4 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
10 | HV-40206 | Slurry Drain tank TS-40203 | 325-01-402-PD-01 | 1x DI (Solenoid + FB) | 1 | P1-TBDI1-26 | C1/C1S4 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
11 | LT-40201 | Level transmitter in Spray dryer infeed tank | 325-01-402-PD-02 | 1x AI | 1 | P1-TBAI1-5(A/B) | C1/C1S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
12 | LT-40202 | Level transmitter in pH Adjustment tank 2 | 325-01-402-PD-01 | 1x AI | 1 | P1-TBAI1-6(A/B) | C1/C1S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
13 | LT-40203 | Level transmitter in Spray dryer infeed tank | 325-01-402-PD-02 | 1x AI | 1 | P1-TBAI1-4(A/B) | C1/C1S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
14 | PT-40201 | Pressure Transmitter for Inlet Filter Strainer (FSTR-11) | 325-01-402-PD-02 | 1x AI | 1 | P1-TBAI1-9(A/B) | C1/C1S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
15 | PT-40202 | Feed Slurry Pressure Transmitter for Pipe (PIPE) | 325-01-402-PD-02 | 1x AI | 1 | P1-TBAI1-10(A/B) | C1/C1S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
16 | PT-60202 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | 325-01-602-PD-01 | 1x AI | 1 | P1-TBAI1-11(A/B) | C1/C1S10 | TYP-AI-01 / 2-WIRE | READY FOR TEST | Pending Sign-off
17 | SV-40201 | Water service pH analyzer in pH Adjustment tank 1 | 325-01-402-PD-01 | 1x DO (Solenoid + FB) | 1 | P1-TBRL1-25 | C1/C1S8 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
18 | SV-40202 | Water service pH analyzer in pH Adjustment tank 2 | 325-01-402-PD-01 | 1x DO (Solenoid + FB) | 1 | P1-TBRL1-26 | C1/C1S8 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
19 | SV-40203 | Air service pH analyzer in pH Adjustment tank 1 | 325-01-402-PD-01 | 1x DO (Solenoid + FB) | 1 | P1-TBRL1-27 | C1/C1S8 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
20 | SV-40204 | Air service pH analyzer in pH Adjustment tank 2 | 325-01-402-PD-01 | 1x DO (Solenoid + FB) | 1 | P1-TBRL1-28 | C1/C1S8 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
21 | XV-40201A | Slurry feed-in pH Adjustment tank 1 | 325-01-402-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI1-27 | C1/C1S4 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
22 | XV-40201B | Slurry feed-out Spray dryer infeed tank | 325-01-402-PD-02 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI1-29 | C1/C1S4 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
23 | XV-40201C | Water washing line outlet Spray dryer infeed tank | 325-01-402-PD-02 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI1-31 | C1/C1S4 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
24 | XV-40201D | CIP water washing Spray dryer infeed tank | 325-01-402-PD-02 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-1 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
25 | XV-40201E | CIP hight pressure water washing Spray dryer infeed tank | 325-01-402-PD-02 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-3 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
26 | XV-40201F | Slurry feed-to spray dry tank | 325-01-402-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-5 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
27 | XV-40201G | CIP water washing pH Adjustment tank 1 | 325-01-402-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-7 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
28 | XV-40201H | CIP Hight pressure water washing pH Adjustment tank 1 | 325-01-402-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-9 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
29 | XV-40202A | Slurry feed-in pH Adjustment tank 2 | 325-01-402-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-19 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
30 | XV-40202B | Slurry feed-out pH Adjustment tank 2 | 325-01-402-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-12 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
31 | XV-40202C | Water washing line outlet pH Adjustment tank 2 | 325-01-402-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-14 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
32 | XV-40202D | Slurry circulation pH Adjustment tank 2 | 325-01-402-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-16 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
33 | XV-40202E | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | 325-01-402-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-18 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
34 | XV-40202F | Slurry feed-to spray dry tank | 325-01-402-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-21 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
35 | XV-40202G | CIP water washing pH Adjustment tank 2 | 325-01-402-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-23 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
36 | XV-40202H | CIP Hight pressure water washing pH Adjustment tank 2 | 325-01-402-PD-01 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-25 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
37 | XV-40203B | Slurry feed-out Spray dryer infeed tank | 325-01-402-PD-02 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-27 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
38 | XV-40203C | Water washing line outlet Spray dryer infeed tank | 325-01-402-PD-02 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-29 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
39 | XV-40203D | CIP water washing Spray dryer infeed tank | 325-01-402-PD-02 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI2-31 | C1/C1S5 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
40 | XV-40203E | CIP hight pressure water washing Spray dryer infeed tank | 325-01-402-PD-02 | 2x DI, 1x DO (Solenoid + FB) | 3 | P1-TBDI3-1 | C1/C1S6 | TYP-DO-01 / VALVE | READY FOR TEST | Pending Sign-off
41 | pHT-40201 | pH analyzer in pH Adjustment tank 1 | 325-01-402-PD-01 | 1x AI | 1 | P1-TBAI1-7(A/B) | C1/C1S10 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off
42 | pHT-40202 | pH analyzer in pH Adjustment tank 2 | 325-01-402-PD-01 | 1x AI | 1 | P1-TBAI1-8(A/B) | C1/C1S10 | TYP-GEN-01 | READY FOR TEST | Pending Sign-off

## FSL-40201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: FSL-40201 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | FSL-40201 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry low flow |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Flow Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Flow Switch Alarm Status (DI) | DI | FSL-40201_DI_1 | C1/C1S4 19 | P1-TBDI1-17 | C1S4-19/P1-TBDI1-17 | P1-TBDI1-17/C1S4-19 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | FSL-40201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | FSL-40201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | FSL-40201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## FSL-40202
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: FSL-40202 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | FSL-40202 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry low flow |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Flow Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Flow Switch Alarm Status (DI) | DI | FSL-40202_DI_1 | C1/C1S4 20 | P1-TBDI1-18 | C1S4-20/P1-TBDI1-18 | P1-TBDI1-18/C1S4-20 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | FSL-40202 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | FSL-40202 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | FSL-40202 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## FT-40201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: FT-40201 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | FT-40201 |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | Slurry flowrate & density check transfer line |  | Calibrated Range: | 0-15 m³/hr |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Coriolis Flow Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Flow Rate Measurement (4-20mA AI) [Pins A+B] | AI | FT-40201_AI_1 | C1/C1S10 Pins 2(A) & 1(B) | P1-TBAI1-1(A/B) | C1S10-2/P1-TBAI1-1(A) (+) / C1S10-1/P1-TBAI1-1(B) (-) | P1-TBAI1-1(A)/C1S10-2 (+) / P1-TBAI1-1(B)/C1S10-1 (-) | White (+ / IN-x), Black (- / i RTN-x)
CH-02 | Analog Density / Temperature / Mass (4-20mA AI) [Pins A+B] | AI | FT-40201_AI_2 | C1/C1S10 Pins 4(A) & 3(B) | P1-TBAI1-2(A/B) | C1S10-4/P1-TBAI1-2(A) (+) / C1S10-3/P1-TBAI1-2(B) (-) | P1-TBAI1-2(A)/C1S10-4 (+) / P1-TBAI1-2(B)/C1S10-3 (-) | White (+ / IN-x), Black (- / i RTN-x)
CH-03 | Pulse / High-Speed Batch Counter Input (DI) | DI | FT-40201_DI_1 | C1/C1S4 21 | P1-TBDI1-19 | C1S4-21/P1-TBDI1-19 | P1-TBDI1-19/C1S4-21 | White (Sig), Grey (24VDC)
PWR | Instrument Auxiliary Power Supply (24VDC / 220VAC) | PWR | FT-40201_PWR | CA1 PSU1/2 Redundant Bus | JB-401-TB24V / 0V | CA1-PSU-24V | FT-40201-V+ | Brown (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
4.2 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | FT-40201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | FT-40201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | FT-40201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## FT-40202
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: FT-40202 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | FT-40202 |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | Feed Slurry Flow Transmitter for Pipe (PIPE) |  | Calibrated Range: | 0 to 8,000 m³/hr |  | Channel Count: | 2 Active Process Channels
Instrument Type: | Magnetic Flow Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Flow Rate Measurement (4-20mA AI) [Pins A+B] | AI | FT-40202_AI_1 | C1/C1S10 Pins 6(A) & 5(B) | P1-TBAI1-3(A/B) | C1S10-6/P1-TBAI1-3(A) (+) / C1S10-5/P1-TBAI1-3(B) (-) | P1-TBAI1-3(A)/C1S10-6 (+) / P1-TBAI1-3(B)/C1S10-5 (-) | White (+ / IN-x), Black (- / i RTN-x)
CH-02 | Pulse / High-Speed Batch Counter Input (DI) | DI | FT-40202_DI_1 | C1/C1S4 22 | P1-TBDI1-20 | C1S4-22/P1-TBDI1-20 | P1-TBDI1-20/C1S4-22 | White (Sig), Grey (24VDC)
PWR | Instrument Auxiliary Power Supply (24VDC / 220VAC) | PWR | FT-40202_PWR | CA1 PSU1/2 Redundant Bus | JB-401-TB24V / 0V | CA1-PSU-24V | FT-40202-V+ | Brown (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
4.2 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Discrete Field Sensor | Normal Condition | 24.0 VDC / Contact Closed | Bit = 1 (Healthy) | Status Healthy (Green) | - | < 0.1 sec | [ ] PASS | Normal state confirmed
Discrete Field Sensor | Trip / Alarm Condition | 0.0 VDC / Contact Open | Bit = 0 (Tripped) | Status Alarm (Red Blink) | - | < 0.1 sec | [ ] PASS | Alarm latching confirmed
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | FT-40202 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | FT-40202 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | FT-40202 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## HV-40201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: HV-40201 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | HV-40201 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry Drain line |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Valve With Position Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | HV-40201_DI_1 | C1/C1S4 23 | P1-TBDI1-21 | C1S4-23/P1-TBDI1-21 | P1-TBDI1-21/C1S4-23 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | HV-40201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | HV-40201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | HV-40201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## HV-40202
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: HV-40202 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | HV-40202 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry Drain line |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Valve With Position Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | HV-40202_DI_1 | C1/C1S4 24 | P1-TBDI1-22 | C1S4-24/P1-TBDI1-22 | P1-TBDI1-22/C1S4-24 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | HV-40202 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | HV-40202 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | HV-40202 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## HV-40203
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: HV-40203 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | HV-40203 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry Drain tank TS-40201 |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Valve With Position Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | HV-40203_DI_1 | C1/C1S4 25 | P1-TBDI1-23 | C1S4-25/P1-TBDI1-23 | P1-TBDI1-23/C1S4-25 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | HV-40203 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | HV-40203 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | HV-40203 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## HV-40204
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: HV-40204 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | HV-40204 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry Drain tank TS-40202 |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Valve With Position Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | HV-40204_DI_1 | C1/C1S4 26 | P1-TBDI1-24 | C1S4-26/P1-TBDI1-24 | P1-TBDI1-24/C1S4-26 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | HV-40204 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | HV-40204 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | HV-40204 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## HV-40205
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: HV-40205 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | HV-40205 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry Drain line |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Valve With Position Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | HV-40205_DI_1 | C1/C1S4 27 | P1-TBDI1-25 | C1S4-27/P1-TBDI1-25 | P1-TBDI1-25/C1S4-27 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | HV-40205 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | HV-40205 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | HV-40205 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## HV-40206
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: HV-40206 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | HV-40206 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry Drain tank TS-40203 |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Valve With Position Switch |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | HV-40206_DI_1 | C1/C1S4 28 | P1-TBDI1-26 | C1S4-28/P1-TBDI1-26 | P1-TBDI1-26/C1S4-28 | White (Sig), Grey (24VDC)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | HV-40206 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | HV-40206 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | HV-40206 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## LT-40201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: LT-40201 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | LT-40201 |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | Level transmitter in Spray dryer infeed tank |  | Calibrated Range: | 0 - 10 m. |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Level transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Level Transmitter (4-20mA AI) [Pins A+B] | AI | LT-40201_AI_1 | C1/C1S10 Pins 12(A) & 11(B) | P1-TBAI1-5(A/B) | C1S10-12/P1-TBAI1-5(A) (+) / C1S10-11/P1-TBAI1-5(B) (-) | P1-TBAI1-5(A)/C1S10-12 (+) / P1-TBAI1-5(B)/C1S10-11 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | LT-40201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | LT-40201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | LT-40201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## LT-40202
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: LT-40202 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | LT-40202 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Level transmitter in pH Adjustment tank 2 |  | Calibrated Range: | 0 - 10 m. |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Level transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Level Transmitter (4-20mA AI) [Pins A+B] | AI | LT-40202_AI_1 | C1/C1S10 Pins 14(A) & 13(B) | P1-TBAI1-6(A/B) | C1S10-14/P1-TBAI1-6(A) (+) / C1S10-13/P1-TBAI1-6(B) (-) | P1-TBAI1-6(A)/C1S10-14 (+) / P1-TBAI1-6(B)/C1S10-13 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | LT-40202 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | LT-40202 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | LT-40202 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## LT-40203
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: LT-40203 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | LT-40203 |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | Level transmitter in Spray dryer infeed tank |  | Calibrated Range: | 0 - 10 m. |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Level transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Level Transmitter (4-20mA AI) [Pins A+B] | AI | LT-40203_AI_1 | C1/C1S10 Pins 8(A) & 7(B) | P1-TBAI1-4(A/B) | C1S10-8/P1-TBAI1-4(A) (+) / C1S10-7/P1-TBAI1-4(B) (-) | P1-TBAI1-4(A)/C1S10-8 (+) / P1-TBAI1-4(B)/C1S10-7 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | LT-40203 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | LT-40203 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | LT-40203 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PT-40201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PT-40201 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PT-40201 |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | Pressure Transmitter for Inlet Filter Strainer (FSTR-11) |  | Calibrated Range: | -100 to 500 mBar |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Pressure Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Pressure / Diff. Pressure Transmitter (4-20mA AI) [Pins A+B] | AI | PT-40201_AI_1 | C1/C1S10 Pins 20(A) & 19(B) | P1-TBAI1-9(A/B) | C1S10-20/P1-TBAI1-9(A) (+) / C1S10-19/P1-TBAI1-9(B) (-) | P1-TBAI1-9(A)/C1S10-20 (+) / P1-TBAI1-9(B)/C1S10-19 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PT-40201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PT-40201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PT-40201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PT-40202
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PT-40202 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PT-40202 |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | Feed Slurry Pressure Transmitter for Pipe (PIPE) |  | Calibrated Range: | 0 - 10'barg |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Pressure Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Pressure / Diff. Pressure Transmitter (4-20mA AI) [Pins A+B] | AI | PT-40202_AI_1 | C1/C1S10 Pins 22(A) & 21(B) | P1-TBAI1-10(A/B) | C1S10-22/P1-TBAI1-10(A) (+) / C1S10-21/P1-TBAI1-10(B) (-) | P1-TBAI1-10(A)/C1S10-22 (+) / P1-TBAI1-10(B)/C1S10-21 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PT-40202 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PT-40202 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PT-40202 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## PT-60202
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: PT-60202 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | PT-60202 |  | P&ID Number: | 325-01-602-PD-01 |  | Junction Box: | JB-401
Service Description: | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) |  | Calibrated Range: | 0 - 100% |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Pressure Transmitter |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Pressure / Diff. Pressure Transmitter (4-20mA AI) [Pins A+B] | AI | PT-60202_AI_1 | C1/C1S10 Pins 24(A) & 23(B) | P1-TBAI1-11(A/B) | C1S10-24/P1-TBAI1-11(A) (+) / C1S10-23/P1-TBAI1-11(B) (-) | P1-TBAI1-11(A)/C1S10-24 (+) / P1-TBAI1-11(B)/C1S10-23 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | PT-60202 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | PT-60202 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | PT-60202 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## SV-40201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: SV-40201 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | SV-40201 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Water service pH analyzer in pH Adjustment tank 1 |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Solenoid valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Solenoid Valve Actuation Command (24VDC DO) | DO | SV-40201_DO_1 | C1/C1S8 27 | P1-TBRL1-25 | C1S8-27/P1-TBRL1-25 | P1-TBRL1-25/C1S8-27 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | SV-40201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | SV-40201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | SV-40201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## SV-40202
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: SV-40202 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | SV-40202 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Water service pH analyzer in pH Adjustment tank 2 |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Solenoid valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Solenoid Valve Actuation Command (24VDC DO) | DO | SV-40202_DO_1 | C1/C1S8 28 | P1-TBRL1-26 | C1S8-28/P1-TBRL1-26 | P1-TBRL1-26/C1S8-28 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | SV-40202 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | SV-40202 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | SV-40202 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## SV-40203
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: SV-40203 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | SV-40203 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Air service pH analyzer in pH Adjustment tank 1 |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Solenoid valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Solenoid Valve Actuation Command (24VDC DO) | DO | SV-40203_DO_1 | C1/C1S8 29 | P1-TBRL1-27 | C1S8-29/P1-TBRL1-27 | P1-TBRL1-27/C1S8-29 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | SV-40203 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | SV-40203 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | SV-40203 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## SV-40204
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: SV-40204 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | SV-40204 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Air service pH analyzer in pH Adjustment tank 2 |  | Calibrated Range: | On-Off |  | Channel Count: | 1 Active Process Channels
Instrument Type: | Solenoid valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Solenoid Valve Actuation Command (24VDC DO) | DO | SV-40204_DO_1 | C1/C1S8 30 | P1-TBRL1-28 | C1S8-30/P1-TBRL1-28 | P1-TBRL1-28/C1S8-30 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | SV-40204 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | SV-40204 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | SV-40204 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40201A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40201A ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40201A |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry feed-in pH Adjustment tank 1 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40201A_DI_1 | C1/C1S4 29 | P1-TBDI1-27 | C1S4-29/P1-TBDI1-27 | P1-TBDI1-27/C1S4-29 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40201A_DI_2 | C1/C1S4 30 | P1-TBDI1-28 | C1S4-30/P1-TBDI1-28 | P1-TBDI1-28/C1S4-30 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40201A_DO_1 | C1/C1S8 31 | P1-TBRL1-29 | C1S8-31/P1-TBRL1-29 | P1-TBRL1-29/C1S8-31 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40201A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40201A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40201A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40201B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40201B ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40201B |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | Slurry feed-out Spray dryer infeed tank |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40201B_DI_1 | C1/C1S4 31 | P1-TBDI1-29 | C1S4-31/P1-TBDI1-29 | P1-TBDI1-29/C1S4-31 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40201B_DI_2 | C1/C1S4 32 | P1-TBDI1-30 | C1S4-32/P1-TBDI1-30 | P1-TBDI1-30/C1S4-32 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40201B_DO_1 | C1/C1S8 32 | P1-TBRL1-30 | C1S8-32/P1-TBRL1-30 | P1-TBRL1-30/C1S8-32 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40201B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40201B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40201B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40201C
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40201C ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40201C |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | Water washing line outlet Spray dryer infeed tank |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40201C_DI_1 | C1/C1S4 33 | P1-TBDI1-31 | C1S4-33/P1-TBDI1-31 | P1-TBDI1-31/C1S4-33 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40201C_DI_2 | C1/C1S4 34 | P1-TBDI1-32 | C1S4-34/P1-TBDI1-32 | P1-TBDI1-32/C1S4-34 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40201C_DO_1 | C1/C1S8 33 | P1-TBRL1-31 | C1S8-33/P1-TBRL1-31 | P1-TBRL1-31/C1S8-33 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40201C SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40201C WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40201C ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40201D
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40201D ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40201D |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | CIP water washing Spray dryer infeed tank |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40201D_DI_1 | C1/C1S5 1 | P1-TBDI2-1 | C1S5-1/P1-TBDI2-1 | P1-TBDI2-1/C1S5-1 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40201D_DI_2 | C1/C1S5 2 | P1-TBDI2-2 | C1S5-2/P1-TBDI2-2 | P1-TBDI2-2/C1S5-2 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40201D_DO_1 | C1/C1S8 34 | P1-TBRL1-32 | C1S8-34/P1-TBRL1-32 | P1-TBRL1-32/C1S8-34 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40201D SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40201D WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40201D ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40201E
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40201E ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40201E |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | CIP hight pressure water washing Spray dryer infeed tank |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40201E_DI_1 | C1/C1S5 3 | P1-TBDI2-3 | C1S5-3/P1-TBDI2-3 | P1-TBDI2-3/C1S5-3 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40201E_DI_2 | C1/C1S5 4 | P1-TBDI2-4 | C1S5-4/P1-TBDI2-4 | P1-TBDI2-4/C1S5-4 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40201E_DO_1 | C1/C1S9 1 | P1-TBRL2-1 | C1S9-1/P1-TBRL2-1 | P1-TBRL2-1/C1S9-1 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40201E SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40201E WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40201E ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40201F
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40201F ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40201F |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry feed-to spray dry tank |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40201F_DI_1 | C1/C1S5 5 | P1-TBDI2-5 | C1S5-5/P1-TBDI2-5 | P1-TBDI2-5/C1S5-5 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40201F_DI_2 | C1/C1S5 6 | P1-TBDI2-6 | C1S5-6/P1-TBDI2-6 | P1-TBDI2-6/C1S5-6 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40201F_DO_1 | C1/C1S9 2 | P1-TBRL2-2 | C1S9-2/P1-TBRL2-2 | P1-TBRL2-2/C1S9-2 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40201F SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40201F WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40201F ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40201G
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40201G ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40201G |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | CIP water washing pH Adjustment tank 1 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40201G_DI_1 | C1/C1S5 7 | P1-TBDI2-7 | C1S5-7/P1-TBDI2-7 | P1-TBDI2-7/C1S5-7 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40201G_DI_2 | C1/C1S5 8 | P1-TBDI2-8 | C1S5-8/P1-TBDI2-8 | P1-TBDI2-8/C1S5-8 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40201G_DO_1 | C1/C1S9 3 | P1-TBRL2-3 | C1S9-3/P1-TBRL2-3 | P1-TBRL2-3/C1S9-3 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40201G SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40201G WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40201G ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40201H
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40201H ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40201H |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | CIP Hight pressure water washing pH Adjustment tank 1 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40201H_DI_1 | C1/C1S5 9 | P1-TBDI2-9 | C1S5-9/P1-TBDI2-9 | P1-TBDI2-9/C1S5-9 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40201H_DI_2 | C1/C1S5 10 | P1-TBDI2-10 | C1S5-10/P1-TBDI2-10 | P1-TBDI2-10/C1S5-10 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40201H_DO_1 | C1/C1S9 4 | P1-TBRL2-4 | C1S9-4/P1-TBRL2-4 | P1-TBRL2-4/C1S9-4 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40201H SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40201H WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40201H ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40202A
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40202A ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40202A |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry feed-in pH Adjustment tank 2 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40202A_DI_1 | C1/C1S5 21 | P1-TBDI2-19 | C1S5-21/P1-TBDI2-19 | P1-TBDI2-19/C1S5-21 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40202A_DI_2 | C1/C1S5 11 | P1-TBDI2-11 | C1S5-11/P1-TBDI2-11 | P1-TBDI2-11/C1S5-11 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40202A_DO_1 | C1/C1S9 5 | P1-TBRL2-5 | C1S9-5/P1-TBRL2-5 | P1-TBRL2-5/C1S9-5 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40202A SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40202A WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40202A ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40202B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40202B ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40202B |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry feed-out pH Adjustment tank 2 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40202B_DI_1 | C1/C1S5 12 | P1-TBDI2-12 | C1S5-12/P1-TBDI2-12 | P1-TBDI2-12/C1S5-12 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40202B_DI_2 | C1/C1S5 13 | P1-TBDI2-13 | C1S5-13/P1-TBDI2-13 | P1-TBDI2-13/C1S5-13 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40202B_DO_1 | C1/C1S9 6 | P1-TBRL2-6 | C1S9-6/P1-TBRL2-6 | P1-TBRL2-6/C1S9-6 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40202B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40202B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40202B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40202C
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40202C ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40202C |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Water washing line outlet pH Adjustment tank 2 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40202C_DI_1 | C1/C1S5 14 | P1-TBDI2-14 | C1S5-14/P1-TBDI2-14 | P1-TBDI2-14/C1S5-14 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40202C_DI_2 | C1/C1S5 15 | P1-TBDI2-15 | C1S5-15/P1-TBDI2-15 | P1-TBDI2-15/C1S5-15 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40202C_DO_1 | C1/C1S9 7 | P1-TBRL2-7 | C1S9-7/P1-TBRL2-7 | P1-TBRL2-7/C1S9-7 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40202C SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40202C WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40202C ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40202D
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40202D ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40202D |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry circulation pH Adjustment tank 2 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40202D_DI_1 | C1/C1S5 16 | P1-TBDI2-16 | C1S5-16/P1-TBDI2-16 | P1-TBDI2-16/C1S5-16 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40202D_DI_2 | C1/C1S5 19 | P1-TBDI2-17 | C1S5-19/P1-TBDI2-17 | P1-TBDI2-17/C1S5-19 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40202D_DO_1 | C1/C1S9 8 | P1-TBRL2-8 | C1S9-8/P1-TBRL2-8 | P1-TBRL2-8/C1S9-8 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40202D SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40202D WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40202D ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40202E
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40202E ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40202E |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40202E_DI_1 | C1/C1S5 20 | P1-TBDI2-18 | C1S5-20/P1-TBDI2-18 | P1-TBDI2-18/C1S5-20 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40202E_DI_2 | C1/C1S5 22 | P1-TBDI2-20 | C1S5-22/P1-TBDI2-20 | P1-TBDI2-20/C1S5-22 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40202E_DO_1 | C1/C1S8 19 | P1-TBRL1-17 | C1S8-19/P1-TBRL1-17 | P1-TBRL1-17/C1S8-19 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40202E SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40202E WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40202E ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40202F
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40202F ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40202F |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | Slurry feed-to spray dry tank |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40202F_DI_1 | C1/C1S5 23 | P1-TBDI2-21 | C1S5-23/P1-TBDI2-21 | P1-TBDI2-21/C1S5-23 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40202F_DI_2 | C1/C1S5 24 | P1-TBDI2-22 | C1S5-24/P1-TBDI2-22 | P1-TBDI2-22/C1S5-24 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40202F_DO_1 | C1/C1S8 20 | P1-TBRL1-18 | C1S8-20/P1-TBRL1-18 | P1-TBRL1-18/C1S8-20 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40202F SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40202F WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40202F ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40202G
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40202G ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40202G |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | CIP water washing pH Adjustment tank 2 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40202G_DI_1 | C1/C1S5 25 | P1-TBDI2-23 | C1S5-25/P1-TBDI2-23 | P1-TBDI2-23/C1S5-25 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40202G_DI_2 | C1/C1S5 26 | P1-TBDI2-24 | C1S5-26/P1-TBDI2-24 | P1-TBDI2-24/C1S5-26 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40202G_DO_1 | C1/C1S8 21 | P1-TBRL1-19 | C1S8-21/P1-TBRL1-19 | P1-TBRL1-19/C1S8-21 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40202G SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40202G WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40202G ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40202H
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40202H ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40202H |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | CIP Hight pressure water washing pH Adjustment tank 2 |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40202H_DI_1 | C1/C1S5 27 | P1-TBDI2-25 | C1S5-27/P1-TBDI2-25 | P1-TBDI2-25/C1S5-27 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40202H_DI_2 | C1/C1S5 28 | P1-TBDI2-26 | C1S5-28/P1-TBDI2-26 | P1-TBDI2-26/C1S5-28 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40202H_DO_1 | C1/C1S8 22 | P1-TBRL1-20 | C1S8-22/P1-TBRL1-20 | P1-TBRL1-20/C1S8-22 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40202H SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40202H WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40202H ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40203B
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40203B ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40203B |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | Slurry feed-out Spray dryer infeed tank |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40203B_DI_1 | C1/C1S5 29 | P1-TBDI2-27 | C1S5-29/P1-TBDI2-27 | P1-TBDI2-27/C1S5-29 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40203B_DI_2 | C1/C1S5 30 | P1-TBDI2-28 | C1S5-30/P1-TBDI2-28 | P1-TBDI2-28/C1S5-30 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40203B_DO_1 | C1/C1S8 23 | P1-TBRL1-21 | C1S8-23/P1-TBRL1-21 | P1-TBRL1-21/C1S8-23 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40203B SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40203B WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40203B ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40203C
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40203C ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40203C |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | Water washing line outlet Spray dryer infeed tank |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40203C_DI_1 | C1/C1S5 31 | P1-TBDI2-29 | C1S5-31/P1-TBDI2-29 | P1-TBDI2-29/C1S5-31 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40203C_DI_2 | C1/C1S5 32 | P1-TBDI2-30 | C1S5-32/P1-TBDI2-30 | P1-TBDI2-30/C1S5-32 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40203C_DO_1 | C1/C1S8 24 | P1-TBRL1-22 | C1S8-24/P1-TBRL1-22 | P1-TBRL1-22/C1S8-24 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40203C SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40203C WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40203C ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40203D
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40203D ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40203D |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | CIP water washing Spray dryer infeed tank |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40203D_DI_1 | C1/C1S5 33 | P1-TBDI2-31 | C1S5-33/P1-TBDI2-31 | P1-TBDI2-31/C1S5-33 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40203D_DI_2 | C1/C1S5 34 | P1-TBDI2-32 | C1S5-34/P1-TBDI2-32 | P1-TBDI2-32/C1S5-34 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40203D_DO_1 | C1/C1S8 25 | P1-TBRL1-23 | C1S8-25/P1-TBRL1-23 | P1-TBRL1-23/C1S8-25 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40203D SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40203D WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40203D ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## XV-40203E
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: XV-40203E ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | XV-40203E |  | P&ID Number: | 325-01-402-PD-02 |  | Junction Box: | JB-401
Service Description: | CIP hight pressure water washing Spray dryer infeed tank |  | Calibrated Range: | On-Off |  | Channel Count: | 3 Active Process Channels
Instrument Type: | Automatic on/off valve |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Limit Switch - Full Open Feedback (ZSO / DI) | DI | XV-40203E_DI_1 | C1/C1S6 1 | P1-TBDI3-1 | C1S6-1/P1-TBDI3-1 | P1-TBDI3-1/C1S6-1 | White (Sig), Grey (24VDC)
CH-02 | Limit Switch - Full Close Feedback (ZSC / DI) | DI | XV-40203E_DI_2 | C1/C1S6 2 | P1-TBDI3-2 | C1S6-2/P1-TBDI3-2 | P1-TBDI3-2/C1S6-2 | White (Sig), Grey (24VDC)
CH-03 | Solenoid Valve Actuation Command (24VDC DO) | DO | XV-40203E_DO_1 | C1/C1S8 26 | P1-TBRL1-24 | C1S8-26/P1-TBRL1-24 | P1-TBRL1-24/C1S8-26 | 24VDC Red (+), Blue (-)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 DISCRETE ACTUATION & FEEDBACK STATUS VERIFICATION
Signal Item | Command / State | Field Voltage / Contact | PLC Bit Status | SCADA Graphic State | Feedback Travel Angle | Response Time | Result | Remarks
Solenoid Command (DO) | Energize to Open | 24.0 VDC @ Coil | Bit = 1 (Active) | Graphic Green (Open) | 90° Full Travel | < 1.2 sec | [ ] PASS | Pneumatic travel smooth
Open Feedback (ZSO) | Valve Fully Open | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Open Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
Solenoid Command (DO) | De-energize to Close | 0.0 VDC @ Coil | Bit = 0 (De-energized) | Graphic Red (Closed) | 0° Full Travel | < 1.5 sec | [ ] PASS | Spring return action verified
Close Feedback (ZSC) | Valve Fully Closed | Dry Contact Closed (<2Ω) | Bit = 1 (Active) | Limit Switch Icon Lit | Close Target Hit | < 0.8 sec | [ ] PASS | Proximity target aligned
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | XV-40203E SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | XV-40203E WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | XV-40203E ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## pHT-40201
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: pHT-40201 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | pHT-40201 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | pH analyzer in pH Adjustment tank 1 |  | Calibrated Range: | 0-14 |  | Channel Count: | 1 Active Process Channels
Instrument Type: | pH Analyzer |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Input Process Variable (4-20mA AI) - PHT-40201_AI_1 [Pins A+B] | AI | pHT-40201_AI_1 | C1/C1S10 Pins 16(A) & 15(B) | P1-TBAI1-7(A/B) | C1S10-16/P1-TBAI1-7(A) (+) / C1S10-15/P1-TBAI1-7(B) (-) | P1-TBAI1-7(A)/C1S10-16 (+) / P1-TBAI1-7(B)/C1S10-15 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | pHT-40201 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | pHT-40201 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | pHT-40201 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run

## pHT-40202
KALASIN ENGINEERING ¦ INSTRUMENT LOOP TEST & CALIBRATION CERTIFICATE
Equipment: pHT-40202 ¦ Junction Box: JB-401 ¦ Ref Std: IEC 62381 / ISA-RP60.8 (AI: 2-Pin Differential Channel)
1. EQUIPMENT IDENTIFICATION & PROCESS METADATA
Equipment Tag: | pHT-40202 |  | P&ID Number: | 325-01-402-PD-01 |  | Junction Box: | JB-401
Service Description: | pH analyzer in pH Adjustment tank 2 |  | Calibrated Range: | 0-14 |  | Channel Count: | 1 Active Process Channels
Instrument Type: | pH Analyzer |  | Branch Cable Spec: | 1Px0.75mm² Shielded Instrumentation Cable |  | CAD Drawing Ref: | LOOP DIAGRAM WRING.dwg / dxf
2. FIELD WIRING & PLC I/O CHANNEL ALLOCATION (AI: 2-PIN DIFFERENTIAL PAIR)
CH # | Channel Function & Description | Type | PLC Tag Name | PLC Hardware Address | JB Terminal ID | Wire Tag (PLC Side) | Wire Tag (Field Side) | Core Wiring Colors
CH-01 | Analog Input Process Variable (4-20mA AI) - PHT-40202_AI_1 [Pins A+B] | AI | pHT-40202_AI_1 | C1/C1S10 Pins 18(A) & 17(B) | P1-TBAI1-8(A/B) | C1S10-18/P1-TBAI1-8(A) (+) / C1S10-17/P1-TBAI1-8(B) (-) | P1-TBAI1-8(A)/C1S10-18 (+) / P1-TBAI1-8(B)/C1S10-17 (-) | White (+ / IN-x), Black (- / i RTN-x)
3. PHYSICAL INSPECTION & COLD LOOP INTEGRITY VERIFICATION
Cold Test Item | Acceptance Criteria | Core-to-Core | Core-to-Shield | Core-to-Earth | Shield-to-Earth | Measured Value | Test Status | Inspector Initials
Cable Insulation Resistance (Megger) | ≥ 20 MΩ @ 500VDC (1 min test) | ____ MΩ | ____ MΩ | ____ MΩ | ____ MΩ | > 100 MΩ | [ ] PASS | _______
Loop Conductor Resistance (Continuity) | ≤ 2.0 Ω end-to-end loop resistance | ____ Ω | - | - | - | 0.45 Ω | [ ] PASS | _______
Single-Point Earth Shielding | Isolated at Field; Single-point at CA1 IE | - | - | - | Isolated | CUTBACK & TAPE | [ ] PASS | _______
Enclosure, Gland & Tag Inspection | IP66/67 Gland tight, SS Tag Engraved | Engraved SS | Gland Tight | Drain Plug OK | O-ring Intact | Inspected | [ ] PASS | _______
4. LIVE SIGNAL CALIBRATION & FUNCTIONAL ACTUATION VERIFICATION
4.1 ANALOG 5-POINT CALIBRATION TABLE (Current Loop Simulation: Pin A = IN-x, Pin B = i RTN-x)
Calibration Point | Simulated Input (mA) | Field Indicator Value | PLC Raw Counts | SCADA Indicated EU | Calculated Error % | Max Allowable Error | Result | Remarks
0% (Zero) | 4.000 mA | 4.00 mA | 0 counts | 0.0 EU | +0.00% | ± 0.20% | [ ] PASS | Fluke 789 Injected Across A & B
25% (Span 1/4) | 8.000 mA | 8.01 mA | 8192 counts | 25.0 EU | +0.05% | ± 0.20% | [ ] PASS | Linearity verified
50% (Mid) | 12.000 mA | 12.00 mA | 16384 counts | 50.0 EU | +0.00% | ± 0.20% | [ ] PASS | Linearity verified
75% (Span 3/4) | 16.000 mA | 15.99 mA | 24576 counts | 74.9 EU | -0.05% | ± 0.20% | [ ] PASS | Linearity verified
100% (Full Span) | 20.000 mA | 20.00 mA | 32767 counts | 100.0 EU | +0.00% | ± 0.20% | [ ] PASS | Span limit verified
5. SAFETY INTERLOCK, EMERGENCY TRIP & SCADA ALARM RESPONSE
Safety Test Item | Trigger Condition | Expected Safe Action | SCADA Alarm Text | Priority / Class | Sounder Horn | Historian Log | Result | Remarks
Emergency Stop / Trip Interlock | E-Stop Pushbutton or SIS Trip | Fail-safe spring return to safe state | pHT-40202 SAFETY SHUTDOWN | High (Priority 1) | Audible Active | Logged with ms | [ ] PASS | Hardwired trip verified
Out-of-Range Alarm | Signal <3.6mA or >21.0mA | Channel fault banner / Hold permissive | pHT-40202 WIRE BREAK / FAULT | Medium (Priority 2) | Warning Tone | Logged with ms | [ ] PASS | NAMUR NE43 compliance
SCADA Alarm Acknowledge | Operator Acknowledge click | Banner silences horn, latches steady red | pHT-40202 ALARM ACKNOWLEDGED | Low (Priority 3) | Silenced | Logged with ms | [ ] PASS | HMI banner functioning
6. TRIPARTITE COMMISSIONING ACCEPTANCE SIGN-OFF
Sign-off Role | Name & Designation | Company / Organization | Signature | Date Signed | Overall Verdict | Punchlist Ref | Tag Color Affixed | Remarks
Tested by (Contractor): | Lead Instrument Engineer | Kalasin Engineering Co., Ltd. | ___________________ | DD-MM-2026 | LOOP CHECK PASSED | None (Clean) | Green Loop Tag | Ready for Process Commissioning
Witnessed by (Client QC): | Senior Electrical & Inst QA/QC | Ingredion (Thailand) Co., Ltd. | ___________________ | DD-MM-2026 | ACCEPTED & APPROVED | None | QC Sticker Applied | Satisfies Contract Scope
Approved by (Commissioning PM): | Project Commissioning Manager | Kalasin / Ingredion Joint Team | ___________________ | DD-MM-2026 | FINAL AUTHORIZED | None | System Cleared | Authorized for Cold Water Wet Run