## Chassis_and_Slot_List
KALASIN ENGINEERING - xCIP AUTOMATION SYSTEM (Ref: x2608003)
MASTER CHASSIS & SLOT ALLOCATION SCHEDULE (CONTROLLOGIX 1756 & EXPANSION RACKS)
TOTAL CHASSIS RACKS |  | TOTAL I/O CAPACITY |  | ACTIVE FIELD I/O |  | SPARE ENGINEERING CAPACITY |  | CONTROLLER CPU |  | DLR NETWORK STANDARD
7 Chassis (C1-C7) |  | 1,210 Channels |  | 763 Points |  | 447 Points (36.9%) |  | 1756-L950TPSXT |  | EtherNet/IP Dual Ring
Chassis ID | Chassis Description & Location | Slot No. | Module Model | Module Description / Functional Role | I/O Type | Capacity (Pts) | Active Points | Spare Points | Spare % | Primary Field Destinations | Network Node / Protocol | Engineering Status
▶ C1 — MAIN CONTROLLER RACK (CHASSIS 1) ¦ Location: Control Cabinet CA1 (Main Control Room) ¦ Net: Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10)
C1 | Main Controller Rack (Chassis 1) | 0 | 1756-L950TPSXT | ControlLogix 5590 Redundant Process Controller | CPU | - | - | - | - | None (CPU/Comm/Spare) | Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) | OPERATIONAL
C1 | Main Controller Rack (Chassis 1) | 1 | 1756-EN4TR | Dual-Port Gigabit EtherNet/IP DLR Comm Adapter | COMM | - | - | - | - | None (CPU/Comm/Spare) | Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) | OPERATIONAL
C1 | Main Controller Rack (Chassis 1) | 2 | 1756-EN4TR | Dual-Port Gigabit EtherNet/IP DLR Comm Adapter | COMM | - | - | - | - | None (CPU/Comm/Spare) | Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) | OPERATIONAL
C1 | Main Controller Rack (Chassis 1) | 3 | 1756-EN4TR | Dual-Port Gigabit EtherNet/IP DLR Comm Adapter | COMM | 32 | 16 | 16 | 50.0% | CA1, JB-401 | Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) | OPERATIONAL
C1 | Main Controller Rack (Chassis 1) | 4 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 32 | 0 | 0.0% | JB-401 | Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) | ASSIGNED
C1 | Main Controller Rack (Chassis 1) | 5 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 12 | 20 | 62.5% | JB-401, JB-601 | Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) | ASSIGNED
C1 | Main Controller Rack (Chassis 1) | 6 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 23 | 9 | 28.1% | JB-601 | Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) | ASSIGNED
C1 | Main Controller Rack (Chassis 1) | 7 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 16 | 16 | 50.0% | CA1, JB-401 | Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) | ASSIGNED
C1 | Main Controller Rack (Chassis 1) | 8 | 1756-OB32 | 32-Channel 24VDC Sourcing Digital Output Module | DO | 32 | 20 | 12 | 37.5% | JB-401, JB-601 | Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) | ASSIGNED
C1 | Main Controller Rack (Chassis 1) | 9 | 1756-OB32 | 32-Channel 24VDC Sourcing Digital Output Module | DO | 32 | 11 | 5 | 15.6% | JB-401 | Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) | ASSIGNED
C1 | Main Controller Rack (Chassis 1) | 10 | 1756-IF16 | 16-Channel High-Speed Isolated Analog Input Module | AI | 16 | 8 | 8 | 50.0% | JB-601 | Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) | ASSIGNED
C1 | Main Controller Rack (Chassis 1) | 11 | 1756-IF16 | 16-Channel High-Speed Isolated Analog Input Module | AI | 16 | 0 | 16 | 100.0% | Spare Channel Bank | Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) | RESERVED
C1 | Main Controller Rack (Chassis 1) | 12 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) | EMPTY SLOT
▶ C2 — I/O EXPANSION RACK 1 (CHASSIS 2) ¦ Location: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11)
C2 | I/O Expansion Rack 1 (Chassis 2) | 0 | 1756-EN4TR | Dual-Port Gigabit EtherNet/IP DLR Comm Adapter | COMM | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 2 (192.168.1.11) | OPERATIONAL
C2 | I/O Expansion Rack 1 (Chassis 2) | 1 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 24 | 8 | 25.0% | JB-402 | EN4TR DLR Ring Node 2 (192.168.1.11) | ASSIGNED
C2 | I/O Expansion Rack 1 (Chassis 2) | 2 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 23 | 9 | 28.1% | JB-602 | EN4TR DLR Ring Node 2 (192.168.1.11) | ASSIGNED
C2 | I/O Expansion Rack 1 (Chassis 2) | 3 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 29 | 0 | 0.0% | JB-607 | EN4TR DLR Ring Node 2 (192.168.1.11) | ASSIGNED
C2 | I/O Expansion Rack 1 (Chassis 2) | 4 | 1756-OB32 | 32-Channel 24VDC Sourcing Digital Output Module | DO | 32 | 32 | 0 | 0.0% | JB-607 | EN4TR DLR Ring Node 2 (192.168.1.11) | ASSIGNED
C2 | I/O Expansion Rack 1 (Chassis 2) | 5 | 1756-OB32 | 32-Channel 24VDC Sourcing Digital Output Module | DO | 32 | 20 | 12 | 37.5% | JB-607 | EN4TR DLR Ring Node 2 (192.168.1.11) | ASSIGNED
C2 | I/O Expansion Rack 1 (Chassis 2) | 6 | 1756-OB32 | 32-Channel 24VDC Sourcing Digital Output Module | DO | 32 | 12 | 20 | 62.5% | JB-402, JB-602 | EN4TR DLR Ring Node 2 (192.168.1.11) | ASSIGNED
C2 | I/O Expansion Rack 1 (Chassis 2) | 7 | 1756-IF16 | 16-Channel High-Speed Isolated Analog Input Module | AI | 32 | 31 | 1 | 3.1% | JB-607 | EN4TR DLR Ring Node 2 (192.168.1.11) | ASSIGNED
C2 | I/O Expansion Rack 1 (Chassis 2) | 8 | 1756-IF16 | 16-Channel High-Speed Isolated Analog Input Module | AI | 32 | 9 | 23 | 71.9% | JB-607 | EN4TR DLR Ring Node 2 (192.168.1.11) | ASSIGNED
C2 | I/O Expansion Rack 1 (Chassis 2) | 9 | 1756-IF16 | 16-Channel High-Speed Isolated Analog Input Module | AI | 16 | 7 | 9 | 56.2% | JB-402 | EN4TR DLR Ring Node 2 (192.168.1.11) | ASSIGNED
C2 | I/O Expansion Rack 1 (Chassis 2) | 10 | 1756-IF16 | 16-Channel High-Speed Isolated Analog Input Module | AI | 16 | 16 | 0 | 0.0% | JB-602 | EN4TR DLR Ring Node 2 (192.168.1.11) | ASSIGNED
C2 | I/O Expansion Rack 1 (Chassis 2) | 11 | 1756-IF16 | 16-Channel High-Speed Isolated Analog Input Module | AI | 16 | 13 | 3 | 18.8% | JB-602 | EN4TR DLR Ring Node 2 (192.168.1.11) | ASSIGNED
C2 | I/O Expansion Rack 1 (Chassis 2) | 12 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | 16 | 16 | 0 | 0.0% | JB-607 | EN4TR DLR Ring Node 2 (192.168.1.11) | EMPTY SLOT
▶ C3 — I/O EXPANSION RACK 2 (CHASSIS 3) ¦ Location: Control Cabinet CA1 (Bay 3) ¦ Net: EN4TR DLR Ring Node 3 (192.168.1.12)
C3 | I/O Expansion Rack 2 (Chassis 3) | 0 | 1756-EN4TR | Dual-Port Gigabit EtherNet/IP DLR Comm Adapter | COMM | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 3 (192.168.1.12) | OPERATIONAL
C3 | I/O Expansion Rack 2 (Chassis 3) | 1 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 22 | 5 | 15.6% | IS-JB-603, JB-618 | EN4TR DLR Ring Node 3 (192.168.1.12) | ASSIGNED
C3 | I/O Expansion Rack 2 (Chassis 3) | 2 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 37 | 18 | 19 | 51.4% | IS-JB-618, JB-618 | EN4TR DLR Ring Node 3 (192.168.1.12) | ASSIGNED
C3 | I/O Expansion Rack 2 (Chassis 3) | 3 | 1756-OB32 | 32-Channel 24VDC Sourcing Digital Output Module | DO | 32 | 9 | 23 | 71.9% | JB-618 | EN4TR DLR Ring Node 3 (192.168.1.12) | ASSIGNED
C3 | I/O Expansion Rack 2 (Chassis 3) | 4 | 1756-IF16 | 16-Channel High-Speed Isolated Analog Input Module | AI | 16 | 7 | 9 | 56.2% | IS-JB-603 | EN4TR DLR Ring Node 3 (192.168.1.12) | ASSIGNED
C3 | I/O Expansion Rack 2 (Chassis 3) | 5 | 1756-IF16 | 16-Channel High-Speed Isolated Analog Input Module | AI | 16 | 13 | 3 | 18.8% | IS-JB-618, JB-618 | EN4TR DLR Ring Node 3 (192.168.1.12) | ASSIGNED
C3 | I/O Expansion Rack 2 (Chassis 3) | 6 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 3 (192.168.1.12) | EMPTY SLOT
C3 | I/O Expansion Rack 2 (Chassis 3) | 7 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 3 (192.168.1.12) | EMPTY SLOT
C3 | I/O Expansion Rack 2 (Chassis 3) | 8 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 3 (192.168.1.12) | EMPTY SLOT
C3 | I/O Expansion Rack 2 (Chassis 3) | 9 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 3 (192.168.1.12) | EMPTY SLOT
C3 | I/O Expansion Rack 2 (Chassis 3) | 10 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 3 (192.168.1.12) | EMPTY SLOT
C3 | I/O Expansion Rack 2 (Chassis 3) | 11 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 3 (192.168.1.12) | EMPTY SLOT
C3 | I/O Expansion Rack 2 (Chassis 3) | 12 | 1756-OF8 | 8-Channel Isolated Analog Current/Voltage Output Module | AO | 8 | 0 | 8 | 100.0% | Spare Channel Bank | EN4TR DLR Ring Node 3 (192.168.1.12) | RESERVED
▶ C4 — I/O EXPANSION RACK 3 (CHASSIS 4) ¦ Location: Control Cabinet CA1 (Bay 4) ¦ Net: EN4TR DLR Ring Node 4 (192.168.1.13)
C4 | I/O Expansion Rack 3 (Chassis 4) | 0 | 1756-EN4TR | Dual-Port Gigabit EtherNet/IP DLR Comm Adapter | COMM | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 4 (192.168.1.13) | OPERATIONAL
C4 | I/O Expansion Rack 3 (Chassis 4) | 1 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 11 | 21 | 65.6% | IS-JB-608, JB-606 | EN4TR DLR Ring Node 4 (192.168.1.13) | ASSIGNED
C4 | I/O Expansion Rack 3 (Chassis 4) | 2 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 17 | 15 | 46.9% | JB-612 | EN4TR DLR Ring Node 4 (192.168.1.13) | ASSIGNED
C4 | I/O Expansion Rack 3 (Chassis 4) | 3 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 15 | 16 | 50.0% | IS-JB-612 | EN4TR DLR Ring Node 4 (192.168.1.13) | ASSIGNED
C4 | I/O Expansion Rack 3 (Chassis 4) | 4 | 1756-OB32 | 32-Channel 24VDC Sourcing Digital Output Module | DO | 32 | 17 | 15 | 46.9% | IS-JB-608, JB-606, JB-612 | EN4TR DLR Ring Node 4 (192.168.1.13) | ASSIGNED
C4 | I/O Expansion Rack 3 (Chassis 4) | 5 | 1756-IF16 | 16-Channel High-Speed Isolated Analog Input Module | AI | 26 | 7 | 19 | 73.1% | IS-JB-608, IS-JB-612, JB-606, JB-608, JB-612 | EN4TR DLR Ring Node 4 (192.168.1.13) | ASSIGNED
C4 | I/O Expansion Rack 3 (Chassis 4) | 6 | 1756-IF16 | 16-Channel High-Speed Isolated Analog Input Module | AI | 16 | 8 | 0 | 0.0% | IS-JB-608, IS-JB-612 | EN4TR DLR Ring Node 4 (192.168.1.13) | ASSIGNED
C4 | I/O Expansion Rack 3 (Chassis 4) | 7 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 4 (192.168.1.13) | EMPTY SLOT
C4 | I/O Expansion Rack 3 (Chassis 4) | 8 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 4 (192.168.1.13) | EMPTY SLOT
C4 | I/O Expansion Rack 3 (Chassis 4) | 9 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 4 (192.168.1.13) | EMPTY SLOT
C4 | I/O Expansion Rack 3 (Chassis 4) | 10 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 4 (192.168.1.13) | EMPTY SLOT
C4 | I/O Expansion Rack 3 (Chassis 4) | 11 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 4 (192.168.1.13) | EMPTY SLOT
C4 | I/O Expansion Rack 3 (Chassis 4) | 12 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR DLR Ring Node 4 (192.168.1.13) | EMPTY SLOT
▶ C5 — REMOTE I/O SKID RIO-200 (CHASSIS 5) ¦ Location: Remote I/O Enclosure RIO-200 (Process Floor 1F) ¦ Net: EN4TR Fiber DLR Ring Node 5 (192.168.1.14)
C5 | Remote I/O Skid RIO-200 (Chassis 5) | 0 | 1756-EN4TR | Dual-Port Gigabit EtherNet/IP DLR Comm Adapter | COMM | - | - | - | - | None (CPU/Comm/Spare) | EN4TR Fiber DLR Ring Node 5 (192.168.1.14) | OPERATIONAL
C5 | Remote I/O Skid RIO-200 (Chassis 5) | 1 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 32 | 0 | 0.0% | RIO-200 | EN4TR Fiber DLR Ring Node 5 (192.168.1.14) | ASSIGNED
C5 | Remote I/O Skid RIO-200 (Chassis 5) | 2 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 8 | 24 | 75.0% | RIO-200 | EN4TR Fiber DLR Ring Node 5 (192.168.1.14) | ASSIGNED
C5 | Remote I/O Skid RIO-200 (Chassis 5) | 3 | 1756-OB32 | 32-Channel 24VDC Sourcing Digital Output Module | DO | 32 | 8 | 24 | 75.0% | RIO-200 | EN4TR Fiber DLR Ring Node 5 (192.168.1.14) | ASSIGNED
C5 | Remote I/O Skid RIO-200 (Chassis 5) | 4 | 1756-IF16 | 16-Channel High-Speed Isolated Analog Input Module | AI | 16 | 9 | 7 | 43.8% | RIO-200 | EN4TR Fiber DLR Ring Node 5 (192.168.1.14) | ASSIGNED
C5 | Remote I/O Skid RIO-200 (Chassis 5) | 5 | 1756-OB32 | 32-Channel 24VDC Sourcing Digital Output Module | DO | 32 | 0 | 32 | 100.0% | Spare Channel Bank | EN4TR Fiber DLR Ring Node 5 (192.168.1.14) | RESERVED
C5 | Remote I/O Skid RIO-200 (Chassis 5) | 6 | 1756-IB32 | 32-Channel 24VDC Sink/Source Digital Input Module | DI | 32 | 0 | 32 | 100.0% | Spare Channel Bank | EN4TR Fiber DLR Ring Node 5 (192.168.1.14) | RESERVED
C5 | Remote I/O Skid RIO-200 (Chassis 5) | 7 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR Fiber DLR Ring Node 5 (192.168.1.14) | EMPTY SLOT
C5 | Remote I/O Skid RIO-200 (Chassis 5) | 8 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR Fiber DLR Ring Node 5 (192.168.1.14) | EMPTY SLOT
C5 | Remote I/O Skid RIO-200 (Chassis 5) | 9 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR Fiber DLR Ring Node 5 (192.168.1.14) | EMPTY SLOT
C5 | Remote I/O Skid RIO-200 (Chassis 5) | 10 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR Fiber DLR Ring Node 5 (192.168.1.14) | EMPTY SLOT
C5 | Remote I/O Skid RIO-200 (Chassis 5) | 11 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR Fiber DLR Ring Node 5 (192.168.1.14) | EMPTY SLOT
C5 | Remote I/O Skid RIO-200 (Chassis 5) | 12 | 1756-N2 | Slot Filler / Future Expansion Space | EMPTY | - | - | - | - | None (CPU/Comm/Spare) | EN4TR Fiber DLR Ring Node 5 (192.168.1.14) | EMPTY SLOT
▶ C6 — MCC AUXILIARY I/O (CHASSIS 6) ¦ Location: Motor Control Center Room (MCC Panel) ¦ Net: MCC Hardwired Trunk Line
C6 | MCC Auxiliary I/O (Chassis 6) | 0 | - | - | - | - | - | - | - | None (CPU/Comm/Spare) | MCC Hardwired Trunk Line | RESERVED
C6 | MCC Auxiliary I/O (Chassis 6) | 1 | - | - | - | - | - | - | - | None (CPU/Comm/Spare) | MCC Hardwired Trunk Line | RESERVED
C6 | MCC Auxiliary I/O (Chassis 6) | 2 | - | - | - | - | - | - | - | None (CPU/Comm/Spare) | MCC Hardwired Trunk Line | RESERVED
C6 | MCC Auxiliary I/O (Chassis 6) | 3 | - | - | - | - | - | - | - | None (CPU/Comm/Spare) | MCC Hardwired Trunk Line | RESERVED
C6 | MCC Auxiliary I/O (Chassis 6) | 4 | - | - | - | - | - | - | - | None (CPU/Comm/Spare) | MCC Hardwired Trunk Line | RESERVED
C6 | MCC Auxiliary I/O (Chassis 6) | 5 | - | - | DO | 8 | 8 | 0 | 0.0% | MCC | MCC Hardwired Trunk Line | ASSIGNED
C6 | MCC Auxiliary I/O (Chassis 6) | 6 | - | - | DI | 10 | 10 | 0 | 0.0% | MCC | MCC Hardwired Trunk Line | ASSIGNED
C6 | MCC Auxiliary I/O (Chassis 6) | 7 | - | - | - | - | - | - | - | None (CPU/Comm/Spare) | MCC Hardwired Trunk Line | RESERVED
▶ C7 — MCC FIELDBUS & NETWORK INTERFACE (CHASSIS 7) ¦ Location: Motor Control Center Room (MCC Panel & Field Bus) ¦ Net: Modbus TCP / EtherNet Trunk
C7 | MCC Fieldbus & Network Interface (Chassis 7) | 0 | - | - | BUS | 20 | 20 | 0 | 0.0% | JB-601, JB-607, JB-612, MCC | Modbus TCP / EtherNet Trunk | ASSIGNED
C7 | MCC Fieldbus & Network Interface (Chassis 7) | 1 | - | - | DI | 32 | 24 | 8 | 25.0% | MCC | Modbus TCP / EtherNet Trunk | ASSIGNED
C7 | MCC Fieldbus & Network Interface (Chassis 7) | 2 | - | - | DI | 32 | 32 | 0 | 0.0% | JB-601, MCC | Modbus TCP / EtherNet Trunk | ASSIGNED
C7 | MCC Fieldbus & Network Interface (Chassis 7) | 3 | - | - | DI | 26 | 26 | 0 | 0.0% | JB-601, MCC | Modbus TCP / EtherNet Trunk | ASSIGNED
C7 | MCC Fieldbus & Network Interface (Chassis 7) | 4 | - | - | DI | 28 | 0 | 28 | 100.0% | MCC | Modbus TCP / EtherNet Trunk | RESERVED
C7 | MCC Fieldbus & Network Interface (Chassis 7) | 5 | - | - | DO | 32 | 24 | 8 | 25.0% | MCC | Modbus TCP / EtherNet Trunk | ASSIGNED
C7 | MCC Fieldbus & Network Interface (Chassis 7) | 6 | - | - | DO | 32 | 32 | 0 | 0.0% | JB-601, MCC | Modbus TCP / EtherNet Trunk | ASSIGNED
C7 | MCC Fieldbus & Network Interface (Chassis 7) | 7 | - | - | DO | 24 | 0 | 24 | 100.0% | MCC | Modbus TCP / EtherNet Trunk | RESERVED

## IO_Master_Source_Destination
KALASIN ENGINEERING - xCIP TURNKEY AUTOMATION (Ref: x2608003)
COMPLETE I/O SOURCE AND DESTINATION WIRING SCHEDULE (TOTAL 1,210 CHANNELS)
SOURCE SPECIFICATION (PLC CABINET / RACK / MODULE TERMINAL / ePLAN WIRE TAG) | [8 empty] | SIGNAL CLASSIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD INSTRUMENT TAG)
Point Ref ID | Chassis | Slot | Point | Chan | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Field Terminal Block | Field Terminal Pin | Instrument Tag | Instrument Description | P&ID Drawing No. | Control / Interlock Logic
C1-S03-P00 | C1 | 3 | 0 | 1 | 1756-IB32 | Spare_DI_0 | Pin 1 | C1S3:1/C1S03-X1:1 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P01 | C1 | 3 | 1 | 2 | 1756-IB32 | Spare_DI_0 | Pin 2 | C1S3:2/C1S03-X1:2 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P02 | C1 | 3 | 2 | 3 | 1756-IB32 | Spare_DI_0 | Pin 3 | C1S3:3/C1S03-X1:3 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P03 | C1 | 3 | 3 | 4 | 1756-IB32 | Spare_DI_0 | Pin 4 | C1S3:4/C1S03-X1:4 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P04 | C1 | 3 | 4 | 5 | 1756-IB32 | Spare_DI_0 | Pin 5 | C1S3:5/C1S03-X1:5 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P05 | C1 | 3 | 5 | 6 | 1756-IB32 | Spare_DI_0 | Pin 6 | C1S3:6/C1S03-X1:6 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P06 | C1 | 3 | 6 | 7 | 1756-IB32 | Spare_DI_0 | Pin 7 | C1S3:7/C1S03-X1:7 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P07 | C1 | 3 | 7 | 8 | 1756-IB32 | Spare_DI_0 | Pin 8 | C1S3:8/C1S03-X1:8 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P08 | C1 | 3 | 8 | 9 | 1756-IB32 | Spare_DI_0 | Pin 9 | C1S3:9/C1S03-X1:9 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P09 | C1 | 3 | 9 | 10 | 1756-IB32 | Spare_DI_0 | Pin 10 | C1S3:10/C1S03-X1:10 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P10 | C1 | 3 | 10 | 11 | 1756-IB32 | Spare_DI_0 | Pin 11 | C1S3:11/C1S03-X1:11 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P11 | C1 | 3 | 11 | 12 | 1756-IB32 | Spare_DI_0 | Pin 12 | C1S3:12/C1S03-X1:12 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P12 | C1 | 3 | 12 | 13 | 1756-IB32 | Spare_DI_0 | Pin 13 | C1S3:13/C1S03-X1:13 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P13 | C1 | 3 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C1S3:14/C1S03-X1:14 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P14 | C1 | 3 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C1S3:15/C1S03-X1:15 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P15 | C1 | 3 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C1S3:16/C1S03-X1:16 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | - | -
C1-S03-P16 | C1 | 3 | 16 | 17 | 1756-IB32 | FSL-40201_DI_1 | Pin 17 | C1S3:17/C1S03-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | FSL-40201 | Flow Switch | 3-25-01-402-PD-01 | Slurry low flow
C1-S03-P17 | C1 | 3 | 17 | 18 | 1756-IB32 | FSL-40202_DI_1 | Pin 18 | C1S3:18/C1S03-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | FSL-40202 | Flow Switch | 3-25-01-402-PD-01 | Slurry low flow
C1-S03-P18 | C1 | 3 | 18 | 19 | 1756-IB32 | FT-40201_DI_1 | Pin 19 | C1S3:19/C1S03-X2:19 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | FT-40201 | Coriolis Flow Transmitter | 3-25-01-402-PD-02 | Slurry flowrate & density check transfer line
C1-S03-P19 | C1 | 3 | 19 | 20 | 1756-IB32 | FT-40202_DI_1 | Pin 20 | C1S3:20/C1S03-X2:20 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | FT-40202 | Magnetic Flow Transmitter | 3-25-01-402-PD-02 | Feed Slurry Flow Transmitter for Pipe (PIPE)
C1-S03-P20 | C1 | 3 | 20 | 21 | 1756-IB32 | HV-40201_DI_1 | Pin 21 | C1S3:21/C1S03-X2:21 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40201 | Manual Valve With Position Switch | 3-25-01-402-PD-01 | Slurry Drain line
C1-S03-P21 | C1 | 3 | 21 | 22 | 1756-IB32 | HV-40202_DI_1 | Pin 22 | C1S3:22/C1S03-X2:22 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40202 | Manual Valve With Position Switch | 3-25-01-402-PD-01 | Slurry Drain line
C1-S03-P22 | C1 | 3 | 22 | 23 | 1756-IB32 | HV-40203_DI_1 | Pin 23 | C1S3:23/C1S03-X2:23 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40203 | Manual Valve With Position Switch | 3-25-01-402-PD-01 | Slurry Drain tank TS-40201
C1-S03-P23 | C1 | 3 | 23 | 24 | 1756-IB32 | HV-40204_DI_1 | Pin 24 | C1S3:24/C1S03-X2:24 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40204 | Manual Valve With Position Switch | 3-25-01-402-PD-01 | Slurry Drain tank TS-40202
C1-S03-P24 | C1 | 3 | 24 | 25 | 1756-IB32 | HV-40205_DI_1 | Pin 25 | C1S3:25/C1S03-X2:25 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | HV-40205 | Manual Valve With Position Switch | 3-25-01-402-PD-02 | Slurry Drain line
C1-S03-P25 | C1 | 3 | 25 | 26 | 1756-IB32 | HV-40206_DI_1 | Pin 26 | C1S3:26/C1S03-X2:26 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | HV-40206 | Manual Valve With Position Switch | 3-25-01-402-PD-02 | Slurry Drain tank TS-40203
C1-S03-P26 | C1 | 3 | 26 | 27 | 1756-IB32 | XV-40201A_DI_1 | Pin 27 | C1S3:27/C1S03-X2:27 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201A |  | 3-25-01-402-PD-01 | Slurry feed-in pH Adjustment tank 1
C1-S03-P27 | C1 | 3 | 27 | 28 | 1756-IB32 | XV-40201A_DI_2 | Pin 28 | C1S3:28/C1S03-X2:28 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201A |  | 3-25-01-402-PD-01 | Slurry feed-in pH Adjustment tank 1
C1-S03-P28 | C1 | 3 | 28 | 29 | 1756-IB32 | XV-40201B_DI_1 | Pin 29 | C1S3:29/C1S03-X2:29 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201B |  | 3-25-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1
C1-S03-P29 | C1 | 3 | 29 | 30 | 1756-IB32 | XV-40201B_DI_2 | Pin 30 | C1S3:30/C1S03-X2:30 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201B |  | 3-25-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1
C1-S03-P30 | C1 | 3 | 30 | 31 | 1756-IB32 | XV-40201C_DI_1 | Pin 31 | C1S3:31/C1S03-X2:31 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201C |  | 3-25-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1
C1-S03-P31 | C1 | 3 | 31 | 32 | 1756-IB32 | XV-40201C_DI_2 | Pin 32 | C1S3:32/C1S03-X2:32 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201C |  | 3-25-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1
C1-S04-P00 | C1 | 4 | 0 | 1 | 1756-IB32 | XV-40201D_DI_1 | Pin 1 | C1S4:1/TBDI1:1A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201D |  | 3-25-01-402-PD-01 | Slurry circulation pH Adjustment tank 1
C1-S04-P01 | C1 | 4 | 1 | 2 | 1756-IB32 | XV-40201D_DI_2 | Pin 2 | C1S4:2/TBDI1:2A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201D |  | 3-25-01-402-PD-01 | Slurry circulation pH Adjustment tank 1
C1-S04-P02 | C1 | 4 | 2 | 3 | 1756-IB32 | XV-40201E_DI_1 | Pin 3 | C1S4:3/TBDI1:3A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201E |  | 3-25-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2
C1-S04-P03 | C1 | 4 | 3 | 4 | 1756-IB32 | XV-40201E_DI_2 | Pin 4 | C1S4:4/TBDI1:4A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201E |  | 3-25-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2
C1-S04-P04 | C1 | 4 | 4 | 5 | 1756-IB32 | XV-40201F_DI_1 | Pin 5 | C1S4:5/TBDI1:5A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201F |  | 3-25-01-402-PD-01 | Slurry feed-to spray dry tank
C1-S04-P05 | C1 | 4 | 5 | 6 | 1756-IB32 | XV-40201F_DI_2 | Pin 6 | C1S4:6/TBDI1:6A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201F |  | 3-25-01-402-PD-01 | Slurry feed-to spray dry tank
C1-S04-P06 | C1 | 4 | 6 | 7 | 1756-IB32 | XV-40201G_DI_1 | Pin 7 | C1S4:7/TBDI1:7A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201G |  | 3-25-01-402-PD-01 | CIP water washing pH Adjustment tank 1
C1-S04-P07 | C1 | 4 | 7 | 8 | 1756-IB32 | XV-40201G_DI_2 | Pin 8 | C1S4:8/TBDI1:8A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201G |  | 3-25-01-402-PD-01 | CIP water washing pH Adjustment tank 1
C1-S04-P08 | C1 | 4 | 8 | 9 | 1756-IB32 | XV-40201H_DI_1 | Pin 9 | C1S4:9/TBDI1:9A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201H |  | 3-25-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 1
C1-S04-P09 | C1 | 4 | 9 | 10 | 1756-IB32 | XV-40201H_DI_2 | Pin 10 | C1S4:10/TBDI1:10A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201H |  | 3-25-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 1
C1-S04-P11 | C1 | 4 | 11 | 12 | 1756-IB32 | XV-40202A_DI_2 | Pin 12 | C1S4:12/TBDI1:12A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202A |  | 3-25-01-402-PD-01 | Slurry feed-in pH Adjustment tank 2
C1-S04-P12 | C1 | 4 | 12 | 13 | 1756-IB32 | XV-40202B_DI_1 | Pin 13 | C1S4:13/TBDI1:13A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202B |  | 3-25-01-402-PD-01 | Slurry feed-out pH Adjustment tank 2
C1-S04-P13 | C1 | 4 | 13 | 14 | 1756-IB32 | XV-40202B_DI_2 | Pin 14 | C1S4:14/TBDI1:14A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202B |  | 3-25-01-402-PD-01 | Slurry feed-out pH Adjustment tank 2
C1-S04-P14 | C1 | 4 | 14 | 15 | 1756-IB32 | XV-40202C_DI_1 | Pin 15 | C1S4:15/TBDI1:15A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202C |  | 3-25-01-402-PD-01 | Water washing line outlet pH Adjustment tank 2
C1-S04-P15 | C1 | 4 | 15 | 16 | 1756-IB32 | XV-40202C_DI_2 | Pin 16 | C1S4:16/TBDI1:16A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202C |  | 3-25-01-402-PD-01 | Water washing line outlet pH Adjustment tank 2
C1-S04-P16 | C1 | 4 | 16 | 17 | 1756-IB32 | XV-40202D_DI_1 | Pin 17 | C1S4:17/C1S04-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202D |  | 3-25-01-402-PD-01 | Slurry circulation pH Adjustment tank 2
C1-S04-P17 | C1 | 4 | 17 | 18 | 1756-IB32 | XV-40202D_DI_2 | Pin 18 | C1S4:18/C1S04-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202D |  | 3-25-01-402-PD-01 | Slurry circulation pH Adjustment tank 2
C1-S04-P18 | C1 | 4 | 18 | 19 | 1756-IB32 | XV-40202E_DI_1 | Pin 19 | C1S4:19/TBDI1:17A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202E |  | 3-25-01-402-PD-01 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1
C1-S04-P19 | C1 | 4 | 19 | 20 | 1756-IB32 | XV-40202A_DI_1 | Pin 20 | C1S4:20/TBDI1:18A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202A |  | 3-25-01-402-PD-01 | Slurry feed-in pH Adjustment tank 2
C1-S04-P19 | C1 | 4 | 19 | 20 | 1756-IB32 | XV-40202E_DI_2 | Pin 20 | C1S4:20/TBDI1:18A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202E |  | 3-25-01-402-PD-01 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1
C1-S04-P20 | C1 | 4 | 20 | 21 | 1756-IB32 | XV-40202F_DI_1 | Pin 21 | C1S4:21/TBDI1:19A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202F |  | 3-25-01-402-PD-01 | Slurry feed-to spray dry tank
C1-S04-P21 | C1 | 4 | 21 | 22 | 1756-IB32 | XV-40202F_DI_2 | Pin 22 | C1S4:22/TBDI1:20A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202F |  | 3-25-01-402-PD-01 | Slurry feed-to spray dry tank
C1-S04-P22 | C1 | 4 | 22 | 23 | 1756-IB32 | XV-40202G_DI_1 | Pin 23 | C1S4:23/TBDI1:21A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202G |  | 3-25-01-402-PD-01 | CIP water washing pH Adjustment tank 2
C1-S04-P23 | C1 | 4 | 23 | 24 | 1756-IB32 | XV-40202G_DI_2 | Pin 24 | C1S4:24/TBDI1:22A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202G |  | 3-25-01-402-PD-01 | CIP water washing pH Adjustment tank 2
C1-S04-P24 | C1 | 4 | 24 | 25 | 1756-IB32 | XV-40202H_DI_1 | Pin 25 | C1S4:25/TBDI1:23A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202H |  | 3-25-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 2
C1-S04-P25 | C1 | 4 | 25 | 26 | 1756-IB32 | XV-40202H_DI_2 | Pin 26 | C1S4:26/TBDI1:24A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202H |  | 3-25-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 2
C1-S04-P26 | C1 | 4 | 26 | 27 | 1756-IB32 | XV-40203B_DI_1 | Pin 27 | C1S4:27/TBDI1:25A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203B |  | 3-25-01-402-PD-02 | Slurry feed-out Spray dryer infeed tank
C1-S04-P27 | C1 | 4 | 27 | 28 | 1756-IB32 | XV-40203B_DI_2 | Pin 28 | C1S4:28/TBDI1:26A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203B |  | 3-25-01-402-PD-02 | Slurry feed-out Spray dryer infeed tank
C1-S04-P28 | C1 | 4 | 28 | 29 | 1756-IB32 | XV-40203C_DI_1 | Pin 29 | C1S4:29/TBDI1:27A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203C |  | 3-25-01-402-PD-02 | Water washing line outlet Spray dryer infeed tank
C1-S04-P29 | C1 | 4 | 29 | 30 | 1756-IB32 | XV-40203C_DI_2 | Pin 30 | C1S4:30/TBDI1:28A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203C |  | 3-25-01-402-PD-02 | Water washing line outlet Spray dryer infeed tank
C1-S04-P30 | C1 | 4 | 30 | 31 | 1756-IB32 | XV-40203D_DI_1 | Pin 31 | C1S4:31/TBDI1:29A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203D |  | 3-25-01-402-PD-02 | CIP water washing Spray dryer infeed tank
C1-S04-P31 | C1 | 4 | 31 | 32 | 1756-IB32 | XV-40203D_DI_2 | Pin 32 | C1S4:32/TBDI1:30A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203D |  | 3-25-01-402-PD-02 | CIP water washing Spray dryer infeed tank
C1-S05-P00 | C1 | 5 | 0 | 1 | 1756-IB32 | XV-40203E_DI_1 | Pin 1 | C1S5:1/TBDI2:1A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S05-X1 | - | XV-40203E |  | 3-25-01-402-PD-02 | CIP hight pressure water washing Spray dryer infeed tank
C1-S05-P01 | C1 | 5 | 1 | 2 | 1756-IB32 | XV-40203E_DI_2 | Pin 2 | C1S5:2/TBDI2:2A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S05-X1 | - | XV-40203E |  | 3-25-01-402-PD-02 | CIP hight pressure water washing Spray dryer infeed tank
C1-S05-P02 | C1 | 5 | 2 | 3 | 1756-IB32 | Spare_DI_0 | Pin 3 | C1S5:3/TBDI2:3A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P03 | C1 | 5 | 3 | 4 | 1756-IB32 | Spare_DI_0 | Pin 4 | C1S5:4/TBDI2:4A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P04 | C1 | 5 | 4 | 5 | 1756-IB32 | Spare_DI_0 | Pin 5 | C1S5:5/TBDI2:5A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P05 | C1 | 5 | 5 | 6 | 1756-IB32 | Spare_DI_0 | Pin 6 | C1S5:6/TBDI2:6A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P06 | C1 | 5 | 6 | 7 | 1756-IB32 | Spare_DI_0 | Pin 7 | C1S5:7/TBDI2:7A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P07 | C1 | 5 | 7 | 8 | 1756-IB32 | Spare_DI_0 | Pin 8 | C1S5:8/TBDI2:8A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P08 | C1 | 5 | 8 | 9 | 1756-IB32 | Spare_DI_0 | Pin 9 | C1S5:9/TBDI2:9A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P09 | C1 | 5 | 9 | 10 | 1756-IB32 | Spare_DI_0 | Pin 10 | C1S5:10/TBDI2:10A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P10 | C1 | 5 | 10 | 11 | 1756-IB32 | Spare_DI_0 | Pin 11 | C1S5:11/TBDI2:11A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P11 | C1 | 5 | 11 | 12 | 1756-IB32 | Spare_DI_0 | Pin 12 | C1S5:12/TBDI2:12A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P12 | C1 | 5 | 12 | 13 | 1756-IB32 | Spare_DI_0 | Pin 13 | C1S5:13/TBDI2:13A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P13 | C1 | 5 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C1S5:14/TBDI2:14A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P14 | C1 | 5 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C1S5:15/TBDI2:15A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P15 | C1 | 5 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C1S5:16/TBDI2:16A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | - | -
C1-S05-P16 | C1 | 5 | 16 | 17 | 1756-IB32 | ES-60202_DI_1 | Pin 17 | C1S5:17/C1S05-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | ES-60202 |  | - | E-Stop for PUPD-11 (Positive Displacement Pump )
C1-S05-P17 | C1 | 5 | 17 | 18 | 1756-IB32 | FS-60205_DI_1 | Pin 18 | C1S5:18/C1S05-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | FS-60205 | Flow Switch | 3-25-01-602-PD-01 | Cooling Water Return Flow Switch for Positive Displacement Pump (PUPD-11)
C1-S05-P18 | C1 | 5 | 18 | 19 | 1756-IB32 | LSL-60201_DI_1 | Pin 19 | C1S5:19/TBDI2:17A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | LSL-60201 |  | 3-25-01-602-PD-11 | Level low switch
C1-S05-P19 | C1 | 5 | 19 | 20 | 1756-IB32 | SV-60201_DI_1 | Pin 20 | C1S5:20/TBDI2:18A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60201 |  | 3-25-01-602-PD-08 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21)
C1-S05-P20 | C1 | 5 | 20 | 21 | 1756-IB32 | SV-60201_DI_2 | Pin 21 | C1S5:21/TBDI2:19A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60201 |  | 3-25-01-602-PD-08 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21)
C1-S05-P21 | C1 | 5 | 21 | 22 | 1756-IB32 | SV-60202_DI_1 | Pin 22 | C1S5:22/TBDI2:20A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60202 |  | 3-25-01-602-PD-08 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22)
C1-S05-P22 | C1 | 5 | 22 | 23 | 1756-IB32 | SV-60202_DI_2 | Pin 23 | C1S5:23/TBDI2:21A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60202 |  | 3-25-01-602-PD-08 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22)
C1-S05-P23 | C1 | 5 | 23 | 24 | 1756-IB32 | SV-60203_DI_1 | Pin 24 | C1S5:24/TBDI2:22A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60203 |  | 3-25-01-602-PD-08 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23)
C1-S05-P24 | C1 | 5 | 24 | 25 | 1756-IB32 | SV-60203_DI_2 | Pin 25 | C1S5:25/TBDI2:23A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60203 |  | 3-25-01-602-PD-08 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23)
C1-S05-P25 | C1 | 5 | 25 | 26 | 1756-IB32 | VS-60205_DI_1 | Pin 26 | C1S5:26/TBDI2:24A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | VS-60205 | Vibration Switch | 3-25-01-602-PD-01 | Vibration Gear Box Vibration Switch for Switch Vibration for PUPD-11 (PUPD-11)
C1-S05-P26 | C1 | 5 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C1S5:27/TBDI2:25A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | - | -
C1-S05-P27 | C1 | 5 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C1S5:28/TBDI2:26A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | - | -
C1-S05-P28 | C1 | 5 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C1S5:29/TBDI2:27A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | - | -
C1-S05-P29 | C1 | 5 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C1S5:30/TBDI2:28A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | - | -
C1-S05-P30 | C1 | 5 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C1S5:31/TBDI2:29A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | - | -
C1-S05-P31 | C1 | 5 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C1S5:32/TBDI2:30A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | - | -
C1-S06-P00 | C1 | 6 | 0 | 1 | 1756-IB32 | XA-60202A_DI_1 | Pin 1 | C1S6:1/TBDI3:1A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202A |  | - | General Alarm Emergency Stop Actuation for XSUP-5601 (Supression Panel)
C1-S06-P01 | C1 | 6 | 1 | 2 | 1756-IB32 | XA-60202B_DI_1 | Pin 2 | C1S6:2/TBDI3:2A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202B |  | - | General Fault Controlled Stop for XSUP-5601 (Supression Panel)
C1-S06-P02 | C1 | 6 | 2 | 3 | 1756-IB32 | XA-60202C_DI_1 | Pin 3 | C1S6:3/TBDI3:3A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202C |  | - | General Armed Status Indicator for XSUP-5601 (Supression Panel)
C1-S06-P03 | C1 | 6 | 3 | 4 | 1756-IB32 | XA-60202D_DI_1 | Pin 4 | C1S6:4/TBDI3:4A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202D |  | - | Power Fault Status Indicator for XSUP-5601 (Supression Panel)
C1-S06-P04 | C1 | 6 | 4 | 5 | 1756-IB32 | XA-60202E_DI_1 | Pin 5 | C1S6:5/TBDI3:5A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202E |  | - | Dryer CHAM-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel)
C1-S06-P05 | C1 | 6 | 5 | 6 | 1756-IB32 | XA-60202F_DI_1 | Pin 6 | C1S6:6/TBDI3:6A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202F |  | - | CHAM-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel)
C1-S06-P06 | C1 | 6 | 6 | 7 | 1756-IB32 | XA-60202G_DI_1 | Pin 7 | C1S6:7/TBDI3:7A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202G |  | - | CYCL-21/22 Emergency Stop Actuation for XSUP-5601 (Supression Panel)
C1-S06-P07 | C1 | 6 | 7 | 8 | 1756-IB32 | XA-60202H_DI_1 | Pin 8 | C1S6:8/TBDI3:8A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202H |  | - | CYCL-21/22 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel)
C1-S06-P08 | C1 | 6 | 8 | 9 | 1756-IB32 | XA-60202I_DI_1 | Pin 9 | C1S6:9/TBDI3:9A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202I |  | - | -
C1-S06-P09 | C1 | 6 | 9 | 10 | 1756-IB32 | XA-60202J_DI_1 | Pin 10 | C1S6:10/TBDI3:10A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202J |  | - | BGHS-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel)
C1-S06-P10 | C1 | 6 | 10 | 11 | 1756-IB32 | XA-60202K_DI_1 | Pin 11 | C1S6:11/TBDI3:11A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202K |  | - | BGHS-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel)
C1-S06-P11 | C1 | 6 | 11 | 12 | 1756-IB32 | XA-60202L_DI_1 | Pin 12 | C1S6:12/TBDI3:12A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202L |  | - | CYCL-31 Emergency Stop Actuation for XSUP-5601 (Supression Panel)
C1-S06-P12 | C1 | 6 | 12 | 13 | 1756-IB32 | XA-60202M_DI_1 | Pin 13 | C1S6:13/TBDI3:13A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202M |  | - | CYCL-31 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel)
C1-S06-P13 | C1 | 6 | 13 | 14 | 1756-IB32 | XV-60202_DI_1 | Pin 14 | C1S6:14/TBDI3:14A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XV-60202 |  | 3-25-01-602-PD-11 | High Pressure Water On/Off Valve for Drain Pipe
C1-S06-P14 | C1 | 6 | 14 | 15 | 1756-IB32 | XV-60202_DI_2 | Pin 15 | C1S6:15/TBDI3:15A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XV-60202 |  | 3-25-01-602-PD-11 | High Pressure Water On/Off Valve for Drain Pipe
C1-S06-P15 | C1 | 6 | 15 | 16 | 1756-IB32 | XV-60205A_DI_1 | Pin 16 | C1S6:16/TBDI3:16A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XV-60205A |  | 3-25-01-602-PD-01 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11)
C1-S06-P16 | C1 | 6 | 16 | 17 | 1756-IB32 | XV-60205A_DI_2 | Pin 17 | C1S6:17/C1S06-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60205A |  | 3-25-01-602-PD-01 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11)
C1-S06-P17 | C1 | 6 | 17 | 18 | 1756-IB32 | XV-60240D_DI_1 | Pin 18 | C1S6:18/C1S06-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60240D |  | - | -
C1-S06-P18 | C1 | 6 | 18 | 19 | 1756-IB32 | XV-60240D_DI_2 | Pin 19 | C1S6:19/TBDI3:17A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60240D |  | 3-25-01-602-PD-05 | -
C1-S06-P19 | C1 | 6 | 19 | 20 | 1756-IB32 | XV-60240D_DI_1 | Pin 20 | C1S6:20/TBDI3:18A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60240D |  | - | -
C1-S06-P20 | C1 | 6 | 20 | 21 | 1756-IB32 | XV-60240D_DI_2 | Pin 21 | C1S6:21/TBDI3:19A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60240D |  | 3-25-01-602-PD-05 | -
C1-S06-P21 | C1 | 6 | 21 | 22 | 1756-IB32 | YA-60205_DI_1 | Pin 22 | C1S6:22/TBDI3:20A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | YA-60205 |  | - | Fault Command
C1-S06-P22 | C1 | 6 | 22 | 23 | 1756-IB32 | YI-60205_DI_1 | Pin 23 | C1S6:23/TBDI3:21A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | YI-60205 |  | - | Run Command
C1-S06-P23 | C1 | 6 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C1S6:24/TBDI3:22A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | - | -
C1-S06-P24 | C1 | 6 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C1S6:25/TBDI3:23A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | - | -
C1-S06-P25 | C1 | 6 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C1S6:26/TBDI3:24A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | - | -
C1-S06-P26 | C1 | 6 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C1S6:27/TBDI3:25A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | - | -
C1-S06-P27 | C1 | 6 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C1S6:28/TBDI3:26A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | - | -
C1-S06-P28 | C1 | 6 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C1S6:29/TBDI3:27A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | - | -
C1-S06-P29 | C1 | 6 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C1S6:30/TBDI3:28A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | - | -
C1-S06-P30 | C1 | 6 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C1S6:31/TBDI3:29A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | - | -
C1-S06-P31 | C1 | 6 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C1S6:32/TBDI3:30A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | - | -
C1-S07-P00 | C1 | 7 | 0 | 1 | 1756-OB32 | Spare_DO_0 | Pin 1 | C1S7:1/TBDI4:1A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P01 | C1 | 7 | 1 | 2 | 1756-OB32 | Spare_DO_0 | Pin 2 | C1S7:2/TBDI4:2A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P02 | C1 | 7 | 2 | 3 | 1756-OB32 | Spare_DO_0 | Pin 3 | C1S7:3/TBDI4:3A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P03 | C1 | 7 | 3 | 4 | 1756-OB32 | Spare_DO_0 | Pin 4 | C1S7:4/TBDI4:4A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P04 | C1 | 7 | 4 | 5 | 1756-OB32 | Spare_DO_0 | Pin 5 | C1S7:5/TBDI4:5A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P05 | C1 | 7 | 5 | 6 | 1756-OB32 | Spare_DO_0 | Pin 6 | C1S7:6/TBDI4:6A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P06 | C1 | 7 | 6 | 7 | 1756-OB32 | Spare_DO_0 | Pin 7 | C1S7:7/TBDI4:7A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P07 | C1 | 7 | 7 | 8 | 1756-OB32 | Spare_DO_0 | Pin 8 | C1S7:8/TBDI4:8A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P08 | C1 | 7 | 8 | 9 | 1756-OB32 | Spare_DO_0 | Pin 9 | C1S7:9/TBDI4:9A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P09 | C1 | 7 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C1S7:10/TBDI4:10A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P10 | C1 | 7 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C1S7:11/TBDI4:11A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P11 | C1 | 7 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C1S7:12/TBDI4:12A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P12 | C1 | 7 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C1S7:13/TBDI4:13A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P13 | C1 | 7 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C1S7:14/TBDI4:14A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P14 | C1 | 7 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C1S7:15/TBDI4:15A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P15 | C1 | 7 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C1S7:16/TBDI4:16A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | - | -
C1-S07-P16 | C1 | 7 | 16 | 17 | 1756-OB32 | XV-40202E_DO_1 | Pin 17 | C1S7:17/C1S07-X2:17 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202E |  | 3-25-01-402-PD-01 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1
C1-S07-P17 | C1 | 7 | 17 | 18 | 1756-OB32 | XV-40202F_DO_1 | Pin 18 | C1S7:18/C1S07-X2:18 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202F |  | 3-25-01-402-PD-01 | Slurry feed-to spray dry tank
C1-S07-P18 | C1 | 7 | 18 | 19 | 1756-OB32 | XV-40202G_DO_1 | Pin 19 | C1S7:19/TBDI4:17A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202G |  | 3-25-01-402-PD-01 | CIP water washing pH Adjustment tank 2
C1-S07-P19 | C1 | 7 | 19 | 20 | 1756-OB32 | XV-40202H_DO_1 | Pin 20 | C1S7:20/TBDI4:18A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202H |  | 3-25-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 2
C1-S07-P20 | C1 | 7 | 20 | 21 | 1756-OB32 | XV-40203B_DO_1 | Pin 21 | C1S7:21/TBDI4:19A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203B |  | 3-25-01-402-PD-02 | Slurry feed-out Spray dryer infeed tank
C1-S07-P21 | C1 | 7 | 21 | 22 | 1756-OB32 | XV-40203C_DO_1 | Pin 22 | C1S7:22/TBDI4:20A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203C |  | 3-25-01-402-PD-02 | Water washing line outlet Spray dryer infeed tank
C1-S07-P22 | C1 | 7 | 22 | 23 | 1756-OB32 | XV-40203D_DO_1 | Pin 23 | C1S7:23/TBDI4:21A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203D |  | 3-25-01-402-PD-02 | CIP water washing Spray dryer infeed tank
C1-S07-P23 | C1 | 7 | 23 | 24 | 1756-OB32 | XV-40203E_DO_1 | Pin 24 | C1S7:24/TBDI4:22A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203E |  | 3-25-01-402-PD-02 | CIP hight pressure water washing Spray dryer infeed tank
C1-S07-P24 | C1 | 7 | 24 | 25 | 1756-OB32 | SV-40201_DO_1 | Pin 25 | C1S7:25/TBDI4:23A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40201 |  | 3-25-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 1
C1-S07-P25 | C1 | 7 | 25 | 26 | 1756-OB32 | SV-40202_DO_1 | Pin 26 | C1S7:26/TBDI4:24A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40202 |  | 3-25-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 2
C1-S07-P26 | C1 | 7 | 26 | 27 | 1756-OB32 | SV-40203_DO_1 | Pin 27 | C1S7:27/TBDI4:25A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40203 |  | 3-25-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 1
C1-S07-P27 | C1 | 7 | 27 | 28 | 1756-OB32 | SV-40204_DO_1 | Pin 28 | C1S7:28/TBDI4:26A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40204 |  | 3-25-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 2
C1-S07-P28 | C1 | 7 | 28 | 29 | 1756-OB32 | XV-40201A_DO_1 | Pin 29 | C1S7:29/TBDI4:27A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201A |  | 3-25-01-402-PD-01 | Slurry feed-in pH Adjustment tank 1
C1-S07-P29 | C1 | 7 | 29 | 30 | 1756-OB32 | XV-40201B_DO_1 | Pin 30 | C1S7:30/TBDI4:28A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201B |  | 3-25-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1
C1-S07-P30 | C1 | 7 | 30 | 31 | 1756-OB32 | XV-40201C_DO_1 | Pin 31 | C1S7:31/TBDI4:29A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201C |  | 3-25-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1
C1-S07-P31 | C1 | 7 | 31 | 32 | 1756-OB32 | XV-40201D_DO_1 | Pin 32 | C1S7:32/TBDI4:30A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201D |  | 3-25-01-402-PD-01 | Slurry circulation pH Adjustment tank 1
C1-S08-P00 | C1 | 8 | 0 | 1 | 1756-OB32 | XV-40201E_DO_1 | Pin 1 | C1S8:1/RL.1:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201E |  | 3-25-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2
C1-S08-P01 | C1 | 8 | 1 | 2 | 1756-OB32 | XV-40201F_DO_1 | Pin 2 | C1S8:2/RL.2:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201F |  | 3-25-01-402-PD-01 | Slurry feed-to spray dry tank
C1-S08-P02 | C1 | 8 | 2 | 3 | 1756-OB32 | XV-40201G_DO_1 | Pin 3 | C1S8:3/RL.3:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201G |  | 3-25-01-402-PD-01 | CIP water washing pH Adjustment tank 1
C1-S08-P03 | C1 | 8 | 3 | 4 | 1756-OB32 | XV-40201H_DO_1 | Pin 4 | C1S8:4/RL.4:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201H |  | 3-25-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 1
C1-S08-P04 | C1 | 8 | 4 | 5 | 1756-OB32 | XV-40202A_DO_1 | Pin 5 | C1S8:5/RL.5:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202A |  | 3-25-01-402-PD-01 | Slurry feed-in pH Adjustment tank 2
C1-S08-P05 | C1 | 8 | 5 | 6 | 1756-OB32 | XV-40202B_DO_1 | Pin 6 | C1S8:6/RL.6:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202B |  | 3-25-01-402-PD-01 | Slurry feed-out pH Adjustment tank 2
C1-S08-P06 | C1 | 8 | 6 | 7 | 1756-OB32 | XV-40202C_DO_1 | Pin 7 | C1S8:7/RL.7:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202C |  | 3-25-01-402-PD-01 | Water washing line outlet pH Adjustment tank 2
C1-S08-P07 | C1 | 8 | 7 | 8 | 1756-OB32 | XV-40202D_DO_1 | Pin 8 | C1S8:8/RL.8:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202D |  | 3-25-01-402-PD-01 | Slurry circulation pH Adjustment tank 2
C1-S08-P08 | C1 | 8 | 8 | 9 | 1756-OB32 | Spare_DO_0 | Pin 9 | C1S8:9/RL.9:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | - | -
C1-S08-P09 | C1 | 8 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C1S8:10/RL.10:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | - | -
C1-S08-P10 | C1 | 8 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C1S8:11/RL.11:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | - | -
C1-S08-P11 | C1 | 8 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C1S8:12/RL.12:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | - | -
C1-S08-P12 | C1 | 8 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C1S8:13/RL.13:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | - | -
C1-S08-P13 | C1 | 8 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C1S8:14/RL.14:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | - | -
C1-S08-P14 | C1 | 8 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C1S8:15/RL.15:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | - | -
C1-S08-P15 | C1 | 8 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C1S8:16/RL.16:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | - | -
C1-S08-P16 | C1 | 8 | 16 | 17 | 1756-OB32 | SV-60201_DO_1 | Pin 17 | C1S8:17/C1S08-X2:17 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60201 |  | 3-25-01-602-PD-08 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21)
C1-S08-P17 | C1 | 8 | 17 | 18 | 1756-OB32 | SV-60202_DO_1 | Pin 18 | C1S8:18/C1S08-X2:18 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60202 |  | 3-25-01-602-PD-08 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22)
C1-S08-P18 | C1 | 8 | 18 | 19 | 1756-OB32 | SV-60230_DO_1 | Pin 19 | C1S8:19/RL.17:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60230 |  | 3-25-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 27 (CYCL-21)
C1-S08-P19 | C1 | 8 | 19 | 20 | 1756-OB32 | SV-60203_DO_1 | Pin 20 | C1S8:20/RL.18:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60203 |  | 3-25-01-602-PD-08 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23)
C1-S08-P20 | C1 | 8 | 20 | 21 | 1756-OB32 | SV-60240A_DO_1 | Pin 21 | C1S8:21/RL.19:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60240A |  | 3-25-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29A (BGHS-21)
C1-S08-P21 | C1 | 8 | 21 | 22 | 1756-OB32 | SV-60231_DO_1 | Pin 22 | C1S8:22/RL.20:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60231 |  | 3-25-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 28 (CYCL-22)
C1-S08-P22 | C1 | 8 | 22 | 23 | 1756-OB32 | SV-60240B_DO_1 | Pin 23 | C1S8:23/RL.21:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60240B |  | 3-25-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29B (BGHS-21)
C1-S08-P23 | C1 | 8 | 23 | 24 | 1756-OB32 | SV-60240C_DO_1 | Pin 24 | C1S8:24/RL.22:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60240C |  | 3-25-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29C (BGHS-21)
C1-S08-P24 | C1 | 8 | 24 | 25 | 1756-OB32 | XV-60240D_DO_1 | Pin 25 | C1S8:25/RL.23:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | XV-60240D |  | - | -
C1-S08-P25 | C1 | 8 | 25 | 26 | 1756-OB32 | XV-60251_DO_1 | Pin 26 | C1S8:26/RL.24:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Infeed Tank | C1S08-X2 | - | XV-60251 |  | 3-25-01-602-PD-01 | Liquid On/Off Valve for Drain Pipe (PIPE)
C1-S08-P26 | C1 | 8 | 26 | 27 | 1756-OB32 | XV-60202_DO_1 | Pin 27 | C1S8:27/RL.25:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | XV-60202 |  | 3-25-01-602-PD-11 | High Pressure Water On/Off Valve for Drain Pipe
C1-S08-P27 | C1 | 8 | 27 | 28 | 1756-OB32 | XV-60205A_DO_1 | Pin 28 | C1S8:28/RL.26:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | XV-60205A |  | 3-25-01-602-PD-01 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11)
C1-S08-P28 | C1 | 8 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C1S8:29/RL.27:A1 | DO | 24VDC Sourcing | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S08-X2 | - | Spare | Spare Channel | - | -
C1-S08-P29 | C1 | 8 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C1S8:30/RL.28:A1 | DO | 24VDC Sourcing | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S08-X2 | - | Spare | Spare Channel | - | -
C1-S08-P30 | C1 | 8 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C1S8:31/RL.29:A1 | DO | 24VDC Sourcing | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S08-X2 | - | Spare | Spare Channel | - | -
C1-S08-P31 | C1 | 8 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C1S8:32/RL.30:A1 | DO | 24VDC Sourcing | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S08-X2 | - | Spare | Spare Channel | - | -
C1-S09-P00 | C1 | 9 | 0 | 1 | 1756-IF16 | FT-40201_AI_1 | Pin 1 | C1S9:1/RL.33:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | FT-40201 | Coriolis Flow Transmitter | 3-25-01-402-PD-02 | Slurry flowrate & density check transfer line
C1-S09-P01 | C1 | 9 | 1 | 2 | 1756-IF16 | FT-40201_AI_2 | Pin 2 | C1S9:2/RL.34:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | FT-40201 | Coriolis Flow Transmitter | 3-25-01-402-PD-02 | Slurry flowrate & density check transfer line
C1-S09-P02 | C1 | 9 | 2 | 3 | 1756-IF16 | FT-40202_AI_1 | Pin 3 | C1S9:3/RL.35:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | FT-40202 | Magnetic Flow Transmitter | 3-25-01-402-PD-02 | Feed Slurry Flow Transmitter for Pipe (PIPE)
C1-S09-P03 | C1 | 9 | 3 | 4 | 1756-IF16 | LT-40203_AI_1 | Pin 4 | C1S9:4/RL.36:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | LT-40203 | Level Transmitter | 3-25-01-402-PD-02 | Level transmitter in Spray dryer infeed tank
C1-S09-P04 | C1 | 9 | 4 | 5 | 1756-IF16 | LT-40201_AI_1 | Pin 5 | C1S9:5/RL.37:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | LT-40201 | Level Transmitter | 3-25-01-402-PD-01 | Level transmitter in pH Adjustment tank 1
C1-S09-P05 | C1 | 9 | 5 | 6 | 1756-IF16 | LT-40202_AI_1 | Pin 6 | C1S9:6/RL.38:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | LT-40202 | Level Transmitter | 3-25-01-402-PD-01 | Level transmitter in pH Adjustment tank 2
C1-S09-P06 | C1 | 9 | 6 | 7 | 1756-IF16 | pHT-40201_AI_1 | Pin 7 | C1S9:7/RL.39:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | pHT-40201 | PH Transmitter | 3-25-01-402-PD-01 | pH analyzer in pH Adjustment tank 1
C1-S09-P07 | C1 | 9 | 7 | 8 | 1756-IF16 | pHT-40202_AI_1 | Pin 8 | C1S9:8/RL.40:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | pHT-40202 | PH Transmitter | 3-25-01-402-PD-01 | pH analyzer in pH Adjustment tank 2
C1-S09-P08 | C1 | 9 | 8 | 9 | 1756-IF16 | PT-40201_AI_1 | Pin 9 | C1S9:9/RL.41:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | PT-40201 | Pressure Transmitter | 3-25-01-402-PD-02 | Pressure Transmitter for Inlet Filter Strainer (FSTR-11)
C1-S09-P09 | C1 | 9 | 9 | 10 | 1756-IF16 | PT-40202_AI_1 | Pin 10 | C1S9:10/RL.42:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | PT-40202 | Pressure Transmitter | 3-25-01-402-PD-02 | Feed Slurry Pressure Transmitter for Pipe (PIPE)
C1-S09-P10 | C1 | 9 | 10 | 11 | 1756-IF16 | PT-60202_AI_1 | Pin 11 | C1S9:11/RL.43:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | PT-60202 | Pressure Transmitter | 3-25-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11)
C1-S09-P11 | C1 | 9 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C1S9:12/RL.44:A1 | AI | 4-20mA HART | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | - | -
C1-S09-P12 | C1 | 9 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C1S9:13/RL.45:A1 | AI | 4-20mA HART | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | - | -
C1-S09-P13 | C1 | 9 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C1S9:14/RL.46:A1 | AI | 4-20mA HART | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | - | -
C1-S09-P14 | C1 | 9 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C1S9:15/RL.47:A1 | AI | 4-20mA HART | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | - | -
C1-S09-P15 | C1 | 9 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C1S9:16/RL.48:A1 | AI | 4-20mA HART | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | - | -
C1-S10-P00 | C1 | 10 | 0 | 1 | 1756-IF16 | DPI-60240_AI_1 | Pin 1 | C1S10:1/C1S10-X1:1 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | DPI-60240 |  | - | Gas Pressure Differntial Pressure (Bag House Air Pulsing)
C1-S10-P01 | C1 | 10 | 1 | 2 | 1756-IF16 | DPT-60202_AI_1 | Pin 2 | C1S10:2/C1S10-X1:2 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | DPT-60202 | Differential Pressure Transmitte | 3-25-01-602-PD-08 | Gas Pressure Differential Transmitter for Air Filter (FICA-31)
C1-S10-P02 | C1 | 10 | 2 | 3 | 1756-IF16 | FT-60201_AI_1 | Pin 3 | C1S10:3/C1S10-X1:3 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | FT-60201 |  | 3-25-01-602-PD-08 | Gas Flow Transmitter for Cooling Conveying Cold Air Duct (DTCA-32)
C1-S10-P03 | C1 | 10 | 3 | 4 | 1756-IF16 | FT-60204_AI_1 | Pin 4 | C1S10:4/C1S10-X1:4 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | FT-60204 |  | 3-25-01-602-PD-10 | Compressed air Flow
C1-S10-P04 | C1 | 10 | 4 | 5 | 1756-IF16 | FT-61307_AI_1 | Pin 5 | C1S10:5/C1S10-X1:5 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | FT-61307 |  | 3-25-01-613-PD-04 | Compressed air Flow
C1-S10-P05 | C1 | 10 | 5 | 6 | 1756-IF16 | PT-60203_AI_1 | Pin 6 | C1S10:6/C1S10-X1:6 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | PT-60203 | Pressure Transmitter | 3-25-01-602-PD-08 | Gas Pressure Transmitter for Cool Air Duct (DTCA-32)
C1-S10-P06 | C1 | 10 | 6 | 7 | 1756-IF16 | PT-60204_AI_1 | Pin 7 | C1S10:7/C1S10-X1:7 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | PT-60204 | Pressure Transmitter | 3-25-01-602-PD-10 | Pressure transmitter
C1-S10-P07 | C1 | 10 | 7 | 8 | 1756-IF16 | PT-60205_AI_1 | Pin 8 | C1S10:8/C1S10-X1:8 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | PT-60205 | Pressure Transmitter | 3-25-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11)
C1-S10-P08 | C1 | 10 | 8 | 9 | 1756-IF16 | Spare_AI_0 | Pin 9 | C1S10:9/C1S10-X1:9 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | - | -
C1-S10-P09 | C1 | 10 | 9 | 10 | 1756-IF16 | Spare_AI_0 | Pin 10 | C1S10:10/C1S10-X1:10 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | - | -
C1-S10-P10 | C1 | 10 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C1S10:11/C1S10-X1:11 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | - | -
C1-S10-P11 | C1 | 10 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C1S10:12/C1S10-X1:12 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | - | -
C1-S10-P12 | C1 | 10 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C1S10:13/C1S10-X1:13 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | - | -
C1-S10-P13 | C1 | 10 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C1S10:14/C1S10-X1:14 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | - | -
C1-S10-P14 | C1 | 10 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C1S10:15/C1S10-X1:15 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | - | -
C1-S10-P15 | C1 | 10 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C1S10:16/C1S10-X1:16 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | - | -
C2-S01-P00 | C2 | 1 | 0 | 1 | 1756-IB32 | FS-40204_DI_1 | Pin 1 | C2S1:1/TBDI1:1A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | FS-40204 | Flow Switch | 325-01-402-PD-01 | Jet Cooker
C2-S01-P01 | C2 | 1 | 1 | 2 | 1756-IB32 | FS-40205_DI_1 | Pin 2 | C2S1:2/TBDI1:2A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | FS-40205 | Flow Switch | 325-01-402-PD-02 | Jet Cooker
C2-S01-P02 | C2 | 1 | 2 | 3 | 1756-IB32 | FT-40221_DI_1 | Pin 3 | C2S1:3/TBDI1:3A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | FT-40221 | Coriolis Flow Transmitter | 325-01-402-PD-02 | Jet Cooker
C2-S01-P03 | C2 | 1 | 3 | 4 | 1756-IB32 | FT-40222_DI_1 | Pin 4 | C2S1:4/TBDI1:4A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | FT-40222 | Coriolis Flow Transmitter | 325-01-402-PD-02 | Jet Cooker
C2-S01-P04 | C2 | 1 | 4 | 5 | 1756-IB32 | HV-40207_DI_1 | Pin 5 | C2S1:5/TBDI1:5A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | HV-40207 | Manual Valve With Position Switch | 325-01-402-PD-01 | Jet Cooker
C2-S01-P05 | C2 | 1 | 5 | 6 | 1756-IB32 | HV-40208_DI_1 | Pin 6 | C2S1:6/TBDI1:6A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | HV-40208 | Manual Valve With Position Switch | 325-01-402-PD-01 | Jet Cooker
C2-S01-P06 | C2 | 1 | 6 | 7 | 1756-IB32 | XV-40203F_DI_1 | Pin 7 | C2S1:7/TBDI1:7A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40203F |  | 325-01-402-PD-02 | Jet Cooker
C2-S01-P07 | C2 | 1 | 7 | 8 | 1756-IB32 | XV-40203F_DI_2 | Pin 8 | C2S1:8/TBDI1:8A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40203F |  | 325-01-402-PD-02 | Jet Cooker
C2-S01-P08 | C2 | 1 | 8 | 9 | 1756-IB32 | XV-40204B_DI_1 | Pin 9 | C2S1:9/TBDI1:9A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40204B |  | 325-01-402-PD-01 | Jet Cooker
C2-S01-P09 | C2 | 1 | 9 | 10 | 1756-IB32 | XV-40204B_DI_2 | Pin 10 | C2S1:10/TBDI1:10A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40204B |  | 325-01-402-PD-01 | Jet Cooker
C2-S01-P10 | C2 | 1 | 10 | 11 | 1756-IB32 | XV-40204C_DI_1 | Pin 11 | C2S1:11/TBDI1:11A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40204C |  | 325-01-402-PD-01 | Jet Cooker
C2-S01-P11 | C2 | 1 | 11 | 12 | 1756-IB32 | XV-40204C_DI_2 | Pin 12 | C2S1:12/TBDI1:12A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40204C |  | 325-01-402-PD-01 | Jet Cooker
C2-S01-P12 | C2 | 1 | 12 | 13 | 1756-IB32 | XV-40205A_DI_1 | Pin 13 | C2S1:13/TBDI1:13A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40205A |  | 325-01-402-PD-02 | Jet Cooker
C2-S01-P13 | C2 | 1 | 13 | 14 | 1756-IB32 | XV-40205A_DI_2 | Pin 14 | C2S1:14/TBDI1:14A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40205A |  | 325-01-402-PD-02 | Jet Cooker
C2-S01-P14 | C2 | 1 | 14 | 15 | 1756-IB32 | XV-40205B_DI_1 | Pin 15 | C2S1:15/TBDI1:15A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40205B |  | 325-01-402-PD-02 | Jet Cooker
C2-S01-P15 | C2 | 1 | 15 | 16 | 1756-IB32 | XV-40205B_DI_2 | Pin 16 | C2S1:16/TBDI1:16A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40205B |  | 325-01-402-PD-02 | Jet Cooker
C2-S01-P16 | C2 | 1 | 16 | 17 | 1756-IB32 | XV-40205C_DI_1 | Pin 17 | C2S1:17/C2S01-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205C |  | 325-01-402-PD-02 | Jet Cooker
C2-S01-P17 | C2 | 1 | 17 | 18 | 1756-IB32 | XV-40205C_DI_2 | Pin 18 | C2S1:18/C2S01-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205C |  | 325-01-402-PD-02 | Jet Cooker
C2-S01-P18 | C2 | 1 | 18 | 19 | 1756-IB32 | XV-40205D_DI_1 | Pin 19 | C2S1:19/TBDI1:17A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205D |  | 325-01-402-PD-02 | Jet Cooker
C2-S01-P19 | C2 | 1 | 19 | 20 | 1756-IB32 | XV-40205D_DI_2 | Pin 20 | C2S1:20/TBDI1:18A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205D |  | 325-01-402-PD-02 | Jet Cooker
C2-S01-P20 | C2 | 1 | 20 | 21 | 1756-IB32 | XV-40205F_DI_1 | Pin 21 | C2S1:21/TBDI1:19A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205F |  | 325-01-402-PD-02 | Jet Cooker
C2-S01-P21 | C2 | 1 | 21 | 22 | 1756-IB32 | XV-40205F_DI_2 | Pin 22 | C2S1:22/TBDI1:20A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205F |  | 325-01-402-PD-02 | Jet Cooker
C2-S01-P22 | C2 | 1 | 22 | 23 | 1756-IB32 | XV-40222_DI_1 | Pin 23 | C2S1:23/TBDI1:21A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40222 |  | 325-01-402-PD-02 | Jet Cooker
C2-S01-P23 | C2 | 1 | 23 | 24 | 1756-IB32 | XV-40222_DI_2 | Pin 24 | C2S1:24/TBDI1:22A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40222 |  | - | Jet Cooker
C2-S01-P24 | C2 | 1 | 24 | 25 | 1756-IB32 | Spare_DI_2 | Pin 25 | C2S1:25/TBDI1:23A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | - | -
C2-S01-P25 | C2 | 1 | 25 | 26 | 1756-IB32 | Spare_DI_2 | Pin 26 | C2S1:26/TBDI1:24A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | - | -
C2-S01-P26 | C2 | 1 | 26 | 27 | 1756-IB32 | Spare_DI_2 | Pin 27 | C2S1:27/TBDI1:25A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | - | -
C2-S01-P27 | C2 | 1 | 27 | 28 | 1756-IB32 | Spare_DI_2 | Pin 28 | C2S1:28/TBDI1:26A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | - | -
C2-S01-P28 | C2 | 1 | 28 | 29 | 1756-IB32 | Spare_DI_2 | Pin 29 | C2S1:29/TBDI1:27A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | - | -
C2-S01-P29 | C2 | 1 | 29 | 30 | 1756-IB32 | Spare_DI_2 | Pin 30 | C2S1:30/TBDI1:28A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | - | -
C2-S01-P30 | C2 | 1 | 30 | 31 | 1756-IB32 | Spare_DI_2 | Pin 31 | C2S1:31/TBDI1:29A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | - | -
C2-S01-P31 | C2 | 1 | 31 | 32 | 1756-IB32 | Spare_DI_2 | Pin 32 | C2S1:32/TBDI1:30A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | - | -
C2-S02-P00 | C2 | 2 | 0 | 1 | 1756-IB32 | FT-60202_DI_1 | Pin 1 | C2S2:1/TBDI2:1A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X1 | - | FT-60202 |  | 3-25-01-602-PD-09 | Steam feed to Spray dryer
C2-S02-P01 | C2 | 2 | 1 | 2 | 1756-IB32 | LSH-60251_DI_1 | Pin 2 | C2S2:2/TBDI2:2A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | LSH-60251 |  | 3-25-01-602-PD-04 | Water Level Switch High for Fire Deluge Pipe (FWDP-22)
C2-S02-P02 | C2 | 2 | 2 | 3 | 1756-IB32 | PSL-60220_DI_1 | Pin 3 | C2S2:3/TBDI2:3A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X1 | - | PSL-60220 |  | 3-25-01-602-PD-04 | Gas Pressure Switch Low for Spray Chamber (CHAM-21)
C2-S02-P03 | C2 | 2 | 3 | 4 | 1756-IB32 | TSH-60230_DI_1 | Pin 4 | C2S2:4/TBDI2:4A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | TSH-60230 |  | 3-25-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21)
C2-S02-P04 | C2 | 2 | 4 | 5 | 1756-IB32 | TSH-60240_DI_1 | Pin 5 | C2S2:5/TBDI2:5A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X1 | - | TSH-60240 |  | 3-25-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22)
C2-S02-P05 | C2 | 2 | 5 | 6 | 1756-IB32 | TSH-60241A_DI_1 | Pin 6 | C2S2:6/TBDI2:6A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSH-60241A |  | 3-25-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21)
C2-S02-P06 | C2 | 2 | 6 | 7 | 1756-IB32 | TSH-60242A_DI_1 | Pin 7 | C2S2:7/TBDI2:7A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | TSH-60242A |  | 3-25-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21)
C2-S02-P07 | C2 | 2 | 7 | 8 | 1756-IB32 | TSH-60243A_DI_1 | Pin 8 | C2S2:8/TBDI2:8A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSH-60243A |  | 3-25-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21)
C2-S02-P08 | C2 | 2 | 8 | 9 | 1756-IB32 | TSL-60241B_DI_1 | Pin 9 | C2S2:9/TBDI2:9A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSL-60241B |  | 3-25-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21)
C2-S02-P09 | C2 | 2 | 9 | 10 | 1756-IB32 | TSL-60242B_DI_1 | Pin 10 | C2S2:10/TBDI2:10A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | TSL-60242B |  | 3-25-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21)
C2-S02-P10 | C2 | 2 | 10 | 11 | 1756-IB32 | TSL-60243B_DI_1 | Pin 11 | C2S2:11/TBDI2:11A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSL-60243B |  | 3-25-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21)
C2-S02-P11 | C2 | 2 | 11 | 12 | 1756-IB32 | XA-60240A_DI_1 | Pin 12 | C2S2:12/TBDI2:12A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60240A |  | - | Alarm 1 for BGHS-21 (Bag House Air Pulsing)
C2-S02-P12 | C2 | 2 | 12 | 13 | 1756-IB32 | XA-60240B_DI_1 | Pin 13 | C2S2:13/TBDI2:13A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60240B |  | - | Alarm 2 for BGHS-21 (Bag House Air Pulsing)
C2-S02-P13 | C2 | 2 | 13 | 14 | 1756-IB32 | XA-60241A_DI_1 | Pin 14 | C2S2:14/TBDI2:14A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60241A |  | - | Alarm 1 for BGHS-21 (Bag House Air Pulsing)
C2-S02-P14 | C2 | 2 | 14 | 15 | 1756-IB32 | XA-60241B_DI_1 | Pin 15 | C2S2:15/TBDI2:15A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60241B |  | - | Alarm 2 for BGHS-21 (Bag House Air Pulsing)
C2-S02-P15 | C2 | 2 | 15 | 16 | 1756-IB32 | XA-60242A_DI_1 | Pin 16 | C2S2:16/TBDI2:16A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | XA-60242A |  | - | Alarm 1 for BGHS-21 (Bag House Air Pulsing)
C2-S02-P16 | C2 | 2 | 16 | 17 | 1756-IB32 | XA-60242B_DI_1 | Pin 17 | C2S2:17/C2S02-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X2 | - | XA-60242B |  | - | Alarm 2 for BGHS-21 (Bag House Air Pulsing)
C2-S02-P17 | C2 | 2 | 17 | 18 | 1756-IB32 | XA-60243A_DI_1 | Pin 18 | C2S2:18/C2S02-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X2 | - | XA-60243A |  | - | Alarm 1 for BGHS-21 (Bag House Air Pulsing)
C2-S02-P18 | C2 | 2 | 18 | 19 | 1756-IB32 | XA-60243B_DI_1 | Pin 19 | C2S2:19/TBDI2:17A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X2 | - | XA-60243B |  | - | Alarm 2 for BGHS-21 (Bag House Air Pulsing)
C2-S02-P19 | C2 | 2 | 19 | 20 | 1756-IB32 | XV-60214_DI_1 | Pin 20 | C2S2:20/TBDI2:18A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60214 |  | 3-25-01-602-PD-03 | Steam feed to Spray dryer
C2-S02-P20 | C2 | 2 | 20 | 21 | 1756-IB32 | XV-60214_DI_2 | Pin 21 | C2S2:21/TBDI2:19A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60214 |  | 3-25-01-602-PD-03 | Steam feed to Spray dryer
C2-S02-P21 | C2 | 2 | 21 | 22 | 1756-IB32 | XV-60241_DI_1 | Pin 22 | C2S2:22/TBDI2:20A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60241 |  | 3-25-01-602-PD-05 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22)
C2-S02-P22 | C2 | 2 | 22 | 23 | 1756-IB32 | XV-60241_DI_2 | Pin 23 | C2S2:23/TBDI2:21A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60241 |  | 3-25-01-602-PD-05 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22)
C2-S02-P23 | C2 | 2 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C2S2:24/TBDI2:22A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | - | -
C2-S02-P24 | C2 | 2 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C2S2:25/TBDI2:23A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | - | -
C2-S02-P25 | C2 | 2 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C2S2:26/TBDI2:24A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | - | -
C2-S02-P26 | C2 | 2 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C2S2:27/TBDI2:25A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | - | -
C2-S02-P27 | C2 | 2 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C2S2:28/TBDI2:26A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | - | -
C2-S02-P28 | C2 | 2 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C2S2:29/TBDI2:27A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | - | -
C2-S02-P29 | C2 | 2 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C2S2:30/TBDI2:28A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | - | -
C2-S02-P30 | C2 | 2 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C2S2:31/TBDI2:29A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | - | -
C2-S02-P31 | C2 | 2 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C2S2:32/TBDI2:30A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | - | -
C2-S03-P00 | C2 | 3 | 0 | 1 | 1756-IB32 | XA-FH-60210A_DI_1 | Pin 1 | C2S3:1/TBDI3:1A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210A |  | - | BMS PANEL POWER ON for AHTR-21
C2-S03-P01 | C2 | 3 | 1 | 2 | 1756-IB32 | XA-FH-60210B_DI_1 | Pin 2 | C2S3:2/TBDI3:2A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210B |  | - | BMS Burner High Fire Purge for AHTR-21
C2-S03-P02 | C2 | 3 | 2 | 3 | 1756-IB32 | XA-FH-60210C_DI_1 | Pin 3 | C2S3:3/TBDI3:3A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210C |  | - | BMS Burner On for AHTR-21
C2-S03-P03 | C2 | 3 | 3 | 4 | 1756-IB32 | XA-FH-60210D_DI_1 | Pin 4 | C2S3:4/TBDI3:4A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210D |  | - | BMS BMS Lockout for AHTR-21
C2-S03-P04 | C2 | 3 | 4 | 5 | 1756-IB32 | XA-FH-60210E_DI_1 | Pin 5 | C2S3:5/TBDI3:5A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210E |  | - | BMS Remote Modet for AHTR-21
C2-S03-P08 | C2 | 3 | 8 | 9 | 1756-IB32 | SV-60207_DI_1 | Pin 9 | C2S3:9/TBDI3:9A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | SV-60207 |  | 3-25-01-602-PD-07 | Instr. Air On/Off Valve for Camera #4 (ACAM-21)
C2-S03-P09 | C2 | 3 | 9 | 10 | 1756-IB32 | SV-60207_DI_2 | Pin 10 | C2S3:10/TBDI3:10A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | SV-60207 |  | 3-25-01-602-PD-07 | Instr. Air On/Off Valve for Camera #4 (ACAM-21)
C2-S03-P10 | C2 | 3 | 10 | 11 | 1756-IB32 | XV-60264_DI_1 | Pin 11 | C2S3:11/TBDI3:11A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264 |  | - | -
C2-S03-P11 | C2 | 3 | 11 | 12 | 1756-IB32 | XV-60264_DI_2 | Pin 12 | C2S3:12/TBDI3:12A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264 |  | - | -
C2-S03-P12 | C2 | 3 | 12 | 13 | 1756-IB32 | XV-60264FN_DI_1 | Pin 13 | C2S3:13/TBDI3:13A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264FN |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D)
C2-S03-P13 | C2 | 3 | 13 | 14 | 1756-IB32 | XV-60264FN_DI_2 | Pin 14 | C2S3:14/TBDI3:14A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264FN |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D)
C2-S03-P14 | C2 | 3 | 14 | 15 | 1756-IB32 | XV-60264FP_DI_1 | Pin 15 | C2S3:15/TBDI3:15A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264FP |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D)
C2-S03-P15 | C2 | 3 | 15 | 16 | 1756-IB32 | XV-60264FP_DI_2 | Pin 16 | C2S3:16/TBDI3:16A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264FP |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D)
C2-S03-P16 | C2 | 3 | 16 | 17 | 1756-IB32 | XV-60201_DI_1 | Pin 17 | C2S3:17/C2S03-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60201 |  | 3-25-01-602-PD-02 | Steam feed to Spray dryer
C2-S03-P17 | C2 | 3 | 17 | 18 | 1756-IB32 | XV-60201_DI_2 | Pin 18 | C2S3:18/C2S03-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60201 |  | 3-25-01-602-PD-02 | Steam feed to Spray dryer
C2-S03-P18 | C2 | 3 | 18 | 19 | 1756-IB32 | XV-60264FQ_DI_1 | Pin 19 | C2S3:19/TBDI3:17A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264FQ |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D)
C2-S03-P19 | C2 | 3 | 19 | 20 | 1756-IB32 | XV-60264FQ_DI_2 | Pin 20 | C2S3:20/TBDI3:18A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264FQ |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D)
C2-S03-P20 | C2 | 3 | 20 | 21 | 1756-IB32 | XV-60261_DI_1 | Pin 21 | C2S3:21/TBDI3:19A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261 |  | - | -
C2-S03-P21 | C2 | 3 | 21 | 22 | 1756-IB32 | XV-60261_DI_2 | Pin 22 | C2S3:22/TBDI3:20A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261 |  | - | -
C2-S03-P22 | C2 | 3 | 22 | 23 | 1756-IB32 | XV-60264FR_DI_1 | Pin 23 | C2S3:23/TBDI3:21A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264FR |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D)
C2-S03-P23 | C2 | 3 | 23 | 24 | 1756-IB32 | XV-60264FR_DI_2 | Pin 24 | C2S3:24/TBDI3:22A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264FR |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D)
C2-S03-P24 | C2 | 3 | 24 | 25 | 1756-IB32 | XV-60261FA_DI_1 | Pin 25 | C2S3:25/TBDI3:23A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261FA |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A)
C2-S03-P25 | C2 | 3 | 25 | 26 | 1756-IB32 | XV-60261FA_DI_2 | Pin 26 | C2S3:26/TBDI3:24A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261FA |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A)
C2-S03-P26 | C2 | 3 | 26 | 27 | 1756-IB32 | XV-60264SN_DI_1 | Pin 27 | C2S3:27/TBDI3:25A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264SN |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #13 (ATVM-11D)
C2-S03-P27 | C2 | 3 | 27 | 28 | 1756-IB32 | XV-60264SN_DI_2 | Pin 28 | C2S3:28/TBDI3:26A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264SN |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #13 (ATVM-11D)
C2-S03-P28 | C2 | 3 | 28 | 29 | 1756-IB32 | XV-60261FB_DI_1 | Pin 29 | C2S3:29/TBDI3:27A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261FB |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A)
C2-S03-P29 | C2 | 3 | 29 | 30 | 1756-IB32 | XV-60261FB_DI_2 | Pin 30 | C2S3:30/TBDI3:28A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261FB |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A)
C2-S03-P30 | C2 | 3 | 30 | 31 | 1756-IB32 | XV-60264SP_DI_1 | Pin 31 | C2S3:31/TBDI3:29A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264SP |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #14 (ATVM-11D)
C2-S03-P31 | C2 | 3 | 31 | 32 | 1756-IB32 | XV-60264SP_DI_2 | Pin 32 | C2S3:32/TBDI3:30A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264SP |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #14 (ATVM-11D)
C2-S04-P00 | C2 | 4 | 0 | 1 | 1756-IB32 | XV-60261FC_DI_1 | Pin 1 | C2S4:1/RL.1:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261FC |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A)
C2-S04-P01 | C2 | 4 | 1 | 2 | 1756-IB32 | XV-60261FC_DI_2 | Pin 2 | C2S4:2/RL.2:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261FC |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A)
C2-S04-P02 | C2 | 4 | 2 | 3 | 1756-IB32 | XV-60264SQ_DI_1 | Pin 3 | C2S4:3/RL.3:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60264SQ |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #15 (ATVM-11D)
C2-S04-P03 | C2 | 4 | 3 | 4 | 1756-IB32 | XV-60264SQ_DI_2 | Pin 4 | C2S4:4/RL.4:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60264SQ |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #15 (ATVM-11D)
C2-S04-P04 | C2 | 4 | 4 | 5 | 1756-IB32 | XV-60261FD_DI_1 | Pin 5 | C2S4:5/RL.5:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261FD |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A)
C2-S04-P05 | C2 | 4 | 5 | 6 | 1756-IB32 | XV-60261FD_DI_2 | Pin 6 | C2S4:6/RL.6:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261FD |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A)
C2-S04-P06 | C2 | 4 | 6 | 7 | 1756-IB32 | XV-60264SR_DI_1 | Pin 7 | C2S4:7/RL.7:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60264SR |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #16 (ATVM-11D)
C2-S04-P07 | C2 | 4 | 7 | 8 | 1756-IB32 | XV-60264SR_DI_2 | Pin 8 | C2S4:8/RL.8:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60264SR |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #16 (ATVM-11D)
C2-S04-P08 | C2 | 4 | 8 | 9 | 1756-IB32 | XV-60261SA_DI_1 | Pin 9 | C2S4:9/RL.9:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SA |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #1 (ATVM-11A)
C2-S04-P09 | C2 | 4 | 9 | 10 | 1756-IB32 | XV-60261SA_DI_2 | Pin 10 | C2S4:10/RL.10:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SA |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #1 (ATVM-11A)
C2-S04-P10 | C2 | 4 | 10 | 11 | 1756-IB32 | XV-60261SB_DI_1 | Pin 11 | C2S4:11/RL.11:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SB |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #2 (ATVM-11A)
C2-S04-P11 | C2 | 4 | 11 | 12 | 1756-IB32 | XV-60261SB_DI_2 | Pin 12 | C2S4:12/RL.12:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SB |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #2 (ATVM-11A)
C2-S04-P12 | C2 | 4 | 12 | 13 | 1756-IB32 | XV-60261SC_DI_1 | Pin 13 | C2S4:13/RL.13:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SC |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #3 (ATVM-11A)
C2-S04-P13 | C2 | 4 | 13 | 14 | 1756-IB32 | XV-60261SC_DI_2 | Pin 14 | C2S4:14/RL.14:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SC |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #3 (ATVM-11A)
C2-S04-P14 | C2 | 4 | 14 | 15 | 1756-IB32 | XV-60261SD_DI_1 | Pin 15 | C2S4:15/RL.15:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SD |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #4 (ATVM-11A)
C2-S04-P15 | C2 | 4 | 15 | 16 | 1756-IB32 | XV-60261SD_DI_2 | Pin 16 | C2S4:16/RL.16:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SD |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #4 (ATVM-11A)
C2-S04-P16 | C2 | 4 | 16 | 17 | 1756-IB32 | XV-60262_DI_1 | Pin 17 | C2S4:17/C2S04-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262 |  | - | -
C2-S04-P17 | C2 | 4 | 17 | 18 | 1756-IB32 | XV-60262_DI_2 | Pin 18 | C2S4:18/C2S04-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262 |  | - | -
C2-S04-P18 | C2 | 4 | 18 | 19 | 1756-IB32 | XV-60262FE_DI_1 | Pin 19 | C2S4:19/RL.17:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FE |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B)
C2-S04-P19 | C2 | 4 | 19 | 20 | 1756-IB32 | XV-60262FE_DI_2 | Pin 20 | C2S4:20/RL.18:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FE |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B)
C2-S04-P20 | C2 | 4 | 20 | 21 | 1756-IB32 | XV-60262FF_DI_1 | Pin 21 | C2S4:21/RL.19:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FF |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B)
C2-S04-P21 | C2 | 4 | 21 | 22 | 1756-IB32 | XV-60262FF_DI_2 | Pin 22 | C2S4:22/RL.20:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FF |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B)
C2-S04-P22 | C2 | 4 | 22 | 23 | 1756-IB32 | XV-60262FG_DI_1 | Pin 23 | C2S4:23/RL.21:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FG |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B)
C2-S04-P23 | C2 | 4 | 23 | 24 | 1756-IB32 | XV-60262FG_DI_2 | Pin 24 | C2S4:24/RL.22:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FG |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B)
C2-S04-P24 | C2 | 4 | 24 | 25 | 1756-IB32 | XV-60262FH_DI_1 | Pin 25 | C2S4:25/RL.23:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FH |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B)
C2-S04-P25 | C2 | 4 | 25 | 26 | 1756-IB32 | XV-60262FH_DI_2 | Pin 26 | C2S4:26/RL.24:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FH |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B)
C2-S04-P26 | C2 | 4 | 26 | 27 | 1756-IB32 | XV-60262SE_DI_1 | Pin 27 | C2S4:27/RL.25:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SE |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #5 (ATVM-11B)
C2-S04-P27 | C2 | 4 | 27 | 28 | 1756-IB32 | XV-60262SE_DI_2 | Pin 28 | C2S4:28/RL.26:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SE |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #5 (ATVM-11B)
C2-S04-P28 | C2 | 4 | 28 | 29 | 1756-IB32 | XV-60262SF_DI_1 | Pin 29 | C2S4:29/RL.27:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SF |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #6 (ATVM-11B)
C2-S04-P29 | C2 | 4 | 29 | 30 | 1756-IB32 | XV-60262SF_DI_2 | Pin 30 | C2S4:30/RL.28:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SF |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #6 (ATVM-11B)
C2-S04-P30 | C2 | 4 | 30 | 31 | 1756-IB32 | XV-60262SG_DI_1 | Pin 31 | C2S4:31/RL.29:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SG |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #7 (ATVM-11B)
C2-S04-P31 | C2 | 4 | 31 | 32 | 1756-IB32 | XV-60262SG_DI_2 | Pin 32 | C2S4:32/RL.30:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SG |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #7 (ATVM-11B)
C2-S05-P00 | C2 | 5 | 0 | 1 | 1756-IB32 | XV-60262SH_DI_1 | Pin 1 | C2S5:1/RL.33:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60262SH |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #8 (ATVM-11B)
C2-S05-P01 | C2 | 5 | 1 | 2 | 1756-IB32 | XV-60262SH_DI_2 | Pin 2 | C2S5:2/RL.34:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60262SH |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #8 (ATVM-11B)
C2-S05-P02 | C2 | 5 | 2 | 3 | 1756-IB32 | XV-60263_DI_1 | Pin 3 | C2S5:3/RL.35:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263 |  | - | -
C2-S05-P03 | C2 | 5 | 3 | 4 | 1756-IB32 | XV-60263_DI_2 | Pin 4 | C2S5:4/RL.36:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263 |  | - | -
C2-S05-P04 | C2 | 5 | 4 | 5 | 1756-IB32 | XV-60263FJ_DI_1 | Pin 5 | C2S5:5/RL.37:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FJ |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C)
C2-S05-P05 | C2 | 5 | 5 | 6 | 1756-IB32 | XV-60263FJ_DI_2 | Pin 6 | C2S5:6/RL.38:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FJ |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C)
C2-S05-P06 | C2 | 5 | 6 | 7 | 1756-IB32 | XV-60263FK_DI_1 | Pin 7 | C2S5:7/RL.39:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FK |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C)
C2-S05-P07 | C2 | 5 | 7 | 8 | 1756-IB32 | XV-60263FK_DI_2 | Pin 8 | C2S5:8/RL.40:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FK |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C)
C2-S05-P08 | C2 | 5 | 8 | 9 | 1756-IB32 | XV-60263FL_DI_1 | Pin 9 | C2S5:9/RL.41:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FL |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C)
C2-S05-P09 | C2 | 5 | 9 | 10 | 1756-IB32 | XV-60263FL_DI_2 | Pin 10 | C2S5:10/RL.42:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FL |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C)
C2-S05-P10 | C2 | 5 | 10 | 11 | 1756-IB32 | XV-60263FM_DI_1 | Pin 11 | C2S5:11/RL.43:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FM |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C)
C2-S05-P11 | C2 | 5 | 11 | 12 | 1756-IB32 | XV-60263FM_DI_2 | Pin 12 | C2S5:12/RL.44:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FM |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C)
C2-S05-P12 | C2 | 5 | 12 | 13 | 1756-IB32 | XV-60263SJ_DI_1 | Pin 13 | C2S5:13/RL.45:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263SJ |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #9 (ATVM-11C)
C2-S05-P13 | C2 | 5 | 13 | 14 | 1756-IB32 | XV-60263SJ_DI_2 | Pin 14 | C2S5:14/RL.46:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263SJ |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #9 (ATVM-11C)
C2-S05-P14 | C2 | 5 | 14 | 15 | 1756-IB32 | XV-60263SK_DI_1 | Pin 15 | C2S5:15/RL.47:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263SK |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #10 (ATVM-11C)
C2-S05-P15 | C2 | 5 | 15 | 16 | 1756-IB32 | XV-60263SK_DI_2 | Pin 16 | C2S5:16/RL.48:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263SK |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #10 (ATVM-11C)
C2-S05-P16 | C2 | 5 | 16 | 17 | 1756-IB32 | XV-60263SL_DI_1 | Pin 17 | C2S5:17/C2S05-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X2 | - | XV-60263SL |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #11 (ATVM-11C)
C2-S05-P17 | C2 | 5 | 17 | 18 | 1756-IB32 | XV-60263SL_DI_2 | Pin 18 | C2S5:18/C2S05-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X2 | - | XV-60263SL |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #11 (ATVM-11C)
C2-S05-P18 | C2 | 5 | 18 | 19 | 1756-IB32 | XV-60263SM_DI_1 | Pin 19 | C2S5:19/RL.49:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X2 | - | XV-60263SM |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #12 (ATVM-11C)
C2-S05-P19 | C2 | 5 | 19 | 20 | 1756-IB32 | XV-60263SM_DI_2 | Pin 20 | C2S5:20/RL.50:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X2 | - | XV-60263SM |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #12 (ATVM-11C)
C2-S05-P20 | C2 | 5 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C2S5:21/RL.51:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | - | -
C2-S05-P21 | C2 | 5 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C2S5:22/RL.52:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | - | -
C2-S05-P22 | C2 | 5 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C2S5:23/RL.53:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | - | -
C2-S05-P23 | C2 | 5 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C2S5:24/RL.54:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | - | -
C2-S05-P24 | C2 | 5 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C2S5:25/RL.55:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | - | -
C2-S05-P25 | C2 | 5 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C2S5:26/RL.56:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | - | -
C2-S05-P26 | C2 | 5 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C2S5:27/RL.57:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | - | -
C2-S05-P27 | C2 | 5 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C2S5:28/RL.58:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | - | -
C2-S05-P28 | C2 | 5 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C2S5:29/RL.59:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | - | -
C2-S05-P29 | C2 | 5 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C2S5:30/RL.60:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | - | -
C2-S05-P30 | C2 | 5 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C2S5:31/RL.61:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | - | -
C2-S05-P31 | C2 | 5 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C2S5:32/RL.62:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | - | -
C2-S06-P00 | C2 | 6 | 0 | 1 | 1756-OB32 | XV-40203F_DO_1 | Pin 1 | C2S6:1/RL.33:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40203F |  | 325-01-402-PD-02 | Jet Cooker
C2-S06-P01 | C2 | 6 | 1 | 2 | 1756-OB32 | XV-40204B_DO_1 | Pin 2 | C2S6:2/RL.34:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40204B |  | 325-01-402-PD-01 | Jet Cooker
C2-S06-P02 | C2 | 6 | 2 | 3 | 1756-OB32 | XV-40204C_DO_1 | Pin 3 | C2S6:3/RL.35:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40204C |  | 325-01-402-PD-01 | Jet Cooker
C2-S06-P03 | C2 | 6 | 3 | 4 | 1756-OB32 | XV-40205A_DO_1 | Pin 4 | C2S6:4/RL.36:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205A |  | 325-01-402-PD-02 | Jet Cooker
C2-S06-P04 | C2 | 6 | 4 | 5 | 1756-OB32 | XV-40205B_DO_1 | Pin 5 | C2S6:5/RL.37:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205B |  | 325-01-402-PD-02 | Jet Cooker
C2-S06-P05 | C2 | 6 | 5 | 6 | 1756-OB32 | XV-40205C_DO_1 | Pin 6 | C2S6:6/RL.38:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205C |  | 325-01-402-PD-02 | Jet Cooker
C2-S06-P06 | C2 | 6 | 6 | 7 | 1756-OB32 | XV-40205D_DO_1 | Pin 7 | C2S6:7/RL.39:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205D |  | 325-01-402-PD-02 | Jet Cooker
C2-S06-P07 | C2 | 6 | 7 | 8 | 1756-OB32 | XV-40205F_DO_1 | Pin 8 | C2S6:8/RL.40:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205F |  | 325-01-402-PD-02 | Jet Cooker
C2-S06-P08 | C2 | 6 | 8 | 9 | 1756-OB32 | XV-40222_DO_1 | Pin 9 | C2S6:9/RL.41:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40222 |  | 325-01-402-PD-02 | Jet Cooker
C2-S06-P09 | C2 | 6 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C2S6:10/RL.42:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | - | -
C2-S06-P10 | C2 | 6 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C2S6:11/RL.43:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | - | -
C2-S06-P11 | C2 | 6 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C2S6:12/RL.44:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | - | -
C2-S06-P12 | C2 | 6 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C2S6:13/RL.45:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | - | -
C2-S06-P13 | C2 | 6 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C2S6:14/RL.46:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | - | -
C2-S06-P14 | C2 | 6 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C2S6:15/RL.47:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | - | -
C2-S06-P15 | C2 | 6 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C2S6:16/RL.48:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | - | -
C2-S06-P16 | C2 | 6 | 16 | 17 | 1756-OB32 | XS-60240B_DO_1 | Pin 17 | C2S6:17/C2S06-X2:17 | DO | 24VDC Sourcing | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S06-X2 | - | XS-60240B |  | - | Fan Command for BGHS-21 (Bag House Air Pulsing)
C2-S06-P17 | C2 | 6 | 17 | 18 | 1756-OB32 | XV-60214_DO_1 | Pin 18 | C2S6:18/C2S06-X2:18 | DO | 24VDC Sourcing | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S06-X2 | - | XV-60214 |  | 3-25-01-602-PD-03 | Steam feed to Spray dryer
C2-S06-P18 | C2 | 6 | 18 | 19 | 1756-OB32 | XV-60241_DO_1 | Pin 19 | C2S6:19/RL.49:A1 | DO | 24VDC Sourcing | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S06-X2 | - | XV-60241 |  | 3-25-01-602-PD-05 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22)
C2-S06-P19 | C2 | 6 | 19 | 20 | 1756-OB32 | Spare_DO_0 | Pin 20 | C2S6:20/RL.50:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | - | -
C2-S06-P20 | C2 | 6 | 20 | 21 | 1756-OB32 | Spare_DO_0 | Pin 21 | C2S6:21/RL.51:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | - | -
C2-S06-P21 | C2 | 6 | 21 | 22 | 1756-OB32 | Spare_DO_0 | Pin 22 | C2S6:22/RL.52:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | - | -
C2-S06-P22 | C2 | 6 | 22 | 23 | 1756-OB32 | Spare_DO_0 | Pin 23 | C2S6:23/RL.53:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | - | -
C2-S06-P23 | C2 | 6 | 23 | 24 | 1756-OB32 | Spare_DO_0 | Pin 24 | C2S6:24/RL.54:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | - | -
C2-S06-P24 | C2 | 6 | 24 | 25 | 1756-OB32 | Spare_DO_0 | Pin 25 | C2S6:25/RL.55:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | - | -
C2-S06-P25 | C2 | 6 | 25 | 26 | 1756-OB32 | Spare_DO_0 | Pin 26 | C2S6:26/RL.56:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | - | -
C2-S06-P26 | C2 | 6 | 26 | 27 | 1756-OB32 | Spare_DO_0 | Pin 27 | C2S6:27/RL.57:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | - | -
C2-S06-P27 | C2 | 6 | 27 | 28 | 1756-OB32 | Spare_DO_0 | Pin 28 | C2S6:28/RL.58:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | - | -
C2-S06-P28 | C2 | 6 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C2S6:29/RL.59:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | - | -
C2-S06-P29 | C2 | 6 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C2S6:30/RL.60:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | - | -
C2-S06-P30 | C2 | 6 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C2S6:31/RL.61:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | - | -
C2-S06-P31 | C2 | 6 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C2S6:32/RL.62:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | - | -
C2-S07-P00 | C2 | 7 | 0 | 1 | 1756-OB32 | SV-60207_DO_1 | Pin 1 | C2S7:1/C2S07-X1:1 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | SV-60207 |  | 3-25-01-602-PD-07 | Instr. Air On/Off Valve for Camera #4 (ACAM-21)
C2-S07-P01 | C2 | 7 | 1 | 2 | 1756-OB32 | XS-FH-60210C_DO_1 | Pin 2 | C2S7:2/C2S07-X1:2 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XS-FH-60210C |  | - | Command Remote Reset for AHTR-21
C2-S07-P02 | C2 | 7 | 2 | 3 | 1756-OB32 | XS-FH-60210D_DO_1 | Pin 3 | C2S7:3/C2S07-X1:3 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XS-FH-60210D |  | - | Spare
C2-S07-P03 | C2 | 7 | 3 | 4 | 1756-OB32 | XV-60201_DO_1 | Pin 4 | C2S7:4/C2S07-X1:4 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60201 |  | 3-25-01-602-PD-02 | Steam feed to Spray dryer
C2-S07-P04 | C2 | 7 | 4 | 5 | 1756-OB32 | XV-60261_DO_1 | Pin 5 | C2S7:5/C2S07-X1:5 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261 |  | - | -
C2-S07-P05 | C2 | 7 | 5 | 6 | 1756-OB32 | XV-60261FA_DO_1 | Pin 6 | C2S7:6/C2S07-X1:6 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261FA |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A)
C2-S07-P06 | C2 | 7 | 6 | 7 | 1756-OB32 | XV-60261FB_DO_1 | Pin 7 | C2S7:7/C2S07-X1:7 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261FB |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A)
C2-S07-P07 | C2 | 7 | 7 | 8 | 1756-OB32 | XV-60261FC_DO_1 | Pin 8 | C2S7:8/C2S07-X1:8 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261FC |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A)
C2-S07-P08 | C2 | 7 | 8 | 9 | 1756-OB32 | XV-60261FD_DO_1 | Pin 9 | C2S7:9/C2S07-X1:9 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261FD |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A)
C2-S07-P09 | C2 | 7 | 9 | 10 | 1756-OB32 | XV-60261SA_DO_1 | Pin 10 | C2S7:10/C2S07-X1:10 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261SA |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #1 (ATVM-11A)
C2-S07-P10 | C2 | 7 | 10 | 11 | 1756-OB32 | XV-60261SB_DO_1 | Pin 11 | C2S7:11/C2S07-X1:11 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261SB |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #2 (ATVM-11A)
C2-S07-P11 | C2 | 7 | 11 | 12 | 1756-OB32 | XV-60261SC_DO_1 | Pin 12 | C2S7:12/C2S07-X1:12 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261SC |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #3 (ATVM-11A)
C2-S07-P12 | C2 | 7 | 12 | 13 | 1756-OB32 | XV-60261SD_DO_1 | Pin 13 | C2S7:13/C2S07-X1:13 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261SD |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #4 (ATVM-11A)
C2-S07-P13 | C2 | 7 | 13 | 14 | 1756-OB32 | XV-60262_DO_1 | Pin 14 | C2S7:14/C2S07-X1:14 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60262 |  | - | -
C2-S07-P14 | C2 | 7 | 14 | 15 | 1756-OB32 | XV-60262FE_DO_1 | Pin 15 | C2S7:15/C2S07-X1:15 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60262FE |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B)
C2-S07-P15 | C2 | 7 | 15 | 16 | 1756-OB32 | XV-60262FF_DO_1 | Pin 16 | C2S7:16/C2S07-X1:16 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60262FF |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B)
C2-S07-P16 | C2 | 7 | 16 | 17 | 1756-OB32 | XV-60262FG_DO_1 | Pin 17 | C2S7:17/C2S07-X2:17 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262FG |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B)
C2-S07-P17 | C2 | 7 | 17 | 18 | 1756-OB32 | XV-60262FH_DO_1 | Pin 18 | C2S7:18/C2S07-X2:18 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262FH |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B)
C2-S07-P18 | C2 | 7 | 18 | 19 | 1756-OB32 | XV-60262SE_DO_1 | Pin 19 | C2S7:19/C2S07-X2:19 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262SE |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #5 (ATVM-11B)
C2-S07-P19 | C2 | 7 | 19 | 20 | 1756-OB32 | XV-60262SF_DO_1 | Pin 20 | C2S7:20/C2S07-X2:20 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262SF |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #6 (ATVM-11B)
C2-S07-P20 | C2 | 7 | 20 | 21 | 1756-OB32 | XV-60262SG_DO_1 | Pin 21 | C2S7:21/C2S07-X2:21 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262SG |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #7 (ATVM-11B)
C2-S07-P21 | C2 | 7 | 21 | 22 | 1756-OB32 | XV-60262SH_DO_1 | Pin 22 | C2S7:22/C2S07-X2:22 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262SH |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #8 (ATVM-11B)
C2-S07-P22 | C2 | 7 | 22 | 23 | 1756-OB32 | XV-60263_DO_1 | Pin 23 | C2S7:23/C2S07-X2:23 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263 |  | - | -
C2-S07-P23 | C2 | 7 | 23 | 24 | 1756-OB32 | XV-60263FJ_DO_1 | Pin 24 | C2S7:24/C2S07-X2:24 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263FJ |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C)
C2-S07-P24 | C2 | 7 | 24 | 25 | 1756-OB32 | XV-60263FK_DO_1 | Pin 25 | C2S7:25/C2S07-X2:25 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263FK |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C)
C2-S07-P25 | C2 | 7 | 25 | 26 | 1756-OB32 | XV-60263FL_DO_1 | Pin 26 | C2S7:26/C2S07-X2:26 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263FL |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C)
C2-S07-P26 | C2 | 7 | 26 | 27 | 1756-OB32 | XV-60263FM_DO_1 | Pin 27 | C2S7:27/C2S07-X2:27 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263FM |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C)
C2-S07-P27 | C2 | 7 | 27 | 28 | 1756-OB32 | XV-60263SJ_DO_1 | Pin 28 | C2S7:28/C2S07-X2:28 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263SJ |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #9 (ATVM-11C)
C2-S07-P28 | C2 | 7 | 28 | 29 | 1756-OB32 | XV-60263SK_DO_1 | Pin 29 | C2S7:29/C2S07-X2:29 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263SK |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #10 (ATVM-11C)
C2-S07-P29 | C2 | 7 | 29 | 30 | 1756-OB32 | XV-60263SL_DO_1 | Pin 30 | C2S7:30/C2S07-X2:30 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263SL |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #11 (ATVM-11C)
C2-S07-P30 | C2 | 7 | 30 | 31 | 1756-OB32 | XV-60263SM_DO_1 | Pin 31 | C2S7:31/C2S07-X2:31 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263SM |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #12 (ATVM-11C)
C2-S07-P31 | C2 | 7 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C2S7:32/C2S07-X2:32 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S07-X2 | - | Spare | Spare Channel | - | -
C2-S08-P00 | C2 | 8 | 0 | 1 | 1756-OB32 | XV-60264_DO_1 | Pin 1 | C2S8:1/C2S08-X1:1 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264 |  | - | -
C2-S08-P01 | C2 | 8 | 1 | 2 | 1756-OB32 | XV-60264FN_DO_1 | Pin 2 | C2S8:2/C2S08-X1:2 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264FN |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D)
C2-S08-P02 | C2 | 8 | 2 | 3 | 1756-OB32 | XV-60264FP_DO_1 | Pin 3 | C2S8:3/C2S08-X1:3 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264FP |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D)
C2-S08-P03 | C2 | 8 | 3 | 4 | 1756-OB32 | XV-60264FQ_DO_1 | Pin 4 | C2S8:4/C2S08-X1:4 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264FQ |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D)
C2-S08-P04 | C2 | 8 | 4 | 5 | 1756-OB32 | XV-60264FR_DO_1 | Pin 5 | C2S8:5/C2S08-X1:5 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264FR |  | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D)
C2-S08-P05 | C2 | 8 | 5 | 6 | 1756-OB32 | XV-60264SN_DO_1 | Pin 6 | C2S8:6/C2S08-X1:6 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264SN |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #13 (ATVM-11D)
C2-S08-P06 | C2 | 8 | 6 | 7 | 1756-OB32 | XV-60264SP_DO_1 | Pin 7 | C2S8:7/C2S08-X1:7 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264SP |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #14 (ATVM-11D)
C2-S08-P07 | C2 | 8 | 7 | 8 | 1756-OB32 | XV-60264SQ_DO_1 | Pin 8 | C2S8:8/C2S08-X1:8 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264SQ |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #15 (ATVM-11D)
C2-S08-P08 | C2 | 8 | 8 | 9 | 1756-OB32 | XV-60264SR_DO_1 | Pin 9 | C2S8:9/C2S08-X1:9 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264SR |  | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #16 (ATVM-11D)
C2-S08-P09 | C2 | 8 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C2S8:10/C2S08-X1:10 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | - | -
C2-S08-P10 | C2 | 8 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C2S8:11/C2S08-X1:11 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | - | -
C2-S08-P11 | C2 | 8 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C2S8:12/C2S08-X1:12 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | - | -
C2-S08-P12 | C2 | 8 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C2S8:13/C2S08-X1:13 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | - | -
C2-S08-P13 | C2 | 8 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C2S8:14/C2S08-X1:14 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | - | -
C2-S08-P14 | C2 | 8 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C2S8:15/C2S08-X1:15 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | - | -
C2-S08-P15 | C2 | 8 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C2S8:16/C2S08-X1:16 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | - | -
C2-S08-P16 | C2 | 8 | 16 | 17 | 1756-OB32 | Spare_DO_0 | Pin 17 | C2S8:17/C2S08-X2:17 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P17 | C2 | 8 | 17 | 18 | 1756-OB32 | Spare_DO_0 | Pin 18 | C2S8:18/C2S08-X2:18 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P18 | C2 | 8 | 18 | 19 | 1756-OB32 | Spare_DO_0 | Pin 19 | C2S8:19/C2S08-X2:19 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P19 | C2 | 8 | 19 | 20 | 1756-OB32 | Spare_DO_0 | Pin 20 | C2S8:20/C2S08-X2:20 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P20 | C2 | 8 | 20 | 21 | 1756-OB32 | Spare_DO_0 | Pin 21 | C2S8:21/C2S08-X2:21 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P21 | C2 | 8 | 21 | 22 | 1756-OB32 | Spare_DO_0 | Pin 22 | C2S8:22/C2S08-X2:22 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P22 | C2 | 8 | 22 | 23 | 1756-OB32 | Spare_DO_0 | Pin 23 | C2S8:23/C2S08-X2:23 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P23 | C2 | 8 | 23 | 24 | 1756-OB32 | Spare_DO_0 | Pin 24 | C2S8:24/C2S08-X2:24 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P24 | C2 | 8 | 24 | 25 | 1756-OB32 | Spare_DO_0 | Pin 25 | C2S8:25/C2S08-X2:25 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P25 | C2 | 8 | 25 | 26 | 1756-OB32 | Spare_DO_0 | Pin 26 | C2S8:26/C2S08-X2:26 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P26 | C2 | 8 | 26 | 27 | 1756-OB32 | Spare_DO_0 | Pin 27 | C2S8:27/C2S08-X2:27 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P27 | C2 | 8 | 27 | 28 | 1756-OB32 | Spare_DO_0 | Pin 28 | C2S8:28/C2S08-X2:28 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P28 | C2 | 8 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C2S8:29/C2S08-X2:29 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P29 | C2 | 8 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C2S8:30/C2S08-X2:30 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P30 | C2 | 8 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C2S8:31/C2S08-X2:31 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S08-P31 | C2 | 8 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C2S8:32/C2S08-X2:32 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | - | -
C2-S09-P00 | C2 | 9 | 0 | 1 | 1756-IF16 | FT-40221_AI_1 | Pin 1 | C2S9:1/C2S09-X1:1 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | FT-40221 | Coriolis Flow Transmitter | 325-01-402-PD-02 | Jet Cooker
C2-S09-P01 | C2 | 9 | 1 | 2 | 1756-IF16 | FT-40221_AI_2 | Pin 2 | C2S9:2/C2S09-X1:2 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | FT-40221 | Coriolis Flow Transmitter | 325-01-402-PD-02 | Jet Cooker
C2-S09-P02 | C2 | 9 | 2 | 3 | 1756-IF16 | FT-40222_AI_1 | Pin 3 | C2S9:3/C2S09-X1:3 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | FT-40222 | Coriolis Flow Transmitter | 325-01-402-PD-02 | Jet Cooker
C2-S09-P03 | C2 | 9 | 3 | 4 | 1756-IF16 | FT-40222_AI_2 | Pin 4 | C2S9:4/C2S09-X1:4 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | FT-40222 | Coriolis Flow Transmitter | 325-01-402-PD-02 | Jet Cooker
C2-S09-P04 | C2 | 9 | 4 | 5 | 1756-IF16 | PT-40222_AI_1 | Pin 5 | C2S9:5/C2S09-X1:5 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | PT-40222 | Pressure Transmitter | 325-01-402-PD-02 | Jet Cooker
C2-S09-P05 | C2 | 9 | 5 | 6 | 1756-IF16 | TT-40221_AI_1 | Pin 6 | C2S9:6/C2S09-X1:6 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | TT-40221 |  | 325-01-402-PD-02 | Jet Cooker
C2-S09-P06 | C2 | 9 | 6 | 7 | 1756-IF16 | TT-40222_AI_1 | Pin 7 | C2S9:7/C2S09-X1:7 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | TT-40222 |  | 325-01-402-PD-02 | Jet Cooker
C2-S09-P07 | C2 | 9 | 7 | 8 | 1756-IF16 | Spare_AI_0 | Pin 8 | C2S9:8/C2S09-X1:8 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | - | -
C2-S09-P08 | C2 | 9 | 8 | 9 | 1756-IF16 | Spare_AI_0 | Pin 9 | C2S9:9/C2S09-X1:9 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | - | -
C2-S09-P09 | C2 | 9 | 9 | 10 | 1756-IF16 | Spare_AI_0 | Pin 10 | C2S9:10/C2S09-X1:10 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | - | -
C2-S09-P10 | C2 | 9 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C2S9:11/C2S09-X1:11 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | - | -
C2-S09-P11 | C2 | 9 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C2S9:12/C2S09-X1:12 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | - | -
C2-S09-P12 | C2 | 9 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C2S9:13/C2S09-X1:13 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | - | -
C2-S09-P13 | C2 | 9 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C2S9:14/C2S09-X1:14 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | - | -
C2-S09-P14 | C2 | 9 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C2S9:15/C2S09-X1:15 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | - | -
C2-S09-P15 | C2 | 9 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C2S9:16/C2S09-X1:16 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | - | -
C2-S10-P00 | C2 | 10 | 0 | 1 | 1756-IF16 | AT-60241_AI_1 | Pin 1 | C2S10:1/C2S10-X1:1 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | AT-60241 | Dust Analyzer Transmitter | 3-25-01-602-PD-05 | Dust Analyzer Transmitter for Exhaust Duct (DTEX-22)
C2-S10-P01 | C2 | 10 | 1 | 2 | 1756-IF16 | DPT-60203_AI_1 | Pin 2 | C2S10:2/C2S10-X1:2 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | DPT-60203 | Differential Pressure Transmitte | 3-25-01-602-PD-03 | Gas Pressure Differential Transmitter for Air Filter (FICA-21)
C2-S10-P02 | C2 | 10 | 2 | 3 | 1756-IF16 | FT-60202_AI_1 | Pin 3 | C2S10:3/C2S10-X1:3 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | FT-60202 |  | 3-25-01-602-PD-09 | Steam feed to Spray dryer
C2-S10-P03 | C2 | 10 | 3 | 4 | 1756-IF16 | PT-60210_AI_1 | Pin 4 | C2S10:4/C2S10-X1:4 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60210 | Pressure Transmitter | 3-25-01-602-PD-03 | Gas Pressure Transmitter for Hot Air Duct (DTHA-21)
C2-S10-P04 | C2 | 10 | 4 | 5 | 1756-IF16 | PT-60215_AI_1 | Pin 5 | C2S10:5/C2S10-X1:5 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60215 | Pressure Transmitter | 3-25-01-602-PD-03 | 15% Polypropylene Glycol Pressure Indicator Transmitter for Heat Recovery Pumping Skid (PUCF-21)
C2-S10-P05 | C2 | 10 | 5 | 6 | 1756-IF16 | PT-60216_AI_1 | Pin 6 | C2S10:6/C2S10-X1:6 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60216 | Pressure Transmitter | 3-25-01-602-PD-03 | Gas Pressure Transmitter for Combustion Air Burner Duct (DTCB-21)
C2-S10-P06 | C2 | 10 | 6 | 7 | 1756-IF16 | PT-60240_AI_1 | Pin 7 | C2S10:7/C2S10-X1:7 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60240 | Pressure Transmitter | 3-25-01-602-PD-05 | Gas Pressure Transmitter for Bag House Exhaust Duct (DTEX-22)
C2-S10-P07 | C2 | 10 | 7 | 8 | 1756-IF16 | PT-60241_AI_1 | Pin 8 | C2S10:8/C2S10-X1:8 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60241 | Pressure Transmitter | 3-25-01-602-PD-05 | Gas Pressure Transmitter for Exhaust Fan (FANE-21)
C2-S10-P08 | C2 | 10 | 8 | 9 | 1756-IF16 | TT-60210_AI_1 | Pin 9 | C2S10:9/C2S10-X1:9 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60210 |  | 3-25-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21)
C2-S10-P09 | C2 | 10 | 9 | 10 | 1756-IF16 | TT-60210A_AI_1 | Pin 10 | C2S10:10/C2S10-X1:10 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60210A |  | - | -
C2-S10-P10 | C2 | 10 | 10 | 11 | 1756-IF16 | TT-60210B_AI_1 | Pin 11 | C2S10:11/C2S10-X1:11 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60210B |  | - | -
C2-S10-P11 | C2 | 10 | 11 | 12 | 1756-IF16 | TT-60211_AI_1 | Pin 12 | C2S10:12/C2S10-X1:12 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60211 |  | 3-25-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21)
C2-S10-P12 | C2 | 10 | 12 | 13 | 1756-IF16 | TT-60212A_AI_1 | Pin 13 | C2S10:13/C2S10-X1:13 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60212A |  | 3-25-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21)
C2-S10-P13 | C2 | 10 | 13 | 14 | 1756-IF16 | TT-60212B_AI_1 | Pin 14 | C2S10:14/C2S10-X1:14 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60212B |  | 3-25-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21)
C2-S10-P14 | C2 | 10 | 14 | 15 | 1756-IF16 | TT-60214_AI_1 | Pin 15 | C2S10:15/C2S10-X1:15 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60214 |  | 3-25-01-602-PD-03 | Steam Temperature Transmitter for Cold Air Duct (DTCA-23)
C2-S10-P15 | C2 | 10 | 15 | 16 | 1756-IF16 | TT-60215A_AI_1 | Pin 16 | C2S10:16/C2S10-X1:16 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60215A |  | 3-25-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21)
C2-S11-P00 | C2 | 11 | 0 | 1 | 1756-IF16 | TT-60215B_AI_1 | Pin 1 | C2S11:1/C2S11-X1:1 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60215B |  | 3-25-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21)
C2-S11-P01 | C2 | 11 | 1 | 2 | 1756-IF16 | TT-60216_AI_1 | Pin 2 | C2S11:2/C2S11-X1:2 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60216 |  | 3-25-01-602-PD-03 | Gas Temperature Transmitter for Combustion Air Burner Duct (DTCB-21)
C2-S11-P02 | C2 | 11 | 2 | 3 | 1756-IF16 | TT-60240_AI_1 | Pin 3 | C2S11:3/C2S11-X1:3 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60240 |  | 3-25-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Fan (FANE-21)
C2-S11-P03 | C2 | 11 | 3 | 4 | 1756-IF16 | TT-60241A_AI_1 | Pin 4 | C2S11:4/C2S11-X1:4 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60241A |  | 3-25-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21)
C2-S11-P04 | C2 | 11 | 4 | 5 | 1756-IF16 | TT-60241B_AI_1 | Pin 5 | C2S11:5/C2S11-X1:5 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60241B |  | 3-25-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21)
C2-S11-P05 | C2 | 11 | 5 | 6 | 1756-IF16 | VT-60210A_AI_1 | Pin 6 | C2S11:6/C2S11-X1:6 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60210A |  | 3-25-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21)
C2-S11-P06 | C2 | 11 | 6 | 7 | 1756-IF16 | VT-60210B_AI_1 | Pin 7 | C2S11:7/C2S11-X1:7 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60210B |  | 3-25-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21)
C2-S11-P07 | C2 | 11 | 7 | 8 | 1756-IF16 | VT-60241A_AI_1 | Pin 8 | C2S11:8/C2S11-X1:8 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60241A |  | 3-25-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21)
C2-S11-P08 | C2 | 11 | 8 | 9 | 1756-IF16 | VT-60241B_AI_1 | Pin 9 | C2S11:9/C2S11-X1:9 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60241B |  | 3-25-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21)
C2-S11-P09 | C2 | 11 | 9 | 10 | 1756-IF16 | FT-60210_AI_1 | Pin 10 | C2S11:10/C2S11-X1:10 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60210 |  | 3-25-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B)
C2-S11-P10 | C2 | 11 | 10 | 11 | 1756-IF16 | FT-60211_AI_1 | Pin 11 | C2S11:11/C2S11-X1:11 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60211 |  | 3-25-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A)
C2-S11-P11 | C2 | 11 | 11 | 12 | 1756-IF16 | FT-60210_AI_2 | Pin 12 | C2S11:12/C2S11-X1:12 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60210 |  | 3-25-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B)
C2-S11-P12 | C2 | 11 | 12 | 13 | 1756-IF16 | FT-60211_AI_2 | Pin 13 | C2S11:13/C2S11-X1:13 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60211 |  | 3-25-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A)
C2-S11-P13 | C2 | 11 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C2S11:14/C2S11-X1:14 | AI | 4-20mA HART | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S11-X1 | - | Spare | Spare Channel | - | -
C2-S11-P14 | C2 | 11 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C2S11:15/C2S11-X1:15 | AI | 4-20mA HART | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S11-X1 | - | Spare | Spare Channel | - | -
C2-S11-P15 | C2 | 11 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C2S11:16/C2S11-X1:16 | AI | 4-20mA HART | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S11-X1 | - | Spare | Spare Channel | - | -
C2-S12-P00 | C2 | 12 | 0 | 1 | 1756-IF16 | FT-60207_AI_1 | Pin 1 | C2S12:1/C2S12-X1:1 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60207 |  | 3-25-01-602-PD-07 | Instr. Air Flow Transmitter for Camera #4 (ACAM-21)
C2-S12-P01 | C2 | 12 | 1 | 2 | 1756-IF16 | FT-60221_AI_1 | Pin 2 | C2S12:2/C2S12-X1:2 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60221 |  | 3-25-01-602-PD-04 | Cool air Flow
C2-S12-P02 | C2 | 12 | 2 | 3 | 1756-IF16 | FT-60261FA_AI_1 | Pin 3 | C2S12:3/C2S12-X1:3 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60261FA |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #1 (AMTV-11A)
C2-S12-P03 | C2 | 12 | 3 | 4 | 1756-IF16 | FT-60261FB_AI_1 | Pin 4 | C2S12:4/C2S12-X1:4 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60261FB |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #2 (AMTV-11A)
C2-S12-P04 | C2 | 12 | 4 | 5 | 1756-IF16 | FT-60261FC_AI_1 | Pin 5 | C2S12:5/C2S12-X1:5 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60261FC |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #3 (AMTV-11A)
C2-S12-P05 | C2 | 12 | 5 | 6 | 1756-IF16 | FT-60261FD_AI_1 | Pin 6 | C2S12:6/C2S12-X1:6 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60261FD |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #4 (AMTV-11A)
C2-S12-P06 | C2 | 12 | 6 | 7 | 1756-IF16 | FT-60262FE_AI_1 | Pin 7 | C2S12:7/C2S12-X1:7 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60262FE |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #5 (AMTV-11B)
C2-S12-P07 | C2 | 12 | 7 | 8 | 1756-IF16 | FT-60262FF_AI_1 | Pin 8 | C2S12:8/C2S12-X1:8 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60262FF |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #6 (AMTV-11B)
C2-S12-P08 | C2 | 12 | 8 | 9 | 1756-IF16 | FT-60262FG_AI_1 | Pin 9 | C2S12:9/C2S12-X1:9 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60262FG |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #7 (AMTV-11B)
C2-S12-P09 | C2 | 12 | 9 | 10 | 1756-IF16 | FT-60262FH_AI_1 | Pin 10 | C2S12:10/C2S12-X1:10 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60262FH |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #8 (AMTV-11B)
C2-S12-P10 | C2 | 12 | 10 | 11 | 1756-IF16 | FT-60263FJ_AI_1 | Pin 11 | C2S12:11/C2S12-X1:11 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60263FJ |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #9 (AMTV-11C)
C2-S12-P11 | C2 | 12 | 11 | 12 | 1756-IF16 | FT-60263FK_AI_1 | Pin 12 | C2S12:12/C2S12-X1:12 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60263FK |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #10 (AMTV-11C)
C2-S12-P12 | C2 | 12 | 12 | 13 | 1756-IF16 | FT-60263FL_AI_1 | Pin 13 | C2S12:13/C2S12-X1:13 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60263FL |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #11 (AMTV-11C)
C2-S12-P13 | C2 | 12 | 13 | 14 | 1756-IF16 | FT-60263FM_AI_1 | Pin 14 | C2S12:14/C2S12-X1:14 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60263FM |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #12 (AMTV-11C)
C2-S12-P14 | C2 | 12 | 14 | 15 | 1756-IF16 | FT-60264FN_AI_1 | Pin 15 | C2S12:15/C2S12-X1:15 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60264FN |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #13 (AMTV-11D)
C2-S12-P15 | C2 | 12 | 15 | 16 | 1756-IF16 | FT-60264FP_AI_1 | Pin 16 | C2S12:16/C2S12-X1:16 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60264FP |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #14 (AMTV-11D)
C2-S13-P00 | C2 | 13 | 0 | 1 | 1756-IF16 | FT-60264FQ_AI_1 | Pin 1 | C2S13:1/C2S13-X1:1 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | FT-60264FQ |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #15 (AMTV-11D)
C2-S13-P01 | C2 | 13 | 1 | 2 | 1756-IF16 | FT-60264FR_AI_1 | Pin 2 | C2S13:2/C2S13-X1:2 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | FT-60264FR |  | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #16 (AMTV-11D)
C2-S13-P02 | C2 | 13 | 2 | 3 | 1756-IF16 | PT-60201_AI_1 | Pin 3 | C2S13:3/C2S13-X1:3 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | PT-60201 | Pressure Transmitter | 3-25-01-602-PD-02 | Steam feed to Spray dryer
C2-S13-P03 | C2 | 13 | 3 | 4 | 1756-IF16 | PT-60207_AI_1 | Pin 4 | C2S13:4/C2S13-X1:4 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | PT-60207 | Pressure Transmitter | 3-25-01-602-PD-07 | Instr. Air Pressure Transmitter for Camera #4 (ACAM-21)
C2-S13-P04 | C2 | 13 | 4 | 5 | 1756-IF16 | PT-60221_AI_1 | Pin 5 | C2S13:5/C2S13-X1:5 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | PT-60221 | Pressure Transmitter | 3-25-01-602-PD-04 | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25)
C2-S13-P05 | C2 | 13 | 5 | 6 | 1756-IF16 | PT-60221_AI_1 | Pin 6 | C2S13:6/C2S13-X1:6 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | PT-60221 | Pressure Transmitter | 3-25-01-602-PD-04 | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25)
C2-S13-P06 | C2 | 13 | 6 | 7 | 1756-IF16 | TI-FH-60210_AI_1 | Pin 7 | C2S13:7/C2S13-X1:7 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | TI-FH-60210 |  | - | Gas Burner Firing Rate Temp Signal to AHTR-21
C2-S13-P07 | C2 | 13 | 7 | 8 | 1756-IF16 | TT-60201_AI_1 | Pin 8 | C2S13:8/C2S13-X1:8 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | TT-60201 |  | 3-25-01-602-PD-02 | Steam feed to Spray dryer
C2-S13-P08 | C2 | 13 | 8 | 9 | 1756-IF16 | TT-60202_AI_1 | Pin 9 | C2S13:9/C2S13-X1:9 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | TT-60202 |  | 3-25-01-602-PD-07 | Compress air temp to camera
C2-S13-P09 | C2 | 13 | 9 | 10 | 1756-IF16 | TT-60207_AI_1 | Pin 10 | C2S13:10/C2S13-X1:10 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | TT-60207 |  | 3-25-01-602-PD-07 | Instr. Air Temperature Transmitter for Air Manifold - Camera #4 (ACAM-21)
C2-S13-P10 | C2 | 13 | 10 | 11 | 1756-IF16 | UY-FH-60210A_AI_1 | Pin 11 | C2S13:11/C2S13-X1:11 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | UY-FH-60210A |  | - | Comb fan VFD Speed Control
C2-S13-P11 | C2 | 13 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C2S13:12/C2S13-X1:12 | AI | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | - | -
C2-S13-P12 | C2 | 13 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C2S13:13/C2S13-X1:13 | AI | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | - | -
C2-S13-P13 | C2 | 13 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C2S13:14/C2S13-X1:14 | AI | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | - | -
C2-S13-P14 | C2 | 13 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C2S13:15/C2S13-X1:15 | AI | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | - | -
C2-S13-P15 | C2 | 13 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C2S13:16/C2S13-X1:16 | AI | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | - | -
C3-S01-P00 | C3 | 1 | 0 | 1 | 1756-IB32 | AT-40201_DI_1 | Pin 1 | C3S1:1/C3S01-X1:1 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | AT-40201 |  | - | -
C3-S01-P01 | C3 | 1 | 1 | 2 | 1756-IB32 | AT-40202_DI_1 | Pin 2 | C3S1:2/C3S01-X1:2 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | AT-40202 |  | - | -
C3-S01-P02 | C3 | 1 | 2 | 3 | 1756-IB32 | AT-40203_DI_1 | Pin 3 | C3S1:3/C3S01-X1:3 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | AT-40203 |  | - | -
C3-S01-P03 | C3 | 1 | 3 | 4 | 1756-IB32 | LSH-60230_DI_1 | Pin 4 | C3S1:4/C3S01-X1:4 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S01-X1 | - | LSH-60230 |  | 3-25-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-21)
C3-S01-P04 | C3 | 1 | 4 | 5 | 1756-IB32 | LSH-60231_DI_1 | Pin 5 | C3S1:5/C3S01-X1:5 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S01-X1 | - | LSH-60231 |  | 3-25-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-22)
C3-S01-P05 | C3 | 1 | 5 | 6 | 1756-IB32 | LSH-60240_DI_1 | Pin 6 | C3S1:6/C3S01-X1:6 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S01-X1 | - | LSH-60240 |  | 3-25-01-602-PD-05 | Powder Level Switch High for Bag House (BGHS-21)
C3-S01-P06 | C3 | 1 | 6 | 7 | 1756-IB32 | PD-60202_DI_1 | Pin 7 | C3S1:7/C3S01-X1:7 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | PD-60202 |  | - | -
C3-S01-P07 | C3 | 1 | 7 | 8 | 1756-IB32 | RV-60204_DI_1 | Pin 8 | C3S1:8/C3S01-X1:8 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | RV-60204 |  | - | -
C3-S01-P08 | C3 | 1 | 8 | 9 | 1756-IB32 | ZS-60201C_DI_1 | Pin 9 | C3S1:9/C3S01-X1:9 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60201C |  | 3-25-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber)
C3-S01-P09 | C3 | 1 | 9 | 10 | 1756-IB32 | ZS-60201D_DI_1 | Pin 10 | C3S1:10/C3S01-X1:10 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60201D |  | 3-25-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber)
C3-S01-P10 | C3 | 1 | 10 | 11 | 1756-IB32 | ZS-60201E_DI_1 | Pin 11 | C3S1:11/C3S01-X1:11 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S01-X1 | - | ZS-60201E |  | 3-25-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber)
C3-S01-P11 | C3 | 1 | 11 | 12 | 1756-IB32 | ZS-60229_DI_1 | Pin 12 | C3S1:12/C3S01-X1:12 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60229 |  | 3-25-01-602-PD-04 | Limit Switch for CY-60230 (Door Service)
C3-S01-P12 | C3 | 1 | 12 | 13 | 1756-IB32 | ZS-60230_DI_1 | Pin 13 | C3S1:13/C3S01-X1:13 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60230 |  | 3-25-01-602-PD-04 | Limit Switch for CY-60231 (Door Service)
C3-S01-P13 | C3 | 1 | 13 | 14 | 1756-IB32 | ZS-60231A_DI_1 | Pin 14 | C3S1:14/C3S01-X1:14 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60231A |  | 3-25-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Spectacle Inserted)
C3-S01-P14 | C3 | 1 | 14 | 15 | 1756-IB32 | ZS-60231B_DI_1 | Pin 15 | C3S1:15/C3S01-X1:15 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60231B |  | 3-25-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Blind Inserted)
C3-S01-P15 | C3 | 1 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C3S1:16/C3S01-X1:16 | DI | 24VDC Dry Contact | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S01-X1 | - | Spare | Spare Channel | - | -
C3-S01-P16 | C3 | 1 | 16 | 17 | 1756-IB32 | DV-61301_DI_1 | Pin 17 | C3S1:17/C3S01-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S01-X2 | - | DV-61301 |  | 3-25-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61301
C3-S01-P17 | C3 | 1 | 17 | 18 | 1756-IB32 | DV-61301_DI_2 | Pin 18 | C3S1:18/C3S01-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S01-X2 | - | DV-61301 |  | 3-25-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61301
C3-S01-P18 | C3 | 1 | 18 | 19 | 1756-IB32 | DV-61302_DI_1 | Pin 19 | C3S1:19/C3S01-X2:19 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S01-X2 | - | DV-61302 |  | 3-25-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61302
C3-S01-P19 | C3 | 1 | 19 | 20 | 1756-IB32 | DV-61302_DI_2 | Pin 20 | C3S1:20/C3S01-X2:20 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S01-X2 | - | DV-61302 |  | 3-25-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61302
C3-S01-P20 | C3 | 1 | 20 | 21 | 1756-IB32 | LS-61303_DI_1 | Pin 21 | C3S1:21/C3S01-X2:21 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 7th / Packing Tower | C3S01-X2 | - | LS-61303 |  | 3-25-01-613-PD-01 | Level switch
C3-S01-P21 | C3 | 1 | 21 | 22 | 1756-IB32 | PSL-61301_DI_1 | Pin 22 | C3S1:22/C3S01-X2:22 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S01-X2 | - | PSL-61301 |  | - | Pressure alarm low
C3-S01-P22 | C3 | 1 | 22 | 23 | 1756-IB32 | PSL-61302_DI_1 | Pin 23 | C3S1:23/C3S01-X2:23 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S01-X2 | - | PSL-61302 |  | 3-25-01-613-PD-01 | Pressure alarm low
C3-S01-P28 | C3 | 1 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C3S1:29/C3S01-X2:29 | DI | 24VDC Dry Contact | SPARE | JB-618 | Packing Tower 8th Floor | Packing Tower | C3S01-X2 | - | Spare | Spare Channel | - | -
C3-S01-P29 | C3 | 1 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C3S1:30/C3S01-X2:30 | DI | 24VDC Dry Contact | SPARE | JB-618 | Packing Tower 8th Floor | Packing Tower | C3S01-X2 | - | Spare | Spare Channel | - | -
C3-S01-P30 | C3 | 1 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C3S1:31/C3S01-X2:31 | DI | 24VDC Dry Contact | SPARE | JB-618 | Packing Tower 8th Floor | Packing Tower | C3S01-X2 | - | Spare | Spare Channel | - | -
C3-S01-P31 | C3 | 1 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C3S1:32/C3S01-X2:32 | DI | 24VDC Dry Contact | SPARE | JB-618 | Packing Tower 8th Floor | Packing Tower | C3S01-X2 | - | Spare | Spare Channel | - | -
C3-S02-P00 | C3 | 2 | 0 | 1 | 1756-IB32 | ISV-61301_DI_1 | Pin 1 | C3S2:1/C3S02-X1:1 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X1 | - | ISV-61301 |  | 3-25-01-613-PD-01 | -
C3-S02-P01 | C3 | 2 | 1 | 2 | 1756-IB32 | LSH-61301_DI_1 | Pin 2 | C3S2:2/C3S02-X1:2 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 7th / Packing Tower | C3S02-X1 | - | LSH-61301 |  | 3-25-01-613-PD-01 | Level alarm high
C3-S02-P02 | C3 | 2 | 2 | 3 | 1756-IB32 | LSH-61303_DI_1 | Pin 3 | C3S2:3/C3S02-X1:3 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 7th / Packing Tower | C3S02-X1 | - | LSH-61303 |  | - | -
C3-S02-P03 | C3 | 2 | 3 | 4 | 1756-IB32 | LSH-61306_DI_1 | Pin 4 | C3S2:4/C3S02-X1:4 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X1 | - | LSH-61306 |  | 3-25-01-613-PD-01 | Level alarm high
C3-S02-P04 | C3 | 2 | 4 | 5 | 1756-IB32 | LSH-61308_DI_1 | Pin 5 | C3S2:5/C3S02-X1:5 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X1 | - | LSH-61308 |  | 3-25-01-613-PD-01 | High Level alarm Cooling cyclone
C3-S02-P05 | C3 | 2 | 5 | 6 | 1756-IB32 | LSL-61302_DI_1 | Pin 6 | C3S2:6/C3S02-X1:6 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 6th / Packing Tower | C3S02-X1 | - | LSL-61302 |  | 3-25-01-613-PD-01 | Level alarm low
C3-S02-P06 | C3 | 2 | 6 | 7 | 1756-IB32 | PSE-61300_DI_1 | Pin 7 | C3S2:7/C3S02-X1:7 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X1 | - | PSE-61300 |  | 3-25-01-613-PD-01 | Explosion Vent PSE-61300
C3-S02-P07 | C3 | 2 | 7 | 8 | 1756-IB32 | PSE-61301_DI_1 | Pin 8 | C3S2:8/C3S02-X1:8 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X1 | - | PSE-61301 |  | 3-25-01-613-PD-01 | Explosion Vent PSE-61301
C3-S02-P08 | C3 | 2 | 8 | 9 | 1756-IB32 | PSE-61304_DI_1 | Pin 9 | C3S2:9/C3S02-X1:9 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X1 | - | PSE-61304 |  | 3-25-01-613-PD-01 | Explosion Vent PSE-61304
C3-S02-P09 | C3 | 2 | 9 | 10 | 1756-IB32 | PSV-61301A_DI_1 | Pin 10 | C3S2:10/C3S02-X1:10 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X1 | - | PSV-61301A |  | 325-01-613-PD-01 | -
C3-S02-P10 | C3 | 2 | 10 | 11 | 1756-IB32 | PSV-61301B_DI_1 | Pin 11 | C3S2:11/C3S02-X1:11 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X1 | - | PSV-61301B |  | 325-01-613-PD-01 | -
C3-S02-P11 | C3 | 2 | 11 | 12 | 1756-IB32 | ZS-61310_DI_1 | Pin 12 | C3S2:12/C3S02-X1:12 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | ZS-61310 |  | 3-25-01-613-PD-01 | Position Magnet Door
C3-S02-P12 | C3 | 2 | 12 | 13 | 1756-IB32 | ZS-61311_DI_1 | Pin 13 | C3S2:13/C3S02-X1:13 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | ZS-61311 |  | 3-25-01-613-PD-01 | Position Magnet Door
C3-S02-P13 | C3 | 2 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C3S2:14/C3S02-X1:14 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P14 | C3 | 2 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C3S2:15/C3S02-X1:15 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P15 | C3 | 2 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C3S2:16/C3S02-X1:16 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P16 | C3 | 2 | 16 | 17 | 1756-IB32 | Spare_DI_0 | Pin 17 | C3S2:17/C3S02-X2:17 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P17 | C3 | 2 | 17 | 18 | 1756-IB32 | Spare_DI_0 | Pin 18 | C3S2:18/C3S02-X2:18 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P18 | C3 | 2 | 18 | 19 | 1756-IB32 | Spare_DI_0 | Pin 19 | C3S2:19/C3S02-X2:19 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P19 | C3 | 2 | 19 | 20 | 1756-IB32 | Spare_DI_0 | Pin 20 | C3S2:20/C3S02-X2:20 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P20 | C3 | 2 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C3S2:21/C3S02-X2:21 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P21 | C3 | 2 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C3S2:22/C3S02-X2:22 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P22 | C3 | 2 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C3S2:23/C3S02-X2:23 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P23 | C3 | 2 | 23 | 24 | 1756-IB32 | PSL-61311_DI_1 | Pin 24 | C3S2:24/C3S02-X2:24 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X2 | - | PSL-61311 |  | 3-25-01-613-PD-04 | Pressure alarm low
C3-S02-P23 | C3 | 2 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C3S2:24/C3S02-X2:24 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P24 | C3 | 2 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C3S2:25/C3S02-X2:25 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P24 | C3 | 2 | 24 | 25 | 1756-IB32 | SV-61304_DI_1 | Pin 25 | C3S2:25/C3S02-X2:25 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X2 | - | SV-61304 |  | 3-25-01-613-PD-01 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304)
C3-S02-P25 | C3 | 2 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C3S2:26/C3S02-X2:26 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P25 | C3 | 2 | 25 | 26 | 1756-IB32 | SV-61304_DI_2 | Pin 26 | C3S2:26/C3S02-X2:26 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X2 | - | SV-61304 |  | 3-25-01-613-PD-01 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304)
C3-S02-P26 | C3 | 2 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C3S2:27/C3S02-X2:27 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P26 | C3 | 2 | 26 | 27 | 1756-IB32 | XV-61301_DI_1 | Pin 27 | C3S2:27/C3S02-X2:27 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | XV-61301 |  | 3-25-01-613-PD-01 | Product feed-out Packing silo
C3-S02-P27 | C3 | 2 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C3S2:28/C3S02-X2:28 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P27 | C3 | 2 | 27 | 28 | 1756-IB32 | XV-61301_DI_2 | Pin 28 | C3S2:28/C3S02-X2:28 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | XV-61301 |  | 3-25-01-613-PD-01 | Product feed-out Packing silo
C3-S02-P28 | C3 | 2 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C3S2:29/C3S02-X2:29 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P29 | C3 | 2 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C3S2:30/C3S02-X2:30 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P30 | C3 | 2 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C3S2:31/C3S02-X2:31 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S02-P31 | C3 | 2 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C3S2:32/C3S02-X2:32 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01 | -
C3-S03-P00 | C3 | 3 | 0 | 1 | 1756-OB32 | DV-61301_DO_1 | Pin 1 | C3S3:1/C3S03-X1:1 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S03-X1 | - | DV-61301 |  | 3-25-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61301
C3-S03-P01 | C3 | 3 | 1 | 2 | 1756-OB32 | DV-61302_DO_1 | Pin 2 | C3S3:2/C3S03-X1:2 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S03-X1 | - | DV-61302 |  | 3-25-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61302
C3-S03-P02 | C3 | 3 | 2 | 3 | 1756-OB32 | SV-61301_DO_1 | Pin 3 | C3S3:3/C3S03-X1:3 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S03-X1 | - | SV-61301 |  | - | Timer compress air pluse solenoid valve
C3-S03-P03 | C3 | 3 | 3 | 4 | 1756-OB32 | SV-61302_DO_1 | Pin 4 | C3S3:4/C3S03-X1:4 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 7th / Packing Tower | C3S03-X1 | - | SV-61302 |  | 3-25-01-613-PD-01 | Air service
C3-S03-P04 | C3 | 3 | 4 | 5 | 1756-OB32 | SV-61303_DO_1 | Pin 5 | C3S3:5/C3S03-X1:5 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S03-X1 | - | SV-61303 |  | 3-25-01-613-PD-01 | Timer compress air pluse solenoid valve
C3-S03-P05 | C3 | 3 | 5 | 6 | 1756-OB32 | SV-61304_DO_1 | Pin 6 | C3S3:6/C3S03-X1:6 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S03-X1 | - | SV-61304 |  | 3-25-01-613-PD-01 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304)
C3-S03-P06 | C3 | 3 | 6 | 7 | 1756-OB32 | SV-61305_DO_1 | Pin 7 | C3S3:7/C3S03-X1:7 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S03-X1 | - | SV-61305 |  | 3-25-01-613-PD-01 | Air service
C3-S03-P07 | C3 | 3 | 7 | 8 | 1756-OB32 | SV-61306_DO_1 | Pin 8 | C3S3:8/C3S03-X1:8 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S03-X1 | - | SV-61306 |  | 3-25-01-613-PD-01 | -
C3-S03-P08 | C3 | 3 | 8 | 9 | 1756-OB32 | XV-61301_DO_1 | Pin 9 | C3S3:9/C3S03-X1:9 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S03-X1 | - | XV-61301 |  | 3-25-01-613-PD-01 | Product feed-out Packing silo
C3-S03-P09 | C3 | 3 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C3S3:10/C3S03-X1:10 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | - | -
C3-S03-P10 | C3 | 3 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C3S3:11/C3S03-X1:11 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | - | -
C3-S03-P11 | C3 | 3 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C3S3:12/C3S03-X1:12 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | - | -
C3-S03-P12 | C3 | 3 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C3S3:13/C3S03-X1:13 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | - | -
C3-S03-P13 | C3 | 3 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C3S3:14/C3S03-X1:14 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | - | -
C3-S03-P14 | C3 | 3 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C3S3:15/C3S03-X1:15 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | - | -
C3-S03-P15 | C3 | 3 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C3S3:16/C3S03-X1:16 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | - | -
C3-S03-P16 | C3 | 3 | 16 | 17 | 1756-OB32 | Spare_DO_0 | Pin 17 | C3S3:17/C3S03-X2:17 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P17 | C3 | 3 | 17 | 18 | 1756-OB32 | Spare_DO_0 | Pin 18 | C3S3:18/C3S03-X2:18 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P18 | C3 | 3 | 18 | 19 | 1756-OB32 | Spare_DO_0 | Pin 19 | C3S3:19/C3S03-X2:19 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P19 | C3 | 3 | 19 | 20 | 1756-OB32 | Spare_DO_0 | Pin 20 | C3S3:20/C3S03-X2:20 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P20 | C3 | 3 | 20 | 21 | 1756-OB32 | Spare_DO_0 | Pin 21 | C3S3:21/C3S03-X2:21 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P21 | C3 | 3 | 21 | 22 | 1756-OB32 | Spare_DO_0 | Pin 22 | C3S3:22/C3S03-X2:22 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P22 | C3 | 3 | 22 | 23 | 1756-OB32 | Spare_DO_0 | Pin 23 | C3S3:23/C3S03-X2:23 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P23 | C3 | 3 | 23 | 24 | 1756-OB32 | Spare_DO_0 | Pin 24 | C3S3:24/C3S03-X2:24 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P24 | C3 | 3 | 24 | 25 | 1756-OB32 | Spare_DO_0 | Pin 25 | C3S3:25/C3S03-X2:25 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P25 | C3 | 3 | 25 | 26 | 1756-OB32 | Spare_DO_0 | Pin 26 | C3S3:26/C3S03-X2:26 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P26 | C3 | 3 | 26 | 27 | 1756-OB32 | Spare_DO_0 | Pin 27 | C3S3:27/C3S03-X2:27 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P27 | C3 | 3 | 27 | 28 | 1756-OB32 | Spare_DO_0 | Pin 28 | C3S3:28/C3S03-X2:28 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P28 | C3 | 3 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C3S3:29/C3S03-X2:29 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P29 | C3 | 3 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C3S3:30/C3S03-X2:30 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P30 | C3 | 3 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C3S3:31/C3S03-X2:31 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S03-P31 | C3 | 3 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C3S3:32/C3S03-X2:32 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | - | -
C3-S04-P00 | C3 | 4 | 0 | 1 | 1756-IF16 | PT-60230_AI_1 | Pin 1 | C3S4:1/C3S04-X1:1 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S04-X1 | - | PT-60230 | Pressure Transmitter | 3-25-01-602-PD-04 | Gas Pressure Transmitter for Conveying Duct (DTCO-21)
C3-S04-P01 | C3 | 4 | 1 | 2 | 1756-IF16 | PT-60231_AI_1 | Pin 2 | C3S4:2/C3S04-X1:2 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S04-X1 | - | PT-60231 | Pressure Transmitter | 3-25-01-602-PD-04 | Gas Pressure Transmitter for Cyclone Exhaust Duct (DTCE-21)
C3-S04-P02 | C3 | 4 | 2 | 3 | 1756-IF16 | TT-60224_AI_1 | Pin 3 | C3S4:3/C3S04-X1:3 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S04-X1 | - | TT-60224 |  | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21)
C3-S04-P03 | C3 | 4 | 3 | 4 | 1756-IF16 | TT-60225_AI_1 | Pin 4 | C3S4:4/C3S04-X1:4 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S04-X1 | - | TT-60225 |  | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21)
C3-S04-P04 | C3 | 4 | 4 | 5 | 1756-IF16 | TT-60226_AI_1 | Pin 5 | C3S4:5/C3S04-X1:5 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 2nd / Spray Dryer | C3S04-X1 | - | TT-60226 |  | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21)
C3-S04-P05 | C3 | 4 | 5 | 6 | 1756-IF16 | TT-60227_AI_1 | Pin 6 | C3S4:6/C3S04-X1:6 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S04-X1 | - | TT-60227 |  | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21)
C3-S04-P06 | C3 | 4 | 6 | 7 | 1756-IF16 | TT-60230_AI_1 | Pin 7 | C3S4:7/C3S04-X1:7 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S04-X1 | - | TT-60230 |  | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Conveying Duct (DTCO-21)
C3-S04-P07 | C3 | 4 | 7 | 8 | 1756-IF16 | Spare_AI_0 | Pin 8 | C3S4:8/C3S04-X1:8 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | - | -
C3-S04-P08 | C3 | 4 | 8 | 9 | 1756-IF16 | Spare_AI_0 | Pin 9 | C3S4:9/C3S04-X1:9 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | - | -
C3-S04-P09 | C3 | 4 | 9 | 10 | 1756-IF16 | Spare_AI_0 | Pin 10 | C3S4:10/C3S04-X1:10 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | - | -
C3-S04-P10 | C3 | 4 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C3S4:11/C3S04-X1:11 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | - | -
C3-S04-P11 | C3 | 4 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C3S4:12/C3S04-X1:12 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | - | -
C3-S04-P12 | C3 | 4 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C3S4:13/C3S04-X1:13 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | - | -
C3-S04-P13 | C3 | 4 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C3S4:14/C3S04-X1:14 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | - | -
C3-S04-P14 | C3 | 4 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C3S4:15/C3S04-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | - | -
C3-S04-P15 | C3 | 4 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C3S4:16/C3S04-X1:16 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | - | -
C3-S05-P00 | C3 | 5 | 0 | 1 | 1756-IF16 | PT-61303_AI_1 | Pin 1 | C3S5:1/C3S05-X1:1 | AI | 4-20mA HART | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | PT-61303 | Pressure Transmitter | 3-25-01-613-PD-01 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31)
C3-S05-P01 | C3 | 5 | 1 | 2 | 1756-IF16 | PT-61306_AI_1 | Pin 2 | C3S5:2/C3S05-X1:2 | AI | 4-20mA HART | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | PT-61306 |  | 3-25-01-613-PD-01 | -
C3-S05-P02 | C3 | 5 | 2 | 3 | 1756-IF16 | TT-61303_AI_1 | Pin 3 | C3S5:3/C3S05-X1:3 | AI | 4-20mA HART | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | TT-61303 |  | 3-25-01-613-PD-01 | -
C3-S05-P03 | C3 | 5 | 3 | 4 | 1756-IF16 | TT-61304_AI_1 | Pin 4 | C3S5:4/C3S05-X1:4 | AI | 4-20mA HART | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | TT-61304 |  | 3-25-01-613-PD-01 | -
C3-S05-P04 | C3 | 5 | 4 | 5 | 1756-IF16 | DPT-61301_AI_1 | Pin 5 | C3S5:5/C3S05-X1:5 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | DPT-61301 | Differential Pressure Transmitte | 3-25-01-613-PD-01 | Vent filter pressure
C3-S05-P05 | C3 | 5 | 5 | 6 | 1756-IF16 | DPT-61302_AI_1 | Pin 6 | C3S5:6/C3S05-X1:6 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | DPT-61302 | Differential Pressure Transmitte | 3-25-01-613-PD-01 | Vent filter pressure
C3-S05-P06 | C3 | 5 | 6 | 7 | 1756-IF16 | LT-61301_AI_1 | Pin 7 | C3S5:7/C3S05-X1:7 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | LT-61301 | Level Transmitter | 3-25-01-613-PD-01 | Level powder in silo
C3-S05-P07 | C3 | 5 | 7 | 8 | 1756-IF16 | PT-61301_AI_1 | Pin 8 | C3S5:8/C3S05-X1:8 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | PT-61301 | Pressure Transmitter | 3-25-01-613-PD-01 | Pressure in silo
C3-S05-P08 | C3 | 5 | 8 | 9 | 1756-IF16 | PT-61303_AI_1 | Pin 9 | C3S5:9/C3S05-X1:9 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | PT-61303 | Pressure Transmitter | 3-25-01-613-PD-01 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31)
C3-S05-P09 | C3 | 5 | 9 | 10 | 1756-IF16 | PT-61304_AI_1 | Pin 10 | C3S5:10/C3S05-X1:10 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | PT-61304 | Pressure Transmitter | 3-25-01-613-PD-01 | Gas Pressure Transmitter for Storage Bin Cyclone Inlet Duct (CYCL-31)
C3-S05-P10 | C3 | 5 | 10 | 11 | 1756-IF16 | PT-61305_AI_1 | Pin 11 | C3S5:11/C3S05-X1:11 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | PT-61305 | Pressure Transmitter | 3-25-01-613-PD-01 | Gas Pressure Transmitter for Exhaust Duct (DTEX-31)
C3-S05-P11 | C3 | 5 | 11 | 12 | 1756-IF16 | TT-61301_AI_1 | Pin 12 | C3S5:12/C3S05-X1:12 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | TT-61301 |  | 3-25-01-613-PD-01 | Gas Temperature Transmitter for Cold Air Duct (DTCA-32)
C3-S05-P12 | C3 | 5 | 12 | 13 | 1756-IF16 | TT-61302_AI_1 | Pin 13 | C3S5:13/C3S05-X1:13 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | TT-61302 |  | 3-25-01-613-PD-01 | Gas and Powder Temperature Transmitter for Cooling Cyclone (CYCL-31)
C3-S05-P13 | C3 | 5 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C3S5:14/C3S05-X1:14 | AI | 4-20mA HART | SPARE | IS-JB-618 | Packing Tower 8th Floor | - | C3S05-X1 | - | Spare | Spare Channel | - | -
C3-S05-P14 | C3 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C3S5:15/C3S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-618 | Packing Tower 8th Floor | - | C3S05-X1 | - | Spare | Spare Channel | - | -
C3-S05-P15 | C3 | 5 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C3S5:16/C3S05-X1:16 | AI | 4-20mA HART | SPARE | IS-JB-618 | Packing Tower 8th Floor | - | C3S05-X1 | - | Spare | Spare Channel | - | -
C3-S13-P00 | C3 | 13 | 0 | 1 | 1756-OF8 | TCV-40222_AO_1 | Pin 1 | C3S13:1/C3S13-X1:1 | AO | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C3S13-X1 | - | TCV-40222 |  | 325-01-402-PD-02 | Jet Cooker
C3-S13-P01 | C3 | 13 | 1 | 2 | 1756-OF8 | TV-60202_AO_1 | Pin 2 | C3S13:2/C3S13-X1:2 | AO | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S13-X1 | - | TV-60202 |  | 3-25-01-602-PD-07 | -
C3-S13-P02 | C3 | 13 | 2 | 3 | 1756-OF8 | TV-60214_AO_1 | Pin 3 | C3S13:3/C3S13-X1:3 | AO | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C3S13-X1 | - | TV-60214 |  | 3-25-01-602-PD-03 | -
C3-S13-P03 | C3 | 13 | 3 | 4 | 1756-OF8 | PV-60201_AO_1 | Pin 4 | C3S13:4/C3S13-X1:4 | AO | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C3S13-X1 | - | PV-60201 |  | 3-25-01-602-PD-02 | -
C3-S13-P04 | C3 | 13 | 4 | 5 | 1756-OF8 | UY-FH-60210B_AO_1 | Pin 5 | C3S13:5/C3S13-X1:5 | AO | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C3S13-X1 | - | UY-FH-60210B |  | - | Demand Signal
C3-S13-P05 | C3 | 13 | 5 | 6 | 1756-OF8 | Spare_AO_0 | Pin 6 | C3S13:6/C3S13-X1:6 | AO | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C3S13-X1 | - | Spare | Spare Channel | - | -
C3-S13-P06 | C3 | 13 | 6 | 7 | 1756-OF8 | Spare_AO_0 | Pin 7 | C3S13:7/C3S13-X1:7 | AO | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C3S13-X1 | - | Spare | Spare Channel | - | -
C3-S13-P07 | C3 | 13 | 7 | 8 | 1756-OF8 | Spare_AO_0 | Pin 8 | C3S13:8/C3S13-X1:8 | AO | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C3S13-X1 | - | Spare | Spare Channel | - | -
C4-S01-P00 | C4 | 1 | 0 | 1 | 1756-IB32 | FT-60203_DI_1 | Pin 1 | C4S1:1/C4S01-X1:1 | DI | 24VDC Dry Contact | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S01-X1 | - | FT-60203 |  | 3-25-01-602-PD-09 | Culinary steam feed to Spray dryer
C4-S01-P01 | C4 | 1 | 1 | 2 | 1756-IB32 | LSH-60250_DI_1 | Pin 2 | C4S1:2/C4S01-X1:2 | DI | 24VDC Dry Contact | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S01-X1 | - | LSH-60250 |  | 3-25-01-602-PD-05 | Water Level Switch High for Fire Deluge Pipe (FWDP-21)
C4-S01-P02 | C4 | 1 | 2 | 3 | 1756-IB32 | XA-60261_DI_1 | Pin 3 | C4S1:3/C4S01-X1:3 | DI | 24VDC Dry Contact | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S01-X1 | - | XA-60261 |  | - | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge)
C4-S01-P03 | C4 | 1 | 3 | 4 | 1756-IB32 | XA-60262_DI_1 | Pin 4 | C4S1:4/C4S01-X1:4 | DI | 24VDC Dry Contact | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S01-X1 | - | XA-60262 |  | - | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge)
C4-S01-P04 | C4 | 1 | 4 | 5 | 1756-IB32 | Spare_DI_0 | Pin 5 | C4S1:5/C4S01-X1:5 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | - | -
C4-S01-P05 | C4 | 1 | 5 | 6 | 1756-IB32 | Spare_DI_0 | Pin 6 | C4S1:6/C4S01-X1:6 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | - | -
C4-S01-P06 | C4 | 1 | 6 | 7 | 1756-IB32 | Spare_DI_0 | Pin 7 | C4S1:7/C4S01-X1:7 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | - | -
C4-S01-P07 | C4 | 1 | 7 | 8 | 1756-IB32 | Spare_DI_0 | Pin 8 | C4S1:8/C4S01-X1:8 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | - | -
C4-S01-P08 | C4 | 1 | 8 | 9 | 1756-IB32 | Spare_DI_0 | Pin 9 | C4S1:9/C4S01-X1:9 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | - | -
C4-S01-P09 | C4 | 1 | 9 | 10 | 1756-IB32 | Spare_DI_0 | Pin 10 | C4S1:10/C4S01-X1:10 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | - | -
C4-S01-P10 | C4 | 1 | 10 | 11 | 1756-IB32 | Spare_DI_0 | Pin 11 | C4S1:11/C4S01-X1:11 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | - | -
C4-S01-P11 | C4 | 1 | 11 | 12 | 1756-IB32 | Spare_DI_0 | Pin 12 | C4S1:12/C4S01-X1:12 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | - | -
C4-S01-P12 | C4 | 1 | 12 | 13 | 1756-IB32 | Spare_DI_0 | Pin 13 | C4S1:13/C4S01-X1:13 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | - | -
C4-S01-P13 | C4 | 1 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C4S1:14/C4S01-X1:14 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | - | -
C4-S01-P14 | C4 | 1 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C4S1:15/C4S01-X1:15 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | - | -
C4-S01-P15 | C4 | 1 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C4S1:16/C4S01-X1:16 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | - | -
C4-S01-P16 | C4 | 1 | 16 | 17 | 1756-IB32 | ZS-60201A_DI_1 | Pin 17 | C4S1:17/C4S01-X2:17 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S01-X2 | - | ZS-60201A |  | 3-25-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber)
C4-S01-P17 | C4 | 1 | 17 | 18 | 1756-IB32 | ZS-60201B_DI_1 | Pin 18 | C4S1:18/C4S01-X2:18 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S01-X2 | - | ZS-60201B |  | 3-25-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber)
C4-S01-P18 | C4 | 1 | 18 | 19 | 1756-IB32 | ZS-60231C_DI_1 | Pin 19 | C4S1:19/C4S01-X2:19 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231C |  | 3-25-01-602-PD-04 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Spool Inserted)
C4-S01-P19 | C4 | 1 | 19 | 20 | 1756-IB32 | ZS-60231D_DI_1 | Pin 20 | C4S1:20/C4S01-X2:20 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231D |  | 3-25-01-602-PD-04 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Blind Inserted)
C4-S01-P20 | C4 | 1 | 20 | 21 | 1756-IB32 | ZS-60231E_DI_1 | Pin 21 | C4S1:21/C4S01-X2:21 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231E |  | 3-25-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Spool Inserted)
C4-S01-P21 | C4 | 1 | 21 | 22 | 1756-IB32 | ZS-60231F_DI_1 | Pin 22 | C4S1:22/C4S01-X2:22 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231F |  | 3-25-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Blind Inserted)
C4-S01-P22 | C4 | 1 | 22 | 23 | 1756-IB32 | ZS-60240_DI_1 | Pin 23 | C4S1:23/C4S01-X2:23 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S01-X2 | - | ZS-60240 |  | 3-25-01-602-PD-05 | Limit Switch for FA-60240 (Door Service)
C4-S01-P23 | C4 | 1 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C4S1:24/C4S01-X2:24 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | - | -
C4-S01-P24 | C4 | 1 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C4S1:25/C4S01-X2:25 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | - | -
C4-S01-P25 | C4 | 1 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C4S1:26/C4S01-X2:26 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | - | -
C4-S01-P26 | C4 | 1 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C4S1:27/C4S01-X2:27 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | - | -
C4-S01-P27 | C4 | 1 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C4S1:28/C4S01-X2:28 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | - | -
C4-S01-P28 | C4 | 1 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C4S1:29/C4S01-X2:29 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | - | -
C4-S01-P29 | C4 | 1 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C4S1:30/C4S01-X2:30 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | - | -
C4-S01-P30 | C4 | 1 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C4S1:31/C4S01-X2:31 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | - | -
C4-S01-P31 | C4 | 1 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C4S1:32/C4S01-X2:32 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | - | -
C4-S02-P00 | C4 | 2 | 0 | 1 | 1756-IB32 | PSL-61305_DI_1 | Pin 1 | C4S2:1/C4S02-X1:1 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | PSL-61305 |  | 3-25-01-613-PD-03 | Pressure alarm low
C4-S02-P01 | C4 | 2 | 1 | 2 | 1756-IB32 | PSL-61306_DI_1 | Pin 2 | C4S2:2/C4S02-X1:2 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | PSL-61306 |  | 3-25-01-613-PD-05 | Pressure alarm low
C4-S02-P02 | C4 | 2 | 2 | 3 | 1756-IB32 | PVM-61301_DI_1 | Pin 3 | C4S2:3/C4S02-X1:3 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | PVM-61301 |  | - | -
C4-S02-P03 | C4 | 2 | 3 | 4 | 1756-IB32 | PVM-61301_DI_2 | Pin 4 | C4S2:4/C4S02-X1:4 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | PVM-61301 |  | - | -
C4-S02-P04 | C4 | 2 | 4 | 5 | 1756-IB32 | XA-61301A_DI_1 | Pin 5 | C4S2:5/C4S02-X1:5 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301A |  | - | Request filter plant
C4-S02-P05 | C4 | 2 | 5 | 6 | 1756-IB32 | XA-61301B_DI_1 | Pin 6 | C4S2:6/C4S02-X1:6 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301B |  | - | Request material transport
C4-S02-P06 | C4 | 2 | 6 | 7 | 1756-IB32 | XA-61301C_DI_1 | Pin 7 | C4S2:7/C4S02-X1:7 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301C |  | - | Request belt plant
C4-S02-P07 | C4 | 2 | 7 | 8 | 1756-IB32 | XA-61301D_DI_1 | Pin 8 | C4S2:8/C4S02-X1:8 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301D |  | - | Machine in operation
C4-S02-P08 | C4 | 2 | 8 | 9 | 1756-IB32 | XA-61301E_DI_1 | Pin 9 | C4S2:9/C4S02-X1:9 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301E |  | - | General Fault
C4-S02-P09 | C4 | 2 | 9 | 10 | 1756-IB32 | XA-61301F_DI_1 | Pin 10 | C4S2:10/C4S02-X1:10 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301F |  | - | Machine is ready
C4-S02-P10 | C4 | 2 | 10 | 11 | 1756-IB32 | XA-61301G_DI_1 | Pin 11 | C4S2:11/C4S02-X1:11 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301G |  | - | Emergency stop activated
C4-S02-P11 | C4 | 2 | 11 | 12 | 1756-IB32 | XA-61301H_DI_1 | Pin 12 | C4S2:12/C4S02-X1:12 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301H |  | - | Silo minimum
C4-S02-P12 | C4 | 2 | 12 | 13 | 1756-IB32 | XA-61301J_DI_1 | Pin 13 | C4S2:13/C4S02-X1:13 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301J |  | - | Silo maximum
C4-S02-P13 | C4 | 2 | 13 | 14 | 1756-IB32 | XV-61302_DI_1 | Pin 14 | C4S2:14/C4S02-X1:14 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | XV-61302 |  | 3-25-01-613-PD-02 | Dust collector feed vent
C4-S02-P14 | C4 | 2 | 14 | 15 | 1756-IB32 | XV-61302_DI_2 | Pin 15 | C4S2:15/C4S02-X1:15 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | XV-61302 |  | 3-25-01-613-PD-02 | Dust collector feed vent
C4-S02-P15 | C4 | 2 | 15 | 16 | 1756-IB32 | XV-61303_DI_1 | Pin 16 | C4S2:16/C4S02-X1:16 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | XV-61303 |  | 3-25-01-613-PD-02 | Dust collector feed from packer
C4-S02-P16 | C4 | 2 | 16 | 17 | 1756-IB32 | XV-61303_DI_2 | Pin 17 | C4S2:17/C4S02-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X2 | - | XV-61303 |  | 3-25-01-613-PD-02 | Dust collector feed from packer
C4-S02-P17 | C4 | 2 | 17 | 18 | 1756-IB32 | Spare_DI_0 | Pin 18 | C4S2:18/C4S02-X2:18 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P18 | C4 | 2 | 18 | 19 | 1756-IB32 | Spare_DI_0 | Pin 19 | C4S2:19/C4S02-X2:19 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P19 | C4 | 2 | 19 | 20 | 1756-IB32 | Spare_DI_0 | Pin 20 | C4S2:20/C4S02-X2:20 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P20 | C4 | 2 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C4S2:21/C4S02-X2:21 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P21 | C4 | 2 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C4S2:22/C4S02-X2:22 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P22 | C4 | 2 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C4S2:23/C4S02-X2:23 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P23 | C4 | 2 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C4S2:24/C4S02-X2:24 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P24 | C4 | 2 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C4S2:25/C4S02-X2:25 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P25 | C4 | 2 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C4S2:26/C4S02-X2:26 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P26 | C4 | 2 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C4S2:27/C4S02-X2:27 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P27 | C4 | 2 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C4S2:28/C4S02-X2:28 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P28 | C4 | 2 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C4S2:29/C4S02-X2:29 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P29 | C4 | 2 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C4S2:30/C4S02-X2:30 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P30 | C4 | 2 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C4S2:31/C4S02-X2:31 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S02-P31 | C4 | 2 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C4S2:32/C4S02-X2:32 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | - | -
C4-S03-P00 | C4 | 3 | 0 | 1 | 1756-IB32 | ISV-61303_DI_1 | Pin 1 | C4S3:1/C4S03-X1:1 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | ISV-61303 |  | 3-25-01-613-PD-03 | Explosion isolation flap valve ISV-61303
C4-S03-P01 | C4 | 3 | 1 | 2 | 1756-IB32 | ISV-61304_DI_1 | Pin 2 | C4S3:2/C4S03-X1:2 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | ISV-61304 |  | 3-25-01-613-PD-05 | Explosion isolation flap valve ISV-61304
C4-S03-P02 | C4 | 3 | 2 | 3 | 1756-IB32 | LSH-61304_DI_1 | Pin 3 | C4S3:3/C4S03-X1:3 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S03-X1 | - | LSH-61304 |  | 3-25-01-613-PD-03 | Big bag level alarm high
C4-S03-P03 | C4 | 3 | 3 | 4 | 1756-IB32 | LSH-61305_DI_1 | Pin 4 | C4S3:4/C4S03-X1:4 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S03-X1 | - | LSH-61305 |  | 3-25-01-613-PD-05 | Big bag level alarm high
C4-S03-P04 | C4 | 3 | 4 | 5 | 1756-IB32 | LSH-61307_DI_1 | Pin 5 | C4S3:5/C4S03-X1:5 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S03-X1 | - | LSH-61307 |  | 3-25-01-613-PD-01 | High Level alarm reject screen
C4-S03-P05 | C4 | 3 | 5 | 6 | 1756-IB32 | LSH-61312_DI_1 | Pin 6 | C4S3:6/C4S03-X1:6 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | LSH-61312 |  | 3-25-01-613-PD-05 | Level alarm high
C4-S03-P06 | C4 | 3 | 6 | 7 | 1756-IB32 | PSE-61302_DI_1 | Pin 7 | C4S3:7/C4S03-X1:7 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | PSE-61302 |  | 3-25-01-613-PD-03 | Explosion Vent PSE-61302
C4-S03-P07 | C4 | 3 | 7 | 8 | 1756-IB32 | PSE-61303_DI_1 | Pin 8 | C4S3:8/C4S03-X1:8 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | PSE-61303 |  | 3-25-01-613-PD-05 | Explosion Vent PSE-61303
C4-S03-P09 | C4 | 3 | 9 | 10 | 1756-IB32 | RV-61301_DI_1 | Pin 10 | C4S3:10/C4S03-X1:10 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | RV-61301 |  | - | -
C4-S03-P10 | C4 | 3 | 10 | 11 | 1756-IB32 | RV-61304_DI_1 | Pin 11 | C4S3:11/C4S03-X1:11 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | RV-61304 |  | - | -
C4-S03-P11 | C4 | 3 | 11 | 12 | 1756-IB32 | RV-61305_DI_1 | Pin 12 | C4S3:12/C4S03-X1:12 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | RV-61305 |  | - | -
C4-S03-P12 | C4 | 3 | 12 | 13 | 1756-IB32 | SC-61301_DI_1 | Pin 13 | C4S3:13/C4S03-X1:13 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | SC-61301 |  | - | -
C4-S03-P13 | C4 | 3 | 13 | 14 | 1756-IB32 | SC-61302_DI_1 | Pin 14 | C4S3:14/C4S03-X1:14 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | SC-61302 |  | - | -
C4-S03-P14 | C4 | 3 | 14 | 15 | 1756-IB32 | ZS-61312_DI_1 | Pin 15 | C4S3:15/C4S03-X1:15 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 3rd / Packing Tower | C4S03-X1 | - | ZS-61312 |  | 3-25-01-613-PD-01 | Position Magnet Door
C4-S03-P15 | C4 | 3 | 15 | 16 | 1756-IB32 | ZS-61313_DI_1 | Pin 16 | C4S3:16/C4S03-X1:16 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 3rd / Packing Tower | C4S03-X1 | - | ZS-61313 |  | 3-25-01-613-PD-01 | Position Magnet Door
C4-S03-P16 | C4 | 3 | 16 | 17 | 1756-IB32 | Spare_DI_0 | Pin 17 | C4S3:17/C4S03-X2:17 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P17 | C4 | 3 | 17 | 18 | 1756-IB32 | Spare_DI_0 | Pin 18 | C4S3:18/C4S03-X2:18 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P18 | C4 | 3 | 18 | 19 | 1756-IB32 | Spare_DI_0 | Pin 19 | C4S3:19/C4S03-X2:19 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P19 | C4 | 3 | 19 | 20 | 1756-IB32 | Spare_DI_0 | Pin 20 | C4S3:20/C4S03-X2:20 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P20 | C4 | 3 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C4S3:21/C4S03-X2:21 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P21 | C4 | 3 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C4S3:22/C4S03-X2:22 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P22 | C4 | 3 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C4S3:23/C4S03-X2:23 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P23 | C4 | 3 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C4S3:24/C4S03-X2:24 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P24 | C4 | 3 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C4S3:25/C4S03-X2:25 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P25 | C4 | 3 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C4S3:26/C4S03-X2:26 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P26 | C4 | 3 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C4S3:27/C4S03-X2:27 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P27 | C4 | 3 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C4S3:28/C4S03-X2:28 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P28 | C4 | 3 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C4S3:29/C4S03-X2:29 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P29 | C4 | 3 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C4S3:30/C4S03-X2:30 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P30 | C4 | 3 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C4S3:31/C4S03-X2:31 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S03-P31 | C4 | 3 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C4S3:32/C4S03-X2:32 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | - | -
C4-S04-P00 | C4 | 4 | 0 | 1 | 1756-OB32 | SV-60220_DO_1 | Pin 1 | C4S4:1/C4S04-X1:1 | DO | 24VDC Sourcing | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S04-X1 | - | SV-60220 |  | 3-25-01-602-PD-04 | PA On/Off Valve for Chamber PSE purge air (CHAM-21)
C4-S04-P01 | C4 | 4 | 1 | 2 | 1756-OB32 | Spare_DO_0 | Pin 2 | C4S4:2/C4S04-X1:2 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P02 | C4 | 4 | 2 | 3 | 1756-OB32 | Spare_DO_0 | Pin 3 | C4S4:3/C4S04-X1:3 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P03 | C4 | 4 | 3 | 4 | 1756-OB32 | Spare_DO_0 | Pin 4 | C4S4:4/C4S04-X1:4 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P04 | C4 | 4 | 4 | 5 | 1756-OB32 | Spare_DO_0 | Pin 5 | C4S4:5/C4S04-X1:5 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P05 | C4 | 4 | 5 | 6 | 1756-OB32 | Spare_DO_0 | Pin 6 | C4S4:6/C4S04-X1:6 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P06 | C4 | 4 | 6 | 7 | 1756-OB32 | Spare_DO_0 | Pin 7 | C4S4:7/C4S04-X1:7 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P07 | C4 | 4 | 7 | 8 | 1756-OB32 | Spare_DO_0 | Pin 8 | C4S4:8/C4S04-X1:8 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P08 | C4 | 4 | 8 | 9 | 1756-OB32 | XA-60201_DO_1 | Pin 9 | C4S4:9/C4S04-X1:9 | DO | 24VDC Sourcing | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S04-X1 | - | XA-60201 |  | 3-25-01-602-PD-03 | LEL gas Buzzer Alarm
C4-S04-P09 | C4 | 4 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C4S4:10/C4S04-X1:10 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P10 | C4 | 4 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C4S4:11/C4S04-X1:11 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P11 | C4 | 4 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C4S4:12/C4S04-X1:12 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P12 | C4 | 4 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C4S4:13/C4S04-X1:13 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P13 | C4 | 4 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C4S4:14/C4S04-X1:14 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P14 | C4 | 4 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C4S4:15/C4S04-X1:15 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P15 | C4 | 4 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C4S4:16/C4S04-X1:16 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | - | -
C4-S04-P16 | C4 | 4 | 16 | 17 | 1756-OB32 | PVM-61301_DO_1 | Pin 17 | C4S4:17/C4S04-X2:17 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | PVM-61301 |  | - | -
C4-S04-P17 | C4 | 4 | 17 | 18 | 1756-OB32 | PVM-61301_DO_2 | Pin 18 | C4S4:18/C4S04-X2:18 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | PVM-61301 |  | - | -
C4-S04-P18 | C4 | 4 | 18 | 19 | 1756-OB32 | SV-61307_DO_1 | Pin 19 | C4S4:19/C4S04-X2:19 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 3rd / Packing Tower | C4S04-X2 | - | SV-61307 |  | 3-25-01-613-PD-01 | -
C4-S04-P19 | C4 | 4 | 19 | 20 | 1756-OB32 | SV-61308_DO_1 | Pin 20 | C4S4:20/C4S04-X2:20 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | SV-61308 |  | - | Timer compress air pluse solenoid valve
C4-S04-P20 | C4 | 4 | 20 | 21 | 1756-OB32 | SV-61309_DO_1 | Pin 21 | C4S4:21/C4S04-X2:21 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | SV-61309 |  | 3-25-01-613-PD-03 | Air service
C4-S04-P21 | C4 | 4 | 21 | 22 | 1756-OB32 | SV-61310_DO_1 | Pin 22 | C4S4:22/C4S04-X2:22 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | SV-61310 |  | - | Timer compress air pluse solenoid valve
C4-S04-P22 | C4 | 4 | 22 | 23 | 1756-OB32 | SV-61311_DO_1 | Pin 23 | C4S4:23/C4S04-X2:23 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | SV-61311 |  | 3-25-01-613-PD-05 | Air service
C4-S04-P23 | C4 | 4 | 23 | 24 | 1756-OB32 | XS-61301A_DO_1 | Pin 24 | C4S4:24/C4S04-X2:24 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301A |  | - | Filter plant in operation
C4-S04-P24 | C4 | 4 | 24 | 25 | 1756-OB32 | XS-61301B_DO_1 | Pin 25 | C4S4:25/C4S04-X2:25 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301B |  | - | Material transport in operation
C4-S04-P25 | C4 | 4 | 25 | 26 | 1756-OB32 | XS-61301C_DO_1 | Pin 26 | C4S4:26/C4S04-X2:26 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301C |  | - | Belt plant in operation
C4-S04-P26 | C4 | 4 | 26 | 27 | 1756-OB32 | XS-61301D_DO_1 | Pin 27 | C4S4:27/C4S04-X2:27 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301D |  | - | Sequence Stop
C4-S04-P27 | C4 | 4 | 27 | 28 | 1756-OB32 | XS-61301E_DO_1 | Pin 28 | C4S4:28/C4S04-X2:28 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301E |  | - | Status from Customer Emergency stop
C4-S04-P28 | C4 | 4 | 28 | 29 | 1756-OB32 | XS-61301F_DO_1 | Pin 29 | C4S4:29/C4S04-X2:29 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301F |  | - | Operation Release
C4-S04-P29 | C4 | 4 | 29 | 30 | 1756-OB32 | XV-61302_DO_1 | Pin 30 | C4S4:30/C4S04-X2:30 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | XV-61302 |  | 3-25-01-613-PD-02 | Dust collector feed vent
C4-S04-P30 | C4 | 4 | 30 | 31 | 1756-OB32 | XV-61303_DO_1 | Pin 31 | C4S4:31/C4S04-X2:31 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | XV-61303 |  | 3-25-01-613-PD-02 | Dust collector feed from packer
C4-S04-P31 | C4 | 4 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C4S4:32/C4S04-X2:32 | DO | 24VDC Sourcing | SPARE | JB-612 | Packing Tower 2th Floor | Packing Tower | C4S04-X2 | - | Spare | Spare Channel | - | -
C4-S05-P00 | C4 | 5 | 0 | 1 | 1756-IF16 | DPT-60201_AI_1 | Pin 1 | C4S5:1/C4S05-X1:1 | AI | 4-20mA HART | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S05-X1 | - | DPT-60201 | Differential Pressure Transmitte | 3-25-01-602-PD-09 | Steam filter pressure
C4-S05-P01 | C4 | 5 | 1 | 2 | 1756-IF16 | FT-60203_AI_1 | Pin 2 | C4S5:2/C4S05-X1:2 | AI | 4-20mA HART | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S05-X1 | - | FT-60203 |  | 3-25-01-602-PD-09 | Culinary steam feed to Spray dryer
C4-S05-P02 | C4 | 5 | 2 | 3 | 1756-IF16 | TT-60245_AI_1 | Pin 3 | C4S5:3/C4S05-X1:3 | AI | 4-20mA HART | ACTIVE | JB-608 | Spray Dryer 8th Floor | 8th / Spray Dryer | C4S05-X1 | - | TT-60245 |  | 3-25-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Stack (DTXS-21)
C4-S05-P03 | C4 | 5 | 3 | 4 | 1756-IF16 | Spare_AI_0 | Pin 4 | C4S5:4/C4S05-X1:4 | AI | 4-20mA HART | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P04 | C4 | 5 | 4 | 5 | 1756-IF16 | Spare_AI_0 | Pin 5 | C4S5:5/C4S05-X1:5 | AI | 4-20mA HART | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P05 | C4 | 5 | 5 | 6 | 1756-IF16 | Spare_AI_0 | Pin 6 | C4S5:6/C4S05-X1:6 | AI | 4-20mA HART | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P06 | C4 | 5 | 6 | 7 | 1756-IF16 | Spare_AI_0 | Pin 7 | C4S5:7/C4S05-X1:7 | AI | 4-20mA HART | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P06 | C4 | 5 | 6 | 7 | 1756-IF16 | Spare_AI_0 | Pin 7 | C4S5:7/C4S05-X1:7 | AI | 4-20mA HART | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P07 | C4 | 5 | 7 | 8 | 1756-IF16 | Spare_AI_0 | Pin 8 | C4S5:8/C4S05-X1:8 | AI | 4-20mA HART | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P07 | C4 | 5 | 7 | 8 | 1756-IF16 | Spare_AI_0 | Pin 8 | C4S5:8/C4S05-X1:8 | AI | 4-20mA HART | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P08 | C4 | 5 | 8 | 9 | 1756-IF16 | PT-61302_AI_1 | Pin 9 | C4S5:9/C4S05-X1:9 | AI | 4-20mA HART | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S05-X1 | - | PT-61302 | Pressure Transmitter | 3-25-01-613-PD-03 | Pressure in vacuum line
C4-S05-P09 | C4 | 5 | 9 | 10 | 1756-IF16 | PT-61309_AI_1 | Pin 10 | C4S5:10/C4S05-X1:10 | AI | 4-20mA HART | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S05-X1 | - | PT-61309 | Pressure Transmitter | 3-25-01-613-PD-04 | Pressure transmitter
C4-S05-P10 | C4 | 5 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C4S5:11/C4S05-X1:11 | AI | 4-20mA HART | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P11 | C4 | 5 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C4S5:12/C4S05-X1:12 | AI | 4-20mA HART | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P12 | C4 | 5 | 12 | 13 | 1756-IF16 | PT-61302_AI_1 | Pin 13 | C4S5:13/C4S05-X1:13 | AI | 4-20mA HART | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S05-X1 | - | PT-61302 | Pressure Transmitter | 3-25-01-613-PD-03 | Pressure in vacuum line
C4-S05-P13 | C4 | 5 | 13 | 14 | 1756-IF16 | PT-61309_AI_1 | Pin 14 | C4S5:14/C4S05-X1:14 | AI | 4-20mA HART | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S05-X1 | - | PT-61309 | Pressure Transmitter | 3-25-01-613-PD-04 | Pressure transmitter
C4-S05-P14 | C4 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P14 | C4 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P14 | C4 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P14 | C4 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P14 | C4 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P14 | C4 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P14 | C4 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P14 | C4 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P14 | C4 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S05-P15 | C4 | 5 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C4S5:16/C4S05-X1:16 | AI | 4-20mA HART | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | - | -
C4-S06-P00 | C4 | 6 | 0 | 1 | 1756-IF16 | PT-60220_AI_1 | Pin 1 | C4S6:1/C4S06-X1:1 | AI | 4-20mA HART | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S06-X1 | - | PT-60220 | Pressure Transmitter | 3-25-01-602-PD-04 | Gas Pressure Transmitter for Chamber (CHAM-21)
C4-S06-P01 | C4 | 6 | 1 | 2 | 1756-IF16 | TT-60220_AI_1 | Pin 2 | C4S6:2/C4S06-X1:2 | AI | 4-20mA HART | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S06-X1 | - | TT-60220 |  | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21)
C4-S06-P02 | C4 | 6 | 2 | 3 | 1756-IF16 | TT-60221_AI_1 | Pin 3 | C4S6:3/C4S06-X1:3 | AI | 4-20mA HART | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S06-X1 | - | TT-60221 |  | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21)
C4-S06-P03 | C4 | 6 | 3 | 4 | 1756-IF16 | TT-60222_AI_1 | Pin 4 | C4S6:4/C4S06-X1:4 | AI | 4-20mA HART | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S06-X1 | - | TT-60222 |  | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21)
C4-S06-P04 | C4 | 6 | 4 | 5 | 1756-IF16 | TT-60223_AI_1 | Pin 5 | C4S6:5/C4S06-X1:5 | AI | 4-20mA HART | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S06-X1 | - | TT-60223 |  | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21)
C4-S06-P05 | C4 | 6 | 5 | 6 | 1756-IF16 | XT-60201_AI_1 | Pin 6 | C4S6:6/C4S06-X1:6 | AI | 4-20mA HART | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S06-X1 | - | XT-60201 |  | 3-25-01-602-PD-03 | LEL gas analyzer
C4-S06-P06 | C4 | 6 | 6 | 7 | 1756-IF16 | DPT-61310_AI_1 | Pin 7 | C4S6:7/C4S06-X1:7 | AI | 4-20mA HART | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S06-X1 | - | DPT-61310 | Differential Pressure Transmitte | 3-25-01-613-PD-03 | Vent filter pressure
C4-S06-P07 | C4 | 6 | 7 | 8 | 1756-IF16 | DPT-61312_AI_1 | Pin 8 | C4S6:8/C4S06-X1:8 | AI | 4-20mA HART | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S06-X1 | - | DPT-61312 |  | 3-25-01-613-PD-05 | -
C5-S01-P00 | C5 | 1 | 0 | 1 | 1756-IB32 | FS-20201_DI_1 | Pin 1 | C5S1:1/C5S01-X1:1 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | FS-20201 |  | 3-25-01-202-PD-01 | -
C5-S01-P01 | C5 | 1 | 1 | 2 | 1756-IB32 | FT-913201_DI_1 | Pin 2 | C5S1:2/C5S01-X1:2 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X1 | - | FT-913201 |  | 3-25-01-913-PD-02 | Flow outlet LPG line
C5-S01-P02 | C5 | 1 | 2 | 3 | 1756-IB32 | FT-936201_DI_1 | Pin 3 | C5S1:3/C5S01-X1:3 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Process Water | C5S01-X1 | - | FT-936201 |  | 3-25-01-930-PD-08 | Process Water
C5-S01-P03 | C5 | 1 | 3 | 4 | 1756-IB32 | FT-936202_DI_1 | Pin 4 | C5S1:4/C5S01-X1:4 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Process Water | C5S01-X1 | - | FT-936202 |  | 3-25-01-930-PD-07 | Process Water
C5-S01-P04 | C5 | 1 | 4 | 5 | 1756-IB32 | LSL-814201_DI_1 | Pin 5 | C5S1:5/C5S01-X1:5 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / CIP Water System | C5S01-X1 | - | LSL-814201 |  | 3-25-01-814-PD-01 | Low Level alarm
C5-S01-P05 | C5 | 1 | 5 | 6 | 1756-IB32 | PK-913201_DI_1 | Pin 6 | C5S1:6/C5S01-X1:6 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X1 | - | PK-913201 |  | - | -
C5-S01-P06 | C5 | 1 | 6 | 7 | 1756-IB32 | PK-913202_DI_1 | Pin 7 | C5S1:7/C5S01-X1:7 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X1 | - | PK-913202 |  | - | -
C5-S01-P07 | C5 | 1 | 7 | 8 | 1756-IB32 | HV-20204_DI_1 | Pin 8 | C5S1:8/C5S01-X1:8 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20204 | Manual Valve With Position Switch | 3-25-01-202-PD-01 | Slurry Drain line
C5-S01-P08 | C5 | 1 | 8 | 9 | 1756-IB32 | HV-20205_DI_1 | Pin 9 | C5S1:9/C5S01-X1:9 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20205 | Manual Valve With Position Switch | 3-25-01-202-PD-01 | Slurry Drain line
C5-S01-P09 | C5 | 1 | 9 | 10 | 1756-IB32 | HV-20206_DI_1 | Pin 10 | C5S1:10/C5S01-X1:10 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20206 | Manual Valve With Position Switch | 3-25-01-202-PD-01 | Slurry Drain line
C5-S01-P10 | C5 | 1 | 10 | 11 | 1756-IB32 | HV-20207_DI_1 | Pin 11 | C5S1:11/C5S01-X1:11 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20207 | Manual Valve With Position Switch | 3-25-01-202-PD-01 | Slurry Drain line
C5-S01-P11 | C5 | 1 | 11 | 12 | 1756-IB32 | HV-20208_DI_1 | Pin 12 | C5S1:12/C5S01-X1:12 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20208 | Manual Valve With Position Switch | 3-25-01-202-PD-02 | Slurry Drain line
C5-S01-P12 | C5 | 1 | 12 | 13 | 1756-IB32 | HV-20209_DI_1 | Pin 13 | C5S1:13/C5S01-X1:13 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20209 | Manual Valve With Position Switch | 3-25-01-202-PD-02 | Slurry Drain line
C5-S01-P13 | C5 | 1 | 13 | 14 | 1756-IB32 | HV-20210_DI_1 | Pin 14 | C5S1:14/C5S01-X1:14 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20210 | Manual Valve With Position Switch | 3-25-01-202-PD-02 | Slurry Drain line
C5-S01-P14 | C5 | 1 | 14 | 15 | 1756-IB32 | XA-80305A_DI_1 | Pin 15 | C5S1:15/C5S01-X1:15 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X1 | - | XA-80305A |  | - | Gas Vaporizer 5 control status
C5-S01-P15 | C5 | 1 | 15 | 16 | 1756-IB32 | XA-80305B_DI_1 | Pin 16 | C5S1:16/C5S01-X1:16 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X1 | - | XA-80305B |  | - | Gas Vaporizer 5 control status
C5-S01-P16 | C5 | 1 | 16 | 17 | 1756-IB32 | XA-80305C_DI_1 | Pin 17 | C5S1:17/C5S01-X2:17 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80305C |  | - | Gas Vaporizer 5 control status
C5-S01-P17 | C5 | 1 | 17 | 18 | 1756-IB32 | XA-80305D_DI_1 | Pin 18 | C5S1:18/C5S01-X2:18 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80305D |  | - | Gas Vaporizer 5 control status
C5-S01-P18 | C5 | 1 | 18 | 19 | 1756-IB32 | XA-80305E_DI_1 | Pin 19 | C5S1:19/C5S01-X2:19 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80305E |  | - | Gas Vaporizer 5 control status
C5-S01-P19 | C5 | 1 | 19 | 20 | 1756-IB32 | XA-80305F_DI_1 | Pin 20 | C5S1:20/C5S01-X2:20 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80305F |  | - | Gas Vaporizer 5 control status
C5-S01-P20 | C5 | 1 | 20 | 21 | 1756-IB32 | XA-80306A_DI_1 | Pin 21 | C5S1:21/C5S01-X2:21 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80306A |  | - | Gas Vaporizer 6 control status
C5-S01-P21 | C5 | 1 | 21 | 22 | 1756-IB32 | XA-80306B_DI_1 | Pin 22 | C5S1:22/C5S01-X2:22 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80306B |  | - | Gas Vaporizer 6 control status
C5-S01-P22 | C5 | 1 | 22 | 23 | 1756-IB32 | XA-80306C_DI_1 | Pin 23 | C5S1:23/C5S01-X2:23 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80306C |  | - | Gas Vaporizer 6 control status
C5-S01-P23 | C5 | 1 | 23 | 24 | 1756-IB32 | XA-80306D_DI_1 | Pin 24 | C5S1:24/C5S01-X2:24 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80306D |  | - | Gas Vaporizer 6 control status
C5-S01-P24 | C5 | 1 | 24 | 25 | 1756-IB32 | XA-80306E_DI_1 | Pin 25 | C5S1:25/C5S01-X2:25 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80306E |  | - | Gas Vaporizer 6 control status
C5-S01-P25 | C5 | 1 | 25 | 26 | 1756-IB32 | XA-80306F_DI_1 | Pin 26 | C5S1:26/C5S01-X2:26 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80306F |  | - | Gas Vaporizer 6 control status
C5-S01-P26 | C5 | 1 | 26 | 27 | 1756-IB32 | XV-20201_DI_1 | Pin 27 | C5S1:27/C5S01-X2:27 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X2 | - | XV-20201 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 1
C5-S01-P27 | C5 | 1 | 27 | 28 | 1756-IB32 | XV-20201_DI_2 | Pin 28 | C5S1:28/C5S01-X2:28 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X2 | - | XV-20201 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 1
C5-S01-P28 | C5 | 1 | 28 | 29 | 1756-IB32 | XV-20202_DI_1 | Pin 29 | C5S1:29/C5S01-X2:29 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X2 | - | XV-20202 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 1
C5-S01-P29 | C5 | 1 | 29 | 30 | 1756-IB32 | XV-20202_DI_2 | Pin 30 | C5S1:30/C5S01-X2:30 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X2 | - | XV-20202 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 1
C5-S01-P30 | C5 | 1 | 30 | 31 | 1756-IB32 | XV-20203_DI_1 | Pin 31 | C5S1:31/C5S01-X2:31 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X2 | - | XV-20203 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 1
C5-S01-P31 | C5 | 1 | 31 | 32 | 1756-IB32 | XV-20203_DI_2 | Pin 32 | C5S1:32/C5S01-X2:32 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X2 | - | XV-20203 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 1
C5-S02-P00 | C5 | 2 | 0 | 1 | 1756-IB32 | XV-20211_DI_1 | Pin 1 | C5S2:1/C5S02-X1:1 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S02-X1 | - | XV-20211 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 2
C5-S02-P01 | C5 | 2 | 1 | 2 | 1756-IB32 | XV-20211_DI_2 | Pin 2 | C5S2:2/C5S02-X1:2 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S02-X1 | - | XV-20211 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 2
C5-S02-P02 | C5 | 2 | 2 | 3 | 1756-IB32 | XV-20212_DI_1 | Pin 3 | C5S2:3/C5S02-X1:3 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S02-X1 | - | XV-20212 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 2
C5-S02-P03 | C5 | 2 | 3 | 4 | 1756-IB32 | XV-20212_DI_2 | Pin 4 | C5S2:4/C5S02-X1:4 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S02-X1 | - | XV-20212 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 2
C5-S02-P04 | C5 | 2 | 4 | 5 | 1756-IB32 | XV-20213_DI_1 | Pin 5 | C5S2:5/C5S02-X1:5 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S02-X1 | - | XV-20213 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 2
C5-S02-P05 | C5 | 2 | 5 | 6 | 1756-IB32 | XV-20213_DI_2 | Pin 6 | C5S2:6/C5S02-X1:6 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S02-X1 | - | XV-20213 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 2
C5-S02-P06 | C5 | 2 | 6 | 7 | 1756-IB32 | XV-913201_DI_1 | Pin 7 | C5S2:7/C5S02-X1:7 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S02-X1 | - | XV-913201 |  | 3-25-01-913-PD-02 | Outlet LPG line
C5-S02-P07 | C5 | 2 | 7 | 8 | 1756-IB32 | XV-913201_DI_1 | Pin 8 | C5S2:8/C5S02-X1:8 | DI | 24VDC Dry Contact | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S02-X1 | - | XV-913201 |  | 3-25-01-913-PD-02 | Outlet LPG line
C5-S02-P08 | C5 | 2 | 8 | 9 | 1756-IB32 | Spare_DI_0 | Pin 9 | C5S2:9/C5S02-X1:9 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | - | -
C5-S02-P09 | C5 | 2 | 9 | 10 | 1756-IB32 | Spare_DI_0 | Pin 10 | C5S2:10/C5S02-X1:10 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | - | -
C5-S02-P10 | C5 | 2 | 10 | 11 | 1756-IB32 | Spare_DI_0 | Pin 11 | C5S2:11/C5S02-X1:11 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | - | -
C5-S02-P11 | C5 | 2 | 11 | 12 | 1756-IB32 | Spare_DI_0 | Pin 12 | C5S2:12/C5S02-X1:12 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | - | -
C5-S02-P12 | C5 | 2 | 12 | 13 | 1756-IB32 | Spare_DI_0 | Pin 13 | C5S2:13/C5S02-X1:13 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | - | -
C5-S02-P13 | C5 | 2 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C5S2:14/C5S02-X1:14 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | - | -
C5-S02-P14 | C5 | 2 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C5S2:15/C5S02-X1:15 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | - | -
C5-S02-P15 | C5 | 2 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C5S2:16/C5S02-X1:16 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | - | -
C5-S02-P16 | C5 | 2 | 16 | 17 | 1756-IB32 | Spare_DI_0 | Pin 17 | C5S2:17/C5S02-X2:17 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P17 | C5 | 2 | 17 | 18 | 1756-IB32 | Spare_DI_0 | Pin 18 | C5S2:18/C5S02-X2:18 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P18 | C5 | 2 | 18 | 19 | 1756-IB32 | Spare_DI_0 | Pin 19 | C5S2:19/C5S02-X2:19 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P19 | C5 | 2 | 19 | 20 | 1756-IB32 | Spare_DI_0 | Pin 20 | C5S2:20/C5S02-X2:20 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P20 | C5 | 2 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C5S2:21/C5S02-X2:21 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P21 | C5 | 2 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C5S2:22/C5S02-X2:22 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P22 | C5 | 2 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C5S2:23/C5S02-X2:23 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P23 | C5 | 2 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C5S2:24/C5S02-X2:24 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P24 | C5 | 2 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C5S2:25/C5S02-X2:25 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P25 | C5 | 2 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C5S2:26/C5S02-X2:26 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P26 | C5 | 2 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C5S2:27/C5S02-X2:27 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P27 | C5 | 2 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C5S2:28/C5S02-X2:28 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P28 | C5 | 2 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C5S2:29/C5S02-X2:29 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P29 | C5 | 2 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C5S2:30/C5S02-X2:30 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P30 | C5 | 2 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C5S2:31/C5S02-X2:31 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S02-P31 | C5 | 2 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C5S2:32/C5S02-X2:32 | DI | 24VDC Dry Contact | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | - | -
C5-S03-P00 | C5 | 3 | 0 | 1 | 1756-OB32 | XA-92201_DO_1 | Pin 1 | C5S3:1/C5S03-X1:1 | DO | 24VDC Sourcing | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Boiler System | C5S03-X1 | - | XA-92201 |  | 3-25-01-922-PD-03 | LEL gas Buzzer Alarm
C5-S03-P01 | C5 | 3 | 1 | 2 | 1756-OB32 | XV-20201_DO_1 | Pin 2 | C5S3:2/C5S03-X1:2 | DO | 24VDC Sourcing | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S03-X1 | - | XV-20201 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 1
C5-S03-P02 | C5 | 3 | 2 | 3 | 1756-OB32 | XV-20202_DO_1 | Pin 3 | C5S3:3/C5S03-X1:3 | DO | 24VDC Sourcing | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S03-X1 | - | XV-20202 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 1
C5-S03-P03 | C5 | 3 | 3 | 4 | 1756-OB32 | XV-20203_DO_1 | Pin 4 | C5S3:4/C5S03-X1:4 | DO | 24VDC Sourcing | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S03-X1 | - | XV-20203 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 1
C5-S03-P04 | C5 | 3 | 4 | 5 | 1756-OB32 | XV-20211_DO_1 | Pin 5 | C5S3:5/C5S03-X1:5 | DO | 24VDC Sourcing | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S03-X1 | - | XV-20211 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 2
C5-S03-P05 | C5 | 3 | 5 | 6 | 1756-OB32 | XV-20212_DO_1 | Pin 6 | C5S3:6/C5S03-X1:6 | DO | 24VDC Sourcing | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S03-X1 | - | XV-20212 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 2
C5-S03-P06 | C5 | 3 | 6 | 7 | 1756-OB32 | XV-20213_DO_1 | Pin 7 | C5S3:7/C5S03-X1:7 | DO | 24VDC Sourcing | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S03-X1 | - | XV-20213 |  | 3-25-01-202-PD-01 | Slurry Preparation Tank 2
C5-S03-P07 | C5 | 3 | 7 | 8 | 1756-OB32 | XV-913201_DO_1 | Pin 8 | C5S3:8/C5S03-X1:8 | DO | 24VDC Sourcing | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S03-X1 | - | XV-913201 |  | 3-25-01-913-PD-02 | Outlet LPG line
C5-S03-P08 | C5 | 3 | 8 | 9 | 1756-OB32 | Spare_DO_0 | Pin 9 | C5S3:9/C5S03-X1:9 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | - | -
C5-S03-P09 | C5 | 3 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C5S3:10/C5S03-X1:10 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | - | -
C5-S03-P10 | C5 | 3 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C5S3:11/C5S03-X1:11 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | - | -
C5-S03-P11 | C5 | 3 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C5S3:12/C5S03-X1:12 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | - | -
C5-S03-P12 | C5 | 3 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C5S3:13/C5S03-X1:13 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | - | -
C5-S03-P13 | C5 | 3 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C5S3:14/C5S03-X1:14 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | - | -
C5-S03-P14 | C5 | 3 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C5S3:15/C5S03-X1:15 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | - | -
C5-S03-P15 | C5 | 3 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C5S3:16/C5S03-X1:16 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | - | -
C5-S03-P16 | C5 | 3 | 16 | 17 | 1756-OB32 | Spare_DO_0 | Pin 17 | C5S3:17/C5S03-X2:17 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P17 | C5 | 3 | 17 | 18 | 1756-OB32 | Spare_DO_0 | Pin 18 | C5S3:18/C5S03-X2:18 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P18 | C5 | 3 | 18 | 19 | 1756-OB32 | Spare_DO_0 | Pin 19 | C5S3:19/C5S03-X2:19 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P19 | C5 | 3 | 19 | 20 | 1756-OB32 | Spare_DO_0 | Pin 20 | C5S3:20/C5S03-X2:20 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P20 | C5 | 3 | 20 | 21 | 1756-OB32 | Spare_DO_0 | Pin 21 | C5S3:21/C5S03-X2:21 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P21 | C5 | 3 | 21 | 22 | 1756-OB32 | Spare_DO_0 | Pin 22 | C5S3:22/C5S03-X2:22 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P22 | C5 | 3 | 22 | 23 | 1756-OB32 | Spare_DO_0 | Pin 23 | C5S3:23/C5S03-X2:23 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P23 | C5 | 3 | 23 | 24 | 1756-OB32 | Spare_DO_0 | Pin 24 | C5S3:24/C5S03-X2:24 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P24 | C5 | 3 | 24 | 25 | 1756-OB32 | Spare_DO_0 | Pin 25 | C5S3:25/C5S03-X2:25 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P25 | C5 | 3 | 25 | 26 | 1756-OB32 | Spare_DO_0 | Pin 26 | C5S3:26/C5S03-X2:26 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P26 | C5 | 3 | 26 | 27 | 1756-OB32 | Spare_DO_0 | Pin 27 | C5S3:27/C5S03-X2:27 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P27 | C5 | 3 | 27 | 28 | 1756-OB32 | Spare_DO_0 | Pin 28 | C5S3:28/C5S03-X2:28 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P28 | C5 | 3 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C5S3:29/C5S03-X2:29 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P29 | C5 | 3 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C5S3:30/C5S03-X2:30 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P30 | C5 | 3 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C5S3:31/C5S03-X2:31 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S03-P31 | C5 | 3 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C5S3:32/C5S03-X2:32 | DO | 24VDC Sourcing | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | - | -
C5-S04-P00 | C5 | 4 | 0 | 1 | 1756-IF16 | EXT-BIILER_AI_1 | Pin 1 | C5S4:1/C5S04-X1:1 | AI | 4-20mA HART | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Boiler System | C5S04-X1 | - | EXT-BIILER |  | External Remote Setpoint | -
C5-S04-P01 | C5 | 4 | 1 | 2 | 1756-IF16 | FT-913201_AI_1 | Pin 2 | C5S4:2/C5S04-X1:2 | AI | 4-20mA HART | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | FT-913201 |  | 3-25-01-913-PD-02 | Flow outlet LPG line
C5-S04-P02 | C5 | 4 | 2 | 3 | 1756-IF16 | FT-913201_AI_2 | Pin 3 | C5S4:3/C5S04-X1:3 | AI | 4-20mA HART | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | FT-913201 |  | 3-25-01-913-PD-02 | Flow outlet LPG line
C5-S04-P03 | C5 | 4 | 3 | 4 | 1756-IF16 | FT-936201_AI_1 | Pin 4 | C5S4:4/C5S04-X1:4 | AI | 4-20mA HART | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Process Water | C5S04-X1 | - | FT-936201 |  | 3-25-01-930-PD-08 | Process Water
C5-S04-P04 | C5 | 4 | 4 | 5 | 1756-IF16 | FT-936202_AI_1 | Pin 5 | C5S4:5/C5S04-X1:5 | AI | 4-20mA HART | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Process Water | C5S04-X1 | - | FT-936202 |  | 3-25-01-930-PD-07 | Process Water
C5-S04-P05 | C5 | 4 | 5 | 6 | 1756-IF16 | LT-913201_AI_1 | Pin 6 | C5S4:6/C5S04-X1:6 | AI | 4-20mA HART | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | LT-913201 | Level Transmitter | 3-25-01-913-PD-01 | Level LPG in storage
C5-S04-P06 | C5 | 4 | 6 | 7 | 1756-IF16 | PT-913201_AI_1 | Pin 7 | C5S4:7/C5S04-X1:7 | AI | 4-20mA HART | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | PT-913201 | Pressure Transmitter | 3-25-01-913-PD-02 | Pressure outlet LPG line
C5-S04-P07 | C5 | 4 | 7 | 8 | 1756-IF16 | XT-92201_AI_1 | Pin 8 | C5S4:8/C5S04-X1:8 | AI | 4-20mA HART | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Boiler System | C5S04-X1 | - | XT-92201 |  | 3-25-01-922-PD-03 | LEL gas analyzer
C5-S04-P08 | C5 | 4 | 8 | 9 | 1756-IF16 | XV-913201_AI_1 | Pin 9 | C5S4:9/C5S04-X1:9 | AI | 4-20mA HART | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | XV-913201 |  | 3-25-01-913-PD-02 | Outlet LPG line
C5-S04-P09 | C5 | 4 | 9 | 10 | 1756-IF16 | Spare_AI_0 | Pin 10 | C5S4:10/C5S04-X1:10 | AI | 4-20mA HART | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | Spare | Spare Channel | 3-25-01-913-PD-02 | -
C5-S04-P10 | C5 | 4 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C5S4:11/C5S04-X1:11 | AI | 4-20mA HART | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | Spare | Spare Channel | 3-25-01-913-PD-02 | -
C5-S04-P11 | C5 | 4 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C5S4:12/C5S04-X1:12 | AI | 4-20mA HART | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | Spare | Spare Channel | 3-25-01-913-PD-02 | -
C5-S04-P12 | C5 | 4 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C5S4:13/C5S04-X1:13 | AI | 4-20mA HART | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | Spare | Spare Channel | 3-25-01-913-PD-02 | -
C5-S04-P13 | C5 | 4 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C5S4:14/C5S04-X1:14 | AI | 4-20mA HART | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | Spare | Spare Channel | 3-25-01-913-PD-02 | -
C5-S04-P14 | C5 | 4 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C5S4:15/C5S04-X1:15 | AI | 4-20mA HART | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S04-X1 | - | Spare | Spare Channel | - | -
C5-S04-P15 | C5 | 4 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C5S4:16/C5S04-X1:16 | AI | 4-20mA HART | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S04-X1 | - | Spare | Spare Channel | - | -
C6-S05-P00 | C6 | 5 | 0 | 1 |  | PCM-2030_DO_1 | Pin 1 | C6S5:1/C6S05-:1 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S05- | - | PCM-2030 |  | 3-25-01-202-PD-01 | -
C6-S05-P01 | C6 | 5 | 1 | 2 |  | PCM-2030_DO_2 | Pin 2 | C6S5:2/C6S05-:2 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S05- | - | PCM-2030 |  | 3-25-01-202-PD-01 | -
C6-S05-P02 | C6 | 5 | 2 | 3 |  | PCM-2031_DO_1 | Pin 3 | C6S5:3/C6S05-:3 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S05- | - | PCM-2031 |  | 3-25-01-202-PD-01 | Start / Stop Command for FVNR PC-2031
C6-S05-P03 | C6 | 5 | 3 | 4 |  | PCM-2031_DO_2 | Pin 4 | C6S5:4/C6S05-:4 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S05- | - | PCM-2031 |  | 3-25-01-202-PD-01 | Start / Stop Command for FVNR PC-2031
C6-S05-P04 | C6 | 5 | 4 | 5 |  | PCY-814201_DO_1 | Pin 5 | C6S5:5/C6S05-:5 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S05- | - | PCY-814201 | PUMP | - | Start / Stop Command to VSD PC-81001
C6-S05-P05 | C6 | 5 | 5 | 6 |  | PCY-814202_DO_1 | Pin 6 | C6S5:6/C6S05-:6 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S05- | - | PCY-814202 | PUMP | - | Start / Stop Command to VSD PC-81002
C6-S05-P06 | C6 | 5 | 6 | 7 |  | XS-80305_DO_1 | Pin 7 | C6S5:7/C6S05-:7 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / LPG System | C6S05- | - | XS-80305 |  | - | Start / Stop Command for Gas Vaporizer 5
C6-S05-P07 | C6 | 5 | 7 | 8 |  | XS-80306_DO_1 | Pin 8 | C6S5:8/C6S05-:8 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / LPG System | C6S05- | - | XS-80306 | Pressure Transmitter | - | Start / Stop Command for Gas Vaporizer 6
C6-S06-P00 | C6 | 6 | 0 | 1 |  | PCM-2030_DI_1 | Pin 1 | C6S6:1/C6S06-:1 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S06- | - | PCM-2030 |  | 3-25-01-202-PD-01 | -
C6-S06-P01 | C6 | 6 | 1 | 2 |  | PCM-2030_DI_2 | Pin 2 | C6S6:2/C6S06-:2 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S06- | - | PCM-2030 |  | 3-25-01-202-PD-01 | -
C6-S06-P02 | C6 | 6 | 2 | 3 |  | PCM-2031_DI_1 | Pin 3 | C6S6:3/C6S06-:3 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S06- | - | PCM-2031 |  | 3-25-01-202-PD-01 | Start / Stop Command for FVNR PC-2031
C6-S06-P03 | C6 | 6 | 3 | 4 |  | PCM-2031_DI_2 | Pin 4 | C6S6:4/C6S06-:4 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S06- | - | PCM-2031 |  | 3-25-01-202-PD-01 | Start / Stop Command for FVNR PC-2031
C6-S06-P04 | C6 | 6 | 4 | 5 |  | PCY-814201_DI_1 | Pin 5 | C6S6:5/C6S06-:5 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S06- | - | PCY-814201 | PUMP | - | Start / Stop Command to VSD PC-81001
C6-S06-P05 | C6 | 6 | 5 | 6 |  | PCY-814201_DI_2 | Pin 6 | C6S6:6/C6S06-:6 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S06- | - | PCY-814201 | PUMP | - | Start / Stop Command to VSD PC-81001
C6-S06-P06 | C6 | 6 | 6 | 7 |  | PCY-814201_DI_3 | Pin 7 | C6S6:7/C6S06-:7 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S06- | - | PCY-814201 | PUMP | - | Start / Stop Command to VSD PC-81001
C6-S06-P07 | C6 | 6 | 7 | 8 |  | PCY-814202_DI_1 | Pin 8 | C6S6:8/C6S06-:8 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S06- | - | PCY-814202 | PUMP | - | Start / Stop Command to VSD PC-81002
C6-S06-P08 | C6 | 6 | 8 | 9 |  | PCY-814202_DI_2 | Pin 9 | C6S6:9/C6S06-:9 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S06- | - | PCY-814202 | PUMP | - | Start / Stop Command to VSD PC-81002
C6-S06-P09 | C6 | 6 | 9 | 10 |  | PCY-814202_DI_3 | Pin 10 | C6S6:10/C6S06-:10 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S06- | - | PCY-814202 | PUMP | - | Start / Stop Command to VSD PC-81002
C7-S00-P00 | C7 | 0 | 0 | 1 |  | ATY-40201_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S00- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40201
C7-S00-P00 | C7 | 0 | 0 | 1 |  | ATY-40202_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S00- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40202
C7-S00-P00 | C7 | 0 | 0 | 1 |  | ATY-40203_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S00- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02 | Start / Stop Command for VSD AT-40203
C7-S00-P00 | C7 | 0 | 0 | 1 |  | BFY-60206_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S00- | - | BFY-60206 |  | - | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan)
C7-S00-P00 | C7 | 0 | 0 | 1 |  | BFY-60210_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S00- | - | BFY-60210 |  | - | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan)
C7-S00-P00 | C7 | 0 | 0 | 1 |  | BFY-60211_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S00- | - | BFY-60211 |  | - | Start / Stop Command for VSD FANC-21 (Combustion Fan)
C7-S00-P00 | C7 | 0 | 0 | 1 |  | BFY-60220_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S00- | - | BFY-60220 |  | - | Start / Stop Command for VSD FANS-22 (Cooling Fan)
C7-S00-P00 | C7 | 0 | 0 | 1 |  | BFY-60240_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S00- | - | BFY-60240 |  | - | Start / Stop Command for VSD FANE-21 (Exhaust Fan)
C7-S00-P00 | C7 | 0 | 0 | 1 |  | BFY-61301_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S00- | - | BFY-61301 |  | - | Start / Stop Command for VSD BF-61301 (Packing silo vent fan )
C7-S00-P00 | C7 | 0 | 0 | 1 |  | BFY-61302_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 2nd / Packing Tower | C7S00- | - | BFY-61302 |  | - | Start / Stop Command for VSD BF-61302 (LEV Blower fan )
C7-S00-P00 | C7 | 0 | 0 | 1 |  | BFY-61303_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S00- | - | BFY-61303 |  | - | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan )
C7-S00-P00 | C7 | 0 | 0 | 1 |  | COM-FH-60210B_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C7S00- | - | COM-FH-60210B |  | - | Communication Signal
C7-S00-P00 | C7 | 0 | 0 | 1 |  | Communication Signal_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C7S00- | - | Communication Signal |  | - | -
C7-S00-P00 | C7 | 0 | 0 | 1 |  | PCY-40201_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S00- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40201
C7-S00-P00 | C7 | 0 | 0 | 1 |  | PCY-40202_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S00- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40202
C7-S00-P00 | C7 | 0 | 0 | 1 |  | PCY-40203_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S00- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump)
C7-S00-P00 | C7 | 0 | 0 | 1 |  | PCY-60205_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S00- | - | PCY-60205 |  | - | -
C7-S00-P00 | C7 | 0 | 0 | 1 |  | PCY-60215_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S00- | - | PCY-60215 | PUMP | - | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump)
C7-S00-P00 | C7 | 0 | 0 | 1 |  | PCY-814201_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C7S00- | - | PCY-814201 | PUMP | - | Start / Stop Command to VSD PC-81001
C7-S00-P00 | C7 | 0 | 0 | 1 |  | PCY-814202_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C7S00- | - | PCY-814202 | PUMP | - | Start / Stop Command to VSD PC-81002
C7-S01-P00 | C7 | 1 | 0 | 1 |  | Spare_DI_0 | Pin 1 | C7S1:1/C7S01-:1 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S01-P01 | C7 | 1 | 1 | 2 |  | Spare_DI_0 | Pin 2 | C7S1:2/C7S01-:2 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S01-P02 | C7 | 1 | 2 | 3 |  | Spare_DI_0 | Pin 3 | C7S1:3/C7S01-:3 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S01-P03 | C7 | 1 | 3 | 4 |  | Spare_DI_0 | Pin 4 | C7S1:4/C7S01-:4 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S01-P04 | C7 | 1 | 4 | 5 |  | Spare_DI_0 | Pin 5 | C7S1:5/C7S01-:5 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S01-P05 | C7 | 1 | 5 | 6 |  | Spare_DI_0 | Pin 6 | C7S1:6/C7S01-:6 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S01-P06 | C7 | 1 | 6 | 7 |  | Spare_DI_0 | Pin 7 | C7S1:7/C7S01-:7 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S01-P07 | C7 | 1 | 7 | 8 |  | Spare_DI_0 | Pin 8 | C7S1:8/C7S01-:8 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S01-P08 | C7 | 1 | 8 | 9 |  | ATY-40201_DI_1 | Pin 9 | C7S1:9/C7S01-:9 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40201
C7-S01-P09 | C7 | 1 | 9 | 10 |  | ATY-40201_DI_2 | Pin 10 | C7S1:10/C7S01-:10 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40201
C7-S01-P10 | C7 | 1 | 10 | 11 |  | ATY-40201_DI_3 | Pin 11 | C7S1:11/C7S01-:11 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40201
C7-S01-P11 | C7 | 1 | 11 | 12 |  | ATY-40202_DI_1 | Pin 12 | C7S1:12/C7S01-:12 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40202
C7-S01-P12 | C7 | 1 | 12 | 13 |  | ATY-40202_DI_2 | Pin 13 | C7S1:13/C7S01-:13 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40202
C7-S01-P13 | C7 | 1 | 13 | 14 |  | ATY-40202_DI_3 | Pin 14 | C7S1:14/C7S01-:14 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40202
C7-S01-P14 | C7 | 1 | 14 | 15 |  | ATY-40203_DI_1 | Pin 15 | C7S1:15/C7S01-:15 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02 | Start / Stop Command for VSD AT-40203
C7-S01-P15 | C7 | 1 | 15 | 16 |  | ATY-40203_DI_2 | Pin 16 | C7S1:16/C7S01-:16 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02 | Start / Stop Command for VSD AT-40203
C7-S01-P16 | C7 | 1 | 16 | 17 |  | ATY-40203_DI_3 | Pin 17 | C7S1:17/C7S01-:17 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02 | Start / Stop Command for VSD AT-40203
C7-S01-P17 | C7 | 1 | 17 | 18 |  | PCY-40201_DI_1 | Pin 18 | C7S1:18/C7S01-:18 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40201
C7-S01-P18 | C7 | 1 | 18 | 19 |  | PCY-40201_DI_2 | Pin 19 | C7S1:19/C7S01-:19 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40201
C7-S01-P19 | C7 | 1 | 19 | 20 |  | PCY-40201_DI_3 | Pin 20 | C7S1:20/C7S01-:20 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40201
C7-S01-P20 | C7 | 1 | 20 | 21 |  | PCY-40202_DI_1 | Pin 21 | C7S1:21/C7S01-:21 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40202
C7-S01-P21 | C7 | 1 | 21 | 22 |  | PCY-40202_DI_2 | Pin 22 | C7S1:22/C7S01-:22 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40202
C7-S01-P22 | C7 | 1 | 22 | 23 |  | PCY-40202_DI_3 | Pin 23 | C7S1:23/C7S01-:23 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40202
C7-S01-P23 | C7 | 1 | 23 | 24 |  | PCY-40203_DI_1 | Pin 24 | C7S1:24/C7S01-:24 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump)
C7-S01-P24 | C7 | 1 | 24 | 25 |  | PCY-40203_DI_2 | Pin 25 | C7S1:25/C7S01-:25 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump)
C7-S01-P25 | C7 | 1 | 25 | 26 |  | PCY-40203_DI_3 | Pin 26 | C7S1:26/C7S01-:26 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump)
C7-S01-P26 | C7 | 1 | 26 | 27 |  | BFY-60206_DI_1 | Pin 27 | C7S1:27/C7S01-:27 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | BFY-60206 |  | - | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan)
C7-S01-P27 | C7 | 1 | 27 | 28 |  | PCM-60205-2_DI_1 | Pin 28 | C7S1:28/C7S01-:28 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-2 |  | - | -
C7-S01-P28 | C7 | 1 | 28 | 29 |  | PCM-60205-2_DI_2 | Pin 29 | C7S1:29/C7S01-:29 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-2 |  | - | -
C7-S01-P29 | C7 | 1 | 29 | 30 |  | PCM-60205-3_DI_1 | Pin 30 | C7S1:30/C7S01-:30 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-3 |  | - | -
C7-S01-P30 | C7 | 1 | 30 | 31 |  | PCM-60205-3_DI_2 | Pin 31 | C7S1:31/C7S01-:31 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-3 |  | - | -
C7-S01-P31 | C7 | 1 | 31 | 32 |  | PCM-60205-4_DI_1 | Pin 32 | C7S1:32/C7S01-:32 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-4 |  | - | -
C7-S02-P00 | C7 | 2 | 0 | 1 |  | PCM-60205-4_DI_2 | Pin 1 | C7S2:1/C7S02-:1 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | PCM-60205-4 |  | - | -
C7-S02-P01 | C7 | 2 | 1 | 2 |  | PCM-60205-5_DI_1 | Pin 2 | C7S2:2/C7S02-:2 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | PCM-60205-5 |  | - | -
C7-S02-P02 | C7 | 2 | 2 | 3 |  | PCM-60205-5_DI_2 | Pin 3 | C7S2:3/C7S02-:3 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | PCM-60205-5 |  | - | -
C7-S02-P03 | C7 | 2 | 3 | 4 |  | PCY-60205_DI_1 | Pin 4 | C7S2:4/C7S02-:4 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S02- | - | PCY-60205 |  | - | -
C7-S02-P04 | C7 | 2 | 4 | 5 |  | PCY-60205_DI_2 | Pin 5 | C7S2:5/C7S02-:5 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S02- | - | PCY-60205 |  | - | -
C7-S02-P05 | C7 | 2 | 5 | 6 |  | RVM-60201_DI_1 | Pin 6 | C7S2:6/C7S02-:6 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60201 |  | - | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve )
C7-S02-P06 | C7 | 2 | 6 | 7 |  | RVM-60201_DI_2 | Pin 7 | C7S2:7/C7S02-:7 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60201 |  | - | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve )
C7-S02-P07 | C7 | 2 | 7 | 8 |  | RVM-60202_DI_1 | Pin 8 | C7S2:8/C7S02-:8 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60202 |  | - | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve )
C7-S02-P08 | C7 | 2 | 8 | 9 |  | RVM-60202_DI_2 | Pin 9 | C7S2:9/C7S02-:9 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60202 |  | - | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve )
C7-S02-P09 | C7 | 2 | 9 | 10 |  | RVM-60203_DI_1 | Pin 10 | C7S2:10/C7S02-:10 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60203 |  | - | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve)
C7-S02-P10 | C7 | 2 | 10 | 11 |  | RVM-60203_DI_2 | Pin 11 | C7S2:11/C7S02-:11 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60203 |  | - | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve)
C7-S02-P11 | C7 | 2 | 11 | 12 |  | BFY-60210_DI_1 | Pin 12 | C7S2:12/C7S02-:12 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | BFY-60210 |  | - | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan)
C7-S02-P12 | C7 | 2 | 12 | 13 |  | BFY-60211_DI_1 | Pin 13 | C7S2:13/C7S02-:13 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | BFY-60211 |  | - | Start / Stop Command for VSD FANC-21 (Combustion Fan)
C7-S02-P13 | C7 | 2 | 13 | 14 |  | BFY-60240_DI_1 | Pin 14 | C7S2:14/C7S02-:14 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | BFY-60240 |  | - | Start / Stop Command for VSD FANE-21 (Exhaust Fan)
C7-S02-P14 | C7 | 2 | 14 | 15 |  | PCY-60215_DI_1 | Pin 15 | C7S2:15/C7S02-:15 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | PCY-60215 | PUMP | - | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump)
C7-S02-P15 | C7 | 2 | 15 | 16 |  | PCY-60215_DI_2 | Pin 16 | C7S2:16/C7S02-:16 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | PCY-60215 | PUMP | - | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump)
C7-S02-P16 | C7 | 2 | 16 | 17 |  | PCY-60215_DI_3 | Pin 17 | C7S2:17/C7S02-:17 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | PCY-60215 | PUMP | - | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump)
C7-S02-P17 | C7 | 2 | 17 | 18 |  | BFY-60220_DI_1 | Pin 18 | C7S2:18/C7S02-:18 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S02- | - | BFY-60220 |  | - | Start / Stop Command for VSD FANS-22 (Cooling Fan)
C7-S02-P18 | C7 | 2 | 18 | 19 |  | BFY-61302_DI_1 | Pin 19 | C7S2:19/C7S02-:19 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 2nd / Packing Tower | C7S02- | - | BFY-61302 |  | - | Start / Stop Command for VSD BF-61302 (LEV Blower fan )
C7-S02-P19 | C7 | 2 | 19 | 20 |  | HS-61307F_DI_1 | Pin 20 | C7S2:20/C7S02-:20 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S02- | - | HS-61307F |  | 3-25-01-613-PD-03 | Start/Stop
C7-S02-P20 | C7 | 2 | 20 | 21 |  | HS-61307G_DI_1 | Pin 21 | C7S2:21/C7S02-:21 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 3rd / Packing Tower | C7S02- | - | HS-61307G |  | 3-25-01-613-PD-03 | Start/Stop
C7-S02-P21 | C7 | 2 | 21 | 22 |  | HS-61307H_DI_1 | Pin 22 | C7S2:22/C7S02-:22 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 3rd / Packing Tower | C7S02- | - | HS-61307H |  | 3-25-01-613-PD-03 | Start/Stop
C7-S02-P22 | C7 | 2 | 22 | 23 |  | HS-61307I_DI_1 | Pin 23 | C7S2:23/C7S02-:23 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307I |  | 3-25-01-613-PD-03 | Start/Stop
C7-S02-P23 | C7 | 2 | 23 | 24 |  | HS-61307J_DI_1 | Pin 24 | C7S2:24/C7S02-:24 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307J |  | 3-25-01-613-PD-03 | Start/Stop
C7-S02-P24 | C7 | 2 | 24 | 25 |  | HS-61307K_DI_1 | Pin 25 | C7S2:25/C7S02-:25 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307K |  | 3-25-01-613-PD-03 | Start/Stop
C7-S02-P25 | C7 | 2 | 25 | 26 |  | HS-61307L_DI_1 | Pin 26 | C7S2:26/C7S02-:26 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307L |  | 3-25-01-613-PD-03 | Start/Stop
C7-S02-P26 | C7 | 2 | 26 | 27 |  | HS-61307M_DI_1 | Pin 27 | C7S2:27/C7S02-:27 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307M |  | 3-25-01-613-PD-03 | Start/Stop
C7-S02-P27 | C7 | 2 | 27 | 28 |  | HS-61307N_DI_1 | Pin 28 | C7S2:28/C7S02-:28 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307N |  | 3-25-01-613-PD-03 | Start/Stop
C7-S02-P28 | C7 | 2 | 28 | 29 |  | HS-61307O_DI_1 | Pin 29 | C7S2:29/C7S02-:29 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307O |  | 3-25-01-613-PD-03 | Start/Stop
C7-S02-P29 | C7 | 2 | 29 | 30 |  | HS-61307P_DI_1 | Pin 30 | C7S2:30/C7S02-:30 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307P |  | 3-25-01-613-PD-03 | Start/Stop
C7-S02-P30 | C7 | 2 | 30 | 31 |  | HS-61307Q_DI_1 | Pin 31 | C7S2:31/C7S02-:31 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307Q |  | 3-25-01-613-PD-03 | Start/Stop
C7-S02-P31 | C7 | 2 | 31 | 32 |  | HS-61307R_DI_1 | Pin 32 | C7S2:32/C7S02-:32 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307R |  | 3-25-01-613-PD-03 | Start/Stop
C7-S03-P00 | C7 | 3 | 0 | 1 |  | RVM-61302_DI_1 | Pin 1 | C7S3:1/C7S03-:1 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S03- | - | RVM-61302 |  | - | Start / Stop Command for FVNR RV-61302
C7-S03-P01 | C7 | 3 | 1 | 2 |  | RVM-61302_DI_2 | Pin 2 | C7S3:2/C7S03-:2 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S03- | - | RVM-61302 |  | - | Start / Stop Command for FVNR RV-61302
C7-S03-P02 | C7 | 3 | 2 | 3 |  | RVM-61303_DI_1 | Pin 3 | C7S3:3/C7S03-:3 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S03- | - | RVM-61303 |  | - | Start / Stop Command for FVNR RV-61303
C7-S03-P03 | C7 | 3 | 3 | 4 |  | RVM-61303_DI_2 | Pin 4 | C7S3:4/C7S03-:4 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S03- | - | RVM-61303 |  | - | Start / Stop Command for FVNR RV-61303
C7-S03-P04 | C7 | 3 | 4 | 5 |  | SCM-61301_DI_1 | Pin 5 | C7S3:5/C7S03-:5 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S03- | - | SCM-61301 |  | - | Start / Stop Command for FVNR SC-61301 (Sifter )
C7-S03-P05 | C7 | 3 | 5 | 6 |  | SCM-61301_DI_2 | Pin 6 | C7S3:6/C7S03-:6 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S03- | - | SCM-61301 |  | - | Start / Stop Command for FVNR SC-61301 (Sifter )
C7-S03-P06 | C7 | 3 | 6 | 7 |  | SCM-61302_DI_2 | Pin 7 | C7S3:7/C7S03-:7 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S03- | - | SCM-61302 |  | - | Start / Stop Command for FVNR SC-61302 (Sifter )
C7-S03-P07 | C7 | 3 | 7 | 8 |  | SCM-61302_DI_1 | Pin 8 | C7S3:8/C7S03-:8 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S03- | - | SCM-61302 |  | - | Start / Stop Command for FVNR SC-61302 (Sifter )
C7-S03-P08 | C7 | 3 | 8 | 9 |  | BFY-61301_DI_1 | Pin 9 | C7S3:9/C7S03-:9 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S03- | - | BFY-61301 |  | - | Start / Stop Command for VSD BF-61301 (Packing silo vent fan )
C7-S03-P09 | C7 | 3 | 9 | 10 |  | BFY-61303_DI_1 | Pin 10 | C7S3:10/C7S03-:10 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | BFY-61303 |  | - | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan )
C7-S03-P10 | C7 | 3 | 10 | 11 |  | BLM-61302_DI_1 | Pin 11 | C7S3:11/C7S03-:11 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S03- | - | BLM-61302 |  | - | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower )
C7-S03-P11 | C7 | 3 | 11 | 12 |  | BLM-61302_DI_2 | Pin 12 | C7S3:12/C7S03-:12 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S03- | - | BLM-61302 |  | - | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower )
C7-S03-P12 | C7 | 3 | 12 | 13 |  | HS-61307A_DI_1 | Pin 13 | C7S3:13/C7S03-:13 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S03- | - | HS-61307A |  | 3-25-01-613-PD-03 | Start/Stop
C7-S03-P13 | C7 | 3 | 13 | 14 |  | HS-61307B_DI_1 | Pin 14 | C7S3:14/C7S03-:14 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S03- | - | HS-61307B |  | 3-25-01-613-PD-03 | Start/Stop
C7-S03-P14 | C7 | 3 | 14 | 15 |  | HS-61307C_DI_1 | Pin 15 | C7S3:15/C7S03-:15 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 7th / Packing Tower | C7S03- | - | HS-61307C |  | 3-25-01-613-PD-03 | Start/Stop
C7-S03-P15 | C7 | 3 | 15 | 16 |  | HS-61307D_DI_1 | Pin 16 | C7S3:16/C7S03-:16 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S03- | - | HS-61307D |  | 3-25-01-613-PD-03 | Start/Stop
C7-S03-P16 | C7 | 3 | 16 | 17 |  | HS-61307E_DI_1 | Pin 17 | C7S3:17/C7S03-:17 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S03- | - | HS-61307E |  | 3-25-01-613-PD-03 | Start/Stop
C7-S03-P17 | C7 | 3 | 17 | 18 |  | RVM-60204_DI_1 | Pin 18 | C7S3:18/C7S03-:18 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-60204 |  | - | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve)
C7-S03-P18 | C7 | 3 | 18 | 19 |  | RVM-60204_DI_2 | Pin 19 | C7S3:19/C7S03-:19 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-60204 |  | - | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve)
C7-S03-P19 | C7 | 3 | 19 | 20 |  | RVM-61301_DI_1 | Pin 20 | C7S3:20/C7S03-:20 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 6th / Packing Tower | C7S03- | - | RVM-61301 |  | - | Start / Stop Command for FVNR RV-61301
C7-S03-P20 | C7 | 3 | 20 | 21 |  | RVM-61301_DI_2 | Pin 21 | C7S3:21/C7S03-:21 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 6th / Packing Tower | C7S03- | - | RVM-61301 |  | - | Start / Stop Command for FVNR RV-61301
C7-S03-P21 | C7 | 3 | 21 | 22 |  | RVM-61304_DI_1 | Pin 22 | C7S3:22/C7S03-:22 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-61304 |  | - | Start / Stop Command for FVNR RV-61304
C7-S03-P22 | C7 | 3 | 22 | 23 |  | RVM-61304_DI_2 | Pin 23 | C7S3:23/C7S03-:23 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-61304 |  | - | Start / Stop Command for FVNR RV-61304
C7-S03-P23 | C7 | 3 | 23 | 24 |  | RVM-61305_DI_1 | Pin 24 | C7S3:24/C7S03-:24 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-61305 |  | - | Start / Stop Command for FVNR RV-61305
C7-S03-P24 | C7 | 3 | 24 | 25 |  | RVM-61305_DI_2 | Pin 25 | C7S3:25/C7S03-:25 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-61305 |  | - | Start / Stop Command for FVNR RV-61305
C7-S03-P25 | C7 | 3 | 25 | 26 |  | PCY-60205_DI_3 | Pin 26 | C7S3:26/C7S03-:26 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S03- | - | PCY-60205 |  | - | -
C7-S04-P04 | C7 | 4 | 4 | 5 |  | Spare_DI_0 | Pin 5 | C7S4:5/C7S04-:5 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P05 | C7 | 4 | 5 | 6 |  | Spare_DI_0 | Pin 6 | C7S4:6/C7S04-:6 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P06 | C7 | 4 | 6 | 7 |  | Spare_DI_0 | Pin 7 | C7S4:7/C7S04-:7 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P07 | C7 | 4 | 7 | 8 |  | Spare_DI_0 | Pin 8 | C7S4:8/C7S04-:8 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P08 | C7 | 4 | 8 | 9 |  | Spare_DI_0 | Pin 9 | C7S4:9/C7S04-:9 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P09 | C7 | 4 | 9 | 10 |  | Spare_DI_0 | Pin 10 | C7S4:10/C7S04-:10 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P10 | C7 | 4 | 10 | 11 |  | Spare_DI_0 | Pin 11 | C7S4:11/C7S04-:11 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P11 | C7 | 4 | 11 | 12 |  | Spare_DI_0 | Pin 12 | C7S4:12/C7S04-:12 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P12 | C7 | 4 | 12 | 13 |  | Spare_DI_0 | Pin 13 | C7S4:13/C7S04-:13 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P13 | C7 | 4 | 13 | 14 |  | Spare_DI_0 | Pin 14 | C7S4:14/C7S04-:14 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P14 | C7 | 4 | 14 | 15 |  | Spare_DI_0 | Pin 15 | C7S4:15/C7S04-:15 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P15 | C7 | 4 | 15 | 16 |  | Spare_DI_0 | Pin 16 | C7S4:16/C7S04-:16 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P16 | C7 | 4 | 16 | 17 |  | Spare_DI_0 | Pin 17 | C7S4:17/C7S04-:17 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P17 | C7 | 4 | 17 | 18 |  | Spare_DI_0 | Pin 18 | C7S4:18/C7S04-:18 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P18 | C7 | 4 | 18 | 19 |  | Spare_DI_0 | Pin 19 | C7S4:19/C7S04-:19 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P19 | C7 | 4 | 19 | 20 |  | Spare_DI_0 | Pin 20 | C7S4:20/C7S04-:20 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P20 | C7 | 4 | 20 | 21 |  | Spare_DI_0 | Pin 21 | C7S4:21/C7S04-:21 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P21 | C7 | 4 | 21 | 22 |  | Spare_DI_0 | Pin 22 | C7S4:22/C7S04-:22 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P22 | C7 | 4 | 22 | 23 |  | Spare_DI_0 | Pin 23 | C7S4:23/C7S04-:23 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P23 | C7 | 4 | 23 | 24 |  | Spare_DI_0 | Pin 24 | C7S4:24/C7S04-:24 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P24 | C7 | 4 | 24 | 25 |  | Spare_DI_0 | Pin 25 | C7S4:25/C7S04-:25 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P25 | C7 | 4 | 25 | 26 |  | Spare_DI_0 | Pin 26 | C7S4:26/C7S04-:26 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P26 | C7 | 4 | 26 | 27 |  | Spare_DI_0 | Pin 27 | C7S4:27/C7S04-:27 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P27 | C7 | 4 | 27 | 28 |  | Spare_DI_0 | Pin 28 | C7S4:28/C7S04-:28 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P28 | C7 | 4 | 28 | 29 |  | Spare_DI_0 | Pin 29 | C7S4:29/C7S04-:29 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P29 | C7 | 4 | 29 | 30 |  | Spare_DI_0 | Pin 30 | C7S4:30/C7S04-:30 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P30 | C7 | 4 | 30 | 31 |  | Spare_DI_0 | Pin 31 | C7S4:31/C7S04-:31 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S04-P31 | C7 | 4 | 31 | 32 |  | Spare_DI_0 | Pin 32 | C7S4:32/C7S04-:32 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | - | -
C7-S05-P00 | C7 | 5 | 0 | 1 |  | Spare_DO_0 | Pin 1 | C7S5:1/C7S05-:1 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S05-P01 | C7 | 5 | 1 | 2 |  | Spare_DO_0 | Pin 2 | C7S5:2/C7S05-:2 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S05-P02 | C7 | 5 | 2 | 3 |  | Spare_DO_0 | Pin 3 | C7S5:3/C7S05-:3 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S05-P03 | C7 | 5 | 3 | 4 |  | Spare_DO_0 | Pin 4 | C7S5:4/C7S05-:4 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S05-P04 | C7 | 5 | 4 | 5 |  | Spare_DO_0 | Pin 5 | C7S5:5/C7S05-:5 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S05-P05 | C7 | 5 | 5 | 6 |  | Spare_DO_0 | Pin 6 | C7S5:6/C7S05-:6 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S05-P06 | C7 | 5 | 6 | 7 |  | Spare_DO_0 | Pin 7 | C7S5:7/C7S05-:7 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S05-P07 | C7 | 5 | 7 | 8 |  | Spare_DO_0 | Pin 8 | C7S5:8/C7S05-:8 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01 | -
C7-S05-P08 | C7 | 5 | 8 | 9 |  | ATY-40201_DO_1 | Pin 9 | C7S5:9/C7S05-:9 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40201
C7-S05-P09 | C7 | 5 | 9 | 10 |  | ATY-40202_DO_1 | Pin 10 | C7S5:10/C7S05-:10 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40202
C7-S05-P10 | C7 | 5 | 10 | 11 |  | ATY-40203_DO_1 | Pin 11 | C7S5:11/C7S05-:11 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S05- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02 | Start / Stop Command for VSD AT-40203
C7-S05-P11 | C7 | 5 | 11 | 12 |  | PCY-40201_DO_1 | Pin 12 | C7S5:12/C7S05-:12 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40201
C7-S05-P12 | C7 | 5 | 12 | 13 |  | PCY-40202_DO_1 | Pin 13 | C7S5:13/C7S05-:13 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40202
C7-S05-P13 | C7 | 5 | 13 | 14 |  | PCY-40203_DO_1 | Pin 14 | C7S5:14/C7S05-:14 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S05- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump)
C7-S05-P14 | C7 | 5 | 14 | 15 |  | BFY-60206_DO_1 | Pin 15 | C7S5:15/C7S05-:15 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | BFY-60206 |  | - | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan)
C7-S05-P15 | C7 | 5 | 15 | 16 |  | PCM-60205-2_DO_1 | Pin 16 | C7S5:16/C7S05-:16 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-2 |  | - | -
C7-S05-P16 | C7 | 5 | 16 | 17 |  | PCM-60205-2_DO_2 | Pin 17 | C7S5:17/C7S05-:17 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-2 |  | - | -
C7-S05-P17 | C7 | 5 | 17 | 18 |  | PCM-60205-3_DO_1 | Pin 18 | C7S5:18/C7S05-:18 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-3 |  | - | -
C7-S05-P18 | C7 | 5 | 18 | 19 |  | PCM-60205-3_DO_2 | Pin 19 | C7S5:19/C7S05-:19 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-3 |  | - | -
C7-S05-P19 | C7 | 5 | 19 | 20 |  | PCM-60205-4_DO_1 | Pin 20 | C7S5:20/C7S05-:20 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-4 |  | - | -
C7-S05-P20 | C7 | 5 | 20 | 21 |  | PCM-60205-4_DO_2 | Pin 21 | C7S5:21/C7S05-:21 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-4 |  | - | -
C7-S05-P21 | C7 | 5 | 21 | 22 |  | PCM-60205-5_DO_1 | Pin 22 | C7S5:22/C7S05-:22 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-5 |  | - | -
C7-S05-P22 | C7 | 5 | 22 | 23 |  | PCM-60205-5_DO_2 | Pin 23 | C7S5:23/C7S05-:23 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-5 |  | - | -
C7-S05-P23 | C7 | 5 | 23 | 24 |  | RVM-60201_DO_1 | Pin 24 | C7S5:24/C7S05-:24 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60201 |  | - | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve )
C7-S05-P24 | C7 | 5 | 24 | 25 |  | RVM-60201_DO_2 | Pin 25 | C7S5:25/C7S05-:25 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60201 |  | - | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve )
C7-S05-P25 | C7 | 5 | 25 | 26 |  | RVM-60202_DO_1 | Pin 26 | C7S5:26/C7S05-:26 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60202 |  | - | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve )
C7-S05-P26 | C7 | 5 | 26 | 27 |  | RVM-60202_DO_2 | Pin 27 | C7S5:27/C7S05-:27 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60202 |  | - | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve )
C7-S05-P27 | C7 | 5 | 27 | 28 |  | RVM-60203_DO_1 | Pin 28 | C7S5:28/C7S05-:28 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60203 |  | - | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve)
C7-S05-P28 | C7 | 5 | 28 | 29 |  | RVM-60203_DO_2 | Pin 29 | C7S5:29/C7S05-:29 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60203 |  | - | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve)
C7-S05-P29 | C7 | 5 | 29 | 30 |  | XS-60205_DO_1 | Pin 30 | C7S5:30/C7S05-:30 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | XS-60205 |  | - | Start / Stop Command for PUPD-11 (Positive Displacement Pump )
C7-S05-P30 | C7 | 5 | 30 | 31 |  | BFY-60210_DO_1 | Pin 31 | C7S5:31/C7S05-:31 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S05- | - | BFY-60210 |  | - | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan)
C7-S05-P31 | C7 | 5 | 31 | 32 |  | BFY-60211_DO_1 | Pin 32 | C7S5:32/C7S05-:32 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S05- | - | BFY-60211 |  | - | Start / Stop Command for VSD FANC-21 (Combustion Fan)
C7-S06-P00 | C7 | 6 | 0 | 1 |  | BFY-60240_DO_1 | Pin 1 | C7S6:1/C7S06-:1 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S06- | - | BFY-60240 |  | - | Start / Stop Command for VSD FANE-21 (Exhaust Fan)
C7-S06-P01 | C7 | 6 | 1 | 2 |  | PCY-60215_DO_1 | Pin 2 | C7S6:2/C7S06-:2 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S06- | - | PCY-60215 | PUMP | - | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump)
C7-S06-P02 | C7 | 6 | 2 | 3 |  | XS-60240A_DO_1 | Pin 3 | C7S6:3/C7S06-:3 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Spray Dryer | C7S06- | - | XS-60240A |  | - | Start / Stop Command for BGHS-21 (Bag House Air Pulsing)
C7-S06-P03 | C7 | 6 | 3 | 4 |  | XS-60241A_DO_1 | Pin 4 | C7S6:4/C7S06-:4 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Spray Dryer | C7S06- | - | XS-60241A |  | - | Start / Stop Command for HTRE-21 (Heater Control Panel)
C7-S06-P04 | C7 | 6 | 4 | 5 |  | XS-60242A_DO_1 | Pin 5 | C7S6:5/C7S06-:5 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 3rd / Spray Dryer | C7S06- | - | XS-60242A |  | - | Start / Stop Command for HTRE-21 (Heater Control Panel)
C7-S06-P04 | C7 | 6 | 4 | 5 |  | XS-60243A_DO_1 | Pin 5 | C7S6:5/C7S06-:5 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Spray Dryer | C7S06- | - | XS-60243A |  | - | Start / Stop Command for HTRE-21 (Heater Control Panel)
C7-S06-P06 | C7 | 6 | 6 | 7 |  | XS-60260_DO_1 | Pin 7 | C7S6:7/C7S06-:7 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 6th / Spray Dryer | C7S06- | - | XS-60260 |  | - | Start / Stop Command for FWDP-21 (Fire Deluge)
C7-S06-P07 | C7 | 6 | 7 | 8 |  | BFY-60220_DO_1 | Pin 8 | C7S6:8/C7S06-:8 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S06- | - | BFY-60220 |  | - | Start / Stop Command for VSD FANS-22 (Cooling Fan)
C7-S06-P08 | C7 | 6 | 8 | 9 |  | XS-FH-60210A_DO_1 | Pin 9 | C7S6:9/C7S06-:9 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S06- | - | XS-FH-60210A |  | - | Start / Stop Command Burner Remote Start for AHTR-21
C7-S06-P09 | C7 | 6 | 9 | 10 |  | XS-FH-60210B_DO_1 | Pin 10 | C7S6:10/C7S06-:10 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S06- | - | XS-FH-60210B |  | - | Start / Stop Command Dryer Interlocks for AHTR-21
C7-S06-P10 | C7 | 6 | 10 | 11 |  | BFY-61302_DO_1 | Pin 11 | C7S6:11/C7S06-:11 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 2nd / Packing Tower | C7S06- | - | BFY-61302 |  | - | Start / Stop Command for VSD BF-61302 (LEV Blower fan )
C7-S06-P11 | C7 | 6 | 11 | 12 |  | RVM-61302_DO_1 | Pin 12 | C7S6:12/C7S06-:12 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S06- | - | RVM-61302 |  | - | Start / Stop Command for FVNR RV-61302
C7-S06-P12 | C7 | 6 | 12 | 13 |  | RVM-61302_DO_2 | Pin 13 | C7S6:13/C7S06-:13 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S06- | - | RVM-61302 |  | - | Start / Stop Command for FVNR RV-61302
C7-S06-P13 | C7 | 6 | 13 | 14 |  | RVM-61303_DO_1 | Pin 14 | C7S6:14/C7S06-:14 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S06- | - | RVM-61303 |  | - | Start / Stop Command for FVNR RV-61303
C7-S06-P14 | C7 | 6 | 14 | 15 |  | RVM-61303_DO_2 | Pin 15 | C7S6:15/C7S06-:15 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S06- | - | RVM-61303 |  | - | Start / Stop Command for FVNR RV-61303
C7-S06-P15 | C7 | 6 | 15 | 16 |  | SCM-61301_DO_1 | Pin 16 | C7S6:16/C7S06-:16 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S06- | - | SCM-61301 |  | - | Start / Stop Command for FVNR SC-61301 (Sifter )
C7-S06-P16 | C7 | 6 | 16 | 17 |  | SCM-61301_DO_2 | Pin 17 | C7S6:17/C7S06-:17 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S06- | - | SCM-61301 |  | - | Start / Stop Command for FVNR SC-61301 (Sifter )
C7-S06-P17 | C7 | 6 | 17 | 18 |  | SCM-61302_DO_1 | Pin 18 | C7S6:18/C7S06-:18 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S06- | - | SCM-61302 |  | - | Start / Stop Command for FVNR SC-61302 (Sifter )
C7-S06-P18 | C7 | 6 | 18 | 19 |  | SCM-61302_DO_2 | Pin 19 | C7S6:19/C7S06-:19 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S06- | - | SCM-61302 |  | - | Start / Stop Command for FVNR SC-61302 (Sifter )
C7-S06-P19 | C7 | 6 | 19 | 20 |  | BFY-61301_DO_1 | Pin 20 | C7S6:20/C7S06-:20 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S06- | - | BFY-61301 |  | - | Start / Stop Command for VSD BF-61301 (Packing silo vent fan )
C7-S06-P20 | C7 | 6 | 20 | 21 |  | BFY-61303_DO_1 | Pin 21 | C7S6:21/C7S06-:21 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | BFY-61303 |  | - | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan )
C7-S06-P21 | C7 | 6 | 21 | 22 |  | BLM-61302_DO_1 | Pin 22 | C7S6:22/C7S06-:22 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S06- | - | BLM-61302 |  | - | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower )
C7-S06-P22 | C7 | 6 | 22 | 23 |  | BLM-61302_DO_2 | Pin 23 | C7S6:23/C7S06-:23 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S06- | - | BLM-61302 |  | - | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower )
C7-S06-P23 | C7 | 6 | 23 | 24 |  | RVM-60204_DO_1 | Pin 24 | C7S6:24/C7S06-:24 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-60204 |  | - | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve)
C7-S06-P24 | C7 | 6 | 24 | 25 |  | RVM-60204_DO_2 | Pin 25 | C7S6:25/C7S06-:25 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-60204 |  | - | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve)
C7-S06-P25 | C7 | 6 | 25 | 26 |  | RVM-61301_DO_1 | Pin 26 | C7S6:26/C7S06-:26 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 6th / Packing Tower | C7S06- | - | RVM-61301 |  | - | Start / Stop Command for FVNR RV-61301
C7-S06-P26 | C7 | 6 | 26 | 27 |  | RVM-61301_DO_2 | Pin 27 | C7S6:27/C7S06-:27 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 6th / Packing Tower | C7S06- | - | RVM-61301 |  | - | Start / Stop Command for FVNR RV-61301
C7-S06-P27 | C7 | 6 | 27 | 28 |  | RVM-61304_DO_1 | Pin 28 | C7S6:28/C7S06-:28 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-61304 |  | - | Start / Stop Command for FVNR RV-61304
C7-S06-P28 | C7 | 6 | 28 | 29 |  | RVM-61304_DO_2 | Pin 29 | C7S6:29/C7S06-:29 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-61304 |  | - | Start / Stop Command for FVNR RV-61304
C7-S06-P29 | C7 | 6 | 29 | 30 |  | RVM-61305_DO_1 | Pin 30 | C7S6:30/C7S06-:30 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-61305 |  | - | Start / Stop Command for FVNR RV-61305
C7-S06-P30 | C7 | 6 | 30 | 31 |  | RVM-61305_DO_2 | Pin 31 | C7S6:31/C7S06-:31 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-61305 |  | - | Start / Stop Command for FVNR RV-61305
C7-S06-P31 | C7 | 6 | 31 | 32 |  | PCY-60205_DO_1 | Pin 32 | C7S6:32/C7S06-:32 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S06- | - | PCY-60205 |  | - | -
C7-S07-P08 | C7 | 7 | 8 | 9 |  | Spare_DO_0 | Pin 9 | C7S7:9/C7S07-:9 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P09 | C7 | 7 | 9 | 10 |  | Spare_DO_0 | Pin 10 | C7S7:10/C7S07-:10 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P10 | C7 | 7 | 10 | 11 |  | Spare_DO_0 | Pin 11 | C7S7:11/C7S07-:11 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P11 | C7 | 7 | 11 | 12 |  | Spare_DO_0 | Pin 12 | C7S7:12/C7S07-:12 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P12 | C7 | 7 | 12 | 13 |  | Spare_DO_0 | Pin 13 | C7S7:13/C7S07-:13 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P13 | C7 | 7 | 13 | 14 |  | Spare_DO_0 | Pin 14 | C7S7:14/C7S07-:14 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P14 | C7 | 7 | 14 | 15 |  | Spare_DO_0 | Pin 15 | C7S7:15/C7S07-:15 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P15 | C7 | 7 | 15 | 16 |  | Spare_DO_0 | Pin 16 | C7S7:16/C7S07-:16 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P16 | C7 | 7 | 16 | 17 |  | Spare_DO_0 | Pin 17 | C7S7:17/C7S07-:17 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P17 | C7 | 7 | 17 | 18 |  | Spare_DO_0 | Pin 18 | C7S7:18/C7S07-:18 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P18 | C7 | 7 | 18 | 19 |  | Spare_DO_0 | Pin 19 | C7S7:19/C7S07-:19 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P19 | C7 | 7 | 19 | 20 |  | Spare_DO_0 | Pin 20 | C7S7:20/C7S07-:20 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P20 | C7 | 7 | 20 | 21 |  | Spare_DO_0 | Pin 21 | C7S7:21/C7S07-:21 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P21 | C7 | 7 | 21 | 22 |  | Spare_DO_0 | Pin 22 | C7S7:22/C7S07-:22 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P22 | C7 | 7 | 22 | 23 |  | Spare_DO_0 | Pin 23 | C7S7:23/C7S07-:23 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P23 | C7 | 7 | 23 | 24 |  | Spare_DO_0 | Pin 24 | C7S7:24/C7S07-:24 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P24 | C7 | 7 | 24 | 25 |  | Spare_DO_0 | Pin 25 | C7S7:25/C7S07-:25 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P25 | C7 | 7 | 25 | 26 |  | Spare_DO_0 | Pin 26 | C7S7:26/C7S07-:26 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P26 | C7 | 7 | 26 | 27 |  | Spare_DO_0 | Pin 27 | C7S7:27/C7S07-:27 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P27 | C7 | 7 | 27 | 28 |  | Spare_DO_0 | Pin 28 | C7S7:28/C7S07-:28 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P28 | C7 | 7 | 28 | 29 |  | Spare_DO_0 | Pin 29 | C7S7:29/C7S07-:29 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P29 | C7 | 7 | 29 | 30 |  | Spare_DO_0 | Pin 30 | C7S7:30/C7S07-:30 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P30 | C7 | 7 | 30 | 31 |  | Spare_DO_0 | Pin 31 | C7S7:31/C7S07-:31 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -
C7-S07-P31 | C7 | 7 | 31 | 32 |  | Spare_DO_0 | Pin 32 | C7S7:32/C7S07-:32 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | - | -

## Chassis_C1
KALASIN ENGINEERING — C1 (MAIN CONTROLLER RACK (CHASSIS 1))
Location: Control Cabinet CA1 (Main Control Room) ¦ Role: 1756-L950TPSXT Controller + DLR Ring Supervisor + Local Fast I/O ¦ Net: Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) ¦ Total Points: 224 (Active: 138, Spare: 86)
SOURCE (PLC RACK / SLOT / TERMINAL / ePLAN TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Type | Status | Destination | Field Location | Floor/Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing
Slot 03 — Module: 1756-IB32 (DI) ¦ Total: 32 Channels (Active: 16, Spare: 16)
C1-S03-P00 | 3 | 0 | 1 | 1756-IB32 | Spare_DI_0 | Pin 1 | C1S3:1/C1S03-X1:1 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P01 | 3 | 1 | 2 | 1756-IB32 | Spare_DI_0 | Pin 2 | C1S3:2/C1S03-X1:2 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P02 | 3 | 2 | 3 | 1756-IB32 | Spare_DI_0 | Pin 3 | C1S3:3/C1S03-X1:3 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P03 | 3 | 3 | 4 | 1756-IB32 | Spare_DI_0 | Pin 4 | C1S3:4/C1S03-X1:4 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P04 | 3 | 4 | 5 | 1756-IB32 | Spare_DI_0 | Pin 5 | C1S3:5/C1S03-X1:5 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P05 | 3 | 5 | 6 | 1756-IB32 | Spare_DI_0 | Pin 6 | C1S3:6/C1S03-X1:6 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P06 | 3 | 6 | 7 | 1756-IB32 | Spare_DI_0 | Pin 7 | C1S3:7/C1S03-X1:7 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P07 | 3 | 7 | 8 | 1756-IB32 | Spare_DI_0 | Pin 8 | C1S3:8/C1S03-X1:8 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P08 | 3 | 8 | 9 | 1756-IB32 | Spare_DI_0 | Pin 9 | C1S3:9/C1S03-X1:9 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P09 | 3 | 9 | 10 | 1756-IB32 | Spare_DI_0 | Pin 10 | C1S3:10/C1S03-X1:10 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P10 | 3 | 10 | 11 | 1756-IB32 | Spare_DI_0 | Pin 11 | C1S3:11/C1S03-X1:11 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P11 | 3 | 11 | 12 | 1756-IB32 | Spare_DI_0 | Pin 12 | C1S3:12/C1S03-X1:12 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P12 | 3 | 12 | 13 | 1756-IB32 | Spare_DI_0 | Pin 13 | C1S3:13/C1S03-X1:13 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P13 | 3 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C1S3:14/C1S03-X1:14 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P14 | 3 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C1S3:15/C1S03-X1:15 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P15 | 3 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C1S3:16/C1S03-X1:16 | DI | 24VDC | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P16 | 3 | 16 | 17 | 1756-IB32 | FSL-40201_DI_1 | Pin 17 | C1S3:17/C1S03-X2:17 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | FSL-40201 | Flow Switch | 3-25-01-402-PD-01
C1-S03-P17 | 3 | 17 | 18 | 1756-IB32 | FSL-40202_DI_1 | Pin 18 | C1S3:18/C1S03-X2:18 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | FSL-40202 | Flow Switch | 3-25-01-402-PD-01
C1-S03-P18 | 3 | 18 | 19 | 1756-IB32 | FT-40201_DI_1 | Pin 19 | C1S3:19/C1S03-X2:19 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | FT-40201 | Coriolis Flow Transmitter | 3-25-01-402-PD-02
C1-S03-P19 | 3 | 19 | 20 | 1756-IB32 | FT-40202_DI_1 | Pin 20 | C1S3:20/C1S03-X2:20 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | FT-40202 | Magnetic Flow Transmitter | 3-25-01-402-PD-02
C1-S03-P20 | 3 | 20 | 21 | 1756-IB32 | HV-40201_DI_1 | Pin 21 | C1S3:21/C1S03-X2:21 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40201 | Manual Valve With Position Switch | 3-25-01-402-PD-01
C1-S03-P21 | 3 | 21 | 22 | 1756-IB32 | HV-40202_DI_1 | Pin 22 | C1S3:22/C1S03-X2:22 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40202 | Manual Valve With Position Switch | 3-25-01-402-PD-01
C1-S03-P22 | 3 | 22 | 23 | 1756-IB32 | HV-40203_DI_1 | Pin 23 | C1S3:23/C1S03-X2:23 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40203 | Manual Valve With Position Switch | 3-25-01-402-PD-01
C1-S03-P23 | 3 | 23 | 24 | 1756-IB32 | HV-40204_DI_1 | Pin 24 | C1S3:24/C1S03-X2:24 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40204 | Manual Valve With Position Switch | 3-25-01-402-PD-01
C1-S03-P24 | 3 | 24 | 25 | 1756-IB32 | HV-40205_DI_1 | Pin 25 | C1S3:25/C1S03-X2:25 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | HV-40205 | Manual Valve With Position Switch | 3-25-01-402-PD-02
C1-S03-P25 | 3 | 25 | 26 | 1756-IB32 | HV-40206_DI_1 | Pin 26 | C1S3:26/C1S03-X2:26 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | HV-40206 | Manual Valve With Position Switch | 3-25-01-402-PD-02
C1-S03-P26 | 3 | 26 | 27 | 1756-IB32 | XV-40201A_DI_1 | Pin 27 | C1S3:27/C1S03-X2:27 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201A |  | 3-25-01-402-PD-01
C1-S03-P27 | 3 | 27 | 28 | 1756-IB32 | XV-40201A_DI_2 | Pin 28 | C1S3:28/C1S03-X2:28 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201A |  | 3-25-01-402-PD-01
C1-S03-P28 | 3 | 28 | 29 | 1756-IB32 | XV-40201B_DI_1 | Pin 29 | C1S3:29/C1S03-X2:29 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201B |  | 3-25-01-402-PD-01
C1-S03-P29 | 3 | 29 | 30 | 1756-IB32 | XV-40201B_DI_2 | Pin 30 | C1S3:30/C1S03-X2:30 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201B |  | 3-25-01-402-PD-01
C1-S03-P30 | 3 | 30 | 31 | 1756-IB32 | XV-40201C_DI_1 | Pin 31 | C1S3:31/C1S03-X2:31 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201C |  | 3-25-01-402-PD-01
C1-S03-P31 | 3 | 31 | 32 | 1756-IB32 | XV-40201C_DI_2 | Pin 32 | C1S3:32/C1S03-X2:32 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201C |  | 3-25-01-402-PD-01
Slot 04 — Module: 1756-IB32 (DI) ¦ Total: 32 Channels (Active: 32, Spare: 0)
C1-S04-P00 | 4 | 0 | 1 | 1756-IB32 | XV-40201D_DI_1 | Pin 1 | C1S4:1/TBDI1:1A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201D |  | 3-25-01-402-PD-01
C1-S04-P01 | 4 | 1 | 2 | 1756-IB32 | XV-40201D_DI_2 | Pin 2 | C1S4:2/TBDI1:2A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201D |  | 3-25-01-402-PD-01
C1-S04-P02 | 4 | 2 | 3 | 1756-IB32 | XV-40201E_DI_1 | Pin 3 | C1S4:3/TBDI1:3A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201E |  | 3-25-01-402-PD-01
C1-S04-P03 | 4 | 3 | 4 | 1756-IB32 | XV-40201E_DI_2 | Pin 4 | C1S4:4/TBDI1:4A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201E |  | 3-25-01-402-PD-01
C1-S04-P04 | 4 | 4 | 5 | 1756-IB32 | XV-40201F_DI_1 | Pin 5 | C1S4:5/TBDI1:5A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201F |  | 3-25-01-402-PD-01
C1-S04-P05 | 4 | 5 | 6 | 1756-IB32 | XV-40201F_DI_2 | Pin 6 | C1S4:6/TBDI1:6A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201F |  | 3-25-01-402-PD-01
C1-S04-P06 | 4 | 6 | 7 | 1756-IB32 | XV-40201G_DI_1 | Pin 7 | C1S4:7/TBDI1:7A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201G |  | 3-25-01-402-PD-01
C1-S04-P07 | 4 | 7 | 8 | 1756-IB32 | XV-40201G_DI_2 | Pin 8 | C1S4:8/TBDI1:8A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201G |  | 3-25-01-402-PD-01
C1-S04-P08 | 4 | 8 | 9 | 1756-IB32 | XV-40201H_DI_1 | Pin 9 | C1S4:9/TBDI1:9A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201H |  | 3-25-01-402-PD-01
C1-S04-P09 | 4 | 9 | 10 | 1756-IB32 | XV-40201H_DI_2 | Pin 10 | C1S4:10/TBDI1:10A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201H |  | 3-25-01-402-PD-01
C1-S04-P11 | 4 | 11 | 12 | 1756-IB32 | XV-40202A_DI_2 | Pin 12 | C1S4:12/TBDI1:12A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202A |  | 3-25-01-402-PD-01
C1-S04-P12 | 4 | 12 | 13 | 1756-IB32 | XV-40202B_DI_1 | Pin 13 | C1S4:13/TBDI1:13A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202B |  | 3-25-01-402-PD-01
C1-S04-P13 | 4 | 13 | 14 | 1756-IB32 | XV-40202B_DI_2 | Pin 14 | C1S4:14/TBDI1:14A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202B |  | 3-25-01-402-PD-01
C1-S04-P14 | 4 | 14 | 15 | 1756-IB32 | XV-40202C_DI_1 | Pin 15 | C1S4:15/TBDI1:15A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202C |  | 3-25-01-402-PD-01
C1-S04-P15 | 4 | 15 | 16 | 1756-IB32 | XV-40202C_DI_2 | Pin 16 | C1S4:16/TBDI1:16A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202C |  | 3-25-01-402-PD-01
C1-S04-P16 | 4 | 16 | 17 | 1756-IB32 | XV-40202D_DI_1 | Pin 17 | C1S4:17/C1S04-X2:17 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202D |  | 3-25-01-402-PD-01
C1-S04-P17 | 4 | 17 | 18 | 1756-IB32 | XV-40202D_DI_2 | Pin 18 | C1S4:18/C1S04-X2:18 | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202D |  | 3-25-01-402-PD-01
C1-S04-P18 | 4 | 18 | 19 | 1756-IB32 | XV-40202E_DI_1 | Pin 19 | C1S4:19/TBDI1:17A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202E |  | 3-25-01-402-PD-01
C1-S04-P19 | 4 | 19 | 20 | 1756-IB32 | XV-40202A_DI_1 | Pin 20 | C1S4:20/TBDI1:18A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202A |  | 3-25-01-402-PD-01
C1-S04-P19 | 4 | 19 | 20 | 1756-IB32 | XV-40202E_DI_2 | Pin 20 | C1S4:20/TBDI1:18A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202E |  | 3-25-01-402-PD-01
C1-S04-P20 | 4 | 20 | 21 | 1756-IB32 | XV-40202F_DI_1 | Pin 21 | C1S4:21/TBDI1:19A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202F |  | 3-25-01-402-PD-01
C1-S04-P21 | 4 | 21 | 22 | 1756-IB32 | XV-40202F_DI_2 | Pin 22 | C1S4:22/TBDI1:20A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202F |  | 3-25-01-402-PD-01
C1-S04-P22 | 4 | 22 | 23 | 1756-IB32 | XV-40202G_DI_1 | Pin 23 | C1S4:23/TBDI1:21A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202G |  | 3-25-01-402-PD-01
C1-S04-P23 | 4 | 23 | 24 | 1756-IB32 | XV-40202G_DI_2 | Pin 24 | C1S4:24/TBDI1:22A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202G |  | 3-25-01-402-PD-01
C1-S04-P24 | 4 | 24 | 25 | 1756-IB32 | XV-40202H_DI_1 | Pin 25 | C1S4:25/TBDI1:23A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202H |  | 3-25-01-402-PD-01
C1-S04-P25 | 4 | 25 | 26 | 1756-IB32 | XV-40202H_DI_2 | Pin 26 | C1S4:26/TBDI1:24A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202H |  | 3-25-01-402-PD-01
C1-S04-P26 | 4 | 26 | 27 | 1756-IB32 | XV-40203B_DI_1 | Pin 27 | C1S4:27/TBDI1:25A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203B |  | 3-25-01-402-PD-02
C1-S04-P27 | 4 | 27 | 28 | 1756-IB32 | XV-40203B_DI_2 | Pin 28 | C1S4:28/TBDI1:26A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203B |  | 3-25-01-402-PD-02
C1-S04-P28 | 4 | 28 | 29 | 1756-IB32 | XV-40203C_DI_1 | Pin 29 | C1S4:29/TBDI1:27A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203C |  | 3-25-01-402-PD-02
C1-S04-P29 | 4 | 29 | 30 | 1756-IB32 | XV-40203C_DI_2 | Pin 30 | C1S4:30/TBDI1:28A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203C |  | 3-25-01-402-PD-02
C1-S04-P30 | 4 | 30 | 31 | 1756-IB32 | XV-40203D_DI_1 | Pin 31 | C1S4:31/TBDI1:29A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203D |  | 3-25-01-402-PD-02
C1-S04-P31 | 4 | 31 | 32 | 1756-IB32 | XV-40203D_DI_2 | Pin 32 | C1S4:32/TBDI1:30A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203D |  | 3-25-01-402-PD-02
Slot 05 — Module: 1756-IB32 (DI) ¦ Total: 32 Channels (Active: 12, Spare: 20)
C1-S05-P00 | 5 | 0 | 1 | 1756-IB32 | XV-40203E_DI_1 | Pin 1 | C1S5:1/TBDI2:1A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S05-X1 | - | XV-40203E |  | 3-25-01-402-PD-02
C1-S05-P01 | 5 | 1 | 2 | 1756-IB32 | XV-40203E_DI_2 | Pin 2 | C1S5:2/TBDI2:2A | DI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S05-X1 | - | XV-40203E |  | 3-25-01-402-PD-02
C1-S05-P02 | 5 | 2 | 3 | 1756-IB32 | Spare_DI_0 | Pin 3 | C1S5:3/TBDI2:3A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P03 | 5 | 3 | 4 | 1756-IB32 | Spare_DI_0 | Pin 4 | C1S5:4/TBDI2:4A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P04 | 5 | 4 | 5 | 1756-IB32 | Spare_DI_0 | Pin 5 | C1S5:5/TBDI2:5A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P05 | 5 | 5 | 6 | 1756-IB32 | Spare_DI_0 | Pin 6 | C1S5:6/TBDI2:6A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P06 | 5 | 6 | 7 | 1756-IB32 | Spare_DI_0 | Pin 7 | C1S5:7/TBDI2:7A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P07 | 5 | 7 | 8 | 1756-IB32 | Spare_DI_0 | Pin 8 | C1S5:8/TBDI2:8A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P08 | 5 | 8 | 9 | 1756-IB32 | Spare_DI_0 | Pin 9 | C1S5:9/TBDI2:9A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P09 | 5 | 9 | 10 | 1756-IB32 | Spare_DI_0 | Pin 10 | C1S5:10/TBDI2:10A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P10 | 5 | 10 | 11 | 1756-IB32 | Spare_DI_0 | Pin 11 | C1S5:11/TBDI2:11A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P11 | 5 | 11 | 12 | 1756-IB32 | Spare_DI_0 | Pin 12 | C1S5:12/TBDI2:12A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P12 | 5 | 12 | 13 | 1756-IB32 | Spare_DI_0 | Pin 13 | C1S5:13/TBDI2:13A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P13 | 5 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C1S5:14/TBDI2:14A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P14 | 5 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C1S5:15/TBDI2:15A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P15 | 5 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C1S5:16/TBDI2:16A | DI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P16 | 5 | 16 | 17 | 1756-IB32 | ES-60202_DI_1 | Pin 17 | C1S5:17/C1S05-X2:17 | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | ES-60202 |  | -
C1-S05-P17 | 5 | 17 | 18 | 1756-IB32 | FS-60205_DI_1 | Pin 18 | C1S5:18/C1S05-X2:18 | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | FS-60205 | Flow Switch | 3-25-01-602-PD-01
C1-S05-P18 | 5 | 18 | 19 | 1756-IB32 | LSL-60201_DI_1 | Pin 19 | C1S5:19/TBDI2:17A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | LSL-60201 |  | 3-25-01-602-PD-11
C1-S05-P19 | 5 | 19 | 20 | 1756-IB32 | SV-60201_DI_1 | Pin 20 | C1S5:20/TBDI2:18A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60201 |  | 3-25-01-602-PD-08
C1-S05-P20 | 5 | 20 | 21 | 1756-IB32 | SV-60201_DI_2 | Pin 21 | C1S5:21/TBDI2:19A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60201 |  | 3-25-01-602-PD-08
C1-S05-P21 | 5 | 21 | 22 | 1756-IB32 | SV-60202_DI_1 | Pin 22 | C1S5:22/TBDI2:20A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60202 |  | 3-25-01-602-PD-08
C1-S05-P22 | 5 | 22 | 23 | 1756-IB32 | SV-60202_DI_2 | Pin 23 | C1S5:23/TBDI2:21A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60202 |  | 3-25-01-602-PD-08
C1-S05-P23 | 5 | 23 | 24 | 1756-IB32 | SV-60203_DI_1 | Pin 24 | C1S5:24/TBDI2:22A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60203 |  | 3-25-01-602-PD-08
C1-S05-P24 | 5 | 24 | 25 | 1756-IB32 | SV-60203_DI_2 | Pin 25 | C1S5:25/TBDI2:23A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60203 |  | 3-25-01-602-PD-08
C1-S05-P25 | 5 | 25 | 26 | 1756-IB32 | VS-60205_DI_1 | Pin 26 | C1S5:26/TBDI2:24A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | VS-60205 | Vibration Switch | 3-25-01-602-PD-01
C1-S05-P26 | 5 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C1S5:27/TBDI2:25A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | -
C1-S05-P27 | 5 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C1S5:28/TBDI2:26A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | -
C1-S05-P28 | 5 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C1S5:29/TBDI2:27A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | -
C1-S05-P29 | 5 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C1S5:30/TBDI2:28A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | -
C1-S05-P30 | 5 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C1S5:31/TBDI2:29A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | -
C1-S05-P31 | 5 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C1S5:32/TBDI2:30A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | -
Slot 06 — Module: 1756-IB32 (DI) ¦ Total: 32 Channels (Active: 23, Spare: 9)
C1-S06-P00 | 6 | 0 | 1 | 1756-IB32 | XA-60202A_DI_1 | Pin 1 | C1S6:1/TBDI3:1A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202A |  | -
C1-S06-P01 | 6 | 1 | 2 | 1756-IB32 | XA-60202B_DI_1 | Pin 2 | C1S6:2/TBDI3:2A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202B |  | -
C1-S06-P02 | 6 | 2 | 3 | 1756-IB32 | XA-60202C_DI_1 | Pin 3 | C1S6:3/TBDI3:3A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202C |  | -
C1-S06-P03 | 6 | 3 | 4 | 1756-IB32 | XA-60202D_DI_1 | Pin 4 | C1S6:4/TBDI3:4A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202D |  | -
C1-S06-P04 | 6 | 4 | 5 | 1756-IB32 | XA-60202E_DI_1 | Pin 5 | C1S6:5/TBDI3:5A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202E |  | -
C1-S06-P05 | 6 | 5 | 6 | 1756-IB32 | XA-60202F_DI_1 | Pin 6 | C1S6:6/TBDI3:6A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202F |  | -
C1-S06-P06 | 6 | 6 | 7 | 1756-IB32 | XA-60202G_DI_1 | Pin 7 | C1S6:7/TBDI3:7A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202G |  | -
C1-S06-P07 | 6 | 7 | 8 | 1756-IB32 | XA-60202H_DI_1 | Pin 8 | C1S6:8/TBDI3:8A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202H |  | -
C1-S06-P08 | 6 | 8 | 9 | 1756-IB32 | XA-60202I_DI_1 | Pin 9 | C1S6:9/TBDI3:9A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202I |  | -
C1-S06-P09 | 6 | 9 | 10 | 1756-IB32 | XA-60202J_DI_1 | Pin 10 | C1S6:10/TBDI3:10A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202J |  | -
C1-S06-P10 | 6 | 10 | 11 | 1756-IB32 | XA-60202K_DI_1 | Pin 11 | C1S6:11/TBDI3:11A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202K |  | -
C1-S06-P11 | 6 | 11 | 12 | 1756-IB32 | XA-60202L_DI_1 | Pin 12 | C1S6:12/TBDI3:12A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202L |  | -
C1-S06-P12 | 6 | 12 | 13 | 1756-IB32 | XA-60202M_DI_1 | Pin 13 | C1S6:13/TBDI3:13A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202M |  | -
C1-S06-P13 | 6 | 13 | 14 | 1756-IB32 | XV-60202_DI_1 | Pin 14 | C1S6:14/TBDI3:14A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XV-60202 |  | 3-25-01-602-PD-11
C1-S06-P14 | 6 | 14 | 15 | 1756-IB32 | XV-60202_DI_2 | Pin 15 | C1S6:15/TBDI3:15A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XV-60202 |  | 3-25-01-602-PD-11
C1-S06-P15 | 6 | 15 | 16 | 1756-IB32 | XV-60205A_DI_1 | Pin 16 | C1S6:16/TBDI3:16A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XV-60205A |  | 3-25-01-602-PD-01
C1-S06-P16 | 6 | 16 | 17 | 1756-IB32 | XV-60205A_DI_2 | Pin 17 | C1S6:17/C1S06-X2:17 | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60205A |  | 3-25-01-602-PD-01
C1-S06-P17 | 6 | 17 | 18 | 1756-IB32 | XV-60240D_DI_1 | Pin 18 | C1S6:18/C1S06-X2:18 | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60240D |  | -
C1-S06-P18 | 6 | 18 | 19 | 1756-IB32 | XV-60240D_DI_2 | Pin 19 | C1S6:19/TBDI3:17A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60240D |  | 3-25-01-602-PD-05
C1-S06-P19 | 6 | 19 | 20 | 1756-IB32 | XV-60240D_DI_1 | Pin 20 | C1S6:20/TBDI3:18A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60240D |  | -
C1-S06-P20 | 6 | 20 | 21 | 1756-IB32 | XV-60240D_DI_2 | Pin 21 | C1S6:21/TBDI3:19A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60240D |  | 3-25-01-602-PD-05
C1-S06-P21 | 6 | 21 | 22 | 1756-IB32 | YA-60205_DI_1 | Pin 22 | C1S6:22/TBDI3:20A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | YA-60205 |  | -
C1-S06-P22 | 6 | 22 | 23 | 1756-IB32 | YI-60205_DI_1 | Pin 23 | C1S6:23/TBDI3:21A | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | YI-60205 |  | -
C1-S06-P23 | 6 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C1S6:24/TBDI3:22A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P24 | 6 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C1S6:25/TBDI3:23A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P25 | 6 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C1S6:26/TBDI3:24A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P26 | 6 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C1S6:27/TBDI3:25A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P27 | 6 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C1S6:28/TBDI3:26A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P28 | 6 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C1S6:29/TBDI3:27A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P29 | 6 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C1S6:30/TBDI3:28A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P30 | 6 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C1S6:31/TBDI3:29A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P31 | 6 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C1S6:32/TBDI3:30A | DI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
Slot 07 — Module: 1756-OB32 (DO) ¦ Total: 32 Channels (Active: 16, Spare: 16)
C1-S07-P00 | 7 | 0 | 1 | 1756-OB32 | Spare_DO_0 | Pin 1 | C1S7:1/TBDI4:1A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P01 | 7 | 1 | 2 | 1756-OB32 | Spare_DO_0 | Pin 2 | C1S7:2/TBDI4:2A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P02 | 7 | 2 | 3 | 1756-OB32 | Spare_DO_0 | Pin 3 | C1S7:3/TBDI4:3A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P03 | 7 | 3 | 4 | 1756-OB32 | Spare_DO_0 | Pin 4 | C1S7:4/TBDI4:4A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P04 | 7 | 4 | 5 | 1756-OB32 | Spare_DO_0 | Pin 5 | C1S7:5/TBDI4:5A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P05 | 7 | 5 | 6 | 1756-OB32 | Spare_DO_0 | Pin 6 | C1S7:6/TBDI4:6A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P06 | 7 | 6 | 7 | 1756-OB32 | Spare_DO_0 | Pin 7 | C1S7:7/TBDI4:7A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P07 | 7 | 7 | 8 | 1756-OB32 | Spare_DO_0 | Pin 8 | C1S7:8/TBDI4:8A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P08 | 7 | 8 | 9 | 1756-OB32 | Spare_DO_0 | Pin 9 | C1S7:9/TBDI4:9A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P09 | 7 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C1S7:10/TBDI4:10A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P10 | 7 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C1S7:11/TBDI4:11A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P11 | 7 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C1S7:12/TBDI4:12A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P12 | 7 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C1S7:13/TBDI4:13A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P13 | 7 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C1S7:14/TBDI4:14A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P14 | 7 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C1S7:15/TBDI4:15A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P15 | 7 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C1S7:16/TBDI4:16A | DO | 24VDC | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P16 | 7 | 16 | 17 | 1756-OB32 | XV-40202E_DO_1 | Pin 17 | C1S7:17/C1S07-X2:17 | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202E |  | 3-25-01-402-PD-01
C1-S07-P17 | 7 | 17 | 18 | 1756-OB32 | XV-40202F_DO_1 | Pin 18 | C1S7:18/C1S07-X2:18 | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202F |  | 3-25-01-402-PD-01
C1-S07-P18 | 7 | 18 | 19 | 1756-OB32 | XV-40202G_DO_1 | Pin 19 | C1S7:19/TBDI4:17A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202G |  | 3-25-01-402-PD-01
C1-S07-P19 | 7 | 19 | 20 | 1756-OB32 | XV-40202H_DO_1 | Pin 20 | C1S7:20/TBDI4:18A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202H |  | 3-25-01-402-PD-01
C1-S07-P20 | 7 | 20 | 21 | 1756-OB32 | XV-40203B_DO_1 | Pin 21 | C1S7:21/TBDI4:19A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203B |  | 3-25-01-402-PD-02
C1-S07-P21 | 7 | 21 | 22 | 1756-OB32 | XV-40203C_DO_1 | Pin 22 | C1S7:22/TBDI4:20A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203C |  | 3-25-01-402-PD-02
C1-S07-P22 | 7 | 22 | 23 | 1756-OB32 | XV-40203D_DO_1 | Pin 23 | C1S7:23/TBDI4:21A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203D |  | 3-25-01-402-PD-02
C1-S07-P23 | 7 | 23 | 24 | 1756-OB32 | XV-40203E_DO_1 | Pin 24 | C1S7:24/TBDI4:22A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203E |  | 3-25-01-402-PD-02
C1-S07-P24 | 7 | 24 | 25 | 1756-OB32 | SV-40201_DO_1 | Pin 25 | C1S7:25/TBDI4:23A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40201 |  | 3-25-01-402-PD-01
C1-S07-P25 | 7 | 25 | 26 | 1756-OB32 | SV-40202_DO_1 | Pin 26 | C1S7:26/TBDI4:24A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40202 |  | 3-25-01-402-PD-01
C1-S07-P26 | 7 | 26 | 27 | 1756-OB32 | SV-40203_DO_1 | Pin 27 | C1S7:27/TBDI4:25A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40203 |  | 3-25-01-402-PD-01
C1-S07-P27 | 7 | 27 | 28 | 1756-OB32 | SV-40204_DO_1 | Pin 28 | C1S7:28/TBDI4:26A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40204 |  | 3-25-01-402-PD-01
C1-S07-P28 | 7 | 28 | 29 | 1756-OB32 | XV-40201A_DO_1 | Pin 29 | C1S7:29/TBDI4:27A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201A |  | 3-25-01-402-PD-01
C1-S07-P29 | 7 | 29 | 30 | 1756-OB32 | XV-40201B_DO_1 | Pin 30 | C1S7:30/TBDI4:28A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201B |  | 3-25-01-402-PD-01
C1-S07-P30 | 7 | 30 | 31 | 1756-OB32 | XV-40201C_DO_1 | Pin 31 | C1S7:31/TBDI4:29A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201C |  | 3-25-01-402-PD-01
C1-S07-P31 | 7 | 31 | 32 | 1756-OB32 | XV-40201D_DO_1 | Pin 32 | C1S7:32/TBDI4:30A | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201D |  | 3-25-01-402-PD-01
Slot 08 — Module: 1756-OB32 (DO) ¦ Total: 32 Channels (Active: 20, Spare: 12)
C1-S08-P00 | 8 | 0 | 1 | 1756-OB32 | XV-40201E_DO_1 | Pin 1 | C1S8:1/RL.1:A1 | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201E |  | 3-25-01-402-PD-01
C1-S08-P01 | 8 | 1 | 2 | 1756-OB32 | XV-40201F_DO_1 | Pin 2 | C1S8:2/RL.2:A1 | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201F |  | 3-25-01-402-PD-01
C1-S08-P02 | 8 | 2 | 3 | 1756-OB32 | XV-40201G_DO_1 | Pin 3 | C1S8:3/RL.3:A1 | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201G |  | 3-25-01-402-PD-01
C1-S08-P03 | 8 | 3 | 4 | 1756-OB32 | XV-40201H_DO_1 | Pin 4 | C1S8:4/RL.4:A1 | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201H |  | 3-25-01-402-PD-01
C1-S08-P04 | 8 | 4 | 5 | 1756-OB32 | XV-40202A_DO_1 | Pin 5 | C1S8:5/RL.5:A1 | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202A |  | 3-25-01-402-PD-01
C1-S08-P05 | 8 | 5 | 6 | 1756-OB32 | XV-40202B_DO_1 | Pin 6 | C1S8:6/RL.6:A1 | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202B |  | 3-25-01-402-PD-01
C1-S08-P06 | 8 | 6 | 7 | 1756-OB32 | XV-40202C_DO_1 | Pin 7 | C1S8:7/RL.7:A1 | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202C |  | 3-25-01-402-PD-01
C1-S08-P07 | 8 | 7 | 8 | 1756-OB32 | XV-40202D_DO_1 | Pin 8 | C1S8:8/RL.8:A1 | DO | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202D |  | 3-25-01-402-PD-01
C1-S08-P08 | 8 | 8 | 9 | 1756-OB32 | Spare_DO_0 | Pin 9 | C1S8:9/RL.9:A1 | DO | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P09 | 8 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C1S8:10/RL.10:A1 | DO | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P10 | 8 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C1S8:11/RL.11:A1 | DO | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P11 | 8 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C1S8:12/RL.12:A1 | DO | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P12 | 8 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C1S8:13/RL.13:A1 | DO | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P13 | 8 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C1S8:14/RL.14:A1 | DO | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P14 | 8 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C1S8:15/RL.15:A1 | DO | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P15 | 8 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C1S8:16/RL.16:A1 | DO | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P16 | 8 | 16 | 17 | 1756-OB32 | SV-60201_DO_1 | Pin 17 | C1S8:17/C1S08-X2:17 | DO | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60201 |  | 3-25-01-602-PD-08
C1-S08-P17 | 8 | 17 | 18 | 1756-OB32 | SV-60202_DO_1 | Pin 18 | C1S8:18/C1S08-X2:18 | DO | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60202 |  | 3-25-01-602-PD-08
C1-S08-P18 | 8 | 18 | 19 | 1756-OB32 | SV-60230_DO_1 | Pin 19 | C1S8:19/RL.17:A1 | DO | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60230 |  | 3-25-01-602-PD-04
C1-S08-P19 | 8 | 19 | 20 | 1756-OB32 | SV-60203_DO_1 | Pin 20 | C1S8:20/RL.18:A1 | DO | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60203 |  | 3-25-01-602-PD-08
C1-S08-P20 | 8 | 20 | 21 | 1756-OB32 | SV-60240A_DO_1 | Pin 21 | C1S8:21/RL.19:A1 | DO | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60240A |  | 3-25-01-602-PD-05
C1-S08-P21 | 8 | 21 | 22 | 1756-OB32 | SV-60231_DO_1 | Pin 22 | C1S8:22/RL.20:A1 | DO | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60231 |  | 3-25-01-602-PD-04
C1-S08-P22 | 8 | 22 | 23 | 1756-OB32 | SV-60240B_DO_1 | Pin 23 | C1S8:23/RL.21:A1 | DO | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60240B |  | 3-25-01-602-PD-05
C1-S08-P23 | 8 | 23 | 24 | 1756-OB32 | SV-60240C_DO_1 | Pin 24 | C1S8:24/RL.22:A1 | DO | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60240C |  | 3-25-01-602-PD-05
C1-S08-P24 | 8 | 24 | 25 | 1756-OB32 | XV-60240D_DO_1 | Pin 25 | C1S8:25/RL.23:A1 | DO | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | XV-60240D |  | -
C1-S08-P25 | 8 | 25 | 26 | 1756-OB32 | XV-60251_DO_1 | Pin 26 | C1S8:26/RL.24:A1 | DO | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Infeed Tank | C1S08-X2 | - | XV-60251 |  | 3-25-01-602-PD-01
C1-S08-P26 | 8 | 26 | 27 | 1756-OB32 | XV-60202_DO_1 | Pin 27 | C1S8:27/RL.25:A1 | DO | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | XV-60202 |  | 3-25-01-602-PD-11
C1-S08-P27 | 8 | 27 | 28 | 1756-OB32 | XV-60205A_DO_1 | Pin 28 | C1S8:28/RL.26:A1 | DO | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | XV-60205A |  | 3-25-01-602-PD-01
C1-S08-P28 | 8 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C1S8:29/RL.27:A1 | DO | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S08-X2 | - | Spare | Spare Channel | -
C1-S08-P29 | 8 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C1S8:30/RL.28:A1 | DO | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S08-X2 | - | Spare | Spare Channel | -
C1-S08-P30 | 8 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C1S8:31/RL.29:A1 | DO | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S08-X2 | - | Spare | Spare Channel | -
C1-S08-P31 | 8 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C1S8:32/RL.30:A1 | DO | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S08-X2 | - | Spare | Spare Channel | -
Slot 09 — Module: 1756-IF16 (AI) ¦ Total: 16 Channels (Active: 11, Spare: 5)
C1-S09-P00 | 9 | 0 | 1 | 1756-IF16 | FT-40201_AI_1 | Pin 1 | C1S9:1/RL.33:A1 | AI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | FT-40201 | Coriolis Flow Transmitter | 3-25-01-402-PD-02
C1-S09-P01 | 9 | 1 | 2 | 1756-IF16 | FT-40201_AI_2 | Pin 2 | C1S9:2/RL.34:A1 | AI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | FT-40201 | Coriolis Flow Transmitter | 3-25-01-402-PD-02
C1-S09-P02 | 9 | 2 | 3 | 1756-IF16 | FT-40202_AI_1 | Pin 3 | C1S9:3/RL.35:A1 | AI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | FT-40202 | Magnetic Flow Transmitter | 3-25-01-402-PD-02
C1-S09-P03 | 9 | 3 | 4 | 1756-IF16 | LT-40203_AI_1 | Pin 4 | C1S9:4/RL.36:A1 | AI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | LT-40203 | Level Transmitter | 3-25-01-402-PD-02
C1-S09-P04 | 9 | 4 | 5 | 1756-IF16 | LT-40201_AI_1 | Pin 5 | C1S9:5/RL.37:A1 | AI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | LT-40201 | Level Transmitter | 3-25-01-402-PD-01
C1-S09-P05 | 9 | 5 | 6 | 1756-IF16 | LT-40202_AI_1 | Pin 6 | C1S9:6/RL.38:A1 | AI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | LT-40202 | Level Transmitter | 3-25-01-402-PD-01
C1-S09-P06 | 9 | 6 | 7 | 1756-IF16 | pHT-40201_AI_1 | Pin 7 | C1S9:7/RL.39:A1 | AI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | pHT-40201 | PH Transmitter | 3-25-01-402-PD-01
C1-S09-P07 | 9 | 7 | 8 | 1756-IF16 | pHT-40202_AI_1 | Pin 8 | C1S9:8/RL.40:A1 | AI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | pHT-40202 | PH Transmitter | 3-25-01-402-PD-01
C1-S09-P08 | 9 | 8 | 9 | 1756-IF16 | PT-40201_AI_1 | Pin 9 | C1S9:9/RL.41:A1 | AI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | PT-40201 | Pressure Transmitter | 3-25-01-402-PD-02
C1-S09-P09 | 9 | 9 | 10 | 1756-IF16 | PT-40202_AI_1 | Pin 10 | C1S9:10/RL.42:A1 | AI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | PT-40202 | Pressure Transmitter | 3-25-01-402-PD-02
C1-S09-P10 | 9 | 10 | 11 | 1756-IF16 | PT-60202_AI_1 | Pin 11 | C1S9:11/RL.43:A1 | AI | 24VDC | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | PT-60202 | Pressure Transmitter | 3-25-01-602-PD-01
C1-S09-P11 | 9 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C1S9:12/RL.44:A1 | AI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | -
C1-S09-P12 | 9 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C1S9:13/RL.45:A1 | AI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | -
C1-S09-P13 | 9 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C1S9:14/RL.46:A1 | AI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | -
C1-S09-P14 | 9 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C1S9:15/RL.47:A1 | AI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | -
C1-S09-P15 | 9 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C1S9:16/RL.48:A1 | AI | 24VDC | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | -
Slot 10 — Module: 1756-IF16 (AI) ¦ Total: 16 Channels (Active: 8, Spare: 8)
C1-S10-P00 | 10 | 0 | 1 | 1756-IF16 | DPI-60240_AI_1 | Pin 1 | C1S10:1/C1S10-X1:1 | AI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | DPI-60240 |  | -
C1-S10-P01 | 10 | 1 | 2 | 1756-IF16 | DPT-60202_AI_1 | Pin 2 | C1S10:2/C1S10-X1:2 | AI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | DPT-60202 | Differential Pressure Transmitte | 3-25-01-602-PD-08
C1-S10-P02 | 10 | 2 | 3 | 1756-IF16 | FT-60201_AI_1 | Pin 3 | C1S10:3/C1S10-X1:3 | AI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | FT-60201 |  | 3-25-01-602-PD-08
C1-S10-P03 | 10 | 3 | 4 | 1756-IF16 | FT-60204_AI_1 | Pin 4 | C1S10:4/C1S10-X1:4 | AI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | FT-60204 |  | 3-25-01-602-PD-10
C1-S10-P04 | 10 | 4 | 5 | 1756-IF16 | FT-61307_AI_1 | Pin 5 | C1S10:5/C1S10-X1:5 | AI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | FT-61307 |  | 3-25-01-613-PD-04
C1-S10-P05 | 10 | 5 | 6 | 1756-IF16 | PT-60203_AI_1 | Pin 6 | C1S10:6/C1S10-X1:6 | AI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | PT-60203 | Pressure Transmitter | 3-25-01-602-PD-08
C1-S10-P06 | 10 | 6 | 7 | 1756-IF16 | PT-60204_AI_1 | Pin 7 | C1S10:7/C1S10-X1:7 | AI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | PT-60204 | Pressure Transmitter | 3-25-01-602-PD-10
C1-S10-P07 | 10 | 7 | 8 | 1756-IF16 | PT-60205_AI_1 | Pin 8 | C1S10:8/C1S10-X1:8 | AI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | PT-60205 | Pressure Transmitter | 3-25-01-602-PD-01
C1-S10-P08 | 10 | 8 | 9 | 1756-IF16 | Spare_AI_0 | Pin 9 | C1S10:9/C1S10-X1:9 | AI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P09 | 10 | 9 | 10 | 1756-IF16 | Spare_AI_0 | Pin 10 | C1S10:10/C1S10-X1:10 | AI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P10 | 10 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C1S10:11/C1S10-X1:11 | AI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P11 | 10 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C1S10:12/C1S10-X1:12 | AI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P12 | 10 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C1S10:13/C1S10-X1:13 | AI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P13 | 10 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C1S10:14/C1S10-X1:14 | AI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P14 | 10 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C1S10:15/C1S10-X1:15 | AI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P15 | 10 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C1S10:16/C1S10-X1:16 | AI | 24VDC | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -

## Chassis_C2
KALASIN ENGINEERING — C2 (I/O EXPANSION RACK 1 (CHASSIS 2))
Location: Control Cabinet CA1 (Bay 2) ¦ Role: Digital & Analog Process I/O Expansion ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 333 (Active: 243, Spare: 90)
SOURCE (PLC RACK / SLOT / TERMINAL / ePLAN TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Type | Status | Destination | Field Location | Floor/Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing
Slot 01 — Module: 1756-IB32 (DI) ¦ Total: 32 Channels (Active: 24, Spare: 8)
C2-S01-P00 | 1 | 0 | 1 | 1756-IB32 | FS-40204_DI_1 | Pin 1 | C2S1:1/TBDI1:1A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | FS-40204 | Flow Switch | 325-01-402-PD-01
C2-S01-P01 | 1 | 1 | 2 | 1756-IB32 | FS-40205_DI_1 | Pin 2 | C2S1:2/TBDI1:2A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | FS-40205 | Flow Switch | 325-01-402-PD-02
C2-S01-P02 | 1 | 2 | 3 | 1756-IB32 | FT-40221_DI_1 | Pin 3 | C2S1:3/TBDI1:3A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | FT-40221 | Coriolis Flow Transmitter | 325-01-402-PD-02
C2-S01-P03 | 1 | 3 | 4 | 1756-IB32 | FT-40222_DI_1 | Pin 4 | C2S1:4/TBDI1:4A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | FT-40222 | Coriolis Flow Transmitter | 325-01-402-PD-02
C2-S01-P04 | 1 | 4 | 5 | 1756-IB32 | HV-40207_DI_1 | Pin 5 | C2S1:5/TBDI1:5A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | HV-40207 | Manual Valve With Position Switch | 325-01-402-PD-01
C2-S01-P05 | 1 | 5 | 6 | 1756-IB32 | HV-40208_DI_1 | Pin 6 | C2S1:6/TBDI1:6A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | HV-40208 | Manual Valve With Position Switch | 325-01-402-PD-01
C2-S01-P06 | 1 | 6 | 7 | 1756-IB32 | XV-40203F_DI_1 | Pin 7 | C2S1:7/TBDI1:7A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40203F |  | 325-01-402-PD-02
C2-S01-P07 | 1 | 7 | 8 | 1756-IB32 | XV-40203F_DI_2 | Pin 8 | C2S1:8/TBDI1:8A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40203F |  | 325-01-402-PD-02
C2-S01-P08 | 1 | 8 | 9 | 1756-IB32 | XV-40204B_DI_1 | Pin 9 | C2S1:9/TBDI1:9A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40204B |  | 325-01-402-PD-01
C2-S01-P09 | 1 | 9 | 10 | 1756-IB32 | XV-40204B_DI_2 | Pin 10 | C2S1:10/TBDI1:10A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40204B |  | 325-01-402-PD-01
C2-S01-P10 | 1 | 10 | 11 | 1756-IB32 | XV-40204C_DI_1 | Pin 11 | C2S1:11/TBDI1:11A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40204C |  | 325-01-402-PD-01
C2-S01-P11 | 1 | 11 | 12 | 1756-IB32 | XV-40204C_DI_2 | Pin 12 | C2S1:12/TBDI1:12A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40204C |  | 325-01-402-PD-01
C2-S01-P12 | 1 | 12 | 13 | 1756-IB32 | XV-40205A_DI_1 | Pin 13 | C2S1:13/TBDI1:13A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40205A |  | 325-01-402-PD-02
C2-S01-P13 | 1 | 13 | 14 | 1756-IB32 | XV-40205A_DI_2 | Pin 14 | C2S1:14/TBDI1:14A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40205A |  | 325-01-402-PD-02
C2-S01-P14 | 1 | 14 | 15 | 1756-IB32 | XV-40205B_DI_1 | Pin 15 | C2S1:15/TBDI1:15A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40205B |  | 325-01-402-PD-02
C2-S01-P15 | 1 | 15 | 16 | 1756-IB32 | XV-40205B_DI_2 | Pin 16 | C2S1:16/TBDI1:16A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40205B |  | 325-01-402-PD-02
C2-S01-P16 | 1 | 16 | 17 | 1756-IB32 | XV-40205C_DI_1 | Pin 17 | C2S1:17/C2S01-X2:17 | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205C |  | 325-01-402-PD-02
C2-S01-P17 | 1 | 17 | 18 | 1756-IB32 | XV-40205C_DI_2 | Pin 18 | C2S1:18/C2S01-X2:18 | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205C |  | 325-01-402-PD-02
C2-S01-P18 | 1 | 18 | 19 | 1756-IB32 | XV-40205D_DI_1 | Pin 19 | C2S1:19/TBDI1:17A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205D |  | 325-01-402-PD-02
C2-S01-P19 | 1 | 19 | 20 | 1756-IB32 | XV-40205D_DI_2 | Pin 20 | C2S1:20/TBDI1:18A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205D |  | 325-01-402-PD-02
C2-S01-P20 | 1 | 20 | 21 | 1756-IB32 | XV-40205F_DI_1 | Pin 21 | C2S1:21/TBDI1:19A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205F |  | 325-01-402-PD-02
C2-S01-P21 | 1 | 21 | 22 | 1756-IB32 | XV-40205F_DI_2 | Pin 22 | C2S1:22/TBDI1:20A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205F |  | 325-01-402-PD-02
C2-S01-P22 | 1 | 22 | 23 | 1756-IB32 | XV-40222_DI_1 | Pin 23 | C2S1:23/TBDI1:21A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40222 |  | 325-01-402-PD-02
C2-S01-P23 | 1 | 23 | 24 | 1756-IB32 | XV-40222_DI_2 | Pin 24 | C2S1:24/TBDI1:22A | DI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40222 |  | -
C2-S01-P24 | 1 | 24 | 25 | 1756-IB32 | Spare_DI_2 | Pin 25 | C2S1:25/TBDI1:23A | DI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P25 | 1 | 25 | 26 | 1756-IB32 | Spare_DI_2 | Pin 26 | C2S1:26/TBDI1:24A | DI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P26 | 1 | 26 | 27 | 1756-IB32 | Spare_DI_2 | Pin 27 | C2S1:27/TBDI1:25A | DI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P27 | 1 | 27 | 28 | 1756-IB32 | Spare_DI_2 | Pin 28 | C2S1:28/TBDI1:26A | DI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P28 | 1 | 28 | 29 | 1756-IB32 | Spare_DI_2 | Pin 29 | C2S1:29/TBDI1:27A | DI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P29 | 1 | 29 | 30 | 1756-IB32 | Spare_DI_2 | Pin 30 | C2S1:30/TBDI1:28A | DI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P30 | 1 | 30 | 31 | 1756-IB32 | Spare_DI_2 | Pin 31 | C2S1:31/TBDI1:29A | DI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P31 | 1 | 31 | 32 | 1756-IB32 | Spare_DI_2 | Pin 32 | C2S1:32/TBDI1:30A | DI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
Slot 02 — Module: 1756-IB32 (DI) ¦ Total: 32 Channels (Active: 23, Spare: 9)
C2-S02-P00 | 2 | 0 | 1 | 1756-IB32 | FT-60202_DI_1 | Pin 1 | C2S2:1/TBDI2:1A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X1 | - | FT-60202 |  | 3-25-01-602-PD-09
C2-S02-P01 | 2 | 1 | 2 | 1756-IB32 | LSH-60251_DI_1 | Pin 2 | C2S2:2/TBDI2:2A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | LSH-60251 |  | 3-25-01-602-PD-04
C2-S02-P02 | 2 | 2 | 3 | 1756-IB32 | PSL-60220_DI_1 | Pin 3 | C2S2:3/TBDI2:3A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X1 | - | PSL-60220 |  | 3-25-01-602-PD-04
C2-S02-P03 | 2 | 3 | 4 | 1756-IB32 | TSH-60230_DI_1 | Pin 4 | C2S2:4/TBDI2:4A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | TSH-60230 |  | 3-25-01-602-PD-04
C2-S02-P04 | 2 | 4 | 5 | 1756-IB32 | TSH-60240_DI_1 | Pin 5 | C2S2:5/TBDI2:5A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X1 | - | TSH-60240 |  | 3-25-01-602-PD-05
C2-S02-P05 | 2 | 5 | 6 | 1756-IB32 | TSH-60241A_DI_1 | Pin 6 | C2S2:6/TBDI2:6A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSH-60241A |  | 3-25-01-602-PD-05
C2-S02-P06 | 2 | 6 | 7 | 1756-IB32 | TSH-60242A_DI_1 | Pin 7 | C2S2:7/TBDI2:7A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | TSH-60242A |  | 3-25-01-602-PD-05
C2-S02-P07 | 2 | 7 | 8 | 1756-IB32 | TSH-60243A_DI_1 | Pin 8 | C2S2:8/TBDI2:8A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSH-60243A |  | 3-25-01-602-PD-05
C2-S02-P08 | 2 | 8 | 9 | 1756-IB32 | TSL-60241B_DI_1 | Pin 9 | C2S2:9/TBDI2:9A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSL-60241B |  | 3-25-01-602-PD-05
C2-S02-P09 | 2 | 9 | 10 | 1756-IB32 | TSL-60242B_DI_1 | Pin 10 | C2S2:10/TBDI2:10A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | TSL-60242B |  | 3-25-01-602-PD-05
C2-S02-P10 | 2 | 10 | 11 | 1756-IB32 | TSL-60243B_DI_1 | Pin 11 | C2S2:11/TBDI2:11A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSL-60243B |  | 3-25-01-602-PD-05
C2-S02-P11 | 2 | 11 | 12 | 1756-IB32 | XA-60240A_DI_1 | Pin 12 | C2S2:12/TBDI2:12A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60240A |  | -
C2-S02-P12 | 2 | 12 | 13 | 1756-IB32 | XA-60240B_DI_1 | Pin 13 | C2S2:13/TBDI2:13A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60240B |  | -
C2-S02-P13 | 2 | 13 | 14 | 1756-IB32 | XA-60241A_DI_1 | Pin 14 | C2S2:14/TBDI2:14A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60241A |  | -
C2-S02-P14 | 2 | 14 | 15 | 1756-IB32 | XA-60241B_DI_1 | Pin 15 | C2S2:15/TBDI2:15A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60241B |  | -
C2-S02-P15 | 2 | 15 | 16 | 1756-IB32 | XA-60242A_DI_1 | Pin 16 | C2S2:16/TBDI2:16A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | XA-60242A |  | -
C2-S02-P16 | 2 | 16 | 17 | 1756-IB32 | XA-60242B_DI_1 | Pin 17 | C2S2:17/C2S02-X2:17 | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X2 | - | XA-60242B |  | -
C2-S02-P17 | 2 | 17 | 18 | 1756-IB32 | XA-60243A_DI_1 | Pin 18 | C2S2:18/C2S02-X2:18 | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X2 | - | XA-60243A |  | -
C2-S02-P18 | 2 | 18 | 19 | 1756-IB32 | XA-60243B_DI_1 | Pin 19 | C2S2:19/TBDI2:17A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X2 | - | XA-60243B |  | -
C2-S02-P19 | 2 | 19 | 20 | 1756-IB32 | XV-60214_DI_1 | Pin 20 | C2S2:20/TBDI2:18A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60214 |  | 3-25-01-602-PD-03
C2-S02-P20 | 2 | 20 | 21 | 1756-IB32 | XV-60214_DI_2 | Pin 21 | C2S2:21/TBDI2:19A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60214 |  | 3-25-01-602-PD-03
C2-S02-P21 | 2 | 21 | 22 | 1756-IB32 | XV-60241_DI_1 | Pin 22 | C2S2:22/TBDI2:20A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60241 |  | 3-25-01-602-PD-05
C2-S02-P22 | 2 | 22 | 23 | 1756-IB32 | XV-60241_DI_2 | Pin 23 | C2S2:23/TBDI2:21A | DI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60241 |  | 3-25-01-602-PD-05
C2-S02-P23 | 2 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C2S2:24/TBDI2:22A | DI | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P24 | 2 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C2S2:25/TBDI2:23A | DI | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P25 | 2 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C2S2:26/TBDI2:24A | DI | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P26 | 2 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C2S2:27/TBDI2:25A | DI | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P27 | 2 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C2S2:28/TBDI2:26A | DI | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P28 | 2 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C2S2:29/TBDI2:27A | DI | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P29 | 2 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C2S2:30/TBDI2:28A | DI | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P30 | 2 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C2S2:31/TBDI2:29A | DI | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P31 | 2 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C2S2:32/TBDI2:30A | DI | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
Slot 03 — Module: 1756-IB32 (DI) ¦ Total: 29 Channels (Active: 29, Spare: 0)
C2-S03-P00 | 3 | 0 | 1 | 1756-IB32 | XA-FH-60210A_DI_1 | Pin 1 | C2S3:1/TBDI3:1A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210A |  | -
C2-S03-P01 | 3 | 1 | 2 | 1756-IB32 | XA-FH-60210B_DI_1 | Pin 2 | C2S3:2/TBDI3:2A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210B |  | -
C2-S03-P02 | 3 | 2 | 3 | 1756-IB32 | XA-FH-60210C_DI_1 | Pin 3 | C2S3:3/TBDI3:3A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210C |  | -
C2-S03-P03 | 3 | 3 | 4 | 1756-IB32 | XA-FH-60210D_DI_1 | Pin 4 | C2S3:4/TBDI3:4A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210D |  | -
C2-S03-P04 | 3 | 4 | 5 | 1756-IB32 | XA-FH-60210E_DI_1 | Pin 5 | C2S3:5/TBDI3:5A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210E |  | -
C2-S03-P08 | 3 | 8 | 9 | 1756-IB32 | SV-60207_DI_1 | Pin 9 | C2S3:9/TBDI3:9A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | SV-60207 |  | 3-25-01-602-PD-07
C2-S03-P09 | 3 | 9 | 10 | 1756-IB32 | SV-60207_DI_2 | Pin 10 | C2S3:10/TBDI3:10A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | SV-60207 |  | 3-25-01-602-PD-07
C2-S03-P10 | 3 | 10 | 11 | 1756-IB32 | XV-60264_DI_1 | Pin 11 | C2S3:11/TBDI3:11A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264 |  | -
C2-S03-P11 | 3 | 11 | 12 | 1756-IB32 | XV-60264_DI_2 | Pin 12 | C2S3:12/TBDI3:12A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264 |  | -
C2-S03-P12 | 3 | 12 | 13 | 1756-IB32 | XV-60264FN_DI_1 | Pin 13 | C2S3:13/TBDI3:13A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264FN |  | 3-25-01-602-PD-02
C2-S03-P13 | 3 | 13 | 14 | 1756-IB32 | XV-60264FN_DI_2 | Pin 14 | C2S3:14/TBDI3:14A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264FN |  | 3-25-01-602-PD-02
C2-S03-P14 | 3 | 14 | 15 | 1756-IB32 | XV-60264FP_DI_1 | Pin 15 | C2S3:15/TBDI3:15A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264FP |  | 3-25-01-602-PD-02
C2-S03-P15 | 3 | 15 | 16 | 1756-IB32 | XV-60264FP_DI_2 | Pin 16 | C2S3:16/TBDI3:16A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264FP |  | 3-25-01-602-PD-02
C2-S03-P16 | 3 | 16 | 17 | 1756-IB32 | XV-60201_DI_1 | Pin 17 | C2S3:17/C2S03-X2:17 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60201 |  | 3-25-01-602-PD-02
C2-S03-P17 | 3 | 17 | 18 | 1756-IB32 | XV-60201_DI_2 | Pin 18 | C2S3:18/C2S03-X2:18 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60201 |  | 3-25-01-602-PD-02
C2-S03-P18 | 3 | 18 | 19 | 1756-IB32 | XV-60264FQ_DI_1 | Pin 19 | C2S3:19/TBDI3:17A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264FQ |  | 3-25-01-602-PD-02
C2-S03-P19 | 3 | 19 | 20 | 1756-IB32 | XV-60264FQ_DI_2 | Pin 20 | C2S3:20/TBDI3:18A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264FQ |  | 3-25-01-602-PD-02
C2-S03-P20 | 3 | 20 | 21 | 1756-IB32 | XV-60261_DI_1 | Pin 21 | C2S3:21/TBDI3:19A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261 |  | -
C2-S03-P21 | 3 | 21 | 22 | 1756-IB32 | XV-60261_DI_2 | Pin 22 | C2S3:22/TBDI3:20A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261 |  | -
C2-S03-P22 | 3 | 22 | 23 | 1756-IB32 | XV-60264FR_DI_1 | Pin 23 | C2S3:23/TBDI3:21A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264FR |  | 3-25-01-602-PD-02
C2-S03-P23 | 3 | 23 | 24 | 1756-IB32 | XV-60264FR_DI_2 | Pin 24 | C2S3:24/TBDI3:22A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264FR |  | 3-25-01-602-PD-02
C2-S03-P24 | 3 | 24 | 25 | 1756-IB32 | XV-60261FA_DI_1 | Pin 25 | C2S3:25/TBDI3:23A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261FA |  | 3-25-01-602-PD-02
C2-S03-P25 | 3 | 25 | 26 | 1756-IB32 | XV-60261FA_DI_2 | Pin 26 | C2S3:26/TBDI3:24A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261FA |  | 3-25-01-602-PD-02
C2-S03-P26 | 3 | 26 | 27 | 1756-IB32 | XV-60264SN_DI_1 | Pin 27 | C2S3:27/TBDI3:25A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264SN |  | 3-25-01-602-PD-02
C2-S03-P27 | 3 | 27 | 28 | 1756-IB32 | XV-60264SN_DI_2 | Pin 28 | C2S3:28/TBDI3:26A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264SN |  | 3-25-01-602-PD-02
C2-S03-P28 | 3 | 28 | 29 | 1756-IB32 | XV-60261FB_DI_1 | Pin 29 | C2S3:29/TBDI3:27A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261FB |  | 3-25-01-602-PD-02
C2-S03-P29 | 3 | 29 | 30 | 1756-IB32 | XV-60261FB_DI_2 | Pin 30 | C2S3:30/TBDI3:28A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261FB |  | 3-25-01-602-PD-02
C2-S03-P30 | 3 | 30 | 31 | 1756-IB32 | XV-60264SP_DI_1 | Pin 31 | C2S3:31/TBDI3:29A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264SP |  | 3-25-01-602-PD-02
C2-S03-P31 | 3 | 31 | 32 | 1756-IB32 | XV-60264SP_DI_2 | Pin 32 | C2S3:32/TBDI3:30A | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264SP |  | 3-25-01-602-PD-02
Slot 04 — Module: 1756-IB32 (DI) ¦ Total: 32 Channels (Active: 32, Spare: 0)
C2-S04-P00 | 4 | 0 | 1 | 1756-IB32 | XV-60261FC_DI_1 | Pin 1 | C2S4:1/RL.1:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261FC |  | 3-25-01-602-PD-02
C2-S04-P01 | 4 | 1 | 2 | 1756-IB32 | XV-60261FC_DI_2 | Pin 2 | C2S4:2/RL.2:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261FC |  | 3-25-01-602-PD-02
C2-S04-P02 | 4 | 2 | 3 | 1756-IB32 | XV-60264SQ_DI_1 | Pin 3 | C2S4:3/RL.3:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60264SQ |  | 3-25-01-602-PD-02
C2-S04-P03 | 4 | 3 | 4 | 1756-IB32 | XV-60264SQ_DI_2 | Pin 4 | C2S4:4/RL.4:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60264SQ |  | 3-25-01-602-PD-02
C2-S04-P04 | 4 | 4 | 5 | 1756-IB32 | XV-60261FD_DI_1 | Pin 5 | C2S4:5/RL.5:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261FD |  | 3-25-01-602-PD-02
C2-S04-P05 | 4 | 5 | 6 | 1756-IB32 | XV-60261FD_DI_2 | Pin 6 | C2S4:6/RL.6:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261FD |  | 3-25-01-602-PD-02
C2-S04-P06 | 4 | 6 | 7 | 1756-IB32 | XV-60264SR_DI_1 | Pin 7 | C2S4:7/RL.7:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60264SR |  | 3-25-01-602-PD-02
C2-S04-P07 | 4 | 7 | 8 | 1756-IB32 | XV-60264SR_DI_2 | Pin 8 | C2S4:8/RL.8:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60264SR |  | 3-25-01-602-PD-02
C2-S04-P08 | 4 | 8 | 9 | 1756-IB32 | XV-60261SA_DI_1 | Pin 9 | C2S4:9/RL.9:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SA |  | 3-25-01-602-PD-02
C2-S04-P09 | 4 | 9 | 10 | 1756-IB32 | XV-60261SA_DI_2 | Pin 10 | C2S4:10/RL.10:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SA |  | 3-25-01-602-PD-02
C2-S04-P10 | 4 | 10 | 11 | 1756-IB32 | XV-60261SB_DI_1 | Pin 11 | C2S4:11/RL.11:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SB |  | 3-25-01-602-PD-02
C2-S04-P11 | 4 | 11 | 12 | 1756-IB32 | XV-60261SB_DI_2 | Pin 12 | C2S4:12/RL.12:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SB |  | 3-25-01-602-PD-02
C2-S04-P12 | 4 | 12 | 13 | 1756-IB32 | XV-60261SC_DI_1 | Pin 13 | C2S4:13/RL.13:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SC |  | 3-25-01-602-PD-02
C2-S04-P13 | 4 | 13 | 14 | 1756-IB32 | XV-60261SC_DI_2 | Pin 14 | C2S4:14/RL.14:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SC |  | 3-25-01-602-PD-02
C2-S04-P14 | 4 | 14 | 15 | 1756-IB32 | XV-60261SD_DI_1 | Pin 15 | C2S4:15/RL.15:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SD |  | 3-25-01-602-PD-02
C2-S04-P15 | 4 | 15 | 16 | 1756-IB32 | XV-60261SD_DI_2 | Pin 16 | C2S4:16/RL.16:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SD |  | 3-25-01-602-PD-02
C2-S04-P16 | 4 | 16 | 17 | 1756-IB32 | XV-60262_DI_1 | Pin 17 | C2S4:17/C2S04-X2:17 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262 |  | -
C2-S04-P17 | 4 | 17 | 18 | 1756-IB32 | XV-60262_DI_2 | Pin 18 | C2S4:18/C2S04-X2:18 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262 |  | -
C2-S04-P18 | 4 | 18 | 19 | 1756-IB32 | XV-60262FE_DI_1 | Pin 19 | C2S4:19/RL.17:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FE |  | 3-25-01-602-PD-02
C2-S04-P19 | 4 | 19 | 20 | 1756-IB32 | XV-60262FE_DI_2 | Pin 20 | C2S4:20/RL.18:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FE |  | 3-25-01-602-PD-02
C2-S04-P20 | 4 | 20 | 21 | 1756-IB32 | XV-60262FF_DI_1 | Pin 21 | C2S4:21/RL.19:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FF |  | 3-25-01-602-PD-02
C2-S04-P21 | 4 | 21 | 22 | 1756-IB32 | XV-60262FF_DI_2 | Pin 22 | C2S4:22/RL.20:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FF |  | 3-25-01-602-PD-02
C2-S04-P22 | 4 | 22 | 23 | 1756-IB32 | XV-60262FG_DI_1 | Pin 23 | C2S4:23/RL.21:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FG |  | 3-25-01-602-PD-02
C2-S04-P23 | 4 | 23 | 24 | 1756-IB32 | XV-60262FG_DI_2 | Pin 24 | C2S4:24/RL.22:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FG |  | 3-25-01-602-PD-02
C2-S04-P24 | 4 | 24 | 25 | 1756-IB32 | XV-60262FH_DI_1 | Pin 25 | C2S4:25/RL.23:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FH |  | 3-25-01-602-PD-02
C2-S04-P25 | 4 | 25 | 26 | 1756-IB32 | XV-60262FH_DI_2 | Pin 26 | C2S4:26/RL.24:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FH |  | 3-25-01-602-PD-02
C2-S04-P26 | 4 | 26 | 27 | 1756-IB32 | XV-60262SE_DI_1 | Pin 27 | C2S4:27/RL.25:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SE |  | 3-25-01-602-PD-02
C2-S04-P27 | 4 | 27 | 28 | 1756-IB32 | XV-60262SE_DI_2 | Pin 28 | C2S4:28/RL.26:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SE |  | 3-25-01-602-PD-02
C2-S04-P28 | 4 | 28 | 29 | 1756-IB32 | XV-60262SF_DI_1 | Pin 29 | C2S4:29/RL.27:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SF |  | 3-25-01-602-PD-02
C2-S04-P29 | 4 | 29 | 30 | 1756-IB32 | XV-60262SF_DI_2 | Pin 30 | C2S4:30/RL.28:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SF |  | 3-25-01-602-PD-02
C2-S04-P30 | 4 | 30 | 31 | 1756-IB32 | XV-60262SG_DI_1 | Pin 31 | C2S4:31/RL.29:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SG |  | 3-25-01-602-PD-02
C2-S04-P31 | 4 | 31 | 32 | 1756-IB32 | XV-60262SG_DI_2 | Pin 32 | C2S4:32/RL.30:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SG |  | 3-25-01-602-PD-02
Slot 05 — Module: 1756-IB32 (DI) ¦ Total: 32 Channels (Active: 20, Spare: 12)
C2-S05-P00 | 5 | 0 | 1 | 1756-IB32 | XV-60262SH_DI_1 | Pin 1 | C2S5:1/RL.33:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60262SH |  | 3-25-01-602-PD-02
C2-S05-P01 | 5 | 1 | 2 | 1756-IB32 | XV-60262SH_DI_2 | Pin 2 | C2S5:2/RL.34:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60262SH |  | 3-25-01-602-PD-02
C2-S05-P02 | 5 | 2 | 3 | 1756-IB32 | XV-60263_DI_1 | Pin 3 | C2S5:3/RL.35:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263 |  | -
C2-S05-P03 | 5 | 3 | 4 | 1756-IB32 | XV-60263_DI_2 | Pin 4 | C2S5:4/RL.36:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263 |  | -
C2-S05-P04 | 5 | 4 | 5 | 1756-IB32 | XV-60263FJ_DI_1 | Pin 5 | C2S5:5/RL.37:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FJ |  | 3-25-01-602-PD-02
C2-S05-P05 | 5 | 5 | 6 | 1756-IB32 | XV-60263FJ_DI_2 | Pin 6 | C2S5:6/RL.38:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FJ |  | 3-25-01-602-PD-02
C2-S05-P06 | 5 | 6 | 7 | 1756-IB32 | XV-60263FK_DI_1 | Pin 7 | C2S5:7/RL.39:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FK |  | 3-25-01-602-PD-02
C2-S05-P07 | 5 | 7 | 8 | 1756-IB32 | XV-60263FK_DI_2 | Pin 8 | C2S5:8/RL.40:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FK |  | 3-25-01-602-PD-02
C2-S05-P08 | 5 | 8 | 9 | 1756-IB32 | XV-60263FL_DI_1 | Pin 9 | C2S5:9/RL.41:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FL |  | 3-25-01-602-PD-02
C2-S05-P09 | 5 | 9 | 10 | 1756-IB32 | XV-60263FL_DI_2 | Pin 10 | C2S5:10/RL.42:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FL |  | 3-25-01-602-PD-02
C2-S05-P10 | 5 | 10 | 11 | 1756-IB32 | XV-60263FM_DI_1 | Pin 11 | C2S5:11/RL.43:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FM |  | 3-25-01-602-PD-02
C2-S05-P11 | 5 | 11 | 12 | 1756-IB32 | XV-60263FM_DI_2 | Pin 12 | C2S5:12/RL.44:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FM |  | 3-25-01-602-PD-02
C2-S05-P12 | 5 | 12 | 13 | 1756-IB32 | XV-60263SJ_DI_1 | Pin 13 | C2S5:13/RL.45:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263SJ |  | 3-25-01-602-PD-02
C2-S05-P13 | 5 | 13 | 14 | 1756-IB32 | XV-60263SJ_DI_2 | Pin 14 | C2S5:14/RL.46:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263SJ |  | 3-25-01-602-PD-02
C2-S05-P14 | 5 | 14 | 15 | 1756-IB32 | XV-60263SK_DI_1 | Pin 15 | C2S5:15/RL.47:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263SK |  | 3-25-01-602-PD-02
C2-S05-P15 | 5 | 15 | 16 | 1756-IB32 | XV-60263SK_DI_2 | Pin 16 | C2S5:16/RL.48:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263SK |  | 3-25-01-602-PD-02
C2-S05-P16 | 5 | 16 | 17 | 1756-IB32 | XV-60263SL_DI_1 | Pin 17 | C2S5:17/C2S05-X2:17 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X2 | - | XV-60263SL |  | 3-25-01-602-PD-02
C2-S05-P17 | 5 | 17 | 18 | 1756-IB32 | XV-60263SL_DI_2 | Pin 18 | C2S5:18/C2S05-X2:18 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X2 | - | XV-60263SL |  | 3-25-01-602-PD-02
C2-S05-P18 | 5 | 18 | 19 | 1756-IB32 | XV-60263SM_DI_1 | Pin 19 | C2S5:19/RL.49:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X2 | - | XV-60263SM |  | 3-25-01-602-PD-02
C2-S05-P19 | 5 | 19 | 20 | 1756-IB32 | XV-60263SM_DI_2 | Pin 20 | C2S5:20/RL.50:A1 | DI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X2 | - | XV-60263SM |  | 3-25-01-602-PD-02
C2-S05-P20 | 5 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C2S5:21/RL.51:A1 | DI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P21 | 5 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C2S5:22/RL.52:A1 | DI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P22 | 5 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C2S5:23/RL.53:A1 | DI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P23 | 5 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C2S5:24/RL.54:A1 | DI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P24 | 5 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C2S5:25/RL.55:A1 | DI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P25 | 5 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C2S5:26/RL.56:A1 | DI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P26 | 5 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C2S5:27/RL.57:A1 | DI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P27 | 5 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C2S5:28/RL.58:A1 | DI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P28 | 5 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C2S5:29/RL.59:A1 | DI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P29 | 5 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C2S5:30/RL.60:A1 | DI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P30 | 5 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C2S5:31/RL.61:A1 | DI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P31 | 5 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C2S5:32/RL.62:A1 | DI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
Slot 06 — Module: 1756-OB32 (DO) ¦ Total: 32 Channels (Active: 12, Spare: 20)
C2-S06-P00 | 6 | 0 | 1 | 1756-OB32 | XV-40203F_DO_1 | Pin 1 | C2S6:1/RL.33:A1 | DO | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40203F |  | 325-01-402-PD-02
C2-S06-P01 | 6 | 1 | 2 | 1756-OB32 | XV-40204B_DO_1 | Pin 2 | C2S6:2/RL.34:A1 | DO | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40204B |  | 325-01-402-PD-01
C2-S06-P02 | 6 | 2 | 3 | 1756-OB32 | XV-40204C_DO_1 | Pin 3 | C2S6:3/RL.35:A1 | DO | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40204C |  | 325-01-402-PD-01
C2-S06-P03 | 6 | 3 | 4 | 1756-OB32 | XV-40205A_DO_1 | Pin 4 | C2S6:4/RL.36:A1 | DO | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205A |  | 325-01-402-PD-02
C2-S06-P04 | 6 | 4 | 5 | 1756-OB32 | XV-40205B_DO_1 | Pin 5 | C2S6:5/RL.37:A1 | DO | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205B |  | 325-01-402-PD-02
C2-S06-P05 | 6 | 5 | 6 | 1756-OB32 | XV-40205C_DO_1 | Pin 6 | C2S6:6/RL.38:A1 | DO | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205C |  | 325-01-402-PD-02
C2-S06-P06 | 6 | 6 | 7 | 1756-OB32 | XV-40205D_DO_1 | Pin 7 | C2S6:7/RL.39:A1 | DO | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205D |  | 325-01-402-PD-02
C2-S06-P07 | 6 | 7 | 8 | 1756-OB32 | XV-40205F_DO_1 | Pin 8 | C2S6:8/RL.40:A1 | DO | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205F |  | 325-01-402-PD-02
C2-S06-P08 | 6 | 8 | 9 | 1756-OB32 | XV-40222_DO_1 | Pin 9 | C2S6:9/RL.41:A1 | DO | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40222 |  | 325-01-402-PD-02
C2-S06-P09 | 6 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C2S6:10/RL.42:A1 | DO | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P10 | 6 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C2S6:11/RL.43:A1 | DO | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P11 | 6 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C2S6:12/RL.44:A1 | DO | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P12 | 6 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C2S6:13/RL.45:A1 | DO | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P13 | 6 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C2S6:14/RL.46:A1 | DO | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P14 | 6 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C2S6:15/RL.47:A1 | DO | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P15 | 6 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C2S6:16/RL.48:A1 | DO | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P16 | 6 | 16 | 17 | 1756-OB32 | XS-60240B_DO_1 | Pin 17 | C2S6:17/C2S06-X2:17 | DO | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S06-X2 | - | XS-60240B |  | -
C2-S06-P17 | 6 | 17 | 18 | 1756-OB32 | XV-60214_DO_1 | Pin 18 | C2S6:18/C2S06-X2:18 | DO | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S06-X2 | - | XV-60214 |  | 3-25-01-602-PD-03
C2-S06-P18 | 6 | 18 | 19 | 1756-OB32 | XV-60241_DO_1 | Pin 19 | C2S6:19/RL.49:A1 | DO | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S06-X2 | - | XV-60241 |  | 3-25-01-602-PD-05
C2-S06-P19 | 6 | 19 | 20 | 1756-OB32 | Spare_DO_0 | Pin 20 | C2S6:20/RL.50:A1 | DO | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P20 | 6 | 20 | 21 | 1756-OB32 | Spare_DO_0 | Pin 21 | C2S6:21/RL.51:A1 | DO | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P21 | 6 | 21 | 22 | 1756-OB32 | Spare_DO_0 | Pin 22 | C2S6:22/RL.52:A1 | DO | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P22 | 6 | 22 | 23 | 1756-OB32 | Spare_DO_0 | Pin 23 | C2S6:23/RL.53:A1 | DO | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P23 | 6 | 23 | 24 | 1756-OB32 | Spare_DO_0 | Pin 24 | C2S6:24/RL.54:A1 | DO | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P24 | 6 | 24 | 25 | 1756-OB32 | Spare_DO_0 | Pin 25 | C2S6:25/RL.55:A1 | DO | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P25 | 6 | 25 | 26 | 1756-OB32 | Spare_DO_0 | Pin 26 | C2S6:26/RL.56:A1 | DO | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P26 | 6 | 26 | 27 | 1756-OB32 | Spare_DO_0 | Pin 27 | C2S6:27/RL.57:A1 | DO | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P27 | 6 | 27 | 28 | 1756-OB32 | Spare_DO_0 | Pin 28 | C2S6:28/RL.58:A1 | DO | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P28 | 6 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C2S6:29/RL.59:A1 | DO | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P29 | 6 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C2S6:30/RL.60:A1 | DO | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P30 | 6 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C2S6:31/RL.61:A1 | DO | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P31 | 6 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C2S6:32/RL.62:A1 | DO | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
Slot 07 — Module: 1756-OB32 (DO) ¦ Total: 32 Channels (Active: 31, Spare: 1)
C2-S07-P00 | 7 | 0 | 1 | 1756-OB32 | SV-60207_DO_1 | Pin 1 | C2S7:1/C2S07-X1:1 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | SV-60207 |  | 3-25-01-602-PD-07
C2-S07-P01 | 7 | 1 | 2 | 1756-OB32 | XS-FH-60210C_DO_1 | Pin 2 | C2S7:2/C2S07-X1:2 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XS-FH-60210C |  | -
C2-S07-P02 | 7 | 2 | 3 | 1756-OB32 | XS-FH-60210D_DO_1 | Pin 3 | C2S7:3/C2S07-X1:3 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XS-FH-60210D |  | -
C2-S07-P03 | 7 | 3 | 4 | 1756-OB32 | XV-60201_DO_1 | Pin 4 | C2S7:4/C2S07-X1:4 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60201 |  | 3-25-01-602-PD-02
C2-S07-P04 | 7 | 4 | 5 | 1756-OB32 | XV-60261_DO_1 | Pin 5 | C2S7:5/C2S07-X1:5 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261 |  | -
C2-S07-P05 | 7 | 5 | 6 | 1756-OB32 | XV-60261FA_DO_1 | Pin 6 | C2S7:6/C2S07-X1:6 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261FA |  | 3-25-01-602-PD-02
C2-S07-P06 | 7 | 6 | 7 | 1756-OB32 | XV-60261FB_DO_1 | Pin 7 | C2S7:7/C2S07-X1:7 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261FB |  | 3-25-01-602-PD-02
C2-S07-P07 | 7 | 7 | 8 | 1756-OB32 | XV-60261FC_DO_1 | Pin 8 | C2S7:8/C2S07-X1:8 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261FC |  | 3-25-01-602-PD-02
C2-S07-P08 | 7 | 8 | 9 | 1756-OB32 | XV-60261FD_DO_1 | Pin 9 | C2S7:9/C2S07-X1:9 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261FD |  | 3-25-01-602-PD-02
C2-S07-P09 | 7 | 9 | 10 | 1756-OB32 | XV-60261SA_DO_1 | Pin 10 | C2S7:10/C2S07-X1:10 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261SA |  | 3-25-01-602-PD-02
C2-S07-P10 | 7 | 10 | 11 | 1756-OB32 | XV-60261SB_DO_1 | Pin 11 | C2S7:11/C2S07-X1:11 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261SB |  | 3-25-01-602-PD-02
C2-S07-P11 | 7 | 11 | 12 | 1756-OB32 | XV-60261SC_DO_1 | Pin 12 | C2S7:12/C2S07-X1:12 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261SC |  | 3-25-01-602-PD-02
C2-S07-P12 | 7 | 12 | 13 | 1756-OB32 | XV-60261SD_DO_1 | Pin 13 | C2S7:13/C2S07-X1:13 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261SD |  | 3-25-01-602-PD-02
C2-S07-P13 | 7 | 13 | 14 | 1756-OB32 | XV-60262_DO_1 | Pin 14 | C2S7:14/C2S07-X1:14 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60262 |  | -
C2-S07-P14 | 7 | 14 | 15 | 1756-OB32 | XV-60262FE_DO_1 | Pin 15 | C2S7:15/C2S07-X1:15 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60262FE |  | 3-25-01-602-PD-02
C2-S07-P15 | 7 | 15 | 16 | 1756-OB32 | XV-60262FF_DO_1 | Pin 16 | C2S7:16/C2S07-X1:16 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60262FF |  | 3-25-01-602-PD-02
C2-S07-P16 | 7 | 16 | 17 | 1756-OB32 | XV-60262FG_DO_1 | Pin 17 | C2S7:17/C2S07-X2:17 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262FG |  | 3-25-01-602-PD-02
C2-S07-P17 | 7 | 17 | 18 | 1756-OB32 | XV-60262FH_DO_1 | Pin 18 | C2S7:18/C2S07-X2:18 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262FH |  | 3-25-01-602-PD-02
C2-S07-P18 | 7 | 18 | 19 | 1756-OB32 | XV-60262SE_DO_1 | Pin 19 | C2S7:19/C2S07-X2:19 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262SE |  | 3-25-01-602-PD-02
C2-S07-P19 | 7 | 19 | 20 | 1756-OB32 | XV-60262SF_DO_1 | Pin 20 | C2S7:20/C2S07-X2:20 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262SF |  | 3-25-01-602-PD-02
C2-S07-P20 | 7 | 20 | 21 | 1756-OB32 | XV-60262SG_DO_1 | Pin 21 | C2S7:21/C2S07-X2:21 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262SG |  | 3-25-01-602-PD-02
C2-S07-P21 | 7 | 21 | 22 | 1756-OB32 | XV-60262SH_DO_1 | Pin 22 | C2S7:22/C2S07-X2:22 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262SH |  | 3-25-01-602-PD-02
C2-S07-P22 | 7 | 22 | 23 | 1756-OB32 | XV-60263_DO_1 | Pin 23 | C2S7:23/C2S07-X2:23 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263 |  | -
C2-S07-P23 | 7 | 23 | 24 | 1756-OB32 | XV-60263FJ_DO_1 | Pin 24 | C2S7:24/C2S07-X2:24 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263FJ |  | 3-25-01-602-PD-02
C2-S07-P24 | 7 | 24 | 25 | 1756-OB32 | XV-60263FK_DO_1 | Pin 25 | C2S7:25/C2S07-X2:25 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263FK |  | 3-25-01-602-PD-02
C2-S07-P25 | 7 | 25 | 26 | 1756-OB32 | XV-60263FL_DO_1 | Pin 26 | C2S7:26/C2S07-X2:26 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263FL |  | 3-25-01-602-PD-02
C2-S07-P26 | 7 | 26 | 27 | 1756-OB32 | XV-60263FM_DO_1 | Pin 27 | C2S7:27/C2S07-X2:27 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263FM |  | 3-25-01-602-PD-02
C2-S07-P27 | 7 | 27 | 28 | 1756-OB32 | XV-60263SJ_DO_1 | Pin 28 | C2S7:28/C2S07-X2:28 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263SJ |  | 3-25-01-602-PD-02
C2-S07-P28 | 7 | 28 | 29 | 1756-OB32 | XV-60263SK_DO_1 | Pin 29 | C2S7:29/C2S07-X2:29 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263SK |  | 3-25-01-602-PD-02
C2-S07-P29 | 7 | 29 | 30 | 1756-OB32 | XV-60263SL_DO_1 | Pin 30 | C2S7:30/C2S07-X2:30 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263SL |  | 3-25-01-602-PD-02
C2-S07-P30 | 7 | 30 | 31 | 1756-OB32 | XV-60263SM_DO_1 | Pin 31 | C2S7:31/C2S07-X2:31 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263SM |  | 3-25-01-602-PD-02
C2-S07-P31 | 7 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C2S7:32/C2S07-X2:32 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S07-X2 | - | Spare | Spare Channel | -
Slot 08 — Module: 1756-OB32 (DO) ¦ Total: 32 Channels (Active: 9, Spare: 23)
C2-S08-P00 | 8 | 0 | 1 | 1756-OB32 | XV-60264_DO_1 | Pin 1 | C2S8:1/C2S08-X1:1 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264 |  | -
C2-S08-P01 | 8 | 1 | 2 | 1756-OB32 | XV-60264FN_DO_1 | Pin 2 | C2S8:2/C2S08-X1:2 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264FN |  | 3-25-01-602-PD-02
C2-S08-P02 | 8 | 2 | 3 | 1756-OB32 | XV-60264FP_DO_1 | Pin 3 | C2S8:3/C2S08-X1:3 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264FP |  | 3-25-01-602-PD-02
C2-S08-P03 | 8 | 3 | 4 | 1756-OB32 | XV-60264FQ_DO_1 | Pin 4 | C2S8:4/C2S08-X1:4 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264FQ |  | 3-25-01-602-PD-02
C2-S08-P04 | 8 | 4 | 5 | 1756-OB32 | XV-60264FR_DO_1 | Pin 5 | C2S8:5/C2S08-X1:5 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264FR |  | 3-25-01-602-PD-02
C2-S08-P05 | 8 | 5 | 6 | 1756-OB32 | XV-60264SN_DO_1 | Pin 6 | C2S8:6/C2S08-X1:6 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264SN |  | 3-25-01-602-PD-02
C2-S08-P06 | 8 | 6 | 7 | 1756-OB32 | XV-60264SP_DO_1 | Pin 7 | C2S8:7/C2S08-X1:7 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264SP |  | 3-25-01-602-PD-02
C2-S08-P07 | 8 | 7 | 8 | 1756-OB32 | XV-60264SQ_DO_1 | Pin 8 | C2S8:8/C2S08-X1:8 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264SQ |  | 3-25-01-602-PD-02
C2-S08-P08 | 8 | 8 | 9 | 1756-OB32 | XV-60264SR_DO_1 | Pin 9 | C2S8:9/C2S08-X1:9 | DO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264SR |  | 3-25-01-602-PD-02
C2-S08-P09 | 8 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C2S8:10/C2S08-X1:10 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P10 | 8 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C2S8:11/C2S08-X1:11 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P11 | 8 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C2S8:12/C2S08-X1:12 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P12 | 8 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C2S8:13/C2S08-X1:13 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P13 | 8 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C2S8:14/C2S08-X1:14 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P14 | 8 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C2S8:15/C2S08-X1:15 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P15 | 8 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C2S8:16/C2S08-X1:16 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P16 | 8 | 16 | 17 | 1756-OB32 | Spare_DO_0 | Pin 17 | C2S8:17/C2S08-X2:17 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P17 | 8 | 17 | 18 | 1756-OB32 | Spare_DO_0 | Pin 18 | C2S8:18/C2S08-X2:18 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P18 | 8 | 18 | 19 | 1756-OB32 | Spare_DO_0 | Pin 19 | C2S8:19/C2S08-X2:19 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P19 | 8 | 19 | 20 | 1756-OB32 | Spare_DO_0 | Pin 20 | C2S8:20/C2S08-X2:20 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P20 | 8 | 20 | 21 | 1756-OB32 | Spare_DO_0 | Pin 21 | C2S8:21/C2S08-X2:21 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P21 | 8 | 21 | 22 | 1756-OB32 | Spare_DO_0 | Pin 22 | C2S8:22/C2S08-X2:22 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P22 | 8 | 22 | 23 | 1756-OB32 | Spare_DO_0 | Pin 23 | C2S8:23/C2S08-X2:23 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P23 | 8 | 23 | 24 | 1756-OB32 | Spare_DO_0 | Pin 24 | C2S8:24/C2S08-X2:24 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P24 | 8 | 24 | 25 | 1756-OB32 | Spare_DO_0 | Pin 25 | C2S8:25/C2S08-X2:25 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P25 | 8 | 25 | 26 | 1756-OB32 | Spare_DO_0 | Pin 26 | C2S8:26/C2S08-X2:26 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P26 | 8 | 26 | 27 | 1756-OB32 | Spare_DO_0 | Pin 27 | C2S8:27/C2S08-X2:27 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P27 | 8 | 27 | 28 | 1756-OB32 | Spare_DO_0 | Pin 28 | C2S8:28/C2S08-X2:28 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P28 | 8 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C2S8:29/C2S08-X2:29 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P29 | 8 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C2S8:30/C2S08-X2:30 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P30 | 8 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C2S8:31/C2S08-X2:31 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P31 | 8 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C2S8:32/C2S08-X2:32 | DO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
Slot 09 — Module: 1756-IF16 (AI) ¦ Total: 16 Channels (Active: 7, Spare: 9)
C2-S09-P00 | 9 | 0 | 1 | 1756-IF16 | FT-40221_AI_1 | Pin 1 | C2S9:1/C2S09-X1:1 | AI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | FT-40221 | Coriolis Flow Transmitter | 325-01-402-PD-02
C2-S09-P01 | 9 | 1 | 2 | 1756-IF16 | FT-40221_AI_2 | Pin 2 | C2S9:2/C2S09-X1:2 | AI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | FT-40221 | Coriolis Flow Transmitter | 325-01-402-PD-02
C2-S09-P02 | 9 | 2 | 3 | 1756-IF16 | FT-40222_AI_1 | Pin 3 | C2S9:3/C2S09-X1:3 | AI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | FT-40222 | Coriolis Flow Transmitter | 325-01-402-PD-02
C2-S09-P03 | 9 | 3 | 4 | 1756-IF16 | FT-40222_AI_2 | Pin 4 | C2S9:4/C2S09-X1:4 | AI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | FT-40222 | Coriolis Flow Transmitter | 325-01-402-PD-02
C2-S09-P04 | 9 | 4 | 5 | 1756-IF16 | PT-40222_AI_1 | Pin 5 | C2S9:5/C2S09-X1:5 | AI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | PT-40222 | Pressure Transmitter | 325-01-402-PD-02
C2-S09-P05 | 9 | 5 | 6 | 1756-IF16 | TT-40221_AI_1 | Pin 6 | C2S9:6/C2S09-X1:6 | AI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | TT-40221 |  | 325-01-402-PD-02
C2-S09-P06 | 9 | 6 | 7 | 1756-IF16 | TT-40222_AI_1 | Pin 7 | C2S9:7/C2S09-X1:7 | AI | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | TT-40222 |  | 325-01-402-PD-02
C2-S09-P07 | 9 | 7 | 8 | 1756-IF16 | Spare_AI_0 | Pin 8 | C2S9:8/C2S09-X1:8 | AI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P08 | 9 | 8 | 9 | 1756-IF16 | Spare_AI_0 | Pin 9 | C2S9:9/C2S09-X1:9 | AI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P09 | 9 | 9 | 10 | 1756-IF16 | Spare_AI_0 | Pin 10 | C2S9:10/C2S09-X1:10 | AI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P10 | 9 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C2S9:11/C2S09-X1:11 | AI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P11 | 9 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C2S9:12/C2S09-X1:12 | AI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P12 | 9 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C2S9:13/C2S09-X1:13 | AI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P13 | 9 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C2S9:14/C2S09-X1:14 | AI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P14 | 9 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C2S9:15/C2S09-X1:15 | AI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P15 | 9 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C2S9:16/C2S09-X1:16 | AI | 24VDC | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
Slot 10 — Module: 1756-IF16 (AI) ¦ Total: 16 Channels (Active: 16, Spare: 0)
C2-S10-P00 | 10 | 0 | 1 | 1756-IF16 | AT-60241_AI_1 | Pin 1 | C2S10:1/C2S10-X1:1 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | AT-60241 | Dust Analyzer Transmitter | 3-25-01-602-PD-05
C2-S10-P01 | 10 | 1 | 2 | 1756-IF16 | DPT-60203_AI_1 | Pin 2 | C2S10:2/C2S10-X1:2 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | DPT-60203 | Differential Pressure Transmitte | 3-25-01-602-PD-03
C2-S10-P02 | 10 | 2 | 3 | 1756-IF16 | FT-60202_AI_1 | Pin 3 | C2S10:3/C2S10-X1:3 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | FT-60202 |  | 3-25-01-602-PD-09
C2-S10-P03 | 10 | 3 | 4 | 1756-IF16 | PT-60210_AI_1 | Pin 4 | C2S10:4/C2S10-X1:4 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60210 | Pressure Transmitter | 3-25-01-602-PD-03
C2-S10-P04 | 10 | 4 | 5 | 1756-IF16 | PT-60215_AI_1 | Pin 5 | C2S10:5/C2S10-X1:5 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60215 | Pressure Transmitter | 3-25-01-602-PD-03
C2-S10-P05 | 10 | 5 | 6 | 1756-IF16 | PT-60216_AI_1 | Pin 6 | C2S10:6/C2S10-X1:6 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60216 | Pressure Transmitter | 3-25-01-602-PD-03
C2-S10-P06 | 10 | 6 | 7 | 1756-IF16 | PT-60240_AI_1 | Pin 7 | C2S10:7/C2S10-X1:7 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60240 | Pressure Transmitter | 3-25-01-602-PD-05
C2-S10-P07 | 10 | 7 | 8 | 1756-IF16 | PT-60241_AI_1 | Pin 8 | C2S10:8/C2S10-X1:8 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60241 | Pressure Transmitter | 3-25-01-602-PD-05
C2-S10-P08 | 10 | 8 | 9 | 1756-IF16 | TT-60210_AI_1 | Pin 9 | C2S10:9/C2S10-X1:9 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60210 |  | 3-25-01-602-PD-03
C2-S10-P09 | 10 | 9 | 10 | 1756-IF16 | TT-60210A_AI_1 | Pin 10 | C2S10:10/C2S10-X1:10 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60210A |  | -
C2-S10-P10 | 10 | 10 | 11 | 1756-IF16 | TT-60210B_AI_1 | Pin 11 | C2S10:11/C2S10-X1:11 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60210B |  | -
C2-S10-P11 | 10 | 11 | 12 | 1756-IF16 | TT-60211_AI_1 | Pin 12 | C2S10:12/C2S10-X1:12 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60211 |  | 3-25-01-602-PD-03
C2-S10-P12 | 10 | 12 | 13 | 1756-IF16 | TT-60212A_AI_1 | Pin 13 | C2S10:13/C2S10-X1:13 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60212A |  | 3-25-01-602-PD-03
C2-S10-P13 | 10 | 13 | 14 | 1756-IF16 | TT-60212B_AI_1 | Pin 14 | C2S10:14/C2S10-X1:14 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60212B |  | 3-25-01-602-PD-03
C2-S10-P14 | 10 | 14 | 15 | 1756-IF16 | TT-60214_AI_1 | Pin 15 | C2S10:15/C2S10-X1:15 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60214 |  | 3-25-01-602-PD-03
C2-S10-P15 | 10 | 15 | 16 | 1756-IF16 | TT-60215A_AI_1 | Pin 16 | C2S10:16/C2S10-X1:16 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60215A |  | 3-25-01-602-PD-03
Slot 11 — Module: 1756-IF16 (AI) ¦ Total: 16 Channels (Active: 13, Spare: 3)
C2-S11-P00 | 11 | 0 | 1 | 1756-IF16 | TT-60215B_AI_1 | Pin 1 | C2S11:1/C2S11-X1:1 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60215B |  | 3-25-01-602-PD-03
C2-S11-P01 | 11 | 1 | 2 | 1756-IF16 | TT-60216_AI_1 | Pin 2 | C2S11:2/C2S11-X1:2 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60216 |  | 3-25-01-602-PD-03
C2-S11-P02 | 11 | 2 | 3 | 1756-IF16 | TT-60240_AI_1 | Pin 3 | C2S11:3/C2S11-X1:3 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60240 |  | 3-25-01-602-PD-05
C2-S11-P03 | 11 | 3 | 4 | 1756-IF16 | TT-60241A_AI_1 | Pin 4 | C2S11:4/C2S11-X1:4 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60241A |  | 3-25-01-602-PD-05
C2-S11-P04 | 11 | 4 | 5 | 1756-IF16 | TT-60241B_AI_1 | Pin 5 | C2S11:5/C2S11-X1:5 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60241B |  | 3-25-01-602-PD-05
C2-S11-P05 | 11 | 5 | 6 | 1756-IF16 | VT-60210A_AI_1 | Pin 6 | C2S11:6/C2S11-X1:6 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60210A |  | 3-25-01-602-PD-03
C2-S11-P06 | 11 | 6 | 7 | 1756-IF16 | VT-60210B_AI_1 | Pin 7 | C2S11:7/C2S11-X1:7 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60210B |  | 3-25-01-602-PD-03
C2-S11-P07 | 11 | 7 | 8 | 1756-IF16 | VT-60241A_AI_1 | Pin 8 | C2S11:8/C2S11-X1:8 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60241A |  | 3-25-01-602-PD-05
C2-S11-P08 | 11 | 8 | 9 | 1756-IF16 | VT-60241B_AI_1 | Pin 9 | C2S11:9/C2S11-X1:9 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60241B |  | 3-25-01-602-PD-05
C2-S11-P09 | 11 | 9 | 10 | 1756-IF16 | FT-60210_AI_1 | Pin 10 | C2S11:10/C2S11-X1:10 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60210 |  | 3-25-01-602-PD-03
C2-S11-P10 | 11 | 10 | 11 | 1756-IF16 | FT-60211_AI_1 | Pin 11 | C2S11:11/C2S11-X1:11 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60211 |  | 3-25-01-602-PD-03
C2-S11-P11 | 11 | 11 | 12 | 1756-IF16 | FT-60210_AI_2 | Pin 12 | C2S11:12/C2S11-X1:12 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60210 |  | 3-25-01-602-PD-03
C2-S11-P12 | 11 | 12 | 13 | 1756-IF16 | FT-60211_AI_2 | Pin 13 | C2S11:13/C2S11-X1:13 | AI | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60211 |  | 3-25-01-602-PD-03
C2-S11-P13 | 11 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C2S11:14/C2S11-X1:14 | AI | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S11-X1 | - | Spare | Spare Channel | -
C2-S11-P14 | 11 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C2S11:15/C2S11-X1:15 | AI | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S11-X1 | - | Spare | Spare Channel | -
C2-S11-P15 | 11 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C2S11:16/C2S11-X1:16 | AI | 24VDC | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S11-X1 | - | Spare | Spare Channel | -
Slot 12 — Module: 1756-IF16 (AI) ¦ Total: 16 Channels (Active: 16, Spare: 0)
C2-S12-P00 | 12 | 0 | 1 | 1756-IF16 | FT-60207_AI_1 | Pin 1 | C2S12:1/C2S12-X1:1 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60207 |  | 3-25-01-602-PD-07
C2-S12-P01 | 12 | 1 | 2 | 1756-IF16 | FT-60221_AI_1 | Pin 2 | C2S12:2/C2S12-X1:2 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60221 |  | 3-25-01-602-PD-04
C2-S12-P02 | 12 | 2 | 3 | 1756-IF16 | FT-60261FA_AI_1 | Pin 3 | C2S12:3/C2S12-X1:3 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60261FA |  | 3-25-01-602-PD-02
C2-S12-P03 | 12 | 3 | 4 | 1756-IF16 | FT-60261FB_AI_1 | Pin 4 | C2S12:4/C2S12-X1:4 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60261FB |  | 3-25-01-602-PD-02
C2-S12-P04 | 12 | 4 | 5 | 1756-IF16 | FT-60261FC_AI_1 | Pin 5 | C2S12:5/C2S12-X1:5 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60261FC |  | 3-25-01-602-PD-02
C2-S12-P05 | 12 | 5 | 6 | 1756-IF16 | FT-60261FD_AI_1 | Pin 6 | C2S12:6/C2S12-X1:6 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60261FD |  | 3-25-01-602-PD-02
C2-S12-P06 | 12 | 6 | 7 | 1756-IF16 | FT-60262FE_AI_1 | Pin 7 | C2S12:7/C2S12-X1:7 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60262FE |  | 3-25-01-602-PD-02
C2-S12-P07 | 12 | 7 | 8 | 1756-IF16 | FT-60262FF_AI_1 | Pin 8 | C2S12:8/C2S12-X1:8 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60262FF |  | 3-25-01-602-PD-02
C2-S12-P08 | 12 | 8 | 9 | 1756-IF16 | FT-60262FG_AI_1 | Pin 9 | C2S12:9/C2S12-X1:9 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60262FG |  | 3-25-01-602-PD-02
C2-S12-P09 | 12 | 9 | 10 | 1756-IF16 | FT-60262FH_AI_1 | Pin 10 | C2S12:10/C2S12-X1:10 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60262FH |  | 3-25-01-602-PD-02
C2-S12-P10 | 12 | 10 | 11 | 1756-IF16 | FT-60263FJ_AI_1 | Pin 11 | C2S12:11/C2S12-X1:11 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60263FJ |  | 3-25-01-602-PD-02
C2-S12-P11 | 12 | 11 | 12 | 1756-IF16 | FT-60263FK_AI_1 | Pin 12 | C2S12:12/C2S12-X1:12 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60263FK |  | 3-25-01-602-PD-02
C2-S12-P12 | 12 | 12 | 13 | 1756-IF16 | FT-60263FL_AI_1 | Pin 13 | C2S12:13/C2S12-X1:13 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60263FL |  | 3-25-01-602-PD-02
C2-S12-P13 | 12 | 13 | 14 | 1756-IF16 | FT-60263FM_AI_1 | Pin 14 | C2S12:14/C2S12-X1:14 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60263FM |  | 3-25-01-602-PD-02
C2-S12-P14 | 12 | 14 | 15 | 1756-IF16 | FT-60264FN_AI_1 | Pin 15 | C2S12:15/C2S12-X1:15 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60264FN |  | 3-25-01-602-PD-02
C2-S12-P15 | 12 | 15 | 16 | 1756-IF16 | FT-60264FP_AI_1 | Pin 16 | C2S12:16/C2S12-X1:16 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60264FP |  | 3-25-01-602-PD-02
Slot 13 — Module: 1756-IF16 (AI) ¦ Total: 16 Channels (Active: 11, Spare: 5)
C2-S13-P00 | 13 | 0 | 1 | 1756-IF16 | FT-60264FQ_AI_1 | Pin 1 | C2S13:1/C2S13-X1:1 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | FT-60264FQ |  | 3-25-01-602-PD-02
C2-S13-P01 | 13 | 1 | 2 | 1756-IF16 | FT-60264FR_AI_1 | Pin 2 | C2S13:2/C2S13-X1:2 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | FT-60264FR |  | 3-25-01-602-PD-02
C2-S13-P02 | 13 | 2 | 3 | 1756-IF16 | PT-60201_AI_1 | Pin 3 | C2S13:3/C2S13-X1:3 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | PT-60201 | Pressure Transmitter | 3-25-01-602-PD-02
C2-S13-P03 | 13 | 3 | 4 | 1756-IF16 | PT-60207_AI_1 | Pin 4 | C2S13:4/C2S13-X1:4 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | PT-60207 | Pressure Transmitter | 3-25-01-602-PD-07
C2-S13-P04 | 13 | 4 | 5 | 1756-IF16 | PT-60221_AI_1 | Pin 5 | C2S13:5/C2S13-X1:5 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | PT-60221 | Pressure Transmitter | 3-25-01-602-PD-04
C2-S13-P05 | 13 | 5 | 6 | 1756-IF16 | PT-60221_AI_1 | Pin 6 | C2S13:6/C2S13-X1:6 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | PT-60221 | Pressure Transmitter | 3-25-01-602-PD-04
C2-S13-P06 | 13 | 6 | 7 | 1756-IF16 | TI-FH-60210_AI_1 | Pin 7 | C2S13:7/C2S13-X1:7 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | TI-FH-60210 |  | -
C2-S13-P07 | 13 | 7 | 8 | 1756-IF16 | TT-60201_AI_1 | Pin 8 | C2S13:8/C2S13-X1:8 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | TT-60201 |  | 3-25-01-602-PD-02
C2-S13-P08 | 13 | 8 | 9 | 1756-IF16 | TT-60202_AI_1 | Pin 9 | C2S13:9/C2S13-X1:9 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | TT-60202 |  | 3-25-01-602-PD-07
C2-S13-P09 | 13 | 9 | 10 | 1756-IF16 | TT-60207_AI_1 | Pin 10 | C2S13:10/C2S13-X1:10 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | TT-60207 |  | 3-25-01-602-PD-07
C2-S13-P10 | 13 | 10 | 11 | 1756-IF16 | UY-FH-60210A_AI_1 | Pin 11 | C2S13:11/C2S13-X1:11 | AI | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | UY-FH-60210A |  | -
C2-S13-P11 | 13 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C2S13:12/C2S13-X1:12 | AI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | -
C2-S13-P12 | 13 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C2S13:13/C2S13-X1:13 | AI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | -
C2-S13-P13 | 13 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C2S13:14/C2S13-X1:14 | AI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | -
C2-S13-P14 | 13 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C2S13:15/C2S13-X1:15 | AI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | -
C2-S13-P15 | 13 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C2S13:16/C2S13-X1:16 | AI | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | -

## Chassis_C3
KALASIN ENGINEERING — C3 (I/O EXPANSION RACK 2 (CHASSIS 3))
Location: Control Cabinet CA1 (Bay 3) ¦ Role: Evaporator, Concentrator & Dosing Skid I/O ¦ Net: EN4TR DLR Ring Node 3 (192.168.1.12) ¦ Total Points: 136 (Active: 74, Spare: 62)
SOURCE (PLC RACK / SLOT / TERMINAL / ePLAN TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Type | Status | Destination | Field Location | Floor/Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing
Slot 01 — Module: 1756-IB32 (DI) ¦ Total: 27 Channels (Active: 22, Spare: 5)
C3-S01-P00 | 1 | 0 | 1 | 1756-IB32 | AT-40201_DI_1 | Pin 1 | C3S1:1/C3S01-X1:1 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | AT-40201 |  | -
C3-S01-P01 | 1 | 1 | 2 | 1756-IB32 | AT-40202_DI_1 | Pin 2 | C3S1:2/C3S01-X1:2 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | AT-40202 |  | -
C3-S01-P02 | 1 | 2 | 3 | 1756-IB32 | AT-40203_DI_1 | Pin 3 | C3S1:3/C3S01-X1:3 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | AT-40203 |  | -
C3-S01-P03 | 1 | 3 | 4 | 1756-IB32 | LSH-60230_DI_1 | Pin 4 | C3S1:4/C3S01-X1:4 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S01-X1 | - | LSH-60230 |  | 3-25-01-602-PD-04
C3-S01-P04 | 1 | 4 | 5 | 1756-IB32 | LSH-60231_DI_1 | Pin 5 | C3S1:5/C3S01-X1:5 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S01-X1 | - | LSH-60231 |  | 3-25-01-602-PD-04
C3-S01-P05 | 1 | 5 | 6 | 1756-IB32 | LSH-60240_DI_1 | Pin 6 | C3S1:6/C3S01-X1:6 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S01-X1 | - | LSH-60240 |  | 3-25-01-602-PD-05
C3-S01-P06 | 1 | 6 | 7 | 1756-IB32 | PD-60202_DI_1 | Pin 7 | C3S1:7/C3S01-X1:7 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | PD-60202 |  | -
C3-S01-P07 | 1 | 7 | 8 | 1756-IB32 | RV-60204_DI_1 | Pin 8 | C3S1:8/C3S01-X1:8 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | RV-60204 |  | -
C3-S01-P08 | 1 | 8 | 9 | 1756-IB32 | ZS-60201C_DI_1 | Pin 9 | C3S1:9/C3S01-X1:9 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60201C |  | 3-25-01-602-PD-04
C3-S01-P09 | 1 | 9 | 10 | 1756-IB32 | ZS-60201D_DI_1 | Pin 10 | C3S1:10/C3S01-X1:10 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60201D |  | 3-25-01-602-PD-04
C3-S01-P10 | 1 | 10 | 11 | 1756-IB32 | ZS-60201E_DI_1 | Pin 11 | C3S1:11/C3S01-X1:11 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S01-X1 | - | ZS-60201E |  | 3-25-01-602-PD-04
C3-S01-P11 | 1 | 11 | 12 | 1756-IB32 | ZS-60229_DI_1 | Pin 12 | C3S1:12/C3S01-X1:12 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60229 |  | 3-25-01-602-PD-04
C3-S01-P12 | 1 | 12 | 13 | 1756-IB32 | ZS-60230_DI_1 | Pin 13 | C3S1:13/C3S01-X1:13 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60230 |  | 3-25-01-602-PD-04
C3-S01-P13 | 1 | 13 | 14 | 1756-IB32 | ZS-60231A_DI_1 | Pin 14 | C3S1:14/C3S01-X1:14 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60231A |  | 3-25-01-602-PD-05
C3-S01-P14 | 1 | 14 | 15 | 1756-IB32 | ZS-60231B_DI_1 | Pin 15 | C3S1:15/C3S01-X1:15 | DI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60231B |  | 3-25-01-602-PD-05
C3-S01-P15 | 1 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C3S1:16/C3S01-X1:16 | DI | 24VDC | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S01-X1 | - | Spare | Spare Channel | -
C3-S01-P16 | 1 | 16 | 17 | 1756-IB32 | DV-61301_DI_1 | Pin 17 | C3S1:17/C3S01-X2:17 | DI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S01-X2 | - | DV-61301 |  | 3-25-01-613-PD-01
C3-S01-P17 | 1 | 17 | 18 | 1756-IB32 | DV-61301_DI_2 | Pin 18 | C3S1:18/C3S01-X2:18 | DI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S01-X2 | - | DV-61301 |  | 3-25-01-613-PD-01
C3-S01-P18 | 1 | 18 | 19 | 1756-IB32 | DV-61302_DI_1 | Pin 19 | C3S1:19/C3S01-X2:19 | DI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S01-X2 | - | DV-61302 |  | 3-25-01-613-PD-01
C3-S01-P19 | 1 | 19 | 20 | 1756-IB32 | DV-61302_DI_2 | Pin 20 | C3S1:20/C3S01-X2:20 | DI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S01-X2 | - | DV-61302 |  | 3-25-01-613-PD-01
C3-S01-P20 | 1 | 20 | 21 | 1756-IB32 | LS-61303_DI_1 | Pin 21 | C3S1:21/C3S01-X2:21 | DI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 7th / Packing Tower | C3S01-X2 | - | LS-61303 |  | 3-25-01-613-PD-01
C3-S01-P21 | 1 | 21 | 22 | 1756-IB32 | PSL-61301_DI_1 | Pin 22 | C3S1:22/C3S01-X2:22 | DI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S01-X2 | - | PSL-61301 |  | -
C3-S01-P22 | 1 | 22 | 23 | 1756-IB32 | PSL-61302_DI_1 | Pin 23 | C3S1:23/C3S01-X2:23 | DI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S01-X2 | - | PSL-61302 |  | 3-25-01-613-PD-01
C3-S01-P28 | 1 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C3S1:29/C3S01-X2:29 | DI | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | Packing Tower | C3S01-X2 | - | Spare | Spare Channel | -
C3-S01-P29 | 1 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C3S1:30/C3S01-X2:30 | DI | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | Packing Tower | C3S01-X2 | - | Spare | Spare Channel | -
C3-S01-P30 | 1 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C3S1:31/C3S01-X2:31 | DI | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | Packing Tower | C3S01-X2 | - | Spare | Spare Channel | -
C3-S01-P31 | 1 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C3S1:32/C3S01-X2:32 | DI | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | Packing Tower | C3S01-X2 | - | Spare | Spare Channel | -
Slot 02 — Module: 1756-IB32 (DI) ¦ Total: 37 Channels (Active: 18, Spare: 19)
C3-S02-P00 | 2 | 0 | 1 | 1756-IB32 | ISV-61301_DI_1 | Pin 1 | C3S2:1/C3S02-X1:1 | DI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X1 | - | ISV-61301 |  | 3-25-01-613-PD-01
C3-S02-P01 | 2 | 1 | 2 | 1756-IB32 | LSH-61301_DI_1 | Pin 2 | C3S2:2/C3S02-X1:2 | DI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 7th / Packing Tower | C3S02-X1 | - | LSH-61301 |  | 3-25-01-613-PD-01
C3-S02-P02 | 2 | 2 | 3 | 1756-IB32 | LSH-61303_DI_1 | Pin 3 | C3S2:3/C3S02-X1:3 | DI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 7th / Packing Tower | C3S02-X1 | - | LSH-61303 |  | -
C3-S02-P03 | 2 | 3 | 4 | 1756-IB32 | LSH-61306_DI_1 | Pin 4 | C3S2:4/C3S02-X1:4 | DI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X1 | - | LSH-61306 |  | 3-25-01-613-PD-01
C3-S02-P04 | 2 | 4 | 5 | 1756-IB32 | LSH-61308_DI_1 | Pin 5 | C3S2:5/C3S02-X1:5 | DI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X1 | - | LSH-61308 |  | 3-25-01-613-PD-01
C3-S02-P05 | 2 | 5 | 6 | 1756-IB32 | LSL-61302_DI_1 | Pin 6 | C3S2:6/C3S02-X1:6 | DI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 6th / Packing Tower | C3S02-X1 | - | LSL-61302 |  | 3-25-01-613-PD-01
C3-S02-P06 | 2 | 6 | 7 | 1756-IB32 | PSE-61300_DI_1 | Pin 7 | C3S2:7/C3S02-X1:7 | DI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X1 | - | PSE-61300 |  | 3-25-01-613-PD-01
C3-S02-P07 | 2 | 7 | 8 | 1756-IB32 | PSE-61301_DI_1 | Pin 8 | C3S2:8/C3S02-X1:8 | DI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X1 | - | PSE-61301 |  | 3-25-01-613-PD-01
C3-S02-P08 | 2 | 8 | 9 | 1756-IB32 | PSE-61304_DI_1 | Pin 9 | C3S2:9/C3S02-X1:9 | DI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X1 | - | PSE-61304 |  | 3-25-01-613-PD-01
C3-S02-P09 | 2 | 9 | 10 | 1756-IB32 | PSV-61301A_DI_1 | Pin 10 | C3S2:10/C3S02-X1:10 | DI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X1 | - | PSV-61301A |  | 325-01-613-PD-01
C3-S02-P10 | 2 | 10 | 11 | 1756-IB32 | PSV-61301B_DI_1 | Pin 11 | C3S2:11/C3S02-X1:11 | DI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X1 | - | PSV-61301B |  | 325-01-613-PD-01
C3-S02-P11 | 2 | 11 | 12 | 1756-IB32 | ZS-61310_DI_1 | Pin 12 | C3S2:12/C3S02-X1:12 | DI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | ZS-61310 |  | 3-25-01-613-PD-01
C3-S02-P12 | 2 | 12 | 13 | 1756-IB32 | ZS-61311_DI_1 | Pin 13 | C3S2:13/C3S02-X1:13 | DI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | ZS-61311 |  | 3-25-01-613-PD-01
C3-S02-P13 | 2 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C3S2:14/C3S02-X1:14 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P14 | 2 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C3S2:15/C3S02-X1:15 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P15 | 2 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C3S2:16/C3S02-X1:16 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P16 | 2 | 16 | 17 | 1756-IB32 | Spare_DI_0 | Pin 17 | C3S2:17/C3S02-X2:17 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P17 | 2 | 17 | 18 | 1756-IB32 | Spare_DI_0 | Pin 18 | C3S2:18/C3S02-X2:18 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P18 | 2 | 18 | 19 | 1756-IB32 | Spare_DI_0 | Pin 19 | C3S2:19/C3S02-X2:19 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P19 | 2 | 19 | 20 | 1756-IB32 | Spare_DI_0 | Pin 20 | C3S2:20/C3S02-X2:20 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P20 | 2 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C3S2:21/C3S02-X2:21 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P21 | 2 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C3S2:22/C3S02-X2:22 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P22 | 2 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C3S2:23/C3S02-X2:23 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P23 | 2 | 23 | 24 | 1756-IB32 | PSL-61311_DI_1 | Pin 24 | C3S2:24/C3S02-X2:24 | DI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X2 | - | PSL-61311 |  | 3-25-01-613-PD-04
C3-S02-P23 | 2 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C3S2:24/C3S02-X2:24 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P24 | 2 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C3S2:25/C3S02-X2:25 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P24 | 2 | 24 | 25 | 1756-IB32 | SV-61304_DI_1 | Pin 25 | C3S2:25/C3S02-X2:25 | DI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X2 | - | SV-61304 |  | 3-25-01-613-PD-01
C3-S02-P25 | 2 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C3S2:26/C3S02-X2:26 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P25 | 2 | 25 | 26 | 1756-IB32 | SV-61304_DI_2 | Pin 26 | C3S2:26/C3S02-X2:26 | DI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X2 | - | SV-61304 |  | 3-25-01-613-PD-01
C3-S02-P26 | 2 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C3S2:27/C3S02-X2:27 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P26 | 2 | 26 | 27 | 1756-IB32 | XV-61301_DI_1 | Pin 27 | C3S2:27/C3S02-X2:27 | DI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | XV-61301 |  | 3-25-01-613-PD-01
C3-S02-P27 | 2 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C3S2:28/C3S02-X2:28 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P27 | 2 | 27 | 28 | 1756-IB32 | XV-61301_DI_2 | Pin 28 | C3S2:28/C3S02-X2:28 | DI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | XV-61301 |  | 3-25-01-613-PD-01
C3-S02-P28 | 2 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C3S2:29/C3S02-X2:29 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P29 | 2 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C3S2:30/C3S02-X2:30 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P30 | 2 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C3S2:31/C3S02-X2:31 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P31 | 2 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C3S2:32/C3S02-X2:32 | DI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
Slot 03 — Module: 1756-OB32 (DO) ¦ Total: 32 Channels (Active: 9, Spare: 23)
C3-S03-P00 | 3 | 0 | 1 | 1756-OB32 | DV-61301_DO_1 | Pin 1 | C3S3:1/C3S03-X1:1 | DO | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S03-X1 | - | DV-61301 |  | 3-25-01-613-PD-01
C3-S03-P01 | 3 | 1 | 2 | 1756-OB32 | DV-61302_DO_1 | Pin 2 | C3S3:2/C3S03-X1:2 | DO | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S03-X1 | - | DV-61302 |  | 3-25-01-613-PD-01
C3-S03-P02 | 3 | 2 | 3 | 1756-OB32 | SV-61301_DO_1 | Pin 3 | C3S3:3/C3S03-X1:3 | DO | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S03-X1 | - | SV-61301 |  | -
C3-S03-P03 | 3 | 3 | 4 | 1756-OB32 | SV-61302_DO_1 | Pin 4 | C3S3:4/C3S03-X1:4 | DO | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 7th / Packing Tower | C3S03-X1 | - | SV-61302 |  | 3-25-01-613-PD-01
C3-S03-P04 | 3 | 4 | 5 | 1756-OB32 | SV-61303_DO_1 | Pin 5 | C3S3:5/C3S03-X1:5 | DO | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S03-X1 | - | SV-61303 |  | 3-25-01-613-PD-01
C3-S03-P05 | 3 | 5 | 6 | 1756-OB32 | SV-61304_DO_1 | Pin 6 | C3S3:6/C3S03-X1:6 | DO | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S03-X1 | - | SV-61304 |  | 3-25-01-613-PD-01
C3-S03-P06 | 3 | 6 | 7 | 1756-OB32 | SV-61305_DO_1 | Pin 7 | C3S3:7/C3S03-X1:7 | DO | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S03-X1 | - | SV-61305 |  | 3-25-01-613-PD-01
C3-S03-P07 | 3 | 7 | 8 | 1756-OB32 | SV-61306_DO_1 | Pin 8 | C3S3:8/C3S03-X1:8 | DO | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S03-X1 | - | SV-61306 |  | 3-25-01-613-PD-01
C3-S03-P08 | 3 | 8 | 9 | 1756-OB32 | XV-61301_DO_1 | Pin 9 | C3S3:9/C3S03-X1:9 | DO | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S03-X1 | - | XV-61301 |  | 3-25-01-613-PD-01
C3-S03-P09 | 3 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C3S3:10/C3S03-X1:10 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P10 | 3 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C3S3:11/C3S03-X1:11 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P11 | 3 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C3S3:12/C3S03-X1:12 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P12 | 3 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C3S3:13/C3S03-X1:13 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P13 | 3 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C3S3:14/C3S03-X1:14 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P14 | 3 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C3S3:15/C3S03-X1:15 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P15 | 3 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C3S3:16/C3S03-X1:16 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P16 | 3 | 16 | 17 | 1756-OB32 | Spare_DO_0 | Pin 17 | C3S3:17/C3S03-X2:17 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P17 | 3 | 17 | 18 | 1756-OB32 | Spare_DO_0 | Pin 18 | C3S3:18/C3S03-X2:18 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P18 | 3 | 18 | 19 | 1756-OB32 | Spare_DO_0 | Pin 19 | C3S3:19/C3S03-X2:19 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P19 | 3 | 19 | 20 | 1756-OB32 | Spare_DO_0 | Pin 20 | C3S3:20/C3S03-X2:20 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P20 | 3 | 20 | 21 | 1756-OB32 | Spare_DO_0 | Pin 21 | C3S3:21/C3S03-X2:21 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P21 | 3 | 21 | 22 | 1756-OB32 | Spare_DO_0 | Pin 22 | C3S3:22/C3S03-X2:22 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P22 | 3 | 22 | 23 | 1756-OB32 | Spare_DO_0 | Pin 23 | C3S3:23/C3S03-X2:23 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P23 | 3 | 23 | 24 | 1756-OB32 | Spare_DO_0 | Pin 24 | C3S3:24/C3S03-X2:24 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P24 | 3 | 24 | 25 | 1756-OB32 | Spare_DO_0 | Pin 25 | C3S3:25/C3S03-X2:25 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P25 | 3 | 25 | 26 | 1756-OB32 | Spare_DO_0 | Pin 26 | C3S3:26/C3S03-X2:26 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P26 | 3 | 26 | 27 | 1756-OB32 | Spare_DO_0 | Pin 27 | C3S3:27/C3S03-X2:27 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P27 | 3 | 27 | 28 | 1756-OB32 | Spare_DO_0 | Pin 28 | C3S3:28/C3S03-X2:28 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P28 | 3 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C3S3:29/C3S03-X2:29 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P29 | 3 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C3S3:30/C3S03-X2:30 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P30 | 3 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C3S3:31/C3S03-X2:31 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P31 | 3 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C3S3:32/C3S03-X2:32 | DO | 24VDC | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
Slot 04 — Module: 1756-IF16 (AI) ¦ Total: 16 Channels (Active: 7, Spare: 9)
C3-S04-P00 | 4 | 0 | 1 | 1756-IF16 | PT-60230_AI_1 | Pin 1 | C3S4:1/C3S04-X1:1 | AI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S04-X1 | - | PT-60230 | Pressure Transmitter | 3-25-01-602-PD-04
C3-S04-P01 | 4 | 1 | 2 | 1756-IF16 | PT-60231_AI_1 | Pin 2 | C3S4:2/C3S04-X1:2 | AI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S04-X1 | - | PT-60231 | Pressure Transmitter | 3-25-01-602-PD-04
C3-S04-P02 | 4 | 2 | 3 | 1756-IF16 | TT-60224_AI_1 | Pin 3 | C3S4:3/C3S04-X1:3 | AI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S04-X1 | - | TT-60224 |  | 3-25-01-602-PD-04
C3-S04-P03 | 4 | 3 | 4 | 1756-IF16 | TT-60225_AI_1 | Pin 4 | C3S4:4/C3S04-X1:4 | AI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S04-X1 | - | TT-60225 |  | 3-25-01-602-PD-04
C3-S04-P04 | 4 | 4 | 5 | 1756-IF16 | TT-60226_AI_1 | Pin 5 | C3S4:5/C3S04-X1:5 | AI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 2nd / Spray Dryer | C3S04-X1 | - | TT-60226 |  | 3-25-01-602-PD-04
C3-S04-P05 | 4 | 5 | 6 | 1756-IF16 | TT-60227_AI_1 | Pin 6 | C3S4:6/C3S04-X1:6 | AI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S04-X1 | - | TT-60227 |  | 3-25-01-602-PD-04
C3-S04-P06 | 4 | 6 | 7 | 1756-IF16 | TT-60230_AI_1 | Pin 7 | C3S4:7/C3S04-X1:7 | AI | 24VDC | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S04-X1 | - | TT-60230 |  | 3-25-01-602-PD-04
C3-S04-P07 | 4 | 7 | 8 | 1756-IF16 | Spare_AI_0 | Pin 8 | C3S4:8/C3S04-X1:8 | AI | 24VDC | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P08 | 4 | 8 | 9 | 1756-IF16 | Spare_AI_0 | Pin 9 | C3S4:9/C3S04-X1:9 | AI | 24VDC | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P09 | 4 | 9 | 10 | 1756-IF16 | Spare_AI_0 | Pin 10 | C3S4:10/C3S04-X1:10 | AI | 24VDC | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P10 | 4 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C3S4:11/C3S04-X1:11 | AI | 24VDC | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P11 | 4 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C3S4:12/C3S04-X1:12 | AI | 24VDC | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P12 | 4 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C3S4:13/C3S04-X1:13 | AI | 24VDC | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P13 | 4 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C3S4:14/C3S04-X1:14 | AI | 24VDC | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P14 | 4 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C3S4:15/C3S04-X1:15 | AI | 24VDC | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P15 | 4 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C3S4:16/C3S04-X1:16 | AI | 24VDC | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
Slot 05 — Module: 1756-IF16 (AI) ¦ Total: 16 Channels (Active: 13, Spare: 3)
C3-S05-P00 | 5 | 0 | 1 | 1756-IF16 | PT-61303_AI_1 | Pin 1 | C3S5:1/C3S05-X1:1 | AI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | PT-61303 | Pressure Transmitter | 3-25-01-613-PD-01
C3-S05-P01 | 5 | 1 | 2 | 1756-IF16 | PT-61306_AI_1 | Pin 2 | C3S5:2/C3S05-X1:2 | AI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | PT-61306 |  | 3-25-01-613-PD-01
C3-S05-P02 | 5 | 2 | 3 | 1756-IF16 | TT-61303_AI_1 | Pin 3 | C3S5:3/C3S05-X1:3 | AI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | TT-61303 |  | 3-25-01-613-PD-01
C3-S05-P03 | 5 | 3 | 4 | 1756-IF16 | TT-61304_AI_1 | Pin 4 | C3S5:4/C3S05-X1:4 | AI | 24VDC | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | TT-61304 |  | 3-25-01-613-PD-01
C3-S05-P04 | 5 | 4 | 5 | 1756-IF16 | DPT-61301_AI_1 | Pin 5 | C3S5:5/C3S05-X1:5 | AI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | DPT-61301 | Differential Pressure Transmitte | 3-25-01-613-PD-01
C3-S05-P05 | 5 | 5 | 6 | 1756-IF16 | DPT-61302_AI_1 | Pin 6 | C3S5:6/C3S05-X1:6 | AI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | DPT-61302 | Differential Pressure Transmitte | 3-25-01-613-PD-01
C3-S05-P06 | 5 | 6 | 7 | 1756-IF16 | LT-61301_AI_1 | Pin 7 | C3S5:7/C3S05-X1:7 | AI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | LT-61301 | Level Transmitter | 3-25-01-613-PD-01
C3-S05-P07 | 5 | 7 | 8 | 1756-IF16 | PT-61301_AI_1 | Pin 8 | C3S5:8/C3S05-X1:8 | AI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | PT-61301 | Pressure Transmitter | 3-25-01-613-PD-01
C3-S05-P08 | 5 | 8 | 9 | 1756-IF16 | PT-61303_AI_1 | Pin 9 | C3S5:9/C3S05-X1:9 | AI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | PT-61303 | Pressure Transmitter | 3-25-01-613-PD-01
C3-S05-P09 | 5 | 9 | 10 | 1756-IF16 | PT-61304_AI_1 | Pin 10 | C3S5:10/C3S05-X1:10 | AI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | PT-61304 | Pressure Transmitter | 3-25-01-613-PD-01
C3-S05-P10 | 5 | 10 | 11 | 1756-IF16 | PT-61305_AI_1 | Pin 11 | C3S5:11/C3S05-X1:11 | AI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | PT-61305 | Pressure Transmitter | 3-25-01-613-PD-01
C3-S05-P11 | 5 | 11 | 12 | 1756-IF16 | TT-61301_AI_1 | Pin 12 | C3S5:12/C3S05-X1:12 | AI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | TT-61301 |  | 3-25-01-613-PD-01
C3-S05-P12 | 5 | 12 | 13 | 1756-IF16 | TT-61302_AI_1 | Pin 13 | C3S5:13/C3S05-X1:13 | AI | 24VDC | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | TT-61302 |  | 3-25-01-613-PD-01
C3-S05-P13 | 5 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C3S5:14/C3S05-X1:14 | AI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | - | C3S05-X1 | - | Spare | Spare Channel | -
C3-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C3S5:15/C3S05-X1:15 | AI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | - | C3S05-X1 | - | Spare | Spare Channel | -
C3-S05-P15 | 5 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C3S5:16/C3S05-X1:16 | AI | 24VDC | SPARE | IS-JB-618 | Packing Tower 8th Floor | - | C3S05-X1 | - | Spare | Spare Channel | -
Slot 13 — Module: 1756-OF8 (AO) ¦ Total: 8 Channels (Active: 5, Spare: 3)
C3-S13-P00 | 13 | 0 | 1 | 1756-OF8 | TCV-40222_AO_1 | Pin 1 | C3S13:1/C3S13-X1:1 | AO | 24VDC | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C3S13-X1 | - | TCV-40222 |  | 325-01-402-PD-02
C3-S13-P01 | 13 | 1 | 2 | 1756-OF8 | TV-60202_AO_1 | Pin 2 | C3S13:2/C3S13-X1:2 | AO | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S13-X1 | - | TV-60202 |  | 3-25-01-602-PD-07
C3-S13-P02 | 13 | 2 | 3 | 1756-OF8 | TV-60214_AO_1 | Pin 3 | C3S13:3/C3S13-X1:3 | AO | 24VDC | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C3S13-X1 | - | TV-60214 |  | 3-25-01-602-PD-03
C3-S13-P03 | 13 | 3 | 4 | 1756-OF8 | PV-60201_AO_1 | Pin 4 | C3S13:4/C3S13-X1:4 | AO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C3S13-X1 | - | PV-60201 |  | 3-25-01-602-PD-02
C3-S13-P04 | 13 | 4 | 5 | 1756-OF8 | UY-FH-60210B_AO_1 | Pin 5 | C3S13:5/C3S13-X1:5 | AO | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C3S13-X1 | - | UY-FH-60210B |  | -
C3-S13-P05 | 13 | 5 | 6 | 1756-OF8 | Spare_AO_0 | Pin 6 | C3S13:6/C3S13-X1:6 | AO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C3S13-X1 | - | Spare | Spare Channel | -
C3-S13-P06 | 13 | 6 | 7 | 1756-OF8 | Spare_AO_0 | Pin 7 | C3S13:7/C3S13-X1:7 | AO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C3S13-X1 | - | Spare | Spare Channel | -
C3-S13-P07 | 13 | 7 | 8 | 1756-OF8 | Spare_AO_0 | Pin 8 | C3S13:8/C3S13-X1:8 | AO | 24VDC | SPARE | JB-607 | Spray Dryer 7th Floor | - | C3S13-X1 | - | Spare | Spare Channel | -

## Chassis_C4
KALASIN ENGINEERING — C4 (I/O EXPANSION RACK 3 (CHASSIS 4))
Location: Control Cabinet CA1 (Bay 4) ¦ Role: Spray Dryer Tower & Exhaust Auxiliary I/O ¦ Net: EN4TR DLR Ring Node 4 (192.168.1.13) ¦ Total Points: 161 (Active: 75, Spare: 86)
SOURCE (PLC RACK / SLOT / TERMINAL / ePLAN TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Type | Status | Destination | Field Location | Floor/Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing
Slot 01 — Module: 1756-IB32 (DI) ¦ Total: 32 Channels (Active: 11, Spare: 21)
C4-S01-P00 | 1 | 0 | 1 | 1756-IB32 | FT-60203_DI_1 | Pin 1 | C4S1:1/C4S01-X1:1 | DI | 24VDC | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S01-X1 | - | FT-60203 |  | 3-25-01-602-PD-09
C4-S01-P01 | 1 | 1 | 2 | 1756-IB32 | LSH-60250_DI_1 | Pin 2 | C4S1:2/C4S01-X1:2 | DI | 24VDC | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S01-X1 | - | LSH-60250 |  | 3-25-01-602-PD-05
C4-S01-P02 | 1 | 2 | 3 | 1756-IB32 | XA-60261_DI_1 | Pin 3 | C4S1:3/C4S01-X1:3 | DI | 24VDC | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S01-X1 | - | XA-60261 |  | -
C4-S01-P03 | 1 | 3 | 4 | 1756-IB32 | XA-60262_DI_1 | Pin 4 | C4S1:4/C4S01-X1:4 | DI | 24VDC | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S01-X1 | - | XA-60262 |  | -
C4-S01-P04 | 1 | 4 | 5 | 1756-IB32 | Spare_DI_0 | Pin 5 | C4S1:5/C4S01-X1:5 | DI | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P05 | 1 | 5 | 6 | 1756-IB32 | Spare_DI_0 | Pin 6 | C4S1:6/C4S01-X1:6 | DI | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P06 | 1 | 6 | 7 | 1756-IB32 | Spare_DI_0 | Pin 7 | C4S1:7/C4S01-X1:7 | DI | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P07 | 1 | 7 | 8 | 1756-IB32 | Spare_DI_0 | Pin 8 | C4S1:8/C4S01-X1:8 | DI | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P08 | 1 | 8 | 9 | 1756-IB32 | Spare_DI_0 | Pin 9 | C4S1:9/C4S01-X1:9 | DI | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P09 | 1 | 9 | 10 | 1756-IB32 | Spare_DI_0 | Pin 10 | C4S1:10/C4S01-X1:10 | DI | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P10 | 1 | 10 | 11 | 1756-IB32 | Spare_DI_0 | Pin 11 | C4S1:11/C4S01-X1:11 | DI | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P11 | 1 | 11 | 12 | 1756-IB32 | Spare_DI_0 | Pin 12 | C4S1:12/C4S01-X1:12 | DI | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P12 | 1 | 12 | 13 | 1756-IB32 | Spare_DI_0 | Pin 13 | C4S1:13/C4S01-X1:13 | DI | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P13 | 1 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C4S1:14/C4S01-X1:14 | DI | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P14 | 1 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C4S1:15/C4S01-X1:15 | DI | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P15 | 1 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C4S1:16/C4S01-X1:16 | DI | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P16 | 1 | 16 | 17 | 1756-IB32 | ZS-60201A_DI_1 | Pin 17 | C4S1:17/C4S01-X2:17 | DI | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S01-X2 | - | ZS-60201A |  | 3-25-01-602-PD-04
C4-S01-P17 | 1 | 17 | 18 | 1756-IB32 | ZS-60201B_DI_1 | Pin 18 | C4S1:18/C4S01-X2:18 | DI | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S01-X2 | - | ZS-60201B |  | 3-25-01-602-PD-04
C4-S01-P18 | 1 | 18 | 19 | 1756-IB32 | ZS-60231C_DI_1 | Pin 19 | C4S1:19/C4S01-X2:19 | DI | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231C |  | 3-25-01-602-PD-04
C4-S01-P19 | 1 | 19 | 20 | 1756-IB32 | ZS-60231D_DI_1 | Pin 20 | C4S1:20/C4S01-X2:20 | DI | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231D |  | 3-25-01-602-PD-04
C4-S01-P20 | 1 | 20 | 21 | 1756-IB32 | ZS-60231E_DI_1 | Pin 21 | C4S1:21/C4S01-X2:21 | DI | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231E |  | 3-25-01-602-PD-05
C4-S01-P21 | 1 | 21 | 22 | 1756-IB32 | ZS-60231F_DI_1 | Pin 22 | C4S1:22/C4S01-X2:22 | DI | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231F |  | 3-25-01-602-PD-05
C4-S01-P22 | 1 | 22 | 23 | 1756-IB32 | ZS-60240_DI_1 | Pin 23 | C4S1:23/C4S01-X2:23 | DI | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S01-X2 | - | ZS-60240 |  | 3-25-01-602-PD-05
C4-S01-P23 | 1 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C4S1:24/C4S01-X2:24 | DI | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P24 | 1 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C4S1:25/C4S01-X2:25 | DI | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P25 | 1 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C4S1:26/C4S01-X2:26 | DI | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P26 | 1 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C4S1:27/C4S01-X2:27 | DI | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P27 | 1 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C4S1:28/C4S01-X2:28 | DI | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P28 | 1 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C4S1:29/C4S01-X2:29 | DI | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P29 | 1 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C4S1:30/C4S01-X2:30 | DI | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P30 | 1 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C4S1:31/C4S01-X2:31 | DI | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P31 | 1 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C4S1:32/C4S01-X2:32 | DI | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
Slot 02 — Module: 1756-IB32 (DI) ¦ Total: 32 Channels (Active: 17, Spare: 15)
C4-S02-P00 | 2 | 0 | 1 | 1756-IB32 | PSL-61305_DI_1 | Pin 1 | C4S2:1/C4S02-X1:1 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | PSL-61305 |  | 3-25-01-613-PD-03
C4-S02-P01 | 2 | 1 | 2 | 1756-IB32 | PSL-61306_DI_1 | Pin 2 | C4S2:2/C4S02-X1:2 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | PSL-61306 |  | 3-25-01-613-PD-05
C4-S02-P02 | 2 | 2 | 3 | 1756-IB32 | PVM-61301_DI_1 | Pin 3 | C4S2:3/C4S02-X1:3 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | PVM-61301 |  | -
C4-S02-P03 | 2 | 3 | 4 | 1756-IB32 | PVM-61301_DI_2 | Pin 4 | C4S2:4/C4S02-X1:4 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | PVM-61301 |  | -
C4-S02-P04 | 2 | 4 | 5 | 1756-IB32 | XA-61301A_DI_1 | Pin 5 | C4S2:5/C4S02-X1:5 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301A |  | -
C4-S02-P05 | 2 | 5 | 6 | 1756-IB32 | XA-61301B_DI_1 | Pin 6 | C4S2:6/C4S02-X1:6 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301B |  | -
C4-S02-P06 | 2 | 6 | 7 | 1756-IB32 | XA-61301C_DI_1 | Pin 7 | C4S2:7/C4S02-X1:7 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301C |  | -
C4-S02-P07 | 2 | 7 | 8 | 1756-IB32 | XA-61301D_DI_1 | Pin 8 | C4S2:8/C4S02-X1:8 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301D |  | -
C4-S02-P08 | 2 | 8 | 9 | 1756-IB32 | XA-61301E_DI_1 | Pin 9 | C4S2:9/C4S02-X1:9 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301E |  | -
C4-S02-P09 | 2 | 9 | 10 | 1756-IB32 | XA-61301F_DI_1 | Pin 10 | C4S2:10/C4S02-X1:10 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301F |  | -
C4-S02-P10 | 2 | 10 | 11 | 1756-IB32 | XA-61301G_DI_1 | Pin 11 | C4S2:11/C4S02-X1:11 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301G |  | -
C4-S02-P11 | 2 | 11 | 12 | 1756-IB32 | XA-61301H_DI_1 | Pin 12 | C4S2:12/C4S02-X1:12 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301H |  | -
C4-S02-P12 | 2 | 12 | 13 | 1756-IB32 | XA-61301J_DI_1 | Pin 13 | C4S2:13/C4S02-X1:13 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301J |  | -
C4-S02-P13 | 2 | 13 | 14 | 1756-IB32 | XV-61302_DI_1 | Pin 14 | C4S2:14/C4S02-X1:14 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | XV-61302 |  | 3-25-01-613-PD-02
C4-S02-P14 | 2 | 14 | 15 | 1756-IB32 | XV-61302_DI_2 | Pin 15 | C4S2:15/C4S02-X1:15 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | XV-61302 |  | 3-25-01-613-PD-02
C4-S02-P15 | 2 | 15 | 16 | 1756-IB32 | XV-61303_DI_1 | Pin 16 | C4S2:16/C4S02-X1:16 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | XV-61303 |  | 3-25-01-613-PD-02
C4-S02-P16 | 2 | 16 | 17 | 1756-IB32 | XV-61303_DI_2 | Pin 17 | C4S2:17/C4S02-X2:17 | DI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X2 | - | XV-61303 |  | 3-25-01-613-PD-02
C4-S02-P17 | 2 | 17 | 18 | 1756-IB32 | Spare_DI_0 | Pin 18 | C4S2:18/C4S02-X2:18 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P18 | 2 | 18 | 19 | 1756-IB32 | Spare_DI_0 | Pin 19 | C4S2:19/C4S02-X2:19 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P19 | 2 | 19 | 20 | 1756-IB32 | Spare_DI_0 | Pin 20 | C4S2:20/C4S02-X2:20 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P20 | 2 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C4S2:21/C4S02-X2:21 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P21 | 2 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C4S2:22/C4S02-X2:22 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P22 | 2 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C4S2:23/C4S02-X2:23 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P23 | 2 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C4S2:24/C4S02-X2:24 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P24 | 2 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C4S2:25/C4S02-X2:25 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P25 | 2 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C4S2:26/C4S02-X2:26 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P26 | 2 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C4S2:27/C4S02-X2:27 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P27 | 2 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C4S2:28/C4S02-X2:28 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P28 | 2 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C4S2:29/C4S02-X2:29 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P29 | 2 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C4S2:30/C4S02-X2:30 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P30 | 2 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C4S2:31/C4S02-X2:31 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P31 | 2 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C4S2:32/C4S02-X2:32 | DI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
Slot 03 — Module: 1756-IB32 (DI) ¦ Total: 31 Channels (Active: 15, Spare: 16)
C4-S03-P00 | 3 | 0 | 1 | 1756-IB32 | ISV-61303_DI_1 | Pin 1 | C4S3:1/C4S03-X1:1 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | ISV-61303 |  | 3-25-01-613-PD-03
C4-S03-P01 | 3 | 1 | 2 | 1756-IB32 | ISV-61304_DI_1 | Pin 2 | C4S3:2/C4S03-X1:2 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | ISV-61304 |  | 3-25-01-613-PD-05
C4-S03-P02 | 3 | 2 | 3 | 1756-IB32 | LSH-61304_DI_1 | Pin 3 | C4S3:3/C4S03-X1:3 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S03-X1 | - | LSH-61304 |  | 3-25-01-613-PD-03
C4-S03-P03 | 3 | 3 | 4 | 1756-IB32 | LSH-61305_DI_1 | Pin 4 | C4S3:4/C4S03-X1:4 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S03-X1 | - | LSH-61305 |  | 3-25-01-613-PD-05
C4-S03-P04 | 3 | 4 | 5 | 1756-IB32 | LSH-61307_DI_1 | Pin 5 | C4S3:5/C4S03-X1:5 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S03-X1 | - | LSH-61307 |  | 3-25-01-613-PD-01
C4-S03-P05 | 3 | 5 | 6 | 1756-IB32 | LSH-61312_DI_1 | Pin 6 | C4S3:6/C4S03-X1:6 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | LSH-61312 |  | 3-25-01-613-PD-05
C4-S03-P06 | 3 | 6 | 7 | 1756-IB32 | PSE-61302_DI_1 | Pin 7 | C4S3:7/C4S03-X1:7 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | PSE-61302 |  | 3-25-01-613-PD-03
C4-S03-P07 | 3 | 7 | 8 | 1756-IB32 | PSE-61303_DI_1 | Pin 8 | C4S3:8/C4S03-X1:8 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | PSE-61303 |  | 3-25-01-613-PD-05
C4-S03-P09 | 3 | 9 | 10 | 1756-IB32 | RV-61301_DI_1 | Pin 10 | C4S3:10/C4S03-X1:10 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | RV-61301 |  | -
C4-S03-P10 | 3 | 10 | 11 | 1756-IB32 | RV-61304_DI_1 | Pin 11 | C4S3:11/C4S03-X1:11 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | RV-61304 |  | -
C4-S03-P11 | 3 | 11 | 12 | 1756-IB32 | RV-61305_DI_1 | Pin 12 | C4S3:12/C4S03-X1:12 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | RV-61305 |  | -
C4-S03-P12 | 3 | 12 | 13 | 1756-IB32 | SC-61301_DI_1 | Pin 13 | C4S3:13/C4S03-X1:13 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | SC-61301 |  | -
C4-S03-P13 | 3 | 13 | 14 | 1756-IB32 | SC-61302_DI_1 | Pin 14 | C4S3:14/C4S03-X1:14 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | SC-61302 |  | -
C4-S03-P14 | 3 | 14 | 15 | 1756-IB32 | ZS-61312_DI_1 | Pin 15 | C4S3:15/C4S03-X1:15 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 3rd / Packing Tower | C4S03-X1 | - | ZS-61312 |  | 3-25-01-613-PD-01
C4-S03-P15 | 3 | 15 | 16 | 1756-IB32 | ZS-61313_DI_1 | Pin 16 | C4S3:16/C4S03-X1:16 | DI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 3rd / Packing Tower | C4S03-X1 | - | ZS-61313 |  | 3-25-01-613-PD-01
C4-S03-P16 | 3 | 16 | 17 | 1756-IB32 | Spare_DI_0 | Pin 17 | C4S3:17/C4S03-X2:17 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P17 | 3 | 17 | 18 | 1756-IB32 | Spare_DI_0 | Pin 18 | C4S3:18/C4S03-X2:18 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P18 | 3 | 18 | 19 | 1756-IB32 | Spare_DI_0 | Pin 19 | C4S3:19/C4S03-X2:19 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P19 | 3 | 19 | 20 | 1756-IB32 | Spare_DI_0 | Pin 20 | C4S3:20/C4S03-X2:20 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P20 | 3 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C4S3:21/C4S03-X2:21 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P21 | 3 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C4S3:22/C4S03-X2:22 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P22 | 3 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C4S3:23/C4S03-X2:23 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P23 | 3 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C4S3:24/C4S03-X2:24 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P24 | 3 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C4S3:25/C4S03-X2:25 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P25 | 3 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C4S3:26/C4S03-X2:26 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P26 | 3 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C4S3:27/C4S03-X2:27 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P27 | 3 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C4S3:28/C4S03-X2:28 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P28 | 3 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C4S3:29/C4S03-X2:29 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P29 | 3 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C4S3:30/C4S03-X2:30 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P30 | 3 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C4S3:31/C4S03-X2:31 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P31 | 3 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C4S3:32/C4S03-X2:32 | DI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
Slot 04 — Module: 1756-OB32 (DO) ¦ Total: 32 Channels (Active: 17, Spare: 15)
C4-S04-P00 | 4 | 0 | 1 | 1756-OB32 | SV-60220_DO_1 | Pin 1 | C4S4:1/C4S04-X1:1 | DO | 24VDC | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S04-X1 | - | SV-60220 |  | 3-25-01-602-PD-04
C4-S04-P01 | 4 | 1 | 2 | 1756-OB32 | Spare_DO_0 | Pin 2 | C4S4:2/C4S04-X1:2 | DO | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P02 | 4 | 2 | 3 | 1756-OB32 | Spare_DO_0 | Pin 3 | C4S4:3/C4S04-X1:3 | DO | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P03 | 4 | 3 | 4 | 1756-OB32 | Spare_DO_0 | Pin 4 | C4S4:4/C4S04-X1:4 | DO | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P04 | 4 | 4 | 5 | 1756-OB32 | Spare_DO_0 | Pin 5 | C4S4:5/C4S04-X1:5 | DO | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P05 | 4 | 5 | 6 | 1756-OB32 | Spare_DO_0 | Pin 6 | C4S4:6/C4S04-X1:6 | DO | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P06 | 4 | 6 | 7 | 1756-OB32 | Spare_DO_0 | Pin 7 | C4S4:7/C4S04-X1:7 | DO | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P07 | 4 | 7 | 8 | 1756-OB32 | Spare_DO_0 | Pin 8 | C4S4:8/C4S04-X1:8 | DO | 24VDC | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P08 | 4 | 8 | 9 | 1756-OB32 | XA-60201_DO_1 | Pin 9 | C4S4:9/C4S04-X1:9 | DO | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S04-X1 | - | XA-60201 |  | 3-25-01-602-PD-03
C4-S04-P09 | 4 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C4S4:10/C4S04-X1:10 | DO | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P10 | 4 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C4S4:11/C4S04-X1:11 | DO | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P11 | 4 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C4S4:12/C4S04-X1:12 | DO | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P12 | 4 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C4S4:13/C4S04-X1:13 | DO | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P13 | 4 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C4S4:14/C4S04-X1:14 | DO | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P14 | 4 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C4S4:15/C4S04-X1:15 | DO | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P15 | 4 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C4S4:16/C4S04-X1:16 | DO | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P16 | 4 | 16 | 17 | 1756-OB32 | PVM-61301_DO_1 | Pin 17 | C4S4:17/C4S04-X2:17 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | PVM-61301 |  | -
C4-S04-P17 | 4 | 17 | 18 | 1756-OB32 | PVM-61301_DO_2 | Pin 18 | C4S4:18/C4S04-X2:18 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | PVM-61301 |  | -
C4-S04-P18 | 4 | 18 | 19 | 1756-OB32 | SV-61307_DO_1 | Pin 19 | C4S4:19/C4S04-X2:19 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 3rd / Packing Tower | C4S04-X2 | - | SV-61307 |  | 3-25-01-613-PD-01
C4-S04-P19 | 4 | 19 | 20 | 1756-OB32 | SV-61308_DO_1 | Pin 20 | C4S4:20/C4S04-X2:20 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | SV-61308 |  | -
C4-S04-P20 | 4 | 20 | 21 | 1756-OB32 | SV-61309_DO_1 | Pin 21 | C4S4:21/C4S04-X2:21 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | SV-61309 |  | 3-25-01-613-PD-03
C4-S04-P21 | 4 | 21 | 22 | 1756-OB32 | SV-61310_DO_1 | Pin 22 | C4S4:22/C4S04-X2:22 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | SV-61310 |  | -
C4-S04-P22 | 4 | 22 | 23 | 1756-OB32 | SV-61311_DO_1 | Pin 23 | C4S4:23/C4S04-X2:23 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | SV-61311 |  | 3-25-01-613-PD-05
C4-S04-P23 | 4 | 23 | 24 | 1756-OB32 | XS-61301A_DO_1 | Pin 24 | C4S4:24/C4S04-X2:24 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301A |  | -
C4-S04-P24 | 4 | 24 | 25 | 1756-OB32 | XS-61301B_DO_1 | Pin 25 | C4S4:25/C4S04-X2:25 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301B |  | -
C4-S04-P25 | 4 | 25 | 26 | 1756-OB32 | XS-61301C_DO_1 | Pin 26 | C4S4:26/C4S04-X2:26 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301C |  | -
C4-S04-P26 | 4 | 26 | 27 | 1756-OB32 | XS-61301D_DO_1 | Pin 27 | C4S4:27/C4S04-X2:27 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301D |  | -
C4-S04-P27 | 4 | 27 | 28 | 1756-OB32 | XS-61301E_DO_1 | Pin 28 | C4S4:28/C4S04-X2:28 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301E |  | -
C4-S04-P28 | 4 | 28 | 29 | 1756-OB32 | XS-61301F_DO_1 | Pin 29 | C4S4:29/C4S04-X2:29 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301F |  | -
C4-S04-P29 | 4 | 29 | 30 | 1756-OB32 | XV-61302_DO_1 | Pin 30 | C4S4:30/C4S04-X2:30 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | XV-61302 |  | 3-25-01-613-PD-02
C4-S04-P30 | 4 | 30 | 31 | 1756-OB32 | XV-61303_DO_1 | Pin 31 | C4S4:31/C4S04-X2:31 | DO | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | XV-61303 |  | 3-25-01-613-PD-02
C4-S04-P31 | 4 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C4S4:32/C4S04-X2:32 | DO | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | Packing Tower | C4S04-X2 | - | Spare | Spare Channel | -
Slot 05 — Module: 1756-IF16 (AI) ¦ Total: 26 Channels (Active: 7, Spare: 19)
C4-S05-P00 | 5 | 0 | 1 | 1756-IF16 | DPT-60201_AI_1 | Pin 1 | C4S5:1/C4S05-X1:1 | AI | 24VDC | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S05-X1 | - | DPT-60201 | Differential Pressure Transmitte | 3-25-01-602-PD-09
C4-S05-P01 | 5 | 1 | 2 | 1756-IF16 | FT-60203_AI_1 | Pin 2 | C4S5:2/C4S05-X1:2 | AI | 24VDC | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S05-X1 | - | FT-60203 |  | 3-25-01-602-PD-09
C4-S05-P02 | 5 | 2 | 3 | 1756-IF16 | TT-60245_AI_1 | Pin 3 | C4S5:3/C4S05-X1:3 | AI | 24VDC | ACTIVE | JB-608 | Spray Dryer 8th Floor | 8th / Spray Dryer | C4S05-X1 | - | TT-60245 |  | 3-25-01-602-PD-05
C4-S05-P03 | 5 | 3 | 4 | 1756-IF16 | Spare_AI_0 | Pin 4 | C4S5:4/C4S05-X1:4 | AI | 24VDC | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P04 | 5 | 4 | 5 | 1756-IF16 | Spare_AI_0 | Pin 5 | C4S5:5/C4S05-X1:5 | AI | 24VDC | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P05 | 5 | 5 | 6 | 1756-IF16 | Spare_AI_0 | Pin 6 | C4S5:6/C4S05-X1:6 | AI | 24VDC | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P06 | 5 | 6 | 7 | 1756-IF16 | Spare_AI_0 | Pin 7 | C4S5:7/C4S05-X1:7 | AI | 24VDC | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P06 | 5 | 6 | 7 | 1756-IF16 | Spare_AI_0 | Pin 7 | C4S5:7/C4S05-X1:7 | AI | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P07 | 5 | 7 | 8 | 1756-IF16 | Spare_AI_0 | Pin 8 | C4S5:8/C4S05-X1:8 | AI | 24VDC | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P07 | 5 | 7 | 8 | 1756-IF16 | Spare_AI_0 | Pin 8 | C4S5:8/C4S05-X1:8 | AI | 24VDC | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P08 | 5 | 8 | 9 | 1756-IF16 | PT-61302_AI_1 | Pin 9 | C4S5:9/C4S05-X1:9 | AI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S05-X1 | - | PT-61302 | Pressure Transmitter | 3-25-01-613-PD-03
C4-S05-P09 | 5 | 9 | 10 | 1756-IF16 | PT-61309_AI_1 | Pin 10 | C4S5:10/C4S05-X1:10 | AI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S05-X1 | - | PT-61309 | Pressure Transmitter | 3-25-01-613-PD-04
C4-S05-P10 | 5 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C4S5:11/C4S05-X1:11 | AI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P11 | 5 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C4S5:12/C4S05-X1:12 | AI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P12 | 5 | 12 | 13 | 1756-IF16 | PT-61302_AI_1 | Pin 13 | C4S5:13/C4S05-X1:13 | AI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S05-X1 | - | PT-61302 | Pressure Transmitter | 3-25-01-613-PD-03
C4-S05-P13 | 5 | 13 | 14 | 1756-IF16 | PT-61309_AI_1 | Pin 14 | C4S5:14/C4S05-X1:14 | AI | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S05-X1 | - | PT-61309 | Pressure Transmitter | 3-25-01-613-PD-04
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 24VDC | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P15 | 5 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C4S5:16/C4S05-X1:16 | AI | 24VDC | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
Slot 06 — Module: 1756-IF16 (AI) ¦ Total: 8 Channels (Active: 8, Spare: 0)
C4-S06-P00 | 6 | 0 | 1 | 1756-IF16 | PT-60220_AI_1 | Pin 1 | C4S6:1/C4S06-X1:1 | AI | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S06-X1 | - | PT-60220 | Pressure Transmitter | 3-25-01-602-PD-04
C4-S06-P01 | 6 | 1 | 2 | 1756-IF16 | TT-60220_AI_1 | Pin 2 | C4S6:2/C4S06-X1:2 | AI | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S06-X1 | - | TT-60220 |  | 3-25-01-602-PD-04
C4-S06-P02 | 6 | 2 | 3 | 1756-IF16 | TT-60221_AI_1 | Pin 3 | C4S6:3/C4S06-X1:3 | AI | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S06-X1 | - | TT-60221 |  | 3-25-01-602-PD-04
C4-S06-P03 | 6 | 3 | 4 | 1756-IF16 | TT-60222_AI_1 | Pin 4 | C4S6:4/C4S06-X1:4 | AI | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S06-X1 | - | TT-60222 |  | 3-25-01-602-PD-04
C4-S06-P04 | 6 | 4 | 5 | 1756-IF16 | TT-60223_AI_1 | Pin 5 | C4S6:5/C4S06-X1:5 | AI | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S06-X1 | - | TT-60223 |  | 3-25-01-602-PD-04
C4-S06-P05 | 6 | 5 | 6 | 1756-IF16 | XT-60201_AI_1 | Pin 6 | C4S6:6/C4S06-X1:6 | AI | 24VDC | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S06-X1 | - | XT-60201 |  | 3-25-01-602-PD-03
C4-S06-P06 | 6 | 6 | 7 | 1756-IF16 | DPT-61310_AI_1 | Pin 7 | C4S6:7/C4S06-X1:7 | AI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S06-X1 | - | DPT-61310 | Differential Pressure Transmitte | 3-25-01-613-PD-03
C4-S06-P07 | 6 | 7 | 8 | 1756-IF16 | DPT-61312_AI_1 | Pin 8 | C4S6:8/C4S06-X1:8 | AI | 24VDC | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S06-X1 | - | DPT-61312 |  | 3-25-01-613-PD-05

## Chassis_C5
KALASIN ENGINEERING — C5 (REMOTE I/O SKID RIO-200 (CHASSIS 5))
Location: Remote I/O Enclosure RIO-200 (Process Floor 1F) ¦ Role: Remote Field I/O via Fiber Optic Trunk (DLR Ring Node 5) ¦ Net: EN4TR Fiber DLR Ring Node 5 (192.168.1.14) ¦ Total Points: 112 (Active: 57, Spare: 55)
SOURCE (PLC RACK / SLOT / TERMINAL / ePLAN TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Type | Status | Destination | Field Location | Floor/Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing
Slot 01 — Module: 1756-IB32 (DI) ¦ Total: 32 Channels (Active: 32, Spare: 0)
C5-S01-P00 | 1 | 0 | 1 | 1756-IB32 | FS-20201_DI_1 | Pin 1 | C5S1:1/C5S01-X1:1 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | FS-20201 |  | 3-25-01-202-PD-01
C5-S01-P01 | 1 | 1 | 2 | 1756-IB32 | FT-913201_DI_1 | Pin 2 | C5S1:2/C5S01-X1:2 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X1 | - | FT-913201 |  | 3-25-01-913-PD-02
C5-S01-P02 | 1 | 2 | 3 | 1756-IB32 | FT-936201_DI_1 | Pin 3 | C5S1:3/C5S01-X1:3 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Process Water | C5S01-X1 | - | FT-936201 |  | 3-25-01-930-PD-08
C5-S01-P03 | 1 | 3 | 4 | 1756-IB32 | FT-936202_DI_1 | Pin 4 | C5S1:4/C5S01-X1:4 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Process Water | C5S01-X1 | - | FT-936202 |  | 3-25-01-930-PD-07
C5-S01-P04 | 1 | 4 | 5 | 1756-IB32 | LSL-814201_DI_1 | Pin 5 | C5S1:5/C5S01-X1:5 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / CIP Water System | C5S01-X1 | - | LSL-814201 |  | 3-25-01-814-PD-01
C5-S01-P05 | 1 | 5 | 6 | 1756-IB32 | PK-913201_DI_1 | Pin 6 | C5S1:6/C5S01-X1:6 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X1 | - | PK-913201 |  | -
C5-S01-P06 | 1 | 6 | 7 | 1756-IB32 | PK-913202_DI_1 | Pin 7 | C5S1:7/C5S01-X1:7 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X1 | - | PK-913202 |  | -
C5-S01-P07 | 1 | 7 | 8 | 1756-IB32 | HV-20204_DI_1 | Pin 8 | C5S1:8/C5S01-X1:8 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20204 | Manual Valve With Position Switch | 3-25-01-202-PD-01
C5-S01-P08 | 1 | 8 | 9 | 1756-IB32 | HV-20205_DI_1 | Pin 9 | C5S1:9/C5S01-X1:9 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20205 | Manual Valve With Position Switch | 3-25-01-202-PD-01
C5-S01-P09 | 1 | 9 | 10 | 1756-IB32 | HV-20206_DI_1 | Pin 10 | C5S1:10/C5S01-X1:10 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20206 | Manual Valve With Position Switch | 3-25-01-202-PD-01
C5-S01-P10 | 1 | 10 | 11 | 1756-IB32 | HV-20207_DI_1 | Pin 11 | C5S1:11/C5S01-X1:11 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20207 | Manual Valve With Position Switch | 3-25-01-202-PD-01
C5-S01-P11 | 1 | 11 | 12 | 1756-IB32 | HV-20208_DI_1 | Pin 12 | C5S1:12/C5S01-X1:12 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20208 | Manual Valve With Position Switch | 3-25-01-202-PD-02
C5-S01-P12 | 1 | 12 | 13 | 1756-IB32 | HV-20209_DI_1 | Pin 13 | C5S1:13/C5S01-X1:13 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20209 | Manual Valve With Position Switch | 3-25-01-202-PD-02
C5-S01-P13 | 1 | 13 | 14 | 1756-IB32 | HV-20210_DI_1 | Pin 14 | C5S1:14/C5S01-X1:14 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X1 | - | HV-20210 | Manual Valve With Position Switch | 3-25-01-202-PD-02
C5-S01-P14 | 1 | 14 | 15 | 1756-IB32 | XA-80305A_DI_1 | Pin 15 | C5S1:15/C5S01-X1:15 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X1 | - | XA-80305A |  | -
C5-S01-P15 | 1 | 15 | 16 | 1756-IB32 | XA-80305B_DI_1 | Pin 16 | C5S1:16/C5S01-X1:16 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X1 | - | XA-80305B |  | -
C5-S01-P16 | 1 | 16 | 17 | 1756-IB32 | XA-80305C_DI_1 | Pin 17 | C5S1:17/C5S01-X2:17 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80305C |  | -
C5-S01-P17 | 1 | 17 | 18 | 1756-IB32 | XA-80305D_DI_1 | Pin 18 | C5S1:18/C5S01-X2:18 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80305D |  | -
C5-S01-P18 | 1 | 18 | 19 | 1756-IB32 | XA-80305E_DI_1 | Pin 19 | C5S1:19/C5S01-X2:19 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80305E |  | -
C5-S01-P19 | 1 | 19 | 20 | 1756-IB32 | XA-80305F_DI_1 | Pin 20 | C5S1:20/C5S01-X2:20 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80305F |  | -
C5-S01-P20 | 1 | 20 | 21 | 1756-IB32 | XA-80306A_DI_1 | Pin 21 | C5S1:21/C5S01-X2:21 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80306A |  | -
C5-S01-P21 | 1 | 21 | 22 | 1756-IB32 | XA-80306B_DI_1 | Pin 22 | C5S1:22/C5S01-X2:22 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80306B |  | -
C5-S01-P22 | 1 | 22 | 23 | 1756-IB32 | XA-80306C_DI_1 | Pin 23 | C5S1:23/C5S01-X2:23 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80306C |  | -
C5-S01-P23 | 1 | 23 | 24 | 1756-IB32 | XA-80306D_DI_1 | Pin 24 | C5S1:24/C5S01-X2:24 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80306D |  | -
C5-S01-P24 | 1 | 24 | 25 | 1756-IB32 | XA-80306E_DI_1 | Pin 25 | C5S1:25/C5S01-X2:25 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80306E |  | -
C5-S01-P25 | 1 | 25 | 26 | 1756-IB32 | XA-80306F_DI_1 | Pin 26 | C5S1:26/C5S01-X2:26 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S01-X2 | - | XA-80306F |  | -
C5-S01-P26 | 1 | 26 | 27 | 1756-IB32 | XV-20201_DI_1 | Pin 27 | C5S1:27/C5S01-X2:27 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X2 | - | XV-20201 |  | 3-25-01-202-PD-01
C5-S01-P27 | 1 | 27 | 28 | 1756-IB32 | XV-20201_DI_2 | Pin 28 | C5S1:28/C5S01-X2:28 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X2 | - | XV-20201 |  | 3-25-01-202-PD-01
C5-S01-P28 | 1 | 28 | 29 | 1756-IB32 | XV-20202_DI_1 | Pin 29 | C5S1:29/C5S01-X2:29 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X2 | - | XV-20202 |  | 3-25-01-202-PD-01
C5-S01-P29 | 1 | 29 | 30 | 1756-IB32 | XV-20202_DI_2 | Pin 30 | C5S1:30/C5S01-X2:30 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X2 | - | XV-20202 |  | 3-25-01-202-PD-01
C5-S01-P30 | 1 | 30 | 31 | 1756-IB32 | XV-20203_DI_1 | Pin 31 | C5S1:31/C5S01-X2:31 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X2 | - | XV-20203 |  | 3-25-01-202-PD-01
C5-S01-P31 | 1 | 31 | 32 | 1756-IB32 | XV-20203_DI_2 | Pin 32 | C5S1:32/C5S01-X2:32 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S01-X2 | - | XV-20203 |  | 3-25-01-202-PD-01
Slot 02 — Module: 1756-IB32 (DI) ¦ Total: 32 Channels (Active: 8, Spare: 24)
C5-S02-P00 | 2 | 0 | 1 | 1756-IB32 | XV-20211_DI_1 | Pin 1 | C5S2:1/C5S02-X1:1 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S02-X1 | - | XV-20211 |  | 3-25-01-202-PD-01
C5-S02-P01 | 2 | 1 | 2 | 1756-IB32 | XV-20211_DI_2 | Pin 2 | C5S2:2/C5S02-X1:2 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S02-X1 | - | XV-20211 |  | 3-25-01-202-PD-01
C5-S02-P02 | 2 | 2 | 3 | 1756-IB32 | XV-20212_DI_1 | Pin 3 | C5S2:3/C5S02-X1:3 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S02-X1 | - | XV-20212 |  | 3-25-01-202-PD-01
C5-S02-P03 | 2 | 3 | 4 | 1756-IB32 | XV-20212_DI_2 | Pin 4 | C5S2:4/C5S02-X1:4 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S02-X1 | - | XV-20212 |  | 3-25-01-202-PD-01
C5-S02-P04 | 2 | 4 | 5 | 1756-IB32 | XV-20213_DI_1 | Pin 5 | C5S2:5/C5S02-X1:5 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S02-X1 | - | XV-20213 |  | 3-25-01-202-PD-01
C5-S02-P05 | 2 | 5 | 6 | 1756-IB32 | XV-20213_DI_2 | Pin 6 | C5S2:6/C5S02-X1:6 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S02-X1 | - | XV-20213 |  | 3-25-01-202-PD-01
C5-S02-P06 | 2 | 6 | 7 | 1756-IB32 | XV-913201_DI_1 | Pin 7 | C5S2:7/C5S02-X1:7 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S02-X1 | - | XV-913201 |  | 3-25-01-913-PD-02
C5-S02-P07 | 2 | 7 | 8 | 1756-IB32 | XV-913201_DI_1 | Pin 8 | C5S2:8/C5S02-X1:8 | DI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S02-X1 | - | XV-913201 |  | 3-25-01-913-PD-02
C5-S02-P08 | 2 | 8 | 9 | 1756-IB32 | Spare_DI_0 | Pin 9 | C5S2:9/C5S02-X1:9 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | -
C5-S02-P09 | 2 | 9 | 10 | 1756-IB32 | Spare_DI_0 | Pin 10 | C5S2:10/C5S02-X1:10 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | -
C5-S02-P10 | 2 | 10 | 11 | 1756-IB32 | Spare_DI_0 | Pin 11 | C5S2:11/C5S02-X1:11 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | -
C5-S02-P11 | 2 | 11 | 12 | 1756-IB32 | Spare_DI_0 | Pin 12 | C5S2:12/C5S02-X1:12 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | -
C5-S02-P12 | 2 | 12 | 13 | 1756-IB32 | Spare_DI_0 | Pin 13 | C5S2:13/C5S02-X1:13 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | -
C5-S02-P13 | 2 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C5S2:14/C5S02-X1:14 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | -
C5-S02-P14 | 2 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C5S2:15/C5S02-X1:15 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | -
C5-S02-P15 | 2 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C5S2:16/C5S02-X1:16 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X1 | - | Spare | Spare Channel | -
C5-S02-P16 | 2 | 16 | 17 | 1756-IB32 | Spare_DI_0 | Pin 17 | C5S2:17/C5S02-X2:17 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P17 | 2 | 17 | 18 | 1756-IB32 | Spare_DI_0 | Pin 18 | C5S2:18/C5S02-X2:18 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P18 | 2 | 18 | 19 | 1756-IB32 | Spare_DI_0 | Pin 19 | C5S2:19/C5S02-X2:19 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P19 | 2 | 19 | 20 | 1756-IB32 | Spare_DI_0 | Pin 20 | C5S2:20/C5S02-X2:20 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P20 | 2 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C5S2:21/C5S02-X2:21 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P21 | 2 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C5S2:22/C5S02-X2:22 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P22 | 2 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C5S2:23/C5S02-X2:23 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P23 | 2 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C5S2:24/C5S02-X2:24 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P24 | 2 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C5S2:25/C5S02-X2:25 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P25 | 2 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C5S2:26/C5S02-X2:26 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P26 | 2 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C5S2:27/C5S02-X2:27 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P27 | 2 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C5S2:28/C5S02-X2:28 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P28 | 2 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C5S2:29/C5S02-X2:29 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P29 | 2 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C5S2:30/C5S02-X2:30 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P30 | 2 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C5S2:31/C5S02-X2:31 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
C5-S02-P31 | 2 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C5S2:32/C5S02-X2:32 | DI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S02-X2 | - | Spare | Spare Channel | -
Slot 03 — Module: 1756-OB32 (DO) ¦ Total: 32 Channels (Active: 8, Spare: 24)
C5-S03-P00 | 3 | 0 | 1 | 1756-OB32 | XA-92201_DO_1 | Pin 1 | C5S3:1/C5S03-X1:1 | DO | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Boiler System | C5S03-X1 | - | XA-92201 |  | 3-25-01-922-PD-03
C5-S03-P01 | 3 | 1 | 2 | 1756-OB32 | XV-20201_DO_1 | Pin 2 | C5S3:2/C5S03-X1:2 | DO | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S03-X1 | - | XV-20201 |  | 3-25-01-202-PD-01
C5-S03-P02 | 3 | 2 | 3 | 1756-OB32 | XV-20202_DO_1 | Pin 3 | C5S3:3/C5S03-X1:3 | DO | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S03-X1 | - | XV-20202 |  | 3-25-01-202-PD-01
C5-S03-P03 | 3 | 3 | 4 | 1756-OB32 | XV-20203_DO_1 | Pin 4 | C5S3:4/C5S03-X1:4 | DO | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S03-X1 | - | XV-20203 |  | 3-25-01-202-PD-01
C5-S03-P04 | 3 | 4 | 5 | 1756-OB32 | XV-20211_DO_1 | Pin 5 | C5S3:5/C5S03-X1:5 | DO | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S03-X1 | - | XV-20211 |  | 3-25-01-202-PD-01
C5-S03-P05 | 3 | 5 | 6 | 1756-OB32 | XV-20212_DO_1 | Pin 6 | C5S3:6/C5S03-X1:6 | DO | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S03-X1 | - | XV-20212 |  | 3-25-01-202-PD-01
C5-S03-P06 | 3 | 6 | 7 | 1756-OB32 | XV-20213_DO_1 | Pin 7 | C5S3:7/C5S03-X1:7 | DO | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Slurry - Out Building | C5S03-X1 | - | XV-20213 |  | 3-25-01-202-PD-01
C5-S03-P07 | 3 | 7 | 8 | 1756-OB32 | XV-913201_DO_1 | Pin 8 | C5S3:8/C5S03-X1:8 | DO | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S03-X1 | - | XV-913201 |  | 3-25-01-913-PD-02
C5-S03-P08 | 3 | 8 | 9 | 1756-OB32 | Spare_DO_0 | Pin 9 | C5S3:9/C5S03-X1:9 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | -
C5-S03-P09 | 3 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C5S3:10/C5S03-X1:10 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | -
C5-S03-P10 | 3 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C5S3:11/C5S03-X1:11 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | -
C5-S03-P11 | 3 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C5S3:12/C5S03-X1:12 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | -
C5-S03-P12 | 3 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C5S3:13/C5S03-X1:13 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | -
C5-S03-P13 | 3 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C5S3:14/C5S03-X1:14 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | -
C5-S03-P14 | 3 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C5S3:15/C5S03-X1:15 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | -
C5-S03-P15 | 3 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C5S3:16/C5S03-X1:16 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X1 | - | Spare | Spare Channel | -
C5-S03-P16 | 3 | 16 | 17 | 1756-OB32 | Spare_DO_0 | Pin 17 | C5S3:17/C5S03-X2:17 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P17 | 3 | 17 | 18 | 1756-OB32 | Spare_DO_0 | Pin 18 | C5S3:18/C5S03-X2:18 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P18 | 3 | 18 | 19 | 1756-OB32 | Spare_DO_0 | Pin 19 | C5S3:19/C5S03-X2:19 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P19 | 3 | 19 | 20 | 1756-OB32 | Spare_DO_0 | Pin 20 | C5S3:20/C5S03-X2:20 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P20 | 3 | 20 | 21 | 1756-OB32 | Spare_DO_0 | Pin 21 | C5S3:21/C5S03-X2:21 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P21 | 3 | 21 | 22 | 1756-OB32 | Spare_DO_0 | Pin 22 | C5S3:22/C5S03-X2:22 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P22 | 3 | 22 | 23 | 1756-OB32 | Spare_DO_0 | Pin 23 | C5S3:23/C5S03-X2:23 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P23 | 3 | 23 | 24 | 1756-OB32 | Spare_DO_0 | Pin 24 | C5S3:24/C5S03-X2:24 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P24 | 3 | 24 | 25 | 1756-OB32 | Spare_DO_0 | Pin 25 | C5S3:25/C5S03-X2:25 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P25 | 3 | 25 | 26 | 1756-OB32 | Spare_DO_0 | Pin 26 | C5S3:26/C5S03-X2:26 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P26 | 3 | 26 | 27 | 1756-OB32 | Spare_DO_0 | Pin 27 | C5S3:27/C5S03-X2:27 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P27 | 3 | 27 | 28 | 1756-OB32 | Spare_DO_0 | Pin 28 | C5S3:28/C5S03-X2:28 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P28 | 3 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C5S3:29/C5S03-X2:29 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P29 | 3 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C5S3:30/C5S03-X2:30 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P30 | 3 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C5S3:31/C5S03-X2:31 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
C5-S03-P31 | 3 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C5S3:32/C5S03-X2:32 | DO | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S03-X2 | - | Spare | Spare Channel | -
Slot 04 — Module: 1756-IF16 (AI) ¦ Total: 16 Channels (Active: 9, Spare: 7)
C5-S04-P00 | 4 | 0 | 1 | 1756-IF16 | EXT-BIILER_AI_1 | Pin 1 | C5S4:1/C5S04-X1:1 | AI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Boiler System | C5S04-X1 | - | EXT-BIILER |  | External Remote Setpoint
C5-S04-P01 | 4 | 1 | 2 | 1756-IF16 | FT-913201_AI_1 | Pin 2 | C5S4:2/C5S04-X1:2 | AI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | FT-913201 |  | 3-25-01-913-PD-02
C5-S04-P02 | 4 | 2 | 3 | 1756-IF16 | FT-913201_AI_2 | Pin 3 | C5S4:3/C5S04-X1:3 | AI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | FT-913201 |  | 3-25-01-913-PD-02
C5-S04-P03 | 4 | 3 | 4 | 1756-IF16 | FT-936201_AI_1 | Pin 4 | C5S4:4/C5S04-X1:4 | AI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Process Water | C5S04-X1 | - | FT-936201 |  | 3-25-01-930-PD-08
C5-S04-P04 | 4 | 4 | 5 | 1756-IF16 | FT-936202_AI_1 | Pin 5 | C5S4:5/C5S04-X1:5 | AI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Process Water | C5S04-X1 | - | FT-936202 |  | 3-25-01-930-PD-07
C5-S04-P05 | 4 | 5 | 6 | 1756-IF16 | LT-913201_AI_1 | Pin 6 | C5S4:6/C5S04-X1:6 | AI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | LT-913201 | Level Transmitter | 3-25-01-913-PD-01
C5-S04-P06 | 4 | 6 | 7 | 1756-IF16 | PT-913201_AI_1 | Pin 7 | C5S4:7/C5S04-X1:7 | AI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | PT-913201 | Pressure Transmitter | 3-25-01-913-PD-02
C5-S04-P07 | 4 | 7 | 8 | 1756-IF16 | XT-92201_AI_1 | Pin 8 | C5S4:8/C5S04-X1:8 | AI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / Boiler System | C5S04-X1 | - | XT-92201 |  | 3-25-01-922-PD-03
C5-S04-P08 | 4 | 8 | 9 | 1756-IF16 | XV-913201_AI_1 | Pin 9 | C5S4:9/C5S04-X1:9 | AI | 24VDC | ACTIVE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | XV-913201 |  | 3-25-01-913-PD-02
C5-S04-P09 | 4 | 9 | 10 | 1756-IF16 | Spare_AI_0 | Pin 10 | C5S4:10/C5S04-X1:10 | AI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | Spare | Spare Channel | 3-25-01-913-PD-02
C5-S04-P10 | 4 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C5S4:11/C5S04-X1:11 | AI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | Spare | Spare Channel | 3-25-01-913-PD-02
C5-S04-P11 | 4 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C5S4:12/C5S04-X1:12 | AI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | Spare | Spare Channel | 3-25-01-913-PD-02
C5-S04-P12 | 4 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C5S4:13/C5S04-X1:13 | AI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | Spare | Spare Channel | 3-25-01-913-PD-02
C5-S04-P13 | 4 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C5S4:14/C5S04-X1:14 | AI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | 1st / LPG System | C5S04-X1 | - | Spare | Spare Channel | 3-25-01-913-PD-02
C5-S04-P14 | 4 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C5S4:15/C5S04-X1:15 | AI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S04-X1 | - | Spare | Spare Channel | -
C5-S04-P15 | 4 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C5S4:16/C5S04-X1:16 | AI | 24VDC | SPARE | RIO-200 | Slurry - Out Building 2nd Floor | - | C5S04-X1 | - | Spare | Spare Channel | -

## Chassis_C6
KALASIN ENGINEERING — C6 (MCC AUXILIARY I/O (CHASSIS 6))
Location: Motor Control Center Room (MCC Panel) ¦ Role: Direct Hardwired Motor Starter Feedback & Permissives ¦ Net: MCC Hardwired Trunk Line ¦ Total Points: 18 (Active: 18, Spare: 0)
SOURCE (PLC RACK / SLOT / TERMINAL / ePLAN TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Type | Status | Destination | Field Location | Floor/Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing
Slot 05 — Module: (DO) ¦ Total: 8 Channels (Active: 8, Spare: 0)
C6-S05-P00 | 5 | 0 | 1 |  | PCM-2030_DO_1 | Pin 1 | C6S5:1/C6S05-:1 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S05- | - | PCM-2030 |  | 3-25-01-202-PD-01
C6-S05-P01 | 5 | 1 | 2 |  | PCM-2030_DO_2 | Pin 2 | C6S5:2/C6S05-:2 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S05- | - | PCM-2030 |  | 3-25-01-202-PD-01
C6-S05-P02 | 5 | 2 | 3 |  | PCM-2031_DO_1 | Pin 3 | C6S5:3/C6S05-:3 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S05- | - | PCM-2031 |  | 3-25-01-202-PD-01
C6-S05-P03 | 5 | 3 | 4 |  | PCM-2031_DO_2 | Pin 4 | C6S5:4/C6S05-:4 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S05- | - | PCM-2031 |  | 3-25-01-202-PD-01
C6-S05-P04 | 5 | 4 | 5 |  | PCY-814201_DO_1 | Pin 5 | C6S5:5/C6S05-:5 | DO | 24VDC | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S05- | - | PCY-814201 | PUMP | -
C6-S05-P05 | 5 | 5 | 6 |  | PCY-814202_DO_1 | Pin 6 | C6S5:6/C6S05-:6 | DO | 24VDC | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S05- | - | PCY-814202 | PUMP | -
C6-S05-P06 | 5 | 6 | 7 |  | XS-80305_DO_1 | Pin 7 | C6S5:7/C6S05-:7 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / LPG System | C6S05- | - | XS-80305 |  | -
C6-S05-P07 | 5 | 7 | 8 |  | XS-80306_DO_1 | Pin 8 | C6S5:8/C6S05-:8 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / LPG System | C6S05- | - | XS-80306 | Pressure Transmitter | -
Slot 06 — Module: (DI) ¦ Total: 10 Channels (Active: 10, Spare: 0)
C6-S06-P00 | 6 | 0 | 1 |  | PCM-2030_DI_1 | Pin 1 | C6S6:1/C6S06-:1 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S06- | - | PCM-2030 |  | 3-25-01-202-PD-01
C6-S06-P01 | 6 | 1 | 2 |  | PCM-2030_DI_2 | Pin 2 | C6S6:2/C6S06-:2 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S06- | - | PCM-2030 |  | 3-25-01-202-PD-01
C6-S06-P02 | 6 | 2 | 3 |  | PCM-2031_DI_1 | Pin 3 | C6S6:3/C6S06-:3 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S06- | - | PCM-2031 |  | 3-25-01-202-PD-01
C6-S06-P03 | 6 | 3 | 4 |  | PCM-2031_DI_2 | Pin 4 | C6S6:4/C6S06-:4 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Slurry - Out Building | C6S06- | - | PCM-2031 |  | 3-25-01-202-PD-01
C6-S06-P04 | 6 | 4 | 5 |  | PCY-814201_DI_1 | Pin 5 | C6S6:5/C6S06-:5 | DI | 24VDC | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S06- | - | PCY-814201 | PUMP | -
C6-S06-P05 | 6 | 5 | 6 |  | PCY-814201_DI_2 | Pin 6 | C6S6:6/C6S06-:6 | DI | 24VDC | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S06- | - | PCY-814201 | PUMP | -
C6-S06-P06 | 6 | 6 | 7 |  | PCY-814201_DI_3 | Pin 7 | C6S6:7/C6S06-:7 | DI | 24VDC | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S06- | - | PCY-814201 | PUMP | -
C6-S06-P07 | 6 | 7 | 8 |  | PCY-814202_DI_1 | Pin 8 | C6S6:8/C6S06-:8 | DI | 24VDC | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S06- | - | PCY-814202 | PUMP | -
C6-S06-P08 | 6 | 8 | 9 |  | PCY-814202_DI_2 | Pin 9 | C6S6:9/C6S06-:9 | DI | 24VDC | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S06- | - | PCY-814202 | PUMP | -
C6-S06-P09 | 6 | 9 | 10 |  | PCY-814202_DI_3 | Pin 10 | C6S6:10/C6S06-:10 | DI | 24VDC | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C6S06- | - | PCY-814202 | PUMP | -

## Chassis_C7
KALASIN ENGINEERING — C7 (MCC FIELDBUS & NETWORK INTERFACE (CHASSIS 7))
Location: Motor Control Center Room (MCC Panel & Field Bus) ¦ Role: Modbus/Fieldbus Gateways & MCC Feeder Interlocks ¦ Net: Modbus TCP / EtherNet Trunk ¦ Total Points: 226 (Active: 158, Spare: 68)
SOURCE (PLC RACK / SLOT / TERMINAL / ePLAN TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Type | Status | Destination | Field Location | Floor/Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing
Slot 00 — Module: (BUS) ¦ Total: 20 Channels (Active: 20, Spare: 0)
C7-S00-P00 | 0 | 0 | 1 |  | ATY-40201_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S00- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01
C7-S00-P00 | 0 | 0 | 1 |  | ATY-40202_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S00- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01
C7-S00-P00 | 0 | 0 | 1 |  | ATY-40203_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S00- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02
C7-S00-P00 | 0 | 0 | 1 |  | BFY-60206_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S00- | - | BFY-60206 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-60210_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S00- | - | BFY-60210 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-60211_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S00- | - | BFY-60211 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-60220_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S00- | - | BFY-60220 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-60240_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S00- | - | BFY-60240 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-61301_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S00- | - | BFY-61301 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-61302_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 2nd / Packing Tower | C7S00- | - | BFY-61302 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-61303_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S00- | - | BFY-61303 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | COM-FH-60210B_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C7S00- | - | COM-FH-60210B |  | -
C7-S00-P00 | 0 | 0 | 1 |  | Communication Signal_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C7S00- | - | Communication Signal |  | -
C7-S00-P00 | 0 | 0 | 1 |  | PCY-40201_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S00- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01
C7-S00-P00 | 0 | 0 | 1 |  | PCY-40202_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S00- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01
C7-S00-P00 | 0 | 0 | 1 |  | PCY-40203_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S00- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02
C7-S00-P00 | 0 | 0 | 1 |  | PCY-60205_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S00- | - | PCY-60205 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | PCY-60215_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S00- | - | PCY-60215 | PUMP | -
C7-S00-P00 | 0 | 0 | 1 |  | PCY-814201_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C7S00- | - | PCY-814201 | PUMP | -
C7-S00-P00 | 0 | 0 | 1 |  | PCY-814202_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 24VDC | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C7S00- | - | PCY-814202 | PUMP | -
Slot 01 — Module: (DI) ¦ Total: 32 Channels (Active: 24, Spare: 8)
C7-S01-P00 | 1 | 0 | 1 |  | Spare_DI_0 | Pin 1 | C7S1:1/C7S01-:1 | DI | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P01 | 1 | 1 | 2 |  | Spare_DI_0 | Pin 2 | C7S1:2/C7S01-:2 | DI | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P02 | 1 | 2 | 3 |  | Spare_DI_0 | Pin 3 | C7S1:3/C7S01-:3 | DI | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P03 | 1 | 3 | 4 |  | Spare_DI_0 | Pin 4 | C7S1:4/C7S01-:4 | DI | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P04 | 1 | 4 | 5 |  | Spare_DI_0 | Pin 5 | C7S1:5/C7S01-:5 | DI | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P05 | 1 | 5 | 6 |  | Spare_DI_0 | Pin 6 | C7S1:6/C7S01-:6 | DI | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P06 | 1 | 6 | 7 |  | Spare_DI_0 | Pin 7 | C7S1:7/C7S01-:7 | DI | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P07 | 1 | 7 | 8 |  | Spare_DI_0 | Pin 8 | C7S1:8/C7S01-:8 | DI | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P08 | 1 | 8 | 9 |  | ATY-40201_DI_1 | Pin 9 | C7S1:9/C7S01-:9 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01
C7-S01-P09 | 1 | 9 | 10 |  | ATY-40201_DI_2 | Pin 10 | C7S1:10/C7S01-:10 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01
C7-S01-P10 | 1 | 10 | 11 |  | ATY-40201_DI_3 | Pin 11 | C7S1:11/C7S01-:11 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01
C7-S01-P11 | 1 | 11 | 12 |  | ATY-40202_DI_1 | Pin 12 | C7S1:12/C7S01-:12 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01
C7-S01-P12 | 1 | 12 | 13 |  | ATY-40202_DI_2 | Pin 13 | C7S1:13/C7S01-:13 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01
C7-S01-P13 | 1 | 13 | 14 |  | ATY-40202_DI_3 | Pin 14 | C7S1:14/C7S01-:14 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01
C7-S01-P14 | 1 | 14 | 15 |  | ATY-40203_DI_1 | Pin 15 | C7S1:15/C7S01-:15 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02
C7-S01-P15 | 1 | 15 | 16 |  | ATY-40203_DI_2 | Pin 16 | C7S1:16/C7S01-:16 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02
C7-S01-P16 | 1 | 16 | 17 |  | ATY-40203_DI_3 | Pin 17 | C7S1:17/C7S01-:17 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02
C7-S01-P17 | 1 | 17 | 18 |  | PCY-40201_DI_1 | Pin 18 | C7S1:18/C7S01-:18 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01
C7-S01-P18 | 1 | 18 | 19 |  | PCY-40201_DI_2 | Pin 19 | C7S1:19/C7S01-:19 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01
C7-S01-P19 | 1 | 19 | 20 |  | PCY-40201_DI_3 | Pin 20 | C7S1:20/C7S01-:20 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01
C7-S01-P20 | 1 | 20 | 21 |  | PCY-40202_DI_1 | Pin 21 | C7S1:21/C7S01-:21 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01
C7-S01-P21 | 1 | 21 | 22 |  | PCY-40202_DI_2 | Pin 22 | C7S1:22/C7S01-:22 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01
C7-S01-P22 | 1 | 22 | 23 |  | PCY-40202_DI_3 | Pin 23 | C7S1:23/C7S01-:23 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01
C7-S01-P23 | 1 | 23 | 24 |  | PCY-40203_DI_1 | Pin 24 | C7S1:24/C7S01-:24 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02
C7-S01-P24 | 1 | 24 | 25 |  | PCY-40203_DI_2 | Pin 25 | C7S1:25/C7S01-:25 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02
C7-S01-P25 | 1 | 25 | 26 |  | PCY-40203_DI_3 | Pin 26 | C7S1:26/C7S01-:26 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02
C7-S01-P26 | 1 | 26 | 27 |  | BFY-60206_DI_1 | Pin 27 | C7S1:27/C7S01-:27 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | BFY-60206 |  | -
C7-S01-P27 | 1 | 27 | 28 |  | PCM-60205-2_DI_1 | Pin 28 | C7S1:28/C7S01-:28 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-2 |  | -
C7-S01-P28 | 1 | 28 | 29 |  | PCM-60205-2_DI_2 | Pin 29 | C7S1:29/C7S01-:29 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-2 |  | -
C7-S01-P29 | 1 | 29 | 30 |  | PCM-60205-3_DI_1 | Pin 30 | C7S1:30/C7S01-:30 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-3 |  | -
C7-S01-P30 | 1 | 30 | 31 |  | PCM-60205-3_DI_2 | Pin 31 | C7S1:31/C7S01-:31 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-3 |  | -
C7-S01-P31 | 1 | 31 | 32 |  | PCM-60205-4_DI_1 | Pin 32 | C7S1:32/C7S01-:32 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-4 |  | -
Slot 02 — Module: (DI) ¦ Total: 32 Channels (Active: 32, Spare: 0)
C7-S02-P00 | 2 | 0 | 1 |  | PCM-60205-4_DI_2 | Pin 1 | C7S2:1/C7S02-:1 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | PCM-60205-4 |  | -
C7-S02-P01 | 2 | 1 | 2 |  | PCM-60205-5_DI_1 | Pin 2 | C7S2:2/C7S02-:2 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | PCM-60205-5 |  | -
C7-S02-P02 | 2 | 2 | 3 |  | PCM-60205-5_DI_2 | Pin 3 | C7S2:3/C7S02-:3 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | PCM-60205-5 |  | -
C7-S02-P03 | 2 | 3 | 4 |  | PCY-60205_DI_1 | Pin 4 | C7S2:4/C7S02-:4 | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S02- | - | PCY-60205 |  | -
C7-S02-P04 | 2 | 4 | 5 |  | PCY-60205_DI_2 | Pin 5 | C7S2:5/C7S02-:5 | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S02- | - | PCY-60205 |  | -
C7-S02-P05 | 2 | 5 | 6 |  | RVM-60201_DI_1 | Pin 6 | C7S2:6/C7S02-:6 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60201 |  | -
C7-S02-P06 | 2 | 6 | 7 |  | RVM-60201_DI_2 | Pin 7 | C7S2:7/C7S02-:7 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60201 |  | -
C7-S02-P07 | 2 | 7 | 8 |  | RVM-60202_DI_1 | Pin 8 | C7S2:8/C7S02-:8 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60202 |  | -
C7-S02-P08 | 2 | 8 | 9 |  | RVM-60202_DI_2 | Pin 9 | C7S2:9/C7S02-:9 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60202 |  | -
C7-S02-P09 | 2 | 9 | 10 |  | RVM-60203_DI_1 | Pin 10 | C7S2:10/C7S02-:10 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60203 |  | -
C7-S02-P10 | 2 | 10 | 11 |  | RVM-60203_DI_2 | Pin 11 | C7S2:11/C7S02-:11 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60203 |  | -
C7-S02-P11 | 2 | 11 | 12 |  | BFY-60210_DI_1 | Pin 12 | C7S2:12/C7S02-:12 | DI | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | BFY-60210 |  | -
C7-S02-P12 | 2 | 12 | 13 |  | BFY-60211_DI_1 | Pin 13 | C7S2:13/C7S02-:13 | DI | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | BFY-60211 |  | -
C7-S02-P13 | 2 | 13 | 14 |  | BFY-60240_DI_1 | Pin 14 | C7S2:14/C7S02-:14 | DI | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | BFY-60240 |  | -
C7-S02-P14 | 2 | 14 | 15 |  | PCY-60215_DI_1 | Pin 15 | C7S2:15/C7S02-:15 | DI | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | PCY-60215 | PUMP | -
C7-S02-P15 | 2 | 15 | 16 |  | PCY-60215_DI_2 | Pin 16 | C7S2:16/C7S02-:16 | DI | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | PCY-60215 | PUMP | -
C7-S02-P16 | 2 | 16 | 17 |  | PCY-60215_DI_3 | Pin 17 | C7S2:17/C7S02-:17 | DI | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | PCY-60215 | PUMP | -
C7-S02-P17 | 2 | 17 | 18 |  | BFY-60220_DI_1 | Pin 18 | C7S2:18/C7S02-:18 | DI | 24VDC | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S02- | - | BFY-60220 |  | -
C7-S02-P18 | 2 | 18 | 19 |  | BFY-61302_DI_1 | Pin 19 | C7S2:19/C7S02-:19 | DI | 24VDC | ACTIVE | MCC | MCC Room | 2nd / Packing Tower | C7S02- | - | BFY-61302 |  | -
C7-S02-P19 | 2 | 19 | 20 |  | HS-61307F_DI_1 | Pin 20 | C7S2:20/C7S02-:20 | DI | 24VDC | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S02- | - | HS-61307F |  | 3-25-01-613-PD-03
C7-S02-P20 | 2 | 20 | 21 |  | HS-61307G_DI_1 | Pin 21 | C7S2:21/C7S02-:21 | DI | 24VDC | ACTIVE | MCC | MCC Room | 3rd / Packing Tower | C7S02- | - | HS-61307G |  | 3-25-01-613-PD-03
C7-S02-P21 | 2 | 21 | 22 |  | HS-61307H_DI_1 | Pin 22 | C7S2:22/C7S02-:22 | DI | 24VDC | ACTIVE | MCC | MCC Room | 3rd / Packing Tower | C7S02- | - | HS-61307H |  | 3-25-01-613-PD-03
C7-S02-P22 | 2 | 22 | 23 |  | HS-61307I_DI_1 | Pin 23 | C7S2:23/C7S02-:23 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307I |  | 3-25-01-613-PD-03
C7-S02-P23 | 2 | 23 | 24 |  | HS-61307J_DI_1 | Pin 24 | C7S2:24/C7S02-:24 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307J |  | 3-25-01-613-PD-03
C7-S02-P24 | 2 | 24 | 25 |  | HS-61307K_DI_1 | Pin 25 | C7S2:25/C7S02-:25 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307K |  | 3-25-01-613-PD-03
C7-S02-P25 | 2 | 25 | 26 |  | HS-61307L_DI_1 | Pin 26 | C7S2:26/C7S02-:26 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307L |  | 3-25-01-613-PD-03
C7-S02-P26 | 2 | 26 | 27 |  | HS-61307M_DI_1 | Pin 27 | C7S2:27/C7S02-:27 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307M |  | 3-25-01-613-PD-03
C7-S02-P27 | 2 | 27 | 28 |  | HS-61307N_DI_1 | Pin 28 | C7S2:28/C7S02-:28 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307N |  | 3-25-01-613-PD-03
C7-S02-P28 | 2 | 28 | 29 |  | HS-61307O_DI_1 | Pin 29 | C7S2:29/C7S02-:29 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307O |  | 3-25-01-613-PD-03
C7-S02-P29 | 2 | 29 | 30 |  | HS-61307P_DI_1 | Pin 30 | C7S2:30/C7S02-:30 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307P |  | 3-25-01-613-PD-03
C7-S02-P30 | 2 | 30 | 31 |  | HS-61307Q_DI_1 | Pin 31 | C7S2:31/C7S02-:31 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307Q |  | 3-25-01-613-PD-03
C7-S02-P31 | 2 | 31 | 32 |  | HS-61307R_DI_1 | Pin 32 | C7S2:32/C7S02-:32 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307R |  | 3-25-01-613-PD-03
Slot 03 — Module: (DI) ¦ Total: 26 Channels (Active: 26, Spare: 0)
C7-S03-P00 | 3 | 0 | 1 |  | RVM-61302_DI_1 | Pin 1 | C7S3:1/C7S03-:1 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S03- | - | RVM-61302 |  | -
C7-S03-P01 | 3 | 1 | 2 |  | RVM-61302_DI_2 | Pin 2 | C7S3:2/C7S03-:2 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S03- | - | RVM-61302 |  | -
C7-S03-P02 | 3 | 2 | 3 |  | RVM-61303_DI_1 | Pin 3 | C7S3:3/C7S03-:3 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S03- | - | RVM-61303 |  | -
C7-S03-P03 | 3 | 3 | 4 |  | RVM-61303_DI_2 | Pin 4 | C7S3:4/C7S03-:4 | DI | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S03- | - | RVM-61303 |  | -
C7-S03-P04 | 3 | 4 | 5 |  | SCM-61301_DI_1 | Pin 5 | C7S3:5/C7S03-:5 | DI | 24VDC | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S03- | - | SCM-61301 |  | -
C7-S03-P05 | 3 | 5 | 6 |  | SCM-61301_DI_2 | Pin 6 | C7S3:6/C7S03-:6 | DI | 24VDC | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S03- | - | SCM-61301 |  | -
C7-S03-P06 | 3 | 6 | 7 |  | SCM-61302_DI_2 | Pin 7 | C7S3:7/C7S03-:7 | DI | 24VDC | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S03- | - | SCM-61302 |  | -
C7-S03-P07 | 3 | 7 | 8 |  | SCM-61302_DI_1 | Pin 8 | C7S3:8/C7S03-:8 | DI | 24VDC | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S03- | - | SCM-61302 |  | -
C7-S03-P08 | 3 | 8 | 9 |  | BFY-61301_DI_1 | Pin 9 | C7S3:9/C7S03-:9 | DI | 24VDC | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S03- | - | BFY-61301 |  | -
C7-S03-P09 | 3 | 9 | 10 |  | BFY-61303_DI_1 | Pin 10 | C7S3:10/C7S03-:10 | DI | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | BFY-61303 |  | -
C7-S03-P10 | 3 | 10 | 11 |  | BLM-61302_DI_1 | Pin 11 | C7S3:11/C7S03-:11 | DI | 24VDC | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S03- | - | BLM-61302 |  | -
C7-S03-P11 | 3 | 11 | 12 |  | BLM-61302_DI_2 | Pin 12 | C7S3:12/C7S03-:12 | DI | 24VDC | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S03- | - | BLM-61302 |  | -
C7-S03-P12 | 3 | 12 | 13 |  | HS-61307A_DI_1 | Pin 13 | C7S3:13/C7S03-:13 | DI | 24VDC | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S03- | - | HS-61307A |  | 3-25-01-613-PD-03
C7-S03-P13 | 3 | 13 | 14 |  | HS-61307B_DI_1 | Pin 14 | C7S3:14/C7S03-:14 | DI | 24VDC | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S03- | - | HS-61307B |  | 3-25-01-613-PD-03
C7-S03-P14 | 3 | 14 | 15 |  | HS-61307C_DI_1 | Pin 15 | C7S3:15/C7S03-:15 | DI | 24VDC | ACTIVE | MCC | MCC Room | 7th / Packing Tower | C7S03- | - | HS-61307C |  | 3-25-01-613-PD-03
C7-S03-P15 | 3 | 15 | 16 |  | HS-61307D_DI_1 | Pin 16 | C7S3:16/C7S03-:16 | DI | 24VDC | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S03- | - | HS-61307D |  | 3-25-01-613-PD-03
C7-S03-P16 | 3 | 16 | 17 |  | HS-61307E_DI_1 | Pin 17 | C7S3:17/C7S03-:17 | DI | 24VDC | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S03- | - | HS-61307E |  | 3-25-01-613-PD-03
C7-S03-P17 | 3 | 17 | 18 |  | RVM-60204_DI_1 | Pin 18 | C7S3:18/C7S03-:18 | DI | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-60204 |  | -
C7-S03-P18 | 3 | 18 | 19 |  | RVM-60204_DI_2 | Pin 19 | C7S3:19/C7S03-:19 | DI | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-60204 |  | -
C7-S03-P19 | 3 | 19 | 20 |  | RVM-61301_DI_1 | Pin 20 | C7S3:20/C7S03-:20 | DI | 24VDC | ACTIVE | MCC | MCC Room | 6th / Packing Tower | C7S03- | - | RVM-61301 |  | -
C7-S03-P20 | 3 | 20 | 21 |  | RVM-61301_DI_2 | Pin 21 | C7S3:21/C7S03-:21 | DI | 24VDC | ACTIVE | MCC | MCC Room | 6th / Packing Tower | C7S03- | - | RVM-61301 |  | -
C7-S03-P21 | 3 | 21 | 22 |  | RVM-61304_DI_1 | Pin 22 | C7S3:22/C7S03-:22 | DI | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-61304 |  | -
C7-S03-P22 | 3 | 22 | 23 |  | RVM-61304_DI_2 | Pin 23 | C7S3:23/C7S03-:23 | DI | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-61304 |  | -
C7-S03-P23 | 3 | 23 | 24 |  | RVM-61305_DI_1 | Pin 24 | C7S3:24/C7S03-:24 | DI | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-61305 |  | -
C7-S03-P24 | 3 | 24 | 25 |  | RVM-61305_DI_2 | Pin 25 | C7S3:25/C7S03-:25 | DI | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-61305 |  | -
C7-S03-P25 | 3 | 25 | 26 |  | PCY-60205_DI_3 | Pin 26 | C7S3:26/C7S03-:26 | DI | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S03- | - | PCY-60205 |  | -
Slot 04 — Module: (DI) ¦ Total: 28 Channels (Active: 0, Spare: 28)
C7-S04-P04 | 4 | 4 | 5 |  | Spare_DI_0 | Pin 5 | C7S4:5/C7S04-:5 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P05 | 4 | 5 | 6 |  | Spare_DI_0 | Pin 6 | C7S4:6/C7S04-:6 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P06 | 4 | 6 | 7 |  | Spare_DI_0 | Pin 7 | C7S4:7/C7S04-:7 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P07 | 4 | 7 | 8 |  | Spare_DI_0 | Pin 8 | C7S4:8/C7S04-:8 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P08 | 4 | 8 | 9 |  | Spare_DI_0 | Pin 9 | C7S4:9/C7S04-:9 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P09 | 4 | 9 | 10 |  | Spare_DI_0 | Pin 10 | C7S4:10/C7S04-:10 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P10 | 4 | 10 | 11 |  | Spare_DI_0 | Pin 11 | C7S4:11/C7S04-:11 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P11 | 4 | 11 | 12 |  | Spare_DI_0 | Pin 12 | C7S4:12/C7S04-:12 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P12 | 4 | 12 | 13 |  | Spare_DI_0 | Pin 13 | C7S4:13/C7S04-:13 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P13 | 4 | 13 | 14 |  | Spare_DI_0 | Pin 14 | C7S4:14/C7S04-:14 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P14 | 4 | 14 | 15 |  | Spare_DI_0 | Pin 15 | C7S4:15/C7S04-:15 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P15 | 4 | 15 | 16 |  | Spare_DI_0 | Pin 16 | C7S4:16/C7S04-:16 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P16 | 4 | 16 | 17 |  | Spare_DI_0 | Pin 17 | C7S4:17/C7S04-:17 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P17 | 4 | 17 | 18 |  | Spare_DI_0 | Pin 18 | C7S4:18/C7S04-:18 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P18 | 4 | 18 | 19 |  | Spare_DI_0 | Pin 19 | C7S4:19/C7S04-:19 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P19 | 4 | 19 | 20 |  | Spare_DI_0 | Pin 20 | C7S4:20/C7S04-:20 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P20 | 4 | 20 | 21 |  | Spare_DI_0 | Pin 21 | C7S4:21/C7S04-:21 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P21 | 4 | 21 | 22 |  | Spare_DI_0 | Pin 22 | C7S4:22/C7S04-:22 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P22 | 4 | 22 | 23 |  | Spare_DI_0 | Pin 23 | C7S4:23/C7S04-:23 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P23 | 4 | 23 | 24 |  | Spare_DI_0 | Pin 24 | C7S4:24/C7S04-:24 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P24 | 4 | 24 | 25 |  | Spare_DI_0 | Pin 25 | C7S4:25/C7S04-:25 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P25 | 4 | 25 | 26 |  | Spare_DI_0 | Pin 26 | C7S4:26/C7S04-:26 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P26 | 4 | 26 | 27 |  | Spare_DI_0 | Pin 27 | C7S4:27/C7S04-:27 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P27 | 4 | 27 | 28 |  | Spare_DI_0 | Pin 28 | C7S4:28/C7S04-:28 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P28 | 4 | 28 | 29 |  | Spare_DI_0 | Pin 29 | C7S4:29/C7S04-:29 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P29 | 4 | 29 | 30 |  | Spare_DI_0 | Pin 30 | C7S4:30/C7S04-:30 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P30 | 4 | 30 | 31 |  | Spare_DI_0 | Pin 31 | C7S4:31/C7S04-:31 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P31 | 4 | 31 | 32 |  | Spare_DI_0 | Pin 32 | C7S4:32/C7S04-:32 | DI | 24VDC | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
Slot 05 — Module: (DO) ¦ Total: 32 Channels (Active: 24, Spare: 8)
C7-S05-P00 | 5 | 0 | 1 |  | Spare_DO_0 | Pin 1 | C7S5:1/C7S05-:1 | DO | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P01 | 5 | 1 | 2 |  | Spare_DO_0 | Pin 2 | C7S5:2/C7S05-:2 | DO | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P02 | 5 | 2 | 3 |  | Spare_DO_0 | Pin 3 | C7S5:3/C7S05-:3 | DO | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P03 | 5 | 3 | 4 |  | Spare_DO_0 | Pin 4 | C7S5:4/C7S05-:4 | DO | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P04 | 5 | 4 | 5 |  | Spare_DO_0 | Pin 5 | C7S5:5/C7S05-:5 | DO | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P05 | 5 | 5 | 6 |  | Spare_DO_0 | Pin 6 | C7S5:6/C7S05-:6 | DO | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P06 | 5 | 6 | 7 |  | Spare_DO_0 | Pin 7 | C7S5:7/C7S05-:7 | DO | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P07 | 5 | 7 | 8 |  | Spare_DO_0 | Pin 8 | C7S5:8/C7S05-:8 | DO | 24VDC | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P08 | 5 | 8 | 9 |  | ATY-40201_DO_1 | Pin 9 | C7S5:9/C7S05-:9 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01
C7-S05-P09 | 5 | 9 | 10 |  | ATY-40202_DO_1 | Pin 10 | C7S5:10/C7S05-:10 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01
C7-S05-P10 | 5 | 10 | 11 |  | ATY-40203_DO_1 | Pin 11 | C7S5:11/C7S05-:11 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S05- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02
C7-S05-P11 | 5 | 11 | 12 |  | PCY-40201_DO_1 | Pin 12 | C7S5:12/C7S05-:12 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01
C7-S05-P12 | 5 | 12 | 13 |  | PCY-40202_DO_1 | Pin 13 | C7S5:13/C7S05-:13 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01
C7-S05-P13 | 5 | 13 | 14 |  | PCY-40203_DO_1 | Pin 14 | C7S5:14/C7S05-:14 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S05- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02
C7-S05-P14 | 5 | 14 | 15 |  | BFY-60206_DO_1 | Pin 15 | C7S5:15/C7S05-:15 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | BFY-60206 |  | -
C7-S05-P15 | 5 | 15 | 16 |  | PCM-60205-2_DO_1 | Pin 16 | C7S5:16/C7S05-:16 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-2 |  | -
C7-S05-P16 | 5 | 16 | 17 |  | PCM-60205-2_DO_2 | Pin 17 | C7S5:17/C7S05-:17 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-2 |  | -
C7-S05-P17 | 5 | 17 | 18 |  | PCM-60205-3_DO_1 | Pin 18 | C7S5:18/C7S05-:18 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-3 |  | -
C7-S05-P18 | 5 | 18 | 19 |  | PCM-60205-3_DO_2 | Pin 19 | C7S5:19/C7S05-:19 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-3 |  | -
C7-S05-P19 | 5 | 19 | 20 |  | PCM-60205-4_DO_1 | Pin 20 | C7S5:20/C7S05-:20 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-4 |  | -
C7-S05-P20 | 5 | 20 | 21 |  | PCM-60205-4_DO_2 | Pin 21 | C7S5:21/C7S05-:21 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-4 |  | -
C7-S05-P21 | 5 | 21 | 22 |  | PCM-60205-5_DO_1 | Pin 22 | C7S5:22/C7S05-:22 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-5 |  | -
C7-S05-P22 | 5 | 22 | 23 |  | PCM-60205-5_DO_2 | Pin 23 | C7S5:23/C7S05-:23 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-5 |  | -
C7-S05-P23 | 5 | 23 | 24 |  | RVM-60201_DO_1 | Pin 24 | C7S5:24/C7S05-:24 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60201 |  | -
C7-S05-P24 | 5 | 24 | 25 |  | RVM-60201_DO_2 | Pin 25 | C7S5:25/C7S05-:25 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60201 |  | -
C7-S05-P25 | 5 | 25 | 26 |  | RVM-60202_DO_1 | Pin 26 | C7S5:26/C7S05-:26 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60202 |  | -
C7-S05-P26 | 5 | 26 | 27 |  | RVM-60202_DO_2 | Pin 27 | C7S5:27/C7S05-:27 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60202 |  | -
C7-S05-P27 | 5 | 27 | 28 |  | RVM-60203_DO_1 | Pin 28 | C7S5:28/C7S05-:28 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60203 |  | -
C7-S05-P28 | 5 | 28 | 29 |  | RVM-60203_DO_2 | Pin 29 | C7S5:29/C7S05-:29 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60203 |  | -
C7-S05-P29 | 5 | 29 | 30 |  | XS-60205_DO_1 | Pin 30 | C7S5:30/C7S05-:30 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | XS-60205 |  | -
C7-S05-P30 | 5 | 30 | 31 |  | BFY-60210_DO_1 | Pin 31 | C7S5:31/C7S05-:31 | DO | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S05- | - | BFY-60210 |  | -
C7-S05-P31 | 5 | 31 | 32 |  | BFY-60211_DO_1 | Pin 32 | C7S5:32/C7S05-:32 | DO | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S05- | - | BFY-60211 |  | -
Slot 06 — Module: (DO) ¦ Total: 32 Channels (Active: 32, Spare: 0)
C7-S06-P00 | 6 | 0 | 1 |  | BFY-60240_DO_1 | Pin 1 | C7S6:1/C7S06-:1 | DO | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S06- | - | BFY-60240 |  | -
C7-S06-P01 | 6 | 1 | 2 |  | PCY-60215_DO_1 | Pin 2 | C7S6:2/C7S06-:2 | DO | 24VDC | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S06- | - | PCY-60215 | PUMP | -
C7-S06-P02 | 6 | 2 | 3 |  | XS-60240A_DO_1 | Pin 3 | C7S6:3/C7S06-:3 | DO | 24VDC | ACTIVE | MCC | MCC Room | 4th / Spray Dryer | C7S06- | - | XS-60240A |  | -
C7-S06-P03 | 6 | 3 | 4 |  | XS-60241A_DO_1 | Pin 4 | C7S6:4/C7S06-:4 | DO | 24VDC | ACTIVE | MCC | MCC Room | 4th / Spray Dryer | C7S06- | - | XS-60241A |  | -
C7-S06-P04 | 6 | 4 | 5 |  | XS-60242A_DO_1 | Pin 5 | C7S6:5/C7S06-:5 | DO | 24VDC | ACTIVE | MCC | MCC Room | 3rd / Spray Dryer | C7S06- | - | XS-60242A |  | -
C7-S06-P04 | 6 | 4 | 5 |  | XS-60243A_DO_1 | Pin 5 | C7S6:5/C7S06-:5 | DO | 24VDC | ACTIVE | MCC | MCC Room | 4th / Spray Dryer | C7S06- | - | XS-60243A |  | -
C7-S06-P06 | 6 | 6 | 7 |  | XS-60260_DO_1 | Pin 7 | C7S6:7/C7S06-:7 | DO | 24VDC | ACTIVE | MCC | MCC Room | 6th / Spray Dryer | C7S06- | - | XS-60260 |  | -
C7-S06-P07 | 6 | 7 | 8 |  | BFY-60220_DO_1 | Pin 8 | C7S6:8/C7S06-:8 | DO | 24VDC | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S06- | - | BFY-60220 |  | -
C7-S06-P08 | 6 | 8 | 9 |  | XS-FH-60210A_DO_1 | Pin 9 | C7S6:9/C7S06-:9 | DO | 24VDC | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S06- | - | XS-FH-60210A |  | -
C7-S06-P09 | 6 | 9 | 10 |  | XS-FH-60210B_DO_1 | Pin 10 | C7S6:10/C7S06-:10 | DO | 24VDC | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S06- | - | XS-FH-60210B |  | -
C7-S06-P10 | 6 | 10 | 11 |  | BFY-61302_DO_1 | Pin 11 | C7S6:11/C7S06-:11 | DO | 24VDC | ACTIVE | MCC | MCC Room | 2nd / Packing Tower | C7S06- | - | BFY-61302 |  | -
C7-S06-P11 | 6 | 11 | 12 |  | RVM-61302_DO_1 | Pin 12 | C7S6:12/C7S06-:12 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S06- | - | RVM-61302 |  | -
C7-S06-P12 | 6 | 12 | 13 |  | RVM-61302_DO_2 | Pin 13 | C7S6:13/C7S06-:13 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S06- | - | RVM-61302 |  | -
C7-S06-P13 | 6 | 13 | 14 |  | RVM-61303_DO_1 | Pin 14 | C7S6:14/C7S06-:14 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S06- | - | RVM-61303 |  | -
C7-S06-P14 | 6 | 14 | 15 |  | RVM-61303_DO_2 | Pin 15 | C7S6:15/C7S06-:15 | DO | 24VDC | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S06- | - | RVM-61303 |  | -
C7-S06-P15 | 6 | 15 | 16 |  | SCM-61301_DO_1 | Pin 16 | C7S6:16/C7S06-:16 | DO | 24VDC | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S06- | - | SCM-61301 |  | -
C7-S06-P16 | 6 | 16 | 17 |  | SCM-61301_DO_2 | Pin 17 | C7S6:17/C7S06-:17 | DO | 24VDC | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S06- | - | SCM-61301 |  | -
C7-S06-P17 | 6 | 17 | 18 |  | SCM-61302_DO_1 | Pin 18 | C7S6:18/C7S06-:18 | DO | 24VDC | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S06- | - | SCM-61302 |  | -
C7-S06-P18 | 6 | 18 | 19 |  | SCM-61302_DO_2 | Pin 19 | C7S6:19/C7S06-:19 | DO | 24VDC | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S06- | - | SCM-61302 |  | -
C7-S06-P19 | 6 | 19 | 20 |  | BFY-61301_DO_1 | Pin 20 | C7S6:20/C7S06-:20 | DO | 24VDC | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S06- | - | BFY-61301 |  | -
C7-S06-P20 | 6 | 20 | 21 |  | BFY-61303_DO_1 | Pin 21 | C7S6:21/C7S06-:21 | DO | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | BFY-61303 |  | -
C7-S06-P21 | 6 | 21 | 22 |  | BLM-61302_DO_1 | Pin 22 | C7S6:22/C7S06-:22 | DO | 24VDC | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S06- | - | BLM-61302 |  | -
C7-S06-P22 | 6 | 22 | 23 |  | BLM-61302_DO_2 | Pin 23 | C7S6:23/C7S06-:23 | DO | 24VDC | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S06- | - | BLM-61302 |  | -
C7-S06-P23 | 6 | 23 | 24 |  | RVM-60204_DO_1 | Pin 24 | C7S6:24/C7S06-:24 | DO | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-60204 |  | -
C7-S06-P24 | 6 | 24 | 25 |  | RVM-60204_DO_2 | Pin 25 | C7S6:25/C7S06-:25 | DO | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-60204 |  | -
C7-S06-P25 | 6 | 25 | 26 |  | RVM-61301_DO_1 | Pin 26 | C7S6:26/C7S06-:26 | DO | 24VDC | ACTIVE | MCC | MCC Room | 6th / Packing Tower | C7S06- | - | RVM-61301 |  | -
C7-S06-P26 | 6 | 26 | 27 |  | RVM-61301_DO_2 | Pin 27 | C7S6:27/C7S06-:27 | DO | 24VDC | ACTIVE | MCC | MCC Room | 6th / Packing Tower | C7S06- | - | RVM-61301 |  | -
C7-S06-P27 | 6 | 27 | 28 |  | RVM-61304_DO_1 | Pin 28 | C7S6:28/C7S06-:28 | DO | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-61304 |  | -
C7-S06-P28 | 6 | 28 | 29 |  | RVM-61304_DO_2 | Pin 29 | C7S6:29/C7S06-:29 | DO | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-61304 |  | -
C7-S06-P29 | 6 | 29 | 30 |  | RVM-61305_DO_1 | Pin 30 | C7S6:30/C7S06-:30 | DO | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-61305 |  | -
C7-S06-P30 | 6 | 30 | 31 |  | RVM-61305_DO_2 | Pin 31 | C7S6:31/C7S06-:31 | DO | 24VDC | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-61305 |  | -
C7-S06-P31 | 6 | 31 | 32 |  | PCY-60205_DO_1 | Pin 32 | C7S6:32/C7S06-:32 | DO | 24VDC | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S06- | - | PCY-60205 |  | -
Slot 07 — Module: (DO) ¦ Total: 24 Channels (Active: 0, Spare: 24)
C7-S07-P08 | 7 | 8 | 9 |  | Spare_DO_0 | Pin 9 | C7S7:9/C7S07-:9 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P09 | 7 | 9 | 10 |  | Spare_DO_0 | Pin 10 | C7S7:10/C7S07-:10 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P10 | 7 | 10 | 11 |  | Spare_DO_0 | Pin 11 | C7S7:11/C7S07-:11 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P11 | 7 | 11 | 12 |  | Spare_DO_0 | Pin 12 | C7S7:12/C7S07-:12 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P12 | 7 | 12 | 13 |  | Spare_DO_0 | Pin 13 | C7S7:13/C7S07-:13 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P13 | 7 | 13 | 14 |  | Spare_DO_0 | Pin 14 | C7S7:14/C7S07-:14 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P14 | 7 | 14 | 15 |  | Spare_DO_0 | Pin 15 | C7S7:15/C7S07-:15 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P15 | 7 | 15 | 16 |  | Spare_DO_0 | Pin 16 | C7S7:16/C7S07-:16 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P16 | 7 | 16 | 17 |  | Spare_DO_0 | Pin 17 | C7S7:17/C7S07-:17 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P17 | 7 | 17 | 18 |  | Spare_DO_0 | Pin 18 | C7S7:18/C7S07-:18 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P18 | 7 | 18 | 19 |  | Spare_DO_0 | Pin 19 | C7S7:19/C7S07-:19 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P19 | 7 | 19 | 20 |  | Spare_DO_0 | Pin 20 | C7S7:20/C7S07-:20 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P20 | 7 | 20 | 21 |  | Spare_DO_0 | Pin 21 | C7S7:21/C7S07-:21 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P21 | 7 | 21 | 22 |  | Spare_DO_0 | Pin 22 | C7S7:22/C7S07-:22 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P22 | 7 | 22 | 23 |  | Spare_DO_0 | Pin 23 | C7S7:23/C7S07-:23 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P23 | 7 | 23 | 24 |  | Spare_DO_0 | Pin 24 | C7S7:24/C7S07-:24 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P24 | 7 | 24 | 25 |  | Spare_DO_0 | Pin 25 | C7S7:25/C7S07-:25 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P25 | 7 | 25 | 26 |  | Spare_DO_0 | Pin 26 | C7S7:26/C7S07-:26 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P26 | 7 | 26 | 27 |  | Spare_DO_0 | Pin 27 | C7S7:27/C7S07-:27 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P27 | 7 | 27 | 28 |  | Spare_DO_0 | Pin 28 | C7S7:28/C7S07-:28 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P28 | 7 | 28 | 29 |  | Spare_DO_0 | Pin 29 | C7S7:29/C7S07-:29 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P29 | 7 | 29 | 30 |  | Spare_DO_0 | Pin 30 | C7S7:30/C7S07-:30 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P30 | 7 | 30 | 31 |  | Spare_DO_0 | Pin 31 | C7S7:31/C7S07-:31 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P31 | 7 | 31 | 32 |  | Spare_DO_0 | Pin 32 | C7S7:32/C7S07-:32 | DO | 24VDC | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -