## Chassis_Slot_Summary
INGREDION (THAILAND) CO., LTD. ¦ PROJECT JET COOKER
PLC I/O SYSTEM ARCHITECTURE & CHASSIS / SLOT SUMMARY REPORT
Master I/O Allocation Sorted by Chassis & Slot ¦ Engineering Deliverable
TOTAL I/O POINTS |  | ACTIVE CHANNELS |  | SPARE CHANNELS |  | TOTAL CHASSIS |  | ACTIVE I/O SLOTS
1,210 |  | 763 |  | 447 |  | 7 |  | 47
Allocated across all chassis |  | 63.1% operational load |  | 36.9% spare capacity |  | C1, C2, C3, C4, C5, C6, C7 |  | Populated module slots
1. I/O Signal Type Distribution
I/O Type | Description | Total Points | Active Points | Spare Points | Spare % | Signal Level / Standard
DI | Digital Input | 636 | 426 | 210 | 33.0% | 24 VDC Sink/Source (Dry Contact / Proximity)
DO | Digital Output | 352 | 186 | 166 | 47.2% | 24 VDC Sourcing (Solenoid Valve / Interlock)
AI | Analog Input | 194 | 126 | 68 | 35.1% | 4 - 20 mA Current Loop (HART / Transmitter)
AO | Analog Output | 8 | 5 | 3 | 37.5% | 4 - 20 mA Current Loop (Control Valve / I-P)
BUS | Communication Bus | 20 | 20 | 0 | 0.0% | Industrial Ethernet / Serial Bus Link
TOTAL | All Signal Types Combined | 1210 | 763 | 447 | 36.9% | -
2. Chassis & Slot Hardware Allocation Matrix (Sorted)
Chassis | Slot | Enclosure / Panel | Slot Address | Module / Card Model | Module Description | I/O Type | Total Pts | Active Pts | Spare Pts | Spare % | Connected Junction Boxes | Channel Range
C1 | 3 | =CA1+MCP-M1 | C1S03 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 32 | 16 | 16 | 50.0% | CA1, JB-401 | Pt 00 - Pt 31
C1 | 4 | =CA1+MCP-M1 | C1S04 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 32 | 32 | 0 | 0.0% | JB-401 | Pt 00 - Pt 31
C1 | 5 | =CA1+MCP-M1 | C1S05 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 32 | 12 | 20 | 62.5% | JB-401, JB-601 | Pt 00 - Pt 31
C1 | 6 | =CA1+MCP-M1 | C1S06 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 32 | 23 | 9 | 28.1% | JB-601 | Pt 00 - Pt 31
C1 | 7 | =CA1+MCP-M1 | C1S07 | 1756-OB32 | 32-Pt 24VDC Digital Output Module | DO | 32 | 16 | 16 | 50.0% | CA1, JB-401 | Pt 00 - Pt 31
C1 | 8 | =CA1+MCP-M1 | C1S08 | 1756-OB32 | 32-Pt 24VDC Digital Output Module | DO | 32 | 20 | 12 | 37.5% | JB-401, JB-601 | Pt 00 - Pt 31
C1 | 9 | =CA1+MCP-M1 | C1S09 | 1756-IF16 | 16-Pt 4-20mA HART Analog Input Module | AI | 16 | 11 | 5 | 31.2% | JB-401 | Pt 00 - Pt 15
C1 | 10 | =CA1+MCP-M1 | C1S10 | 1756-IF16 | 16-Pt 4-20mA HART Analog Input Module | AI | 16 | 8 | 8 | 50.0% | JB-601 | Pt 00 - Pt 15
C2 | 1 | =CA1+MCP-M2 | C2S01 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 32 | 24 | 8 | 25.0% | JB-402 | Pt 00 - Pt 31
C2 | 2 | =CA1+MCP-M2 | C2S02 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 32 | 23 | 9 | 28.1% | JB-602 | Pt 00 - Pt 31
C2 | 3 | =CA1+MCP-M2 | C2S03 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 29 | 29 | 0 | 0.0% | JB-607 | Pt 00 - Pt 31
C2 | 4 | =CA1+MCP-M2 | C2S04 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 32 | 32 | 0 | 0.0% | JB-607 | Pt 00 - Pt 31
C2 | 5 | =CA1+MCP-M2 | C2S05 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 32 | 20 | 12 | 37.5% | JB-607 | Pt 00 - Pt 31
C2 | 6 | =CA1+MCP-M2 | C2S06 | 1756-OB32 | 32-Pt 24VDC Digital Output Module | DO | 32 | 12 | 20 | 62.5% | JB-402, JB-602 | Pt 00 - Pt 31
C2 | 7 | =CA1+MCP-M2 | C2S07 | 1756-OB32 | 32-Pt 24VDC Digital Output Module | DO | 32 | 31 | 1 | 3.1% | JB-607 | Pt 00 - Pt 31
C2 | 8 | =CA1+MCP-M2 | C2S08 | 1756-OB32 | 32-Pt 24VDC Digital Output Module | DO | 32 | 9 | 23 | 71.9% | JB-607 | Pt 00 - Pt 31
C2 | 9 | =CA1+MCP-M2 | C2S09 | 1756-IF16 | 16-Pt 4-20mA HART Analog Input Module | AI | 16 | 7 | 9 | 56.2% | JB-402 | Pt 00 - Pt 15
C2 | 10 | =CA1+MCP-M2 | C2S10 | 1756-IF16 | 16-Pt 4-20mA HART Analog Input Module | AI | 16 | 16 | 0 | 0.0% | JB-602 | Pt 00 - Pt 15
C2 | 11 | =CA1+MCP-M2 | C2S11 | 1756-IF16 | 16-Pt 4-20mA HART Analog Input Module | AI | 16 | 13 | 3 | 18.8% | JB-602 | Pt 00 - Pt 15
C2 | 12 | =CA1+MCP-M2 | C2S12 | 1756-IF16 | 16-Pt 4-20mA HART Analog Input Module | AI | 16 | 16 | 0 | 0.0% | JB-607 | Pt 00 - Pt 15
C2 | 13 | =CA1+MCP-M2 | C2S13 | 1756-IF16 | 16-Pt 4-20mA HART Analog Input Module | AI | 16 | 11 | 5 | 31.2% | JB-607 | Pt 00 - Pt 15
C3 | 1 | =CA1+MCP-M3 | C3S01 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 27 | 22 | 5 | 18.5% | IS-JB-603, JB-618 | Pt 00 - Pt 31
C3 | 2 | =CA1+MCP-M3 | C3S02 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 37 | 18 | 19 | 51.4% | IS-JB-618, JB-618 | Pt 00 - Pt 31
C3 | 3 | =CA1+MCP-M3 | C3S03 | 1756-OB32 | 32-Pt 24VDC Digital Output Module | DO | 32 | 9 | 23 | 71.9% | JB-618 | Pt 00 - Pt 31
C3 | 4 | =CA1+MCP-M3 | C3S04 | 1756-IF16 | 16-Pt 4-20mA HART Analog Input Module | AI | 16 | 7 | 9 | 56.2% | IS-JB-603 | Pt 00 - Pt 15
C3 | 5 | =CA1+MCP-M3 | C3S05 | 1756-IF16 | 16-Pt 4-20mA HART Analog Input Module | AI | 16 | 13 | 3 | 18.8% | IS-JB-618, JB-618 | Pt 00 - Pt 15
C3 | 13 | =CA1+MCP-M2 | C3S13 | 1756-OF8 | 8-Pt 4-20mA HART Analog Output Module | AO | 8 | 5 | 3 | 37.5% | JB-402, JB-602, JB-607 | Pt 00 - Pt 07
C4 | 1 | =CA1+MCP-M4 | C4S01 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 32 | 11 | 21 | 65.6% | IS-JB-608, JB-606 | Pt 00 - Pt 31
C4 | 2 | =CA1+MCP-M4 | C4S02 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 32 | 17 | 15 | 46.9% | JB-612 | Pt 00 - Pt 31
C4 | 3 | =CA1+MCP-M4 | C4S03 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 31 | 15 | 16 | 51.6% | IS-JB-612 | Pt 00 - Pt 31
C4 | 4 | =CA1+MCP-M4 | C4S04 | 1756-OB32 | 32-Pt 24VDC Digital Output Module | DO | 32 | 17 | 15 | 46.9% | IS-JB-608, JB-606, JB-612 | Pt 00 - Pt 31
C4 | 5 | =CA1+MCP-M4 | C4S05 | 1756-IF16 | 16-Pt 4-20mA HART Analog Input Module | AI | 26 | 7 | 19 | 73.1% | IS-JB-608, IS-JB-612, JB-606, JB-608, JB-612 | Pt 00 - Pt 15
C4 | 6 | =CA1+MCP-M4 | C4S06 | 1756-IF16 | 16-Pt 4-20mA HART Analog Input Module | AI | 8 | 8 | 0 | 0.0% | IS-JB-608, IS-JB-612 | Pt 00 - Pt 07
C5 | 1 | =CA1+MCP-M5 | C5S01 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 32 | 32 | 0 | 0.0% | RIO-200 | Pt 00 - Pt 31
C5 | 2 | =CA1+MCP-M5 | C5S02 | 1756-IB32 | 32-Pt 24VDC Digital Input Module | DI | 32 | 8 | 24 | 75.0% | RIO-200 | Pt 00 - Pt 31
C5 | 3 | =CA1+MCP-M5 | C5S03 | 1756-OB32 | 32-Pt 24VDC Digital Output Module | DO | 32 | 8 | 24 | 75.0% | RIO-200 | Pt 00 - Pt 31
C5 | 4 | =CA1+MCP-M5 | C5S04 | 1756-IF16 | 16-Pt 4-20mA HART Analog Input Module | AI | 16 | 9 | 7 | 43.8% | RIO-200 | Pt 00 - Pt 15
C6 | 5 | MCC | C6S05 | - | MCC Draw-out Terminal / Bus Interface | DO | 8 | 8 | 0 | 0.0% | MCC | Pt 00 - Pt 07
C6 | 6 | MCC | C6S06 | - | MCC Draw-out Terminal / Bus Interface | DI | 10 | 10 | 0 | 0.0% | MCC | Pt 00 - Pt 09
C7 | 0 | MCC | C7S00 | - | MCC Draw-out Terminal / Bus Interface | BUS | 20 | 20 | 0 | 0.0% | JB-601, JB-607, JB-612, MCC | Pt 00 - Pt 00
C7 | 1 | MCC | C7S01 | - | MCC Draw-out Terminal / Bus Interface | DI | 32 | 24 | 8 | 25.0% | MCC | Pt 00 - Pt 31
C7 | 2 | MCC | C7S02 | - | MCC Draw-out Terminal / Bus Interface | DI | 32 | 32 | 0 | 0.0% | JB-601, MCC | Pt 00 - Pt 31
C7 | 3 | MCC | C7S03 | - | MCC Draw-out Terminal / Bus Interface | DI | 26 | 26 | 0 | 0.0% | JB-601, MCC | Pt 00 - Pt 25
C7 | 4 | MCC | C7S04 | - | MCC Draw-out Terminal / Bus Interface | DI | 28 | 0 | 28 | 100.0% | MCC | Pt 04 - Pt 31
C7 | 5 | MCC | C7S05 | - | MCC Draw-out Terminal / Bus Interface | DO | 32 | 24 | 8 | 25.0% | MCC | Pt 00 - Pt 31
C7 | 6 | MCC | C7S06 | - | MCC Draw-out Terminal / Bus Interface | DO | 32 | 32 | 0 | 0.0% | JB-601, MCC | Pt 00 - Pt 31
C7 | 7 | MCC | C7S07 | - | MCC Draw-out Terminal / Bus Interface | DO | 24 | 0 | 24 | 100.0% | MCC | Pt 08 - Pt 31

## IO_List_Master_Sorted
INGREDION (THAILAND) CO., LTD. ¦ PROJECT JET COOKER ¦ MASTER INSTRUMENT I/O LIST
I/O Points Sorted by Chassis, Slot, Point ¦ Rockwell ControlLogix 1756 Platform ¦ AEC Industrial Engineering
Seq No. | Chassis | Slot | Point | Channel Code | Terminal Block | Module / Card | I/O Type | Signal Standard | Instrument Tag | Instrument Description | Control Description | PLC Tag Name | P&ID No. | Destination JB | JB Location | Zone | Floor | Panel Enclosure | Status | Required I/O Spec
1 | C1 | 3 | 0 | C1S03,00 | C1S03-X1 | 1756-IB32-0 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
2 | C1 | 3 | 1 | C1S03,01 | C1S03-X1 | 1756-IB32-1 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
3 | C1 | 3 | 2 | C1S03,02 | C1S03-X1 | 1756-IB32-2 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
4 | C1 | 3 | 3 | C1S03,03 | C1S03-X1 | 1756-IB32-3 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
5 | C1 | 3 | 4 | C1S03,04 | C1S03-X1 | 1756-IB32-4 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
6 | C1 | 3 | 5 | C1S03,05 | C1S03-X1 | 1756-IB32-5 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
7 | C1 | 3 | 6 | C1S03,06 | C1S03-X1 | 1756-IB32-6 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
8 | C1 | 3 | 7 | C1S03,07 | C1S03-X1 | 1756-IB32-7 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
9 | C1 | 3 | 8 | C1S03,08 | C1S03-X1 | 1756-IB32-8 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
10 | C1 | 3 | 9 | C1S03,09 | C1S03-X1 | 1756-IB32-9 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
11 | C1 | 3 | 10 | C1S03,10 | C1S03-X1 | 1756-IB32-10 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
12 | C1 | 3 | 11 | C1S03,11 | C1S03-X1 | 1756-IB32-11 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
13 | C1 | 3 | 12 | C1S03,12 | C1S03-X1 | 1756-IB32-12 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
14 | C1 | 3 | 13 | C1S03,13 | C1S03-X1 | 1756-IB32-13 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
15 | C1 | 3 | 14 | C1S03,14 | C1S03-X1 | 1756-IB32-14 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
16 | C1 | 3 | 15 | C1S03,15 | C1S03-X1 | 1756-IB32-15 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | CA1 | Main Control Cabinet | Main Control Cabinet | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
17 | C1 | 3 | 16 | C1S03,16 | C1S03-X2 | 1756-IB32-16 | DI | Dry Contact | FSL-40201 | Flow Switch | Slurry low flow | FSL-40201_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
18 | C1 | 3 | 17 | C1S03,17 | C1S03-X2 | 1756-IB32-17 | DI | Dry Contact | FSL-40202 | Flow Switch | Slurry low flow | FSL-40202_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
19 | C1 | 3 | 18 | C1S03,18 | C1S03-X2 | 1756-IB32-18 | DI | 4 - 20 mA,Pulse | FT-40201 | Coriolis Flow Transmitter | Slurry flowrate & density check transfer line | FT-40201_DI_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0
20 | C1 | 3 | 19 | C1S03,19 | C1S03-X2 | 1756-IB32-19 | DI | 4 - 20 mA,Pulse | FT-40202 | Magnetic Flow Transmitter | Feed Slurry Flow Transmitter for Pipe (PIPE) | FT-40202_DI_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0
21 | C1 | 3 | 20 | C1S03,20 | C1S03-X2 | 1756-IB32-20 | DI | Dry Contact | HV-40201 | Manual Valve With Position Switch | Slurry Drain line | HV-40201_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
22 | C1 | 3 | 21 | C1S03,21 | C1S03-X2 | 1756-IB32-21 | DI | Dry Contact | HV-40202 | Manual Valve With Position Switch | Slurry Drain line | HV-40202_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
23 | C1 | 3 | 22 | C1S03,22 | C1S03-X2 | 1756-IB32-22 | DI | Dry Contact | HV-40203 | Manual Valve With Position Switch | Slurry Drain tank TS-40201 | HV-40203_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
24 | C1 | 3 | 23 | C1S03,23 | C1S03-X2 | 1756-IB32-23 | DI | Dry Contact | HV-40204 | Manual Valve With Position Switch | Slurry Drain tank TS-40202 | HV-40204_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
25 | C1 | 3 | 24 | C1S03,24 | C1S03-X2 | 1756-IB32-24 | DI | Dry Contact | HV-40205 | Manual Valve With Position Switch | Slurry Drain line | HV-40205_DI_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
26 | C1 | 3 | 25 | C1S03,25 | C1S03-X2 | 1756-IB32-25 | DI | Dry Contact | HV-40206 | Manual Valve With Position Switch | Slurry Drain tank TS-40203 | HV-40206_DI_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
27 | C1 | 3 | 26 | C1S03,26 | C1S03-X2 | 1756-IB32-26 | DI | 24 VDC energized | XV-40201A | 0 | Slurry feed-in pH Adjustment tank 1 | XV-40201A_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
28 | C1 | 3 | 27 | C1S03,27 | C1S03-X2 | 1756-IB32-27 | DI | 24 VDC energized | XV-40201A | 0 | Slurry feed-in pH Adjustment tank 1 | XV-40201A_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
29 | C1 | 3 | 28 | C1S03,28 | C1S03-X2 | 1756-IB32-28 | DI | 24 VDC energized | XV-40201B | 0 | Slurry feed-out pH Adjustment tank 1 | XV-40201B_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
30 | C1 | 3 | 29 | C1S03,29 | C1S03-X2 | 1756-IB32-29 | DI | 24 VDC energized | XV-40201B | 0 | Slurry feed-out pH Adjustment tank 1 | XV-40201B_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
31 | C1 | 3 | 30 | C1S03,30 | C1S03-X2 | 1756-IB32-30 | DI | 24 VDC energized | XV-40201C | 0 | Water washing line outlet pH Adjustment tank 1 | XV-40201C_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
32 | C1 | 3 | 31 | C1S03,31 | C1S03-X2 | 1756-IB32-31 | DI | 24 VDC energized | XV-40201C | 0 | Water washing line outlet pH Adjustment tank 1 | XV-40201C_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
33 | C1 | 4 | 0 | C1S04,00 | C1S04-X1 | 1756-IB32-0 | DI | 24 VDC energized | XV-40201D | 0 | Slurry circulation pH Adjustment tank 1 | XV-40201D_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
34 | C1 | 4 | 1 | C1S04,01 | C1S04-X1 | 1756-IB32-1 | DI | 24 VDC energized | XV-40201D | 0 | Slurry circulation pH Adjustment tank 1 | XV-40201D_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
35 | C1 | 4 | 2 | C1S04,02 | C1S04-X1 | 1756-IB32-2 | DI | 24 VDC energized | XV-40201E | 0 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | XV-40201E_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
36 | C1 | 4 | 3 | C1S04,03 | C1S04-X1 | 1756-IB32-3 | DI | 24 VDC energized | XV-40201E | 0 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | XV-40201E_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
37 | C1 | 4 | 4 | C1S04,04 | C1S04-X1 | 1756-IB32-4 | DI | 24 VDC energized | XV-40201F | 0 | Slurry feed-to spray dry tank | XV-40201F_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
38 | C1 | 4 | 5 | C1S04,05 | C1S04-X1 | 1756-IB32-5 | DI | 24 VDC energized | XV-40201F | 0 | Slurry feed-to spray dry tank | XV-40201F_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
39 | C1 | 4 | 6 | C1S04,06 | C1S04-X1 | 1756-IB32-6 | DI | 24 VDC energized | XV-40201G | 0 | CIP water washing pH Adjustment tank 1 | XV-40201G_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
40 | C1 | 4 | 7 | C1S04,07 | C1S04-X1 | 1756-IB32-7 | DI | 24 VDC energized | XV-40201G | 0 | CIP water washing pH Adjustment tank 1 | XV-40201G_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
41 | C1 | 4 | 8 | C1S04,08 | C1S04-X1 | 1756-IB32-8 | DI | 24 VDC energized | XV-40201H | 0 | CIP Hight pressure water washing pH Adjustment tank 1 | XV-40201H_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
42 | C1 | 4 | 9 | C1S04,09 | C1S04-X1 | 1756-IB32-9 | DI | 24 VDC energized | XV-40201H | 0 | CIP Hight pressure water washing pH Adjustment tank 1 | XV-40201H_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
43 | C1 | 4 | 11 | C1S04,11 | C1S04-X1 | 1756-IB32-11 | DI | 24 VDC energized | XV-40202A | 0 | Slurry feed-in pH Adjustment tank 2 | XV-40202A_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
44 | C1 | 4 | 12 | C1S04,12 | C1S04-X1 | 1756-IB32-12 | DI | 24 VDC energized | XV-40202B | 0 | Slurry feed-out pH Adjustment tank 2 | XV-40202B_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
45 | C1 | 4 | 13 | C1S04,13 | C1S04-X1 | 1756-IB32-13 | DI | 24 VDC energized | XV-40202B | 0 | Slurry feed-out pH Adjustment tank 2 | XV-40202B_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
46 | C1 | 4 | 14 | C1S04,14 | C1S04-X1 | 1756-IB32-14 | DI | 24 VDC energized | XV-40202C | 0 | Water washing line outlet pH Adjustment tank 2 | XV-40202C_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
47 | C1 | 4 | 15 | C1S04,15 | C1S04-X1 | 1756-IB32-15 | DI | 24 VDC energized | XV-40202C | 0 | Water washing line outlet pH Adjustment tank 2 | XV-40202C_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
48 | C1 | 4 | 16 | C1S04,16 | C1S04-X2 | 1756-IB32-16 | DI | 24 VDC energized | XV-40202D | 0 | Slurry circulation pH Adjustment tank 2 | XV-40202D_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
49 | C1 | 4 | 17 | C1S04,17 | C1S04-X2 | 1756-IB32-17 | DI | 24 VDC energized | XV-40202D | 0 | Slurry circulation pH Adjustment tank 2 | XV-40202D_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
50 | C1 | 4 | 18 | C1S04,18 | C1S04-X2 | 1756-IB32-18 | DI | 24 VDC energized | XV-40202E | 0 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | XV-40202E_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
51 | C1 | 4 | 19 | C1S04,19 | C1S04-X2 | 1756-IB32-19 | DI | 24 VDC energized | XV-40202A | 0 | Slurry feed-in pH Adjustment tank 2 | XV-40202A_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
52 | C1 | 4 | 19 | C1S04,19 | C1S04-X2 | 1756-IB32-19 | DI | 24 VDC energized | XV-40202E | 0 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | XV-40202E_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
53 | C1 | 4 | 20 | C1S04,20 | C1S04-X2 | 1756-IB32-20 | DI | 24 VDC energized | XV-40202F | 0 | Slurry feed-to spray dry tank | XV-40202F_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
54 | C1 | 4 | 21 | C1S04,21 | C1S04-X2 | 1756-IB32-21 | DI | 24 VDC energized | XV-40202F | 0 | Slurry feed-to spray dry tank | XV-40202F_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
55 | C1 | 4 | 22 | C1S04,22 | C1S04-X2 | 1756-IB32-22 | DI | 24 VDC energized | XV-40202G | 0 | CIP water washing pH Adjustment tank 2 | XV-40202G_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
56 | C1 | 4 | 23 | C1S04,23 | C1S04-X2 | 1756-IB32-23 | DI | 24 VDC energized | XV-40202G | 0 | CIP water washing pH Adjustment tank 2 | XV-40202G_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
57 | C1 | 4 | 24 | C1S04,24 | C1S04-X2 | 1756-IB32-24 | DI | 24 VDC energized | XV-40202H | 0 | CIP Hight pressure water washing pH Adjustment tank 2 | XV-40202H_DI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
58 | C1 | 4 | 25 | C1S04,25 | C1S04-X2 | 1756-IB32-25 | DI | 24 VDC energized | XV-40202H | 0 | CIP Hight pressure water washing pH Adjustment tank 2 | XV-40202H_DI_2 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
59 | C1 | 4 | 26 | C1S04,26 | C1S04-X2 | 1756-IB32-26 | DI | 24 VDC energized | XV-40203B | 0 | Slurry feed-out Spray dryer infeed tank | XV-40203B_DI_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
60 | C1 | 4 | 27 | C1S04,27 | C1S04-X2 | 1756-IB32-27 | DI | 24 VDC energized | XV-40203B | 0 | Slurry feed-out Spray dryer infeed tank | XV-40203B_DI_2 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
61 | C1 | 4 | 28 | C1S04,28 | C1S04-X2 | 1756-IB32-28 | DI | 24 VDC energized | XV-40203C | 0 | Water washing line outlet Spray dryer infeed tank | XV-40203C_DI_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
62 | C1 | 4 | 29 | C1S04,29 | C1S04-X2 | 1756-IB32-29 | DI | 24 VDC energized | XV-40203C | 0 | Water washing line outlet Spray dryer infeed tank | XV-40203C_DI_2 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
63 | C1 | 4 | 30 | C1S04,30 | C1S04-X2 | 1756-IB32-30 | DI | 24 VDC energized | XV-40203D | 0 | CIP water washing Spray dryer infeed tank | XV-40203D_DI_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
64 | C1 | 4 | 31 | C1S04,31 | C1S04-X2 | 1756-IB32-31 | DI | 24 VDC energized | XV-40203D | 0 | CIP water washing Spray dryer infeed tank | XV-40203D_DI_2 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
65 | C1 | 5 | 0 | C1S05,00 | C1S05-X1 | 1756-IB32-0 | DI | 24 VDC energized | XV-40203E | 0 | CIP hight pressure water washing Spray dryer infeed tank | XV-40203E_DI_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
66 | C1 | 5 | 1 | C1S05,01 | C1S05-X1 | 1756-IB32-1 | DI | 24 VDC energized | XV-40203E | 0 | CIP hight pressure water washing Spray dryer infeed tank | XV-40203E_DI_2 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
67 | C1 | 5 | 2 | C1S05,02 | C1S05-X1 | 1756-IB32-2 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
68 | C1 | 5 | 3 | C1S05,03 | C1S05-X1 | 1756-IB32-3 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
69 | C1 | 5 | 4 | C1S05,04 | C1S05-X1 | 1756-IB32-4 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
70 | C1 | 5 | 5 | C1S05,05 | C1S05-X1 | 1756-IB32-5 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
71 | C1 | 5 | 6 | C1S05,06 | C1S05-X1 | 1756-IB32-6 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
72 | C1 | 5 | 7 | C1S05,07 | C1S05-X1 | 1756-IB32-7 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
73 | C1 | 5 | 8 | C1S05,08 | C1S05-X1 | 1756-IB32-8 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
74 | C1 | 5 | 9 | C1S05,09 | C1S05-X1 | 1756-IB32-9 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
75 | C1 | 5 | 10 | C1S05,10 | C1S05-X1 | 1756-IB32-10 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
76 | C1 | 5 | 11 | C1S05,11 | C1S05-X1 | 1756-IB32-11 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
77 | C1 | 5 | 12 | C1S05,12 | C1S05-X1 | 1756-IB32-12 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
78 | C1 | 5 | 13 | C1S05,13 | C1S05-X1 | 1756-IB32-13 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
79 | C1 | 5 | 14 | C1S05,14 | C1S05-X1 | 1756-IB32-14 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
80 | C1 | 5 | 15 | C1S05,15 | C1S05-X1 | 1756-IB32-15 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
81 | C1 | 5 | 16 | C1S05,16 | C1S05-X2 | 1756-IB32-16 | DI | 0 | ES-60202 | 0 | E-Stop for PUPD-11 (Positive Displacement Pump ) | ES-60202_DI_1 | 325-01-600-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
82 | C1 | 5 | 17 | C1S05,17 | C1S05-X2 | 1756-IB32-17 | DI | 0 | FS-60205 | Flow Switch | Cooling Water Return Flow Switch for Positive Displacement Pump (PUPD-11) | FS-60205_DI_1 | 3-25-01-602-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
83 | C1 | 5 | 18 | C1S05,18 | C1S05-X2 | 1756-IB32-18 | DI | Dry Contact | LSL-60201 | 0 | Level low switch | LSL-60201_DI_1 | 3-25-01-602-PD-11 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
84 | C1 | 5 | 19 | C1S05,19 | C1S05-X2 | 1756-IB32-19 | DI | 24 VDC energized | SV-60201 | 0 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) | SV-60201_DI_1 | 3-25-01-602-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
85 | C1 | 5 | 20 | C1S05,20 | C1S05-X2 | 1756-IB32-20 | DI | 24 VDC energized | SV-60201 | 0 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) | SV-60201_DI_2 | 3-25-01-602-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
86 | C1 | 5 | 21 | C1S05,21 | C1S05-X2 | 1756-IB32-21 | DI | 24 VDC energized | SV-60202 | 0 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) | SV-60202_DI_1 | 3-25-01-602-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
87 | C1 | 5 | 22 | C1S05,22 | C1S05-X2 | 1756-IB32-22 | DI | 24 VDC energized | SV-60202 | 0 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) | SV-60202_DI_2 | 3-25-01-602-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
88 | C1 | 5 | 23 | C1S05,23 | C1S05-X2 | 1756-IB32-23 | DI | 24 VDC energized | SV-60203 | 0 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) | SV-60203_DI_1 | 3-25-01-602-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
89 | C1 | 5 | 24 | C1S05,24 | C1S05-X2 | 1756-IB32-24 | DI | 24 VDC energized | SV-60203 | 0 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) | SV-60203_DI_2 | 3-25-01-602-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
90 | C1 | 5 | 25 | C1S05,25 | C1S05-X2 | 1756-IB32-25 | DI | Dry Contact | VS-60205 | Vibration Switch | Vibration Gear Box Vibration Switch for Switch Vibration for PUPD-11 (PUPD-11) | VS-60205_DI_1 | 3-25-01-602-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
91 | C1 | 5 | 26 | C1S05,26 | C1S05-X2 | 1756-IB32-26 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
92 | C1 | 5 | 27 | C1S05,27 | C1S05-X2 | 1756-IB32-27 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
93 | C1 | 5 | 28 | C1S05,28 | C1S05-X2 | 1756-IB32-28 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
94 | C1 | 5 | 29 | C1S05,29 | C1S05-X2 | 1756-IB32-29 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
95 | C1 | 5 | 30 | C1S05,30 | C1S05-X2 | 1756-IB32-30 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
96 | C1 | 5 | 31 | C1S05,31 | C1S05-X2 | 1756-IB32-31 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
97 | C1 | 6 | 0 | C1S06,00 | C1S06-X1 | 1756-IB32-0 | DI | Dry Contact | XA-60202A | 0 | General Alarm Emergency Stop Actuation for XSUP-5601 (Supression Panel) | XA-60202A_DI_1 | 325-01-600-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
98 | C1 | 6 | 1 | C1S06,01 | C1S06-X1 | 1756-IB32-1 | DI | Dry Contact | XA-60202B | 0 | General Fault Controlled Stop for XSUP-5601 (Supression Panel) | XA-60202B_DI_1 | 325-01-600-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
99 | C1 | 6 | 2 | C1S06,02 | C1S06-X1 | 1756-IB32-2 | DI | Dry Contact | XA-60202C | 0 | General Armed Status Indicator for XSUP-5601 (Supression Panel) | XA-60202C_DI_1 | 325-01-600-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
100 | C1 | 6 | 3 | C1S06,03 | C1S06-X1 | 1756-IB32-3 | DI | Dry Contact | XA-60202D | 0 | Power Fault Status Indicator for XSUP-5601 (Supression Panel) | XA-60202D_DI_1 | 325-01-600-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
101 | C1 | 6 | 4 | C1S06,04 | C1S06-X1 | 1756-IB32-4 | DI | Dry Contact | XA-60202E | 0 | Dryer CHAM-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | XA-60202E_DI_1 | 325-01-600-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
102 | C1 | 6 | 5 | C1S06,05 | C1S06-X1 | 1756-IB32-5 | DI | Dry Contact | XA-60202F | 0 | CHAM-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | XA-60202F_DI_1 | 325-01-600-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
103 | C1 | 6 | 6 | C1S06,06 | C1S06-X1 | 1756-IB32-6 | DI | Dry Contact | XA-60202G | 0 | CYCL-21/22 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | XA-60202G_DI_1 | 325-01-600-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
104 | C1 | 6 | 7 | C1S06,07 | C1S06-X1 | 1756-IB32-7 | DI | Dry Contact | XA-60202H | 0 | CYCL-21/22 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | XA-60202H_DI_1 | 325-01-600-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
105 | C1 | 6 | 8 | C1S06,08 | C1S06-X1 | 1756-IB32-8 | DI | - | XA-60202I | - | - | XA-60202I_DI_1 | 325-01-600-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
106 | C1 | 6 | 9 | C1S06,09 | C1S06-X1 | 1756-IB32-9 | DI | Dry Contact | XA-60202J | 0 | BGHS-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | XA-60202J_DI_1 | 325-01-600-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
107 | C1 | 6 | 10 | C1S06,10 | C1S06-X1 | 1756-IB32-10 | DI | Dry Contact | XA-60202K | 0 | BGHS-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | XA-60202K_DI_1 | 325-01-600-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
108 | C1 | 6 | 11 | C1S06,11 | C1S06-X1 | 1756-IB32-11 | DI | Dry Contact | XA-60202L | 0 | CYCL-31 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | XA-60202L_DI_1 | 325-01-600-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
109 | C1 | 6 | 12 | C1S06,12 | C1S06-X1 | 1756-IB32-12 | DI | Dry Contact | XA-60202M | 0 | CYCL-31 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | XA-60202M_DI_1 | 325-01-600-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
110 | C1 | 6 | 13 | C1S06,13 | C1S06-X1 | 1756-IB32-13 | DI | 24 VDC energized | XV-60202 | 0 | High Pressure Water On/Off Valve for Drain Pipe | XV-60202_DI_1 | 3-25-01-602-PD-11 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
111 | C1 | 6 | 14 | C1S06,14 | C1S06-X1 | 1756-IB32-14 | DI | 24 VDC energized | XV-60202 | 0 | High Pressure Water On/Off Valve for Drain Pipe | XV-60202_DI_2 | 3-25-01-602-PD-11 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
112 | C1 | 6 | 15 | C1S06,15 | C1S06-X1 | 1756-IB32-15 | DI | 24 VDC energized,Dry Contact | XV-60205A | 0 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) | XV-60205A_DI_1 | 3-25-01-602-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
113 | C1 | 6 | 16 | C1S06,16 | C1S06-X2 | 1756-IB32-16 | DI | 24 VDC energized,Dry Contact | XV-60205A | 0 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) | XV-60205A_DI_2 | 3-25-01-602-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
114 | C1 | 6 | 17 | C1S06,17 | C1S06-X2 | 1756-IB32-17 | DI | - | XV-60240D | - | - | XV-60240D_DI_1 | 325-01-600-PD-05 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
115 | C1 | 6 | 18 | C1S06,18 | C1S06-X2 | 1756-IB32-18 | DI | - | XV-60240D | - | - | XV-60240D_DI_2 | 3-25-01-602-PD-05 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
116 | C1 | 6 | 19 | C1S06,19 | C1S06-X2 | 1756-IB32-19 | DI | - | XV-60240D | - | - | XV-60240D_DI_1 | 325-01-600-PD-05 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
117 | C1 | 6 | 20 | C1S06,20 | C1S06-X2 | 1756-IB32-20 | DI | - | XV-60240D | - | - | XV-60240D_DI_2 | 3-25-01-602-PD-05 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
118 | C1 | 6 | 21 | C1S06,21 | C1S06-X2 | 1756-IB32-21 | DI | 0 | YA-60205 | 0 | Fault Command | YA-60205_DI_1 | 325-01-600-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
119 | C1 | 6 | 22 | C1S06,22 | C1S06-X2 | 1756-IB32-22 | DI | 0 | YI-60205 | 0 | Run Command | YI-60205_DI_1 | 325-01-600-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
120 | C1 | 6 | 23 | C1S06,23 | C1S06-X2 | 1756-IB32-23 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
121 | C1 | 6 | 24 | C1S06,24 | C1S06-X2 | 1756-IB32-24 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
122 | C1 | 6 | 25 | C1S06,25 | C1S06-X2 | 1756-IB32-25 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
123 | C1 | 6 | 26 | C1S06,26 | C1S06-X2 | 1756-IB32-26 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
124 | C1 | 6 | 27 | C1S06,27 | C1S06-X2 | 1756-IB32-27 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
125 | C1 | 6 | 28 | C1S06,28 | C1S06-X2 | 1756-IB32-28 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
126 | C1 | 6 | 29 | C1S06,29 | C1S06-X2 | 1756-IB32-29 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
127 | C1 | 6 | 30 | C1S06,30 | C1S06-X2 | 1756-IB32-30 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
128 | C1 | 6 | 31 | C1S06,31 | C1S06-X2 | 1756-IB32-31 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
129 | C1 | 7 | 0 | C1S07,00 | C1S07-X1 | 1756-OB32-0 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
130 | C1 | 7 | 1 | C1S07,01 | C1S07-X1 | 1756-OB32-1 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
131 | C1 | 7 | 2 | C1S07,02 | C1S07-X1 | 1756-OB32-2 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
132 | C1 | 7 | 3 | C1S07,03 | C1S07-X1 | 1756-OB32-3 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
133 | C1 | 7 | 4 | C1S07,04 | C1S07-X1 | 1756-OB32-4 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
134 | C1 | 7 | 5 | C1S07,05 | C1S07-X1 | 1756-OB32-5 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
135 | C1 | 7 | 6 | C1S07,06 | C1S07-X1 | 1756-OB32-6 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
136 | C1 | 7 | 7 | C1S07,07 | C1S07-X1 | 1756-OB32-7 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
137 | C1 | 7 | 8 | C1S07,08 | C1S07-X1 | 1756-OB32-8 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
138 | C1 | 7 | 9 | C1S07,09 | C1S07-X1 | 1756-OB32-9 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
139 | C1 | 7 | 10 | C1S07,10 | C1S07-X1 | 1756-OB32-10 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
140 | C1 | 7 | 11 | C1S07,11 | C1S07-X1 | 1756-OB32-11 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
141 | C1 | 7 | 12 | C1S07,12 | C1S07-X1 | 1756-OB32-12 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
142 | C1 | 7 | 13 | C1S07,13 | C1S07-X1 | 1756-OB32-13 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
143 | C1 | 7 | 14 | C1S07,14 | C1S07-X1 | 1756-OB32-14 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
144 | C1 | 7 | 15 | C1S07,15 | C1S07-X1 | 1756-OB32-15 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | CA1 | Main Control Cabinet | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
145 | C1 | 7 | 16 | C1S07,16 | C1S07-X2 | 1756-OB32-16 | DO | 24 VDC energized | XV-40202E | 0 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | XV-40202E_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
146 | C1 | 7 | 17 | C1S07,17 | C1S07-X2 | 1756-OB32-17 | DO | 24 VDC energized | XV-40202F | 0 | Slurry feed-to spray dry tank | XV-40202F_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
147 | C1 | 7 | 18 | C1S07,18 | C1S07-X2 | 1756-OB32-18 | DO | 24 VDC energized | XV-40202G | 0 | CIP water washing pH Adjustment tank 2 | XV-40202G_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
148 | C1 | 7 | 19 | C1S07,19 | C1S07-X2 | 1756-OB32-19 | DO | 24 VDC energized | XV-40202H | 0 | CIP Hight pressure water washing pH Adjustment tank 2 | XV-40202H_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
149 | C1 | 7 | 20 | C1S07,20 | C1S07-X2 | 1756-OB32-20 | DO | 24 VDC energized | XV-40203B | 0 | Slurry feed-out Spray dryer infeed tank | XV-40203B_DO_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
150 | C1 | 7 | 21 | C1S07,21 | C1S07-X2 | 1756-OB32-21 | DO | 24 VDC energized | XV-40203C | 0 | Water washing line outlet Spray dryer infeed tank | XV-40203C_DO_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
151 | C1 | 7 | 22 | C1S07,22 | C1S07-X2 | 1756-OB32-22 | DO | 24 VDC energized | XV-40203D | 0 | CIP water washing Spray dryer infeed tank | XV-40203D_DO_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
152 | C1 | 7 | 23 | C1S07,23 | C1S07-X2 | 1756-OB32-23 | DO | 24 VDC energized | XV-40203E | 0 | CIP hight pressure water washing Spray dryer infeed tank | XV-40203E_DO_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
153 | C1 | 7 | 24 | C1S07,24 | C1S07-X2 | 1756-OB32-24 | DO | 24 VDC energized | SV-40201 | 0 | Water service pH analyzer in pH Adjustment tank 1 | SV-40201_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
154 | C1 | 7 | 25 | C1S07,25 | C1S07-X2 | 1756-OB32-25 | DO | 24 VDC energized | SV-40202 | 0 | Water service pH analyzer in pH Adjustment tank 2 | SV-40202_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
155 | C1 | 7 | 26 | C1S07,26 | C1S07-X2 | 1756-OB32-26 | DO | 24 VDC energized | SV-40203 | 0 | Air service pH analyzer in pH Adjustment tank 1 | SV-40203_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
156 | C1 | 7 | 27 | C1S07,27 | C1S07-X2 | 1756-OB32-27 | DO | 24 VDC energized | SV-40204 | 0 | Air service pH analyzer in pH Adjustment tank 2 | SV-40204_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
157 | C1 | 7 | 28 | C1S07,28 | C1S07-X2 | 1756-OB32-28 | DO | 24 VDC energized | XV-40201A | 0 | Slurry feed-in pH Adjustment tank 1 | XV-40201A_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
158 | C1 | 7 | 29 | C1S07,29 | C1S07-X2 | 1756-OB32-29 | DO | 24 VDC energized | XV-40201B | 0 | Slurry feed-out pH Adjustment tank 1 | XV-40201B_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
159 | C1 | 7 | 30 | C1S07,30 | C1S07-X2 | 1756-OB32-30 | DO | 24 VDC energized | XV-40201C | 0 | Water washing line outlet pH Adjustment tank 1 | XV-40201C_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
160 | C1 | 7 | 31 | C1S07,31 | C1S07-X2 | 1756-OB32-31 | DO | 24 VDC energized | XV-40201D | 0 | Slurry circulation pH Adjustment tank 1 | XV-40201D_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
161 | C1 | 8 | 0 | C1S08,00 | C1S08-X1 | 1756-OB32-0 | DO | 24 VDC energized | XV-40201E | 0 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | XV-40201E_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
162 | C1 | 8 | 1 | C1S08,01 | C1S08-X1 | 1756-OB32-1 | DO | 24 VDC energized | XV-40201F | 0 | Slurry feed-to spray dry tank | XV-40201F_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
163 | C1 | 8 | 2 | C1S08,02 | C1S08-X1 | 1756-OB32-2 | DO | 24 VDC energized | XV-40201G | 0 | CIP water washing pH Adjustment tank 1 | XV-40201G_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
164 | C1 | 8 | 3 | C1S08,03 | C1S08-X1 | 1756-OB32-3 | DO | 24 VDC energized | XV-40201H | 0 | CIP Hight pressure water washing pH Adjustment tank 1 | XV-40201H_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
165 | C1 | 8 | 4 | C1S08,04 | C1S08-X1 | 1756-OB32-4 | DO | 24 VDC energized | XV-40202A | 0 | Slurry feed-in pH Adjustment tank 2 | XV-40202A_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
166 | C1 | 8 | 5 | C1S08,05 | C1S08-X1 | 1756-OB32-5 | DO | 24 VDC energized | XV-40202B | 0 | Slurry feed-out pH Adjustment tank 2 | XV-40202B_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
167 | C1 | 8 | 6 | C1S08,06 | C1S08-X1 | 1756-OB32-6 | DO | 24 VDC energized | XV-40202C | 0 | Water washing line outlet pH Adjustment tank 2 | XV-40202C_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
168 | C1 | 8 | 7 | C1S08,07 | C1S08-X1 | 1756-OB32-7 | DO | 24 VDC energized | XV-40202D | 0 | Slurry circulation pH Adjustment tank 2 | XV-40202D_DO_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
169 | C1 | 8 | 8 | C1S08,08 | C1S08-X1 | 1756-OB32-8 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
170 | C1 | 8 | 9 | C1S08,09 | C1S08-X1 | 1756-OB32-9 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
171 | C1 | 8 | 10 | C1S08,10 | C1S08-X1 | 1756-OB32-10 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
172 | C1 | 8 | 11 | C1S08,11 | C1S08-X1 | 1756-OB32-11 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
173 | C1 | 8 | 12 | C1S08,12 | C1S08-X1 | 1756-OB32-12 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
174 | C1 | 8 | 13 | C1S08,13 | C1S08-X1 | 1756-OB32-13 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
175 | C1 | 8 | 14 | C1S08,14 | C1S08-X1 | 1756-OB32-14 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
176 | C1 | 8 | 15 | C1S08,15 | C1S08-X1 | 1756-OB32-15 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
177 | C1 | 8 | 16 | C1S08,16 | C1S08-X2 | 1756-OB32-16 | DO | 24 VDC energized | SV-60201 | 0 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) | SV-60201_DO_1 | 3-25-01-602-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
178 | C1 | 8 | 17 | C1S08,17 | C1S08-X2 | 1756-OB32-17 | DO | 24 VDC energized | SV-60202 | 0 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) | SV-60202_DO_1 | 3-25-01-602-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
179 | C1 | 8 | 18 | C1S08,18 | C1S08-X2 | 1756-OB32-18 | DO | 24 VDC energized | SV-60230 | 0 | PA On/Off Valve for Cyclone Air Hammer 27 (CYCL-21) | SV-60230_DO_1 | 3-25-01-602-PD-04 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
180 | C1 | 8 | 19 | C1S08,19 | C1S08-X2 | 1756-OB32-19 | DO | 24 VDC energized | SV-60203 | 0 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) | SV-60203_DO_1 | 3-25-01-602-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
181 | C1 | 8 | 20 | C1S08,20 | C1S08-X2 | 1756-OB32-20 | DO | 24 VDC energized | SV-60240A | 0 | PA On/Off Valve for Cyclone Air Hammer 29A (BGHS-21) | SV-60240A_DO_1 | 3-25-01-602-PD-05 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
182 | C1 | 8 | 21 | C1S08,21 | C1S08-X2 | 1756-OB32-21 | DO | 24 VDC energized | SV-60231 | 0 | PA On/Off Valve for Cyclone Air Hammer 28 (CYCL-22) | SV-60231_DO_1 | 3-25-01-602-PD-04 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
183 | C1 | 8 | 22 | C1S08,22 | C1S08-X2 | 1756-OB32-22 | DO | 24 VDC energized | SV-60240B | 0 | PA On/Off Valve for Cyclone Air Hammer 29B (BGHS-21) | SV-60240B_DO_1 | 3-25-01-602-PD-05 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
184 | C1 | 8 | 23 | C1S08,23 | C1S08-X2 | 1756-OB32-23 | DO | 24 VDC energized | SV-60240C | 0 | PA On/Off Valve for Cyclone Air Hammer 29C (BGHS-21) | SV-60240C_DO_1 | 3-25-01-602-PD-05 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
185 | C1 | 8 | 24 | C1S08,24 | C1S08-X2 | 1756-OB32-24 | DO | - | XV-60240D | - | - | XV-60240D_DO_1 | 325-01-600-PD-05 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
186 | C1 | 8 | 25 | C1S08,25 | C1S08-X2 | 1756-OB32-25 | DO | 24 VDC energized | XV-60251 | 0 | Liquid On/Off Valve for Drain Pipe (PIPE) | XV-60251_DO_1 | 3-25-01-602-PD-01 | JB-601 | Spray Dryer 1st Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
187 | C1 | 8 | 26 | C1S08,26 | C1S08-X2 | 1756-OB32-26 | DO | 24 VDC energized | XV-60202 | 0 | High Pressure Water On/Off Valve for Drain Pipe | XV-60202_DO_1 | 3-25-01-602-PD-11 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
188 | C1 | 8 | 27 | C1S08,27 | C1S08-X2 | 1756-OB32-27 | DO | 24 VDC energized,Dry Contact | XV-60205A | 0 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) | XV-60205A_DO_1 | 3-25-01-602-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
189 | C1 | 8 | 28 | C1S08,28 | C1S08-X2 | 1756-OB32-28 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
190 | C1 | 8 | 29 | C1S08,29 | C1S08-X2 | 1756-OB32-29 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
191 | C1 | 8 | 30 | C1S08,30 | C1S08-X2 | 1756-OB32-30 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
192 | C1 | 8 | 31 | C1S08,31 | C1S08-X2 | 1756-OB32-31 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
193 | C1 | 9 | 0 | C1S09,00 | C1S09-X1 | 1756-IF16-0 | AI | 4 - 20 mA,Pulse | FT-40201 | Coriolis Flow Transmitter | Slurry flowrate & density check transfer line | FT-40201_AI_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0
194 | C1 | 9 | 1 | C1S09,01 | C1S09-X1 | 1756-IF16-1 | AI | 4 - 20 mA,Pulse | FT-40201 | Coriolis Flow Transmitter | Slurry flowrate & density check transfer line | FT-40201_AI_2 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0
195 | C1 | 9 | 2 | C1S09,02 | C1S09-X1 | 1756-IF16-2 | AI | 4 - 20 mA,Pulse | FT-40202 | Magnetic Flow Transmitter | Feed Slurry Flow Transmitter for Pipe (PIPE) | FT-40202_AI_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0
196 | C1 | 9 | 3 | C1S09,03 | C1S09-X1 | 1756-IF16-3 | AI | 4 - 20 mA | LT-40203 | Level Transmitter | Level transmitter in Spray dryer infeed tank | LT-40203_AI_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
197 | C1 | 9 | 4 | C1S09,04 | C1S09-X1 | 1756-IF16-4 | AI | 4 - 20 mA | LT-40201 | Level Transmitter | Level transmitter in pH Adjustment tank 1 | LT-40201_AI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
198 | C1 | 9 | 5 | C1S09,05 | C1S09-X1 | 1756-IF16-5 | AI | 4 - 20 mA | LT-40202 | Level Transmitter | Level transmitter in pH Adjustment tank 2 | LT-40202_AI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
199 | C1 | 9 | 6 | C1S09,06 | C1S09-X1 | 1756-IF16-6 | AI | 4 - 20 mA | pHT-40201 | PH Transmitter | pH analyzer in pH Adjustment tank 1 | pHT-40201_AI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
200 | C1 | 9 | 7 | C1S09,07 | C1S09-X1 | 1756-IF16-7 | AI | 4 - 20 mA | pHT-40202 | PH Transmitter | pH analyzer in pH Adjustment tank 2 | pHT-40202_AI_1 | 3-25-01-402-PD-01 | JB-401 | Infeed 2nd Floor | PH Adjustment | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
201 | C1 | 9 | 8 | C1S09,08 | C1S09-X1 | 1756-IF16-8 | AI | 4 - 20 mA | PT-40201 | Pressure Transmitter | Pressure Transmitter for Inlet Filter Strainer (FSTR-11) | PT-40201_AI_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
202 | C1 | 9 | 9 | C1S09,09 | C1S09-X1 | 1756-IF16-9 | AI | 4 - 20 mA | PT-40202 | Pressure Transmitter | Feed Slurry Pressure Transmitter for Pipe (PIPE) | PT-40202_AI_1 | 3-25-01-402-PD-02 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
203 | C1 | 9 | 10 | C1S09,10 | C1S09-X1 | 1756-IF16-10 | AI | 4 - 20 mA | PT-60202 | Pressure Transmitter | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | PT-60202_AI_1 | 3-25-01-602-PD-01 | JB-401 | Infeed 2nd Floor | Infeed Tank | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
204 | C1 | 9 | 11 | C1S09,11 | C1S09-X1 | 1756-IF16-11 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
205 | C1 | 9 | 12 | C1S09,12 | C1S09-X1 | 1756-IF16-12 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
206 | C1 | 9 | 13 | C1S09,13 | C1S09-X1 | 1756-IF16-13 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
207 | C1 | 9 | 14 | C1S09,14 | C1S09-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
208 | C1 | 9 | 15 | C1S09,15 | C1S09-X1 | 1756-IF16-15 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-401 | Infeed 2nd Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
209 | C1 | 10 | 0 | C1S10,00 | C1S10-X1 | 1756-IF16-0 | AI | 4 - 20 mA | DPI-60240 | 0 | Gas Pressure Differntial Pressure (Bag House Air Pulsing) | DPI-60240_AI_1 | 325-01-600-PD-05 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
210 | C1 | 10 | 1 | C1S10,01 | C1S10-X1 | 1756-IF16-1 | AI | 4 - 20 mA | DPT-60202 | Differential Pressure Transmitte | Gas Pressure Differential Transmitter for Air Filter (FICA-31) | DPT-60202_AI_1 | 3-25-01-602-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
211 | C1 | 10 | 2 | C1S10,02 | C1S10-X1 | 1756-IF16-2 | AI | 4 - 20 mA | FT-60201 | 0 | Gas Flow Transmitter for Cooling Conveying Cold Air Duct (DTCA-32) | FT-60201_AI_1 | 3-25-01-602-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
212 | C1 | 10 | 3 | C1S10,03 | C1S10-X1 | 1756-IF16-3 | AI | 4 - 20 mA | FT-60204 | 0 | Compressed air Flow | FT-60204_AI_1 | 3-25-01-602-PD-10 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
213 | C1 | 10 | 4 | C1S10,04 | C1S10-X1 | 1756-IF16-4 | AI | 4 - 20 mA | FT-61307 | 0 | Compressed air Flow | FT-61307_AI_1 | 3-25-01-613-PD-04 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
214 | C1 | 10 | 5 | C1S10,05 | C1S10-X1 | 1756-IF16-5 | AI | 4 - 20 mA | PT-60203 | Pressure Transmitter | Gas Pressure Transmitter for Cool Air Duct (DTCA-32) | PT-60203_AI_1 | 3-25-01-602-PD-08 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
215 | C1 | 10 | 6 | C1S10,06 | C1S10-X1 | 1756-IF16-6 | AI | 4 - 20 mA | PT-60204 | Pressure Transmitter | Pressure transmitter | PT-60204_AI_1 | 3-25-01-602-PD-10 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
216 | C1 | 10 | 7 | C1S10,07 | C1S10-X1 | 1756-IF16-7 | AI | 4 - 20 mA | PT-60205 | Pressure Transmitter | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | PT-60205_AI_1 | 3-25-01-602-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | =CA1+MCP-M1 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
217 | C1 | 10 | 8 | C1S10,08 | C1S10-X1 | 1756-IF16-8 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
218 | C1 | 10 | 9 | C1S10,09 | C1S10-X1 | 1756-IF16-9 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
219 | C1 | 10 | 10 | C1S10,10 | C1S10-X1 | 1756-IF16-10 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
220 | C1 | 10 | 11 | C1S10,11 | C1S10-X1 | 1756-IF16-11 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
221 | C1 | 10 | 12 | C1S10,12 | C1S10-X1 | 1756-IF16-12 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
222 | C1 | 10 | 13 | C1S10,13 | C1S10-X1 | 1756-IF16-13 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
223 | C1 | 10 | 14 | C1S10,14 | C1S10-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
224 | C1 | 10 | 15 | C1S10,15 | C1S10-X1 | 1756-IF16-15 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-601 | Spray Dryer 1st Floor | - | - | =CA1+MCP-M1 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
225 | C2 | 1 | 0 | C2S01,00 | C2S01-X1 | 1756-IB32-0 | DI | Dry Contact | FS-40204 | Flow Switch | Jet Cooker | FS-40204_DI_1 | 325-01-402-PD-01 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
226 | C2 | 1 | 1 | C2S01,01 | C2S01-X1 | 1756-IB32-1 | DI | Dry Contact | FS-40205 | Flow Switch | Jet Cooker | FS-40205_DI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
227 | C2 | 1 | 2 | C2S01,02 | C2S01-X1 | 1756-IB32-2 | DI | 4 - 20 mA,Pulse | FT-40221 | Coriolis Flow Transmitter | Jet Cooker | FT-40221_DI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0
228 | C2 | 1 | 3 | C2S01,03 | C2S01-X1 | 1756-IB32-3 | DI | 4 - 20 mA,Pulse | FT-40222 | Coriolis Flow Transmitter | Jet Cooker | FT-40222_DI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0
229 | C2 | 1 | 4 | C2S01,04 | C2S01-X1 | 1756-IB32-4 | DI | Dry Contact | HV-40207 | Manual Valve With Position Switch | Jet Cooker | HV-40207_DI_1 | 325-01-402-PD-01 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
230 | C2 | 1 | 5 | C2S01,05 | C2S01-X1 | 1756-IB32-5 | DI | Dry Contact | HV-40208 | Manual Valve With Position Switch | Jet Cooker | HV-40208_DI_1 | 325-01-402-PD-01 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
231 | C2 | 1 | 6 | C2S01,06 | C2S01-X1 | 1756-IB32-6 | DI | 24 VDC energized | XV-40203F | 0 | Jet Cooker | XV-40203F_DI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
232 | C2 | 1 | 7 | C2S01,07 | C2S01-X1 | 1756-IB32-7 | DI | 24 VDC energized | XV-40203F | 0 | Jet Cooker | XV-40203F_DI_2 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
233 | C2 | 1 | 8 | C2S01,08 | C2S01-X1 | 1756-IB32-8 | DI | 24 VDC energized | XV-40204B | 0 | Jet Cooker | XV-40204B_DI_1 | 325-01-402-PD-01 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
234 | C2 | 1 | 9 | C2S01,09 | C2S01-X1 | 1756-IB32-9 | DI | 24 VDC energized | XV-40204B | 0 | Jet Cooker | XV-40204B_DI_2 | 325-01-402-PD-01 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
235 | C2 | 1 | 10 | C2S01,10 | C2S01-X1 | 1756-IB32-10 | DI | 24 VDC energized | XV-40204C | 0 | Jet Cooker | XV-40204C_DI_1 | 325-01-402-PD-01 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
236 | C2 | 1 | 11 | C2S01,11 | C2S01-X1 | 1756-IB32-11 | DI | 24 VDC energized | XV-40204C | 0 | Jet Cooker | XV-40204C_DI_2 | 325-01-402-PD-01 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
237 | C2 | 1 | 12 | C2S01,12 | C2S01-X1 | 1756-IB32-12 | DI | 24 VDC energized | XV-40205A | 0 | Jet Cooker | XV-40205A_DI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
238 | C2 | 1 | 13 | C2S01,13 | C2S01-X1 | 1756-IB32-13 | DI | 24 VDC energized | XV-40205A | 0 | Jet Cooker | XV-40205A_DI_2 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
239 | C2 | 1 | 14 | C2S01,14 | C2S01-X1 | 1756-IB32-14 | DI | 24 VDC energized | XV-40205B | 0 | Jet Cooker | XV-40205B_DI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
240 | C2 | 1 | 15 | C2S01,15 | C2S01-X1 | 1756-IB32-15 | DI | 24 VDC energized | XV-40205B | 0 | Jet Cooker | XV-40205B_DI_2 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
241 | C2 | 1 | 16 | C2S01,16 | C2S01-X2 | 1756-IB32-16 | DI | 24 VDC energized | XV-40205C | 0 | Jet Cooker | XV-40205C_DI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
242 | C2 | 1 | 17 | C2S01,17 | C2S01-X2 | 1756-IB32-17 | DI | 24 VDC energized | XV-40205C | 0 | Jet Cooker | XV-40205C_DI_2 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
243 | C2 | 1 | 18 | C2S01,18 | C2S01-X2 | 1756-IB32-18 | DI | 24 VDC energized | XV-40205D | 0 | Jet Cooker | XV-40205D_DI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
244 | C2 | 1 | 19 | C2S01,19 | C2S01-X2 | 1756-IB32-19 | DI | 24 VDC energized | XV-40205D | 0 | Jet Cooker | XV-40205D_DI_2 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
245 | C2 | 1 | 20 | C2S01,20 | C2S01-X2 | 1756-IB32-20 | DI | 24 VDC energized | XV-40205F | 0 | Jet Cooker | XV-40205F_DI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
246 | C2 | 1 | 21 | C2S01,21 | C2S01-X2 | 1756-IB32-21 | DI | 24 VDC energized | XV-40205F | 0 | Jet Cooker | XV-40205F_DI_2 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
247 | C2 | 1 | 22 | C2S01,22 | C2S01-X2 | 1756-IB32-22 | DI | 24 VDC energized | XV-40222 | 0 | Jet Cooker | XV-40222_DI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
248 | C2 | 1 | 23 | C2S01,23 | C2S01-X2 | 1756-IB32-23 | DI | 24 VDC energized | XV-40222 | 0 | Jet Cooker | XV-40222_DI_2 | - | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
249 | C2 | 1 | 24 | C2S01,24 | C2S01-X2 | 1756-IB32-24 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_2 | - | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
250 | C2 | 1 | 25 | C2S01,25 | C2S01-X2 | 1756-IB32-25 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_2 | - | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
251 | C2 | 1 | 26 | C2S01,26 | C2S01-X2 | 1756-IB32-26 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_2 | - | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
252 | C2 | 1 | 27 | C2S01,27 | C2S01-X2 | 1756-IB32-27 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_2 | - | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
253 | C2 | 1 | 28 | C2S01,28 | C2S01-X2 | 1756-IB32-28 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_2 | - | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
254 | C2 | 1 | 29 | C2S01,29 | C2S01-X2 | 1756-IB32-29 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_2 | - | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
255 | C2 | 1 | 30 | C2S01,30 | C2S01-X2 | 1756-IB32-30 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_2 | - | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
256 | C2 | 1 | 31 | C2S01,31 | C2S01-X2 | 1756-IB32-31 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_2 | - | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
257 | C2 | 2 | 0 | C2S02,00 | C2S02-X1 | 1756-IB32-0 | DI | 4 - 20 mA | FT-60202 | 0 | Steam feed to Spray dryer | FT-60202_DI_1 | 3-25-01-602-PD-09 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0
258 | C2 | 2 | 1 | C2S02,01 | C2S02-X1 | 1756-IB32-1 | DI | Dry Contact | LSH-60251 | 0 | Water Level Switch High for Fire Deluge Pipe (FWDP-22) | LSH-60251_DI_1 | 3-25-01-602-PD-04 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
259 | C2 | 2 | 2 | C2S02,02 | C2S02-X1 | 1756-IB32-2 | DI | Dry Contact | PSL-60220 | 0 | Gas Pressure Switch Low for Spray Chamber (CHAM-21) | PSL-60220_DI_1 | 3-25-01-602-PD-04 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
260 | C2 | 2 | 3 | C2S02,03 | C2S02-X1 | 1756-IB32-3 | DI | Dry Contact | TSH-60230 | 0 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | TSH-60230_DI_1 | 3-25-01-602-PD-04 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 3rd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
261 | C2 | 2 | 4 | C2S02,04 | C2S02-X1 | 1756-IB32-4 | DI | Dry Contact | TSH-60240 | 0 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | TSH-60240_DI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
262 | C2 | 2 | 5 | C2S02,05 | C2S02-X1 | 1756-IB32-5 | DI | Dry Contact | TSH-60241A | 0 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | TSH-60241A_DI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
263 | C2 | 2 | 6 | C2S02,06 | C2S02-X1 | 1756-IB32-6 | DI | Dry Contact | TSH-60242A | 0 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | TSH-60242A_DI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 3rd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
264 | C2 | 2 | 7 | C2S02,07 | C2S02-X1 | 1756-IB32-7 | DI | Dry Contact | TSH-60243A | 0 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | TSH-60243A_DI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
265 | C2 | 2 | 8 | C2S02,08 | C2S02-X1 | 1756-IB32-8 | DI | Dry Contact | TSL-60241B | 0 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | TSL-60241B_DI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
266 | C2 | 2 | 9 | C2S02,09 | C2S02-X1 | 1756-IB32-9 | DI | Dry Contact | TSL-60242B | 0 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | TSL-60242B_DI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 3rd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
267 | C2 | 2 | 10 | C2S02,10 | C2S02-X1 | 1756-IB32-10 | DI | Dry Contact | TSL-60243B | 0 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | TSL-60243B_DI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
268 | C2 | 2 | 11 | C2S02,11 | C2S02-X1 | 1756-IB32-11 | DI | Dry Contact | XA-60240A | 0 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | XA-60240A_DI_1 | 325-01-600-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
269 | C2 | 2 | 12 | C2S02,12 | C2S02-X1 | 1756-IB32-12 | DI | Dry Contact | XA-60240B | 0 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | XA-60240B_DI_1 | 325-01-600-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
270 | C2 | 2 | 13 | C2S02,13 | C2S02-X1 | 1756-IB32-13 | DI | Dry Contact | XA-60241A | 0 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | XA-60241A_DI_1 | 325-01-600-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
271 | C2 | 2 | 14 | C2S02,14 | C2S02-X1 | 1756-IB32-14 | DI | Dry Contact | XA-60241B | 0 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | XA-60241B_DI_1 | 325-01-600-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
272 | C2 | 2 | 15 | C2S02,15 | C2S02-X1 | 1756-IB32-15 | DI | Dry Contact | XA-60242A | 0 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | XA-60242A_DI_1 | 325-01-600-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 3rd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
273 | C2 | 2 | 16 | C2S02,16 | C2S02-X2 | 1756-IB32-16 | DI | Dry Contact | XA-60242B | 0 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | XA-60242B_DI_1 | 325-01-600-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 3rd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
274 | C2 | 2 | 17 | C2S02,17 | C2S02-X2 | 1756-IB32-17 | DI | Dry Contact | XA-60243A | 0 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | XA-60243A_DI_1 | 325-01-600-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
275 | C2 | 2 | 18 | C2S02,18 | C2S02-X2 | 1756-IB32-18 | DI | Dry Contact | XA-60243B | 0 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | XA-60243B_DI_1 | 325-01-600-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
276 | C2 | 2 | 19 | C2S02,19 | C2S02-X2 | 1756-IB32-19 | DI | 24 VDC energized | XV-60214 | 0 | Steam feed to Spray dryer | XV-60214_DI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
277 | C2 | 2 | 20 | C2S02,20 | C2S02-X2 | 1756-IB32-20 | DI | 24 VDC energized | XV-60214 | 0 | Steam feed to Spray dryer | XV-60214_DI_2 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
278 | C2 | 2 | 21 | C2S02,21 | C2S02-X2 | 1756-IB32-21 | DI | 24 VDC energized,Dry Contact | XV-60241 | 0 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | XV-60241_DI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
279 | C2 | 2 | 22 | C2S02,22 | C2S02-X2 | 1756-IB32-22 | DI | 24 VDC energized,Dry Contact | XV-60241 | 0 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | XV-60241_DI_2 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
280 | C2 | 2 | 23 | C2S02,23 | C2S02-X2 | 1756-IB32-23 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-602 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
281 | C2 | 2 | 24 | C2S02,24 | C2S02-X2 | 1756-IB32-24 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-602 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
282 | C2 | 2 | 25 | C2S02,25 | C2S02-X2 | 1756-IB32-25 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-602 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
283 | C2 | 2 | 26 | C2S02,26 | C2S02-X2 | 1756-IB32-26 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-602 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
284 | C2 | 2 | 27 | C2S02,27 | C2S02-X2 | 1756-IB32-27 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-602 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
285 | C2 | 2 | 28 | C2S02,28 | C2S02-X2 | 1756-IB32-28 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-602 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
286 | C2 | 2 | 29 | C2S02,29 | C2S02-X2 | 1756-IB32-29 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-602 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
287 | C2 | 2 | 30 | C2S02,30 | C2S02-X2 | 1756-IB32-30 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-602 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
288 | C2 | 2 | 31 | C2S02,31 | C2S02-X2 | 1756-IB32-31 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-602 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
289 | C2 | 3 | 0 | C2S03,00 | C2S03-X1 | 1756-IB32-0 | DI | Dry Contact | XA-FH-60210A | 0 | BMS PANEL POWER ON for AHTR-21 | XA-FH-60210A_DI_1 | 325-01-600-PD-06 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
290 | C2 | 3 | 1 | C2S03,01 | C2S03-X1 | 1756-IB32-1 | DI | Dry Contact | XA-FH-60210B | 0 | BMS Burner High Fire Purge for AHTR-21 | XA-FH-60210B_DI_1 | 325-01-600-PD-06 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
291 | C2 | 3 | 2 | C2S03,02 | C2S03-X1 | 1756-IB32-2 | DI | Dry Contact | XA-FH-60210C | 0 | BMS Burner On for AHTR-21 | XA-FH-60210C_DI_1 | 325-01-600-PD-06 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
292 | C2 | 3 | 3 | C2S03,03 | C2S03-X1 | 1756-IB32-3 | DI | Dry Contact | XA-FH-60210D | 0 | BMS BMS Lockout for AHTR-21 | XA-FH-60210D_DI_1 | 325-01-600-PD-06 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
293 | C2 | 3 | 4 | C2S03,04 | C2S03-X1 | 1756-IB32-4 | DI | Dry Contact | XA-FH-60210E | 0 | BMS Remote Modet for AHTR-21 | XA-FH-60210E_DI_1 | 325-01-600-PD-06 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
294 | C2 | 3 | 8 | C2S03,08 | C2S03-X1 | 1756-IB32-8 | DI | 24 VDC energized | SV-60207 | 0 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) | SV-60207_DI_1 | 3-25-01-602-PD-07 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
295 | C2 | 3 | 9 | C2S03,09 | C2S03-X1 | 1756-IB32-9 | DI | 24 VDC energized | SV-60207 | 0 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) | SV-60207_DI_2 | 3-25-01-602-PD-07 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
296 | C2 | 3 | 10 | C2S03,10 | C2S03-X1 | 1756-IB32-10 | DI | - | XV-60264 | - | - | XV-60264_DI_1 | 325-01-600-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
297 | C2 | 3 | 11 | C2S03,11 | C2S03-X1 | 1756-IB32-11 | DI | - | XV-60264 | - | - | XV-60264_DI_2 | 325-01-600-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
298 | C2 | 3 | 12 | C2S03,12 | C2S03-X1 | 1756-IB32-12 | DI | 24 VDC energized,Dry Contact | XV-60264FN | 0 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) | XV-60264FN_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
299 | C2 | 3 | 13 | C2S03,13 | C2S03-X1 | 1756-IB32-13 | DI | 24 VDC energized,Dry Contact | XV-60264FN | 0 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) | XV-60264FN_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
300 | C2 | 3 | 14 | C2S03,14 | C2S03-X1 | 1756-IB32-14 | DI | 24 VDC energized,Dry Contact | XV-60264FP | 0 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) | XV-60264FP_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
301 | C2 | 3 | 15 | C2S03,15 | C2S03-X1 | 1756-IB32-15 | DI | 24 VDC energized,Dry Contact | XV-60264FP | 0 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) | XV-60264FP_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
302 | C2 | 3 | 16 | C2S03,16 | C2S03-X2 | 1756-IB32-16 | DI | 24 VDC energized | XV-60201 | 0 | Steam feed to Spray dryer | XV-60201_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
303 | C2 | 3 | 17 | C2S03,17 | C2S03-X2 | 1756-IB32-17 | DI | 24 VDC energized | XV-60201 | 0 | Steam feed to Spray dryer | XV-60201_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
304 | C2 | 3 | 18 | C2S03,18 | C2S03-X2 | 1756-IB32-18 | DI | 24 VDC energized,Dry Contact | XV-60264FQ | 0 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) | XV-60264FQ_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
305 | C2 | 3 | 19 | C2S03,19 | C2S03-X2 | 1756-IB32-19 | DI | 24 VDC energized,Dry Contact | XV-60264FQ | 0 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) | XV-60264FQ_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
306 | C2 | 3 | 20 | C2S03,20 | C2S03-X2 | 1756-IB32-20 | DI | - | XV-60261 | - | - | XV-60261_DI_1 | 325-01-600-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
307 | C2 | 3 | 21 | C2S03,21 | C2S03-X2 | 1756-IB32-21 | DI | - | XV-60261 | - | - | XV-60261_DI_2 | 325-01-600-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
308 | C2 | 3 | 22 | C2S03,22 | C2S03-X2 | 1756-IB32-22 | DI | 24 VDC energized,Dry Contact | XV-60264FR | 0 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) | XV-60264FR_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
309 | C2 | 3 | 23 | C2S03,23 | C2S03-X2 | 1756-IB32-23 | DI | 24 VDC energized,Dry Contact | XV-60264FR | 0 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) | XV-60264FR_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
310 | C2 | 3 | 24 | C2S03,24 | C2S03-X2 | 1756-IB32-24 | DI | 24 VDC energized,Dry Contact | XV-60261FA | 0 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) | XV-60261FA_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
311 | C2 | 3 | 25 | C2S03,25 | C2S03-X2 | 1756-IB32-25 | DI | 24 VDC energized,Dry Contact | XV-60261FA | 0 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) | XV-60261FA_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
312 | C2 | 3 | 26 | C2S03,26 | C2S03-X2 | 1756-IB32-26 | DI | 24 VDC energized,Dry Contact | XV-60264SN | 0 | Steam On/Off Valve for Nozzle #13 (ATVM-11D) | XV-60264SN_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
313 | C2 | 3 | 27 | C2S03,27 | C2S03-X2 | 1756-IB32-27 | DI | 24 VDC energized,Dry Contact | XV-60264SN | 0 | Steam On/Off Valve for Nozzle #13 (ATVM-11D) | XV-60264SN_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
314 | C2 | 3 | 28 | C2S03,28 | C2S03-X2 | 1756-IB32-28 | DI | 24 VDC energized,Dry Contact | XV-60261FB | 0 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) | XV-60261FB_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
315 | C2 | 3 | 29 | C2S03,29 | C2S03-X2 | 1756-IB32-29 | DI | 24 VDC energized,Dry Contact | XV-60261FB | 0 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) | XV-60261FB_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
316 | C2 | 3 | 30 | C2S03,30 | C2S03-X2 | 1756-IB32-30 | DI | 24 VDC energized,Dry Contact | XV-60264SP | 0 | Steam On/Off Valve for Nozzle #14 (ATVM-11D) | XV-60264SP_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
317 | C2 | 3 | 31 | C2S03,31 | C2S03-X2 | 1756-IB32-31 | DI | 24 VDC energized,Dry Contact | XV-60264SP | 0 | Steam On/Off Valve for Nozzle #14 (ATVM-11D) | XV-60264SP_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
318 | C2 | 4 | 0 | C2S04,00 | C2S04-X1 | 1756-IB32-0 | DI | 24 VDC energized,Dry Contact | XV-60261FC | 0 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) | XV-60261FC_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
319 | C2 | 4 | 1 | C2S04,01 | C2S04-X1 | 1756-IB32-1 | DI | 24 VDC energized,Dry Contact | XV-60261FC | 0 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) | XV-60261FC_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
320 | C2 | 4 | 2 | C2S04,02 | C2S04-X1 | 1756-IB32-2 | DI | 24 VDC energized,Dry Contact | XV-60264SQ | 0 | Steam On/Off Valve for Nozzle #15 (ATVM-11D) | XV-60264SQ_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
321 | C2 | 4 | 3 | C2S04,03 | C2S04-X1 | 1756-IB32-3 | DI | 24 VDC energized,Dry Contact | XV-60264SQ | 0 | Steam On/Off Valve for Nozzle #15 (ATVM-11D) | XV-60264SQ_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
322 | C2 | 4 | 4 | C2S04,04 | C2S04-X1 | 1756-IB32-4 | DI | 24 VDC energized,Dry Contact | XV-60261FD | 0 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) | XV-60261FD_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
323 | C2 | 4 | 5 | C2S04,05 | C2S04-X1 | 1756-IB32-5 | DI | 24 VDC energized,Dry Contact | XV-60261FD | 0 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) | XV-60261FD_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
324 | C2 | 4 | 6 | C2S04,06 | C2S04-X1 | 1756-IB32-6 | DI | 24 VDC energized,Dry Contact | XV-60264SR | 0 | Steam On/Off Valve for Nozzle #16 (ATVM-11D) | XV-60264SR_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
325 | C2 | 4 | 7 | C2S04,07 | C2S04-X1 | 1756-IB32-7 | DI | 24 VDC energized,Dry Contact | XV-60264SR | 0 | Steam On/Off Valve for Nozzle #16 (ATVM-11D) | XV-60264SR_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
326 | C2 | 4 | 8 | C2S04,08 | C2S04-X1 | 1756-IB32-8 | DI | 24 VDC energized,Dry Contact | XV-60261SA | 0 | Steam On/Off Valve for Nozzle #1 (ATVM-11A) | XV-60261SA_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
327 | C2 | 4 | 9 | C2S04,09 | C2S04-X1 | 1756-IB32-9 | DI | 24 VDC energized,Dry Contact | XV-60261SA | 0 | Steam On/Off Valve for Nozzle #1 (ATVM-11A) | XV-60261SA_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
328 | C2 | 4 | 10 | C2S04,10 | C2S04-X1 | 1756-IB32-10 | DI | 24 VDC energized,Dry Contact | XV-60261SB | 0 | Steam On/Off Valve for Nozzle #2 (ATVM-11A) | XV-60261SB_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
329 | C2 | 4 | 11 | C2S04,11 | C2S04-X1 | 1756-IB32-11 | DI | 24 VDC energized,Dry Contact | XV-60261SB | 0 | Steam On/Off Valve for Nozzle #2 (ATVM-11A) | XV-60261SB_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
330 | C2 | 4 | 12 | C2S04,12 | C2S04-X1 | 1756-IB32-12 | DI | 24 VDC energized,Dry Contact | XV-60261SC | 0 | Steam On/Off Valve for Nozzle #3 (ATVM-11A) | XV-60261SC_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
331 | C2 | 4 | 13 | C2S04,13 | C2S04-X1 | 1756-IB32-13 | DI | 24 VDC energized,Dry Contact | XV-60261SC | 0 | Steam On/Off Valve for Nozzle #3 (ATVM-11A) | XV-60261SC_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
332 | C2 | 4 | 14 | C2S04,14 | C2S04-X1 | 1756-IB32-14 | DI | 24 VDC energized,Dry Contact | XV-60261SD | 0 | Steam On/Off Valve for Nozzle #4 (ATVM-11A) | XV-60261SD_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
333 | C2 | 4 | 15 | C2S04,15 | C2S04-X1 | 1756-IB32-15 | DI | 24 VDC energized,Dry Contact | XV-60261SD | 0 | Steam On/Off Valve for Nozzle #4 (ATVM-11A) | XV-60261SD_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
334 | C2 | 4 | 16 | C2S04,16 | C2S04-X2 | 1756-IB32-16 | DI | - | XV-60262 | - | - | XV-60262_DI_1 | 325-01-600-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
335 | C2 | 4 | 17 | C2S04,17 | C2S04-X2 | 1756-IB32-17 | DI | - | XV-60262 | - | - | XV-60262_DI_2 | 325-01-600-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
336 | C2 | 4 | 18 | C2S04,18 | C2S04-X2 | 1756-IB32-18 | DI | 24 VDC energized,Dry Contact | XV-60262FE | 0 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) | XV-60262FE_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
337 | C2 | 4 | 19 | C2S04,19 | C2S04-X2 | 1756-IB32-19 | DI | 24 VDC energized,Dry Contact | XV-60262FE | 0 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) | XV-60262FE_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
338 | C2 | 4 | 20 | C2S04,20 | C2S04-X2 | 1756-IB32-20 | DI | 24 VDC energized,Dry Contact | XV-60262FF | 0 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) | XV-60262FF_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
339 | C2 | 4 | 21 | C2S04,21 | C2S04-X2 | 1756-IB32-21 | DI | 24 VDC energized,Dry Contact | XV-60262FF | 0 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) | XV-60262FF_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
340 | C2 | 4 | 22 | C2S04,22 | C2S04-X2 | 1756-IB32-22 | DI | 24 VDC energized,Dry Contact | XV-60262FG | 0 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) | XV-60262FG_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
341 | C2 | 4 | 23 | C2S04,23 | C2S04-X2 | 1756-IB32-23 | DI | 24 VDC energized,Dry Contact | XV-60262FG | 0 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) | XV-60262FG_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
342 | C2 | 4 | 24 | C2S04,24 | C2S04-X2 | 1756-IB32-24 | DI | 24 VDC energized,Dry Contact | XV-60262FH | 0 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) | XV-60262FH_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
343 | C2 | 4 | 25 | C2S04,25 | C2S04-X2 | 1756-IB32-25 | DI | 24 VDC energized,Dry Contact | XV-60262FH | 0 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) | XV-60262FH_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
344 | C2 | 4 | 26 | C2S04,26 | C2S04-X2 | 1756-IB32-26 | DI | 24 VDC energized,Dry Contact | XV-60262SE | 0 | Steam On/Off Valve for Nozzle #5 (ATVM-11B) | XV-60262SE_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
345 | C2 | 4 | 27 | C2S04,27 | C2S04-X2 | 1756-IB32-27 | DI | 24 VDC energized,Dry Contact | XV-60262SE | 0 | Steam On/Off Valve for Nozzle #5 (ATVM-11B) | XV-60262SE_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
346 | C2 | 4 | 28 | C2S04,28 | C2S04-X2 | 1756-IB32-28 | DI | 24 VDC energized,Dry Contact | XV-60262SF | 0 | Steam On/Off Valve for Nozzle #6 (ATVM-11B) | XV-60262SF_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
347 | C2 | 4 | 29 | C2S04,29 | C2S04-X2 | 1756-IB32-29 | DI | 24 VDC energized,Dry Contact | XV-60262SF | 0 | Steam On/Off Valve for Nozzle #6 (ATVM-11B) | XV-60262SF_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
348 | C2 | 4 | 30 | C2S04,30 | C2S04-X2 | 1756-IB32-30 | DI | 24 VDC energized,Dry Contact | XV-60262SG | 0 | Steam On/Off Valve for Nozzle #7 (ATVM-11B) | XV-60262SG_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
349 | C2 | 4 | 31 | C2S04,31 | C2S04-X2 | 1756-IB32-31 | DI | 24 VDC energized,Dry Contact | XV-60262SG | 0 | Steam On/Off Valve for Nozzle #7 (ATVM-11B) | XV-60262SG_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
350 | C2 | 5 | 0 | C2S05,00 | C2S05-X1 | 1756-IB32-0 | DI | 24 VDC energized,Dry Contact | XV-60262SH | 0 | Steam On/Off Valve for Nozzle #8 (ATVM-11B) | XV-60262SH_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
351 | C2 | 5 | 1 | C2S05,01 | C2S05-X1 | 1756-IB32-1 | DI | 24 VDC energized,Dry Contact | XV-60262SH | 0 | Steam On/Off Valve for Nozzle #8 (ATVM-11B) | XV-60262SH_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
352 | C2 | 5 | 2 | C2S05,02 | C2S05-X1 | 1756-IB32-2 | DI | - | XV-60263 | - | - | XV-60263_DI_1 | 325-01-600-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
353 | C2 | 5 | 3 | C2S05,03 | C2S05-X1 | 1756-IB32-3 | DI | - | XV-60263 | - | - | XV-60263_DI_2 | 325-01-600-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
354 | C2 | 5 | 4 | C2S05,04 | C2S05-X1 | 1756-IB32-4 | DI | 24 VDC energized,Dry Contact | XV-60263FJ | 0 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) | XV-60263FJ_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
355 | C2 | 5 | 5 | C2S05,05 | C2S05-X1 | 1756-IB32-5 | DI | 24 VDC energized,Dry Contact | XV-60263FJ | 0 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) | XV-60263FJ_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
356 | C2 | 5 | 6 | C2S05,06 | C2S05-X1 | 1756-IB32-6 | DI | 24 VDC energized,Dry Contact | XV-60263FK | 0 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) | XV-60263FK_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
357 | C2 | 5 | 7 | C2S05,07 | C2S05-X1 | 1756-IB32-7 | DI | 24 VDC energized,Dry Contact | XV-60263FK | 0 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) | XV-60263FK_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
358 | C2 | 5 | 8 | C2S05,08 | C2S05-X1 | 1756-IB32-8 | DI | 24 VDC energized,Dry Contact | XV-60263FL | 0 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) | XV-60263FL_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
359 | C2 | 5 | 9 | C2S05,09 | C2S05-X1 | 1756-IB32-9 | DI | 24 VDC energized,Dry Contact | XV-60263FL | 0 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) | XV-60263FL_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
360 | C2 | 5 | 10 | C2S05,10 | C2S05-X1 | 1756-IB32-10 | DI | 24 VDC energized,Dry Contact | XV-60263FM | 0 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) | XV-60263FM_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
361 | C2 | 5 | 11 | C2S05,11 | C2S05-X1 | 1756-IB32-11 | DI | 24 VDC energized,Dry Contact | XV-60263FM | 0 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) | XV-60263FM_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
362 | C2 | 5 | 12 | C2S05,12 | C2S05-X1 | 1756-IB32-12 | DI | 24 VDC energized,Dry Contact | XV-60263SJ | 0 | Steam On/Off Valve for Nozzle #9 (ATVM-11C) | XV-60263SJ_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
363 | C2 | 5 | 13 | C2S05,13 | C2S05-X1 | 1756-IB32-13 | DI | 24 VDC energized,Dry Contact | XV-60263SJ | 0 | Steam On/Off Valve for Nozzle #9 (ATVM-11C) | XV-60263SJ_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
364 | C2 | 5 | 14 | C2S05,14 | C2S05-X1 | 1756-IB32-14 | DI | 24 VDC energized,Dry Contact | XV-60263SK | 0 | Steam On/Off Valve for Nozzle #10 (ATVM-11C) | XV-60263SK_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
365 | C2 | 5 | 15 | C2S05,15 | C2S05-X1 | 1756-IB32-15 | DI | 24 VDC energized,Dry Contact | XV-60263SK | 0 | Steam On/Off Valve for Nozzle #10 (ATVM-11C) | XV-60263SK_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
366 | C2 | 5 | 16 | C2S05,16 | C2S05-X2 | 1756-IB32-16 | DI | 24 VDC energized,Dry Contact | XV-60263SL | 0 | Steam On/Off Valve for Nozzle #11 (ATVM-11C) | XV-60263SL_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
367 | C2 | 5 | 17 | C2S05,17 | C2S05-X2 | 1756-IB32-17 | DI | 24 VDC energized,Dry Contact | XV-60263SL | 0 | Steam On/Off Valve for Nozzle #11 (ATVM-11C) | XV-60263SL_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
368 | C2 | 5 | 18 | C2S05,18 | C2S05-X2 | 1756-IB32-18 | DI | 24 VDC energized,Dry Contact | XV-60263SM | 0 | Steam On/Off Valve for Nozzle #12 (ATVM-11C) | XV-60263SM_DI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
369 | C2 | 5 | 19 | C2S05,19 | C2S05-X2 | 1756-IB32-19 | DI | 24 VDC energized,Dry Contact | XV-60263SM | 0 | Steam On/Off Valve for Nozzle #12 (ATVM-11C) | XV-60263SM_DI_2 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
370 | C2 | 5 | 20 | C2S05,20 | C2S05-X2 | 1756-IB32-20 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-607 | Spray Dryer 7th Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
371 | C2 | 5 | 21 | C2S05,21 | C2S05-X2 | 1756-IB32-21 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-607 | Spray Dryer 7th Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
372 | C2 | 5 | 22 | C2S05,22 | C2S05-X2 | 1756-IB32-22 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-607 | Spray Dryer 7th Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
373 | C2 | 5 | 23 | C2S05,23 | C2S05-X2 | 1756-IB32-23 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-607 | Spray Dryer 7th Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
374 | C2 | 5 | 24 | C2S05,24 | C2S05-X2 | 1756-IB32-24 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-607 | Spray Dryer 7th Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
375 | C2 | 5 | 25 | C2S05,25 | C2S05-X2 | 1756-IB32-25 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-607 | Spray Dryer 7th Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
376 | C2 | 5 | 26 | C2S05,26 | C2S05-X2 | 1756-IB32-26 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-607 | Spray Dryer 7th Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
377 | C2 | 5 | 27 | C2S05,27 | C2S05-X2 | 1756-IB32-27 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-607 | Spray Dryer 7th Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
378 | C2 | 5 | 28 | C2S05,28 | C2S05-X2 | 1756-IB32-28 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-607 | Spray Dryer 7th Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
379 | C2 | 5 | 29 | C2S05,29 | C2S05-X2 | 1756-IB32-29 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-607 | Spray Dryer 7th Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
380 | C2 | 5 | 30 | C2S05,30 | C2S05-X2 | 1756-IB32-30 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-607 | Spray Dryer 7th Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
381 | C2 | 5 | 31 | C2S05,31 | C2S05-X2 | 1756-IB32-31 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-607 | Spray Dryer 7th Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
382 | C2 | 6 | 0 | C2S06,00 | C2S06-X1 | 1756-OB32-0 | DO | 24 VDC energized | XV-40203F | 0 | Jet Cooker | XV-40203F_DO_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
383 | C2 | 6 | 1 | C2S06,01 | C2S06-X1 | 1756-OB32-1 | DO | 24 VDC energized | XV-40204B | 0 | Jet Cooker | XV-40204B_DO_1 | 325-01-402-PD-01 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
384 | C2 | 6 | 2 | C2S06,02 | C2S06-X1 | 1756-OB32-2 | DO | 24 VDC energized | XV-40204C | 0 | Jet Cooker | XV-40204C_DO_1 | 325-01-402-PD-01 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
385 | C2 | 6 | 3 | C2S06,03 | C2S06-X1 | 1756-OB32-3 | DO | 24 VDC energized | XV-40205A | 0 | Jet Cooker | XV-40205A_DO_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
386 | C2 | 6 | 4 | C2S06,04 | C2S06-X1 | 1756-OB32-4 | DO | 24 VDC energized | XV-40205B | 0 | Jet Cooker | XV-40205B_DO_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
387 | C2 | 6 | 5 | C2S06,05 | C2S06-X1 | 1756-OB32-5 | DO | 24 VDC energized | XV-40205C | 0 | Jet Cooker | XV-40205C_DO_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
388 | C2 | 6 | 6 | C2S06,06 | C2S06-X1 | 1756-OB32-6 | DO | 24 VDC energized | XV-40205D | 0 | Jet Cooker | XV-40205D_DO_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
389 | C2 | 6 | 7 | C2S06,07 | C2S06-X1 | 1756-OB32-7 | DO | 24 VDC energized | XV-40205F | 0 | Jet Cooker | XV-40205F_DO_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
390 | C2 | 6 | 8 | C2S06,08 | C2S06-X1 | 1756-OB32-8 | DO | 24 VDC energized | XV-40222 | 0 | Jet Cooker | XV-40222_DO_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
391 | C2 | 6 | 9 | C2S06,09 | C2S06-X1 | 1756-OB32-9 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
392 | C2 | 6 | 10 | C2S06,10 | C2S06-X1 | 1756-OB32-10 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
393 | C2 | 6 | 11 | C2S06,11 | C2S06-X1 | 1756-OB32-11 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
394 | C2 | 6 | 12 | C2S06,12 | C2S06-X1 | 1756-OB32-12 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
395 | C2 | 6 | 13 | C2S06,13 | C2S06-X1 | 1756-OB32-13 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
396 | C2 | 6 | 14 | C2S06,14 | C2S06-X1 | 1756-OB32-14 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
397 | C2 | 6 | 15 | C2S06,15 | C2S06-X1 | 1756-OB32-15 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
398 | C2 | 6 | 16 | C2S06,16 | C2S06-X2 | 1756-OB32-16 | DO | Dry Contact | XS-60240B | 0 | Fan Command for BGHS-21 (Bag House Air Pulsing) | XS-60240B_DO_1 | 325-01-600-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
399 | C2 | 6 | 17 | C2S06,17 | C2S06-X2 | 1756-OB32-17 | DO | 24 VDC energized | XV-60214 | 0 | Steam feed to Spray dryer | XV-60214_DO_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
400 | C2 | 6 | 18 | C2S06,18 | C2S06-X2 | 1756-OB32-18 | DO | 24 VDC energized,Dry Contact | XV-60241 | 0 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | XV-60241_DO_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
401 | C2 | 6 | 19 | C2S06,19 | C2S06-X2 | 1756-OB32-19 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
402 | C2 | 6 | 20 | C2S06,20 | C2S06-X2 | 1756-OB32-20 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
403 | C2 | 6 | 21 | C2S06,21 | C2S06-X2 | 1756-OB32-21 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
404 | C2 | 6 | 22 | C2S06,22 | C2S06-X2 | 1756-OB32-22 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
405 | C2 | 6 | 23 | C2S06,23 | C2S06-X2 | 1756-OB32-23 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
406 | C2 | 6 | 24 | C2S06,24 | C2S06-X2 | 1756-OB32-24 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
407 | C2 | 6 | 25 | C2S06,25 | C2S06-X2 | 1756-OB32-25 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
408 | C2 | 6 | 26 | C2S06,26 | C2S06-X2 | 1756-OB32-26 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
409 | C2 | 6 | 27 | C2S06,27 | C2S06-X2 | 1756-OB32-27 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
410 | C2 | 6 | 28 | C2S06,28 | C2S06-X2 | 1756-OB32-28 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
411 | C2 | 6 | 29 | C2S06,29 | C2S06-X2 | 1756-OB32-29 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
412 | C2 | 6 | 30 | C2S06,30 | C2S06-X2 | 1756-OB32-30 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
413 | C2 | 6 | 31 | C2S06,31 | C2S06-X2 | 1756-OB32-31 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
414 | C2 | 7 | 0 | C2S07,00 | C2S07-X1 | 1756-OB32-0 | DO | 24 VDC energized | SV-60207 | 0 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) | SV-60207_DO_1 | 3-25-01-602-PD-07 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
415 | C2 | 7 | 1 | C2S07,01 | C2S07-X1 | 1756-OB32-1 | DO | Dry Contact | XS-FH-60210C | 0 | Command Remote Reset for AHTR-21 | XS-FH-60210C_DO_1 | 325-01-600-PD-06 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
416 | C2 | 7 | 2 | C2S07,02 | C2S07-X1 | 1756-OB32-2 | DO | Dry Contact | XS-FH-60210D | 0 | Spare | XS-FH-60210D_DO_1 | 325-01-600-PD-06 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
417 | C2 | 7 | 3 | C2S07,03 | C2S07-X1 | 1756-OB32-3 | DO | 24 VDC energized | XV-60201 | 0 | Steam feed to Spray dryer | XV-60201_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
418 | C2 | 7 | 4 | C2S07,04 | C2S07-X1 | 1756-OB32-4 | DO | - | XV-60261 | - | - | XV-60261_DO_1 | 325-01-600-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
419 | C2 | 7 | 5 | C2S07,05 | C2S07-X1 | 1756-OB32-5 | DO | 24 VDC energized,Dry Contact | XV-60261FA | 0 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) | XV-60261FA_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
420 | C2 | 7 | 6 | C2S07,06 | C2S07-X1 | 1756-OB32-6 | DO | 24 VDC energized,Dry Contact | XV-60261FB | 0 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) | XV-60261FB_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
421 | C2 | 7 | 7 | C2S07,07 | C2S07-X1 | 1756-OB32-7 | DO | 24 VDC energized,Dry Contact | XV-60261FC | 0 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) | XV-60261FC_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
422 | C2 | 7 | 8 | C2S07,08 | C2S07-X1 | 1756-OB32-8 | DO | 24 VDC energized,Dry Contact | XV-60261FD | 0 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) | XV-60261FD_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
423 | C2 | 7 | 9 | C2S07,09 | C2S07-X1 | 1756-OB32-9 | DO | 24 VDC energized,Dry Contact | XV-60261SA | 0 | Steam On/Off Valve for Nozzle #1 (ATVM-11A) | XV-60261SA_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
424 | C2 | 7 | 10 | C2S07,10 | C2S07-X1 | 1756-OB32-10 | DO | 24 VDC energized,Dry Contact | XV-60261SB | 0 | Steam On/Off Valve for Nozzle #2 (ATVM-11A) | XV-60261SB_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
425 | C2 | 7 | 11 | C2S07,11 | C2S07-X1 | 1756-OB32-11 | DO | 24 VDC energized,Dry Contact | XV-60261SC | 0 | Steam On/Off Valve for Nozzle #3 (ATVM-11A) | XV-60261SC_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
426 | C2 | 7 | 12 | C2S07,12 | C2S07-X1 | 1756-OB32-12 | DO | 24 VDC energized,Dry Contact | XV-60261SD | 0 | Steam On/Off Valve for Nozzle #4 (ATVM-11A) | XV-60261SD_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
427 | C2 | 7 | 13 | C2S07,13 | C2S07-X1 | 1756-OB32-13 | DO | - | XV-60262 | - | - | XV-60262_DO_1 | 325-01-600-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
428 | C2 | 7 | 14 | C2S07,14 | C2S07-X1 | 1756-OB32-14 | DO | 24 VDC energized,Dry Contact | XV-60262FE | 0 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) | XV-60262FE_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
429 | C2 | 7 | 15 | C2S07,15 | C2S07-X1 | 1756-OB32-15 | DO | 24 VDC energized,Dry Contact | XV-60262FF | 0 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) | XV-60262FF_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
430 | C2 | 7 | 16 | C2S07,16 | C2S07-X2 | 1756-OB32-16 | DO | 24 VDC energized,Dry Contact | XV-60262FG | 0 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) | XV-60262FG_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
431 | C2 | 7 | 17 | C2S07,17 | C2S07-X2 | 1756-OB32-17 | DO | 24 VDC energized,Dry Contact | XV-60262FH | 0 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) | XV-60262FH_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
432 | C2 | 7 | 18 | C2S07,18 | C2S07-X2 | 1756-OB32-18 | DO | 24 VDC energized,Dry Contact | XV-60262SE | 0 | Steam On/Off Valve for Nozzle #5 (ATVM-11B) | XV-60262SE_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
433 | C2 | 7 | 19 | C2S07,19 | C2S07-X2 | 1756-OB32-19 | DO | 24 VDC energized,Dry Contact | XV-60262SF | 0 | Steam On/Off Valve for Nozzle #6 (ATVM-11B) | XV-60262SF_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
434 | C2 | 7 | 20 | C2S07,20 | C2S07-X2 | 1756-OB32-20 | DO | 24 VDC energized,Dry Contact | XV-60262SG | 0 | Steam On/Off Valve for Nozzle #7 (ATVM-11B) | XV-60262SG_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
435 | C2 | 7 | 21 | C2S07,21 | C2S07-X2 | 1756-OB32-21 | DO | 24 VDC energized,Dry Contact | XV-60262SH | 0 | Steam On/Off Valve for Nozzle #8 (ATVM-11B) | XV-60262SH_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
436 | C2 | 7 | 22 | C2S07,22 | C2S07-X2 | 1756-OB32-22 | DO | - | XV-60263 | - | - | XV-60263_DO_1 | 325-01-600-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
437 | C2 | 7 | 23 | C2S07,23 | C2S07-X2 | 1756-OB32-23 | DO | 24 VDC energized,Dry Contact | XV-60263FJ | 0 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) | XV-60263FJ_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
438 | C2 | 7 | 24 | C2S07,24 | C2S07-X2 | 1756-OB32-24 | DO | 24 VDC energized,Dry Contact | XV-60263FK | 0 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) | XV-60263FK_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
439 | C2 | 7 | 25 | C2S07,25 | C2S07-X2 | 1756-OB32-25 | DO | 24 VDC energized,Dry Contact | XV-60263FL | 0 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) | XV-60263FL_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
440 | C2 | 7 | 26 | C2S07,26 | C2S07-X2 | 1756-OB32-26 | DO | 24 VDC energized,Dry Contact | XV-60263FM | 0 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) | XV-60263FM_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
441 | C2 | 7 | 27 | C2S07,27 | C2S07-X2 | 1756-OB32-27 | DO | 24 VDC energized,Dry Contact | XV-60263SJ | 0 | Steam On/Off Valve for Nozzle #9 (ATVM-11C) | XV-60263SJ_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
442 | C2 | 7 | 28 | C2S07,28 | C2S07-X2 | 1756-OB32-28 | DO | 24 VDC energized,Dry Contact | XV-60263SK | 0 | Steam On/Off Valve for Nozzle #10 (ATVM-11C) | XV-60263SK_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
443 | C2 | 7 | 29 | C2S07,29 | C2S07-X2 | 1756-OB32-29 | DO | 24 VDC energized,Dry Contact | XV-60263SL | 0 | Steam On/Off Valve for Nozzle #11 (ATVM-11C) | XV-60263SL_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
444 | C2 | 7 | 30 | C2S07,30 | C2S07-X2 | 1756-OB32-30 | DO | 24 VDC energized,Dry Contact | XV-60263SM | 0 | Steam On/Off Valve for Nozzle #12 (ATVM-11C) | XV-60263SM_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
445 | C2 | 7 | 31 | C2S07,31 | C2S07-X2 | 1756-OB32-31 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
446 | C2 | 8 | 0 | C2S08,00 | C2S08-X1 | 1756-OB32-0 | DO | - | XV-60264 | - | - | XV-60264_DO_1 | 325-01-600-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
447 | C2 | 8 | 1 | C2S08,01 | C2S08-X1 | 1756-OB32-1 | DO | 24 VDC energized,Dry Contact | XV-60264FN | 0 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) | XV-60264FN_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
448 | C2 | 8 | 2 | C2S08,02 | C2S08-X1 | 1756-OB32-2 | DO | 24 VDC energized,Dry Contact | XV-60264FP | 0 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) | XV-60264FP_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
449 | C2 | 8 | 3 | C2S08,03 | C2S08-X1 | 1756-OB32-3 | DO | 24 VDC energized,Dry Contact | XV-60264FQ | 0 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) | XV-60264FQ_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
450 | C2 | 8 | 4 | C2S08,04 | C2S08-X1 | 1756-OB32-4 | DO | 24 VDC energized,Dry Contact | XV-60264FR | 0 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) | XV-60264FR_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
451 | C2 | 8 | 5 | C2S08,05 | C2S08-X1 | 1756-OB32-5 | DO | 24 VDC energized,Dry Contact | XV-60264SN | 0 | Steam On/Off Valve for Nozzle #13 (ATVM-11D) | XV-60264SN_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
452 | C2 | 8 | 6 | C2S08,06 | C2S08-X1 | 1756-OB32-6 | DO | 24 VDC energized,Dry Contact | XV-60264SP | 0 | Steam On/Off Valve for Nozzle #14 (ATVM-11D) | XV-60264SP_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
453 | C2 | 8 | 7 | C2S08,07 | C2S08-X1 | 1756-OB32-7 | DO | 24 VDC energized,Dry Contact | XV-60264SQ | 0 | Steam On/Off Valve for Nozzle #15 (ATVM-11D) | XV-60264SQ_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
454 | C2 | 8 | 8 | C2S08,08 | C2S08-X1 | 1756-OB32-8 | DO | 24 VDC energized,Dry Contact | XV-60264SR | 0 | Steam On/Off Valve for Nozzle #16 (ATVM-11D) | XV-60264SR_DO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
455 | C2 | 8 | 9 | C2S08,09 | C2S08-X1 | 1756-OB32-9 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
456 | C2 | 8 | 10 | C2S08,10 | C2S08-X1 | 1756-OB32-10 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
457 | C2 | 8 | 11 | C2S08,11 | C2S08-X1 | 1756-OB32-11 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
458 | C2 | 8 | 12 | C2S08,12 | C2S08-X1 | 1756-OB32-12 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
459 | C2 | 8 | 13 | C2S08,13 | C2S08-X1 | 1756-OB32-13 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
460 | C2 | 8 | 14 | C2S08,14 | C2S08-X1 | 1756-OB32-14 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
461 | C2 | 8 | 15 | C2S08,15 | C2S08-X1 | 1756-OB32-15 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
462 | C2 | 8 | 16 | C2S08,16 | C2S08-X2 | 1756-OB32-16 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
463 | C2 | 8 | 17 | C2S08,17 | C2S08-X2 | 1756-OB32-17 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
464 | C2 | 8 | 18 | C2S08,18 | C2S08-X2 | 1756-OB32-18 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
465 | C2 | 8 | 19 | C2S08,19 | C2S08-X2 | 1756-OB32-19 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
466 | C2 | 8 | 20 | C2S08,20 | C2S08-X2 | 1756-OB32-20 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
467 | C2 | 8 | 21 | C2S08,21 | C2S08-X2 | 1756-OB32-21 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
468 | C2 | 8 | 22 | C2S08,22 | C2S08-X2 | 1756-OB32-22 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
469 | C2 | 8 | 23 | C2S08,23 | C2S08-X2 | 1756-OB32-23 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
470 | C2 | 8 | 24 | C2S08,24 | C2S08-X2 | 1756-OB32-24 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
471 | C2 | 8 | 25 | C2S08,25 | C2S08-X2 | 1756-OB32-25 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
472 | C2 | 8 | 26 | C2S08,26 | C2S08-X2 | 1756-OB32-26 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
473 | C2 | 8 | 27 | C2S08,27 | C2S08-X2 | 1756-OB32-27 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
474 | C2 | 8 | 28 | C2S08,28 | C2S08-X2 | 1756-OB32-28 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
475 | C2 | 8 | 29 | C2S08,29 | C2S08-X2 | 1756-OB32-29 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
476 | C2 | 8 | 30 | C2S08,30 | C2S08-X2 | 1756-OB32-30 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
477 | C2 | 8 | 31 | C2S08,31 | C2S08-X2 | 1756-OB32-31 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
478 | C2 | 9 | 0 | C2S09,00 | C2S09-X1 | 1756-IF16-0 | AI | 4 - 20 mA,Pulse | FT-40221 | Coriolis Flow Transmitter | Jet Cooker | FT-40221_AI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0
479 | C2 | 9 | 1 | C2S09,01 | C2S09-X1 | 1756-IF16-1 | AI | 4 - 20 mA,Pulse | FT-40221 | Coriolis Flow Transmitter | Jet Cooker | FT-40221_AI_2 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0
480 | C2 | 9 | 2 | C2S09,02 | C2S09-X1 | 1756-IF16-2 | AI | 4 - 20 mA,Pulse | FT-40222 | Coriolis Flow Transmitter | Jet Cooker | FT-40222_AI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0
481 | C2 | 9 | 3 | C2S09,03 | C2S09-X1 | 1756-IF16-3 | AI | 4 - 20 mA,Pulse | FT-40222 | Coriolis Flow Transmitter | Jet Cooker | FT-40222_AI_2 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0
482 | C2 | 9 | 4 | C2S09,04 | C2S09-X1 | 1756-IF16-4 | AI | 4 - 20 mA | PT-40222 | Pressure Transmitter | Jet Cooker | PT-40222_AI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
483 | C2 | 9 | 5 | C2S09,05 | C2S09-X1 | 1756-IF16-5 | AI | 4 - 20 mA | TT-40221 | 0 | Jet Cooker | TT-40221_AI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
484 | C2 | 9 | 6 | C2S09,06 | C2S09-X1 | 1756-IF16-6 | AI | 4 - 20 mA | TT-40222 | 0 | Jet Cooker | TT-40222_AI_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
485 | C2 | 9 | 7 | C2S09,07 | C2S09-X1 | 1756-IF16-7 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
486 | C2 | 9 | 8 | C2S09,08 | C2S09-X1 | 1756-IF16-8 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
487 | C2 | 9 | 9 | C2S09,09 | C2S09-X1 | 1756-IF16-9 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
488 | C2 | 9 | 10 | C2S09,10 | C2S09-X1 | 1756-IF16-10 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
489 | C2 | 9 | 11 | C2S09,11 | C2S09-X1 | 1756-IF16-11 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
490 | C2 | 9 | 12 | C2S09,12 | C2S09-X1 | 1756-IF16-12 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
491 | C2 | 9 | 13 | C2S09,13 | C2S09-X1 | 1756-IF16-13 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
492 | C2 | 9 | 14 | C2S09,14 | C2S09-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
493 | C2 | 9 | 15 | C2S09,15 | C2S09-X1 | 1756-IF16-15 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-402 | Jet Cooker 2nd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
494 | C2 | 10 | 0 | C2S10,00 | C2S10-X1 | 1756-IF16-0 | AI | 4 - 20 mA | AT-60241 | Dust Analyzer Transmitter | Dust Analyzer Transmitter for Exhaust Duct (DTEX-22) | AT-60241_AI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
495 | C2 | 10 | 1 | C2S10,01 | C2S10-X1 | 1756-IF16-1 | AI | 4 - 20 mA | DPT-60203 | Differential Pressure Transmitte | Gas Pressure Differential Transmitter for Air Filter (FICA-21) | DPT-60203_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
496 | C2 | 10 | 2 | C2S10,02 | C2S10-X1 | 1756-IF16-2 | AI | 4 - 20 mA | FT-60202 | 0 | Steam feed to Spray dryer | FT-60202_AI_1 | 3-25-01-602-PD-09 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0
497 | C2 | 10 | 3 | C2S10,03 | C2S10-X1 | 1756-IF16-3 | AI | 4 - 20 mA | PT-60210 | Pressure Transmitter | Gas Pressure Transmitter for Hot Air Duct (DTHA-21) | PT-60210_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
498 | C2 | 10 | 4 | C2S10,04 | C2S10-X1 | 1756-IF16-4 | AI | 4 - 20 mA | PT-60215 | Pressure Transmitter | 15% Polypropylene Glycol Pressure Indicator Transmitter for Heat Recovery Pumping Skid (PUCF-21) | PT-60215_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
499 | C2 | 10 | 5 | C2S10,05 | C2S10-X1 | 1756-IF16-5 | AI | 4 - 20 mA | PT-60216 | Pressure Transmitter | Gas Pressure Transmitter for Combustion Air Burner Duct (DTCB-21) | PT-60216_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
500 | C2 | 10 | 6 | C2S10,06 | C2S10-X1 | 1756-IF16-6 | AI | 4 - 20 mA | PT-60240 | Pressure Transmitter | Gas Pressure Transmitter for Bag House Exhaust Duct (DTEX-22) | PT-60240_AI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
501 | C2 | 10 | 7 | C2S10,07 | C2S10-X1 | 1756-IF16-7 | AI | 4 - 20 mA | PT-60241 | Pressure Transmitter | Gas Pressure Transmitter for Exhaust Fan (FANE-21) | PT-60241_AI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
502 | C2 | 10 | 8 | C2S10,08 | C2S10-X1 | 1756-IF16-8 | AI | 4 - 20 mA | TT-60210 | 0 | Gas Temperature Element for Hot Air Duct (DTHA-21) | TT-60210_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
503 | C2 | 10 | 9 | C2S10,09 | C2S10-X1 | 1756-IF16-9 | AI | - | TT-60210A | - | - | TT-60210A_AI_1 | 325-01-600-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
504 | C2 | 10 | 10 | C2S10,10 | C2S10-X1 | 1756-IF16-10 | AI | - | TT-60210B | - | - | TT-60210B_AI_1 | 325-01-600-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
505 | C2 | 10 | 11 | C2S10,11 | C2S10-X1 | 1756-IF16-11 | AI | 4 - 20 mA | TT-60211 | 0 | Gas Temperature Element for Hot Air Duct (DTHA-21) | TT-60211_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
506 | C2 | 10 | 12 | C2S10,12 | C2S10-X1 | 1756-IF16-12 | AI | 4 - 20 mA | TT-60212A | 0 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | TT-60212A_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
507 | C2 | 10 | 13 | C2S10,13 | C2S10-X1 | 1756-IF16-13 | AI | 4 - 20 mA | TT-60212B | 0 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | TT-60212B_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
508 | C2 | 10 | 14 | C2S10,14 | C2S10-X1 | 1756-IF16-14 | AI | 4 - 20 mA | TT-60214 | 0 | Steam Temperature Transmitter for Cold Air Duct (DTCA-23) | TT-60214_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
509 | C2 | 10 | 15 | C2S10,15 | C2S10-X1 | 1756-IF16-15 | AI | 4 - 20 mA | TT-60215A | 0 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | TT-60215A_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
510 | C2 | 11 | 0 | C2S11,00 | C2S11-X1 | 1756-IF16-0 | AI | 4 - 20 mA | TT-60215B | 0 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | TT-60215B_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
511 | C2 | 11 | 1 | C2S11,01 | C2S11-X1 | 1756-IF16-1 | AI | 4 - 20 mA | TT-60216 | 0 | Gas Temperature Transmitter for Combustion Air Burner Duct (DTCB-21) | TT-60216_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
512 | C2 | 11 | 2 | C2S11,02 | C2S11-X1 | 1756-IF16-2 | AI | 4 - 20 mA | TT-60240 | 0 | Gas Temperature Transmitter for Exhaust Fan (FANE-21) | TT-60240_AI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
513 | C2 | 11 | 3 | C2S11,03 | C2S11-X1 | 1756-IF16-3 | AI | 4 - 20 mA | TT-60241A | 0 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | TT-60241A_AI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
514 | C2 | 11 | 4 | C2S11,04 | C2S11-X1 | 1756-IF16-4 | AI | 4 - 20 mA | TT-60241B | 0 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | TT-60241B_AI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
515 | C2 | 11 | 5 | C2S11,05 | C2S11-X1 | 1756-IF16-5 | AI | 4 - 20 mA | VT-60210A | 0 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | VT-60210A_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
516 | C2 | 11 | 6 | C2S11,06 | C2S11-X1 | 1756-IF16-6 | AI | 4 - 20 mA | VT-60210B | 0 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | VT-60210B_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
517 | C2 | 11 | 7 | C2S11,07 | C2S11-X1 | 1756-IF16-7 | AI | 4 - 20 mA | VT-60241A | 0 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | VT-60241A_AI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
518 | C2 | 11 | 8 | C2S11,08 | C2S11-X1 | 1756-IF16-8 | AI | 4 - 20 mA | VT-60241B | 0 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | VT-60241B_AI_1 | 3-25-01-602-PD-05 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
519 | C2 | 11 | 9 | C2S11,09 | C2S11-X1 | 1756-IF16-9 | AI | 4 - 20 mA | FT-60210 | 0 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) | FT-60210_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=2,AO=0,Bus=0
520 | C2 | 11 | 10 | C2S11,10 | C2S11-X1 | 1756-IF16-10 | AI | 4 - 20 mA | FT-60211 | 0 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) | FT-60211_AI_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=2,AO=0,Bus=0
521 | C2 | 11 | 11 | C2S11,11 | C2S11-X1 | 1756-IF16-11 | AI | 4 - 20 mA | FT-60210 | 0 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) | FT-60210_AI_2 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=2,AO=0,Bus=0
522 | C2 | 11 | 12 | C2S11,12 | C2S11-X1 | 1756-IF16-12 | AI | 4 - 20 mA | FT-60211 | 0 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) | FT-60211_AI_2 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=2,AO=0,Bus=0
523 | C2 | 11 | 13 | C2S11,13 | C2S11-X1 | 1756-IF16-13 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-602 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
524 | C2 | 11 | 14 | C2S11,14 | C2S11-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-602 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
525 | C2 | 11 | 15 | C2S11,15 | C2S11-X1 | 1756-IF16-15 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-602 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
526 | C2 | 12 | 0 | C2S12,00 | C2S12-X1 | 1756-IF16-0 | AI | 4 - 20 mA | FT-60207 | 0 | Instr. Air Flow Transmitter for Camera #4 (ACAM-21) | FT-60207_AI_1 | 3-25-01-602-PD-07 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
527 | C2 | 12 | 1 | C2S12,01 | C2S12-X1 | 1756-IF16-1 | AI | 4 - 20 mA | FT-60221 | 0 | Cool air Flow | FT-60221_AI_1 | 3-25-01-602-PD-04 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
528 | C2 | 12 | 2 | C2S12,02 | C2S12-X1 | 1756-IF16-2 | AI | 4 - 20 mA | FT-60261FA | 0 | Feed Slurry Flow Transmitter for Nozzle #1 (AMTV-11A) | FT-60261FA_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
529 | C2 | 12 | 3 | C2S12,03 | C2S12-X1 | 1756-IF16-3 | AI | 4 - 20 mA | FT-60261FB | 0 | Feed Slurry Flow Transmitter for Nozzle #2 (AMTV-11A) | FT-60261FB_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
530 | C2 | 12 | 4 | C2S12,04 | C2S12-X1 | 1756-IF16-4 | AI | 4 - 20 mA | FT-60261FC | 0 | Feed Slurry Flow Transmitter for Nozzle #3 (AMTV-11A) | FT-60261FC_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
531 | C2 | 12 | 5 | C2S12,05 | C2S12-X1 | 1756-IF16-5 | AI | 4 - 20 mA | FT-60261FD | 0 | Feed Slurry Flow Transmitter for Nozzle #4 (AMTV-11A) | FT-60261FD_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
532 | C2 | 12 | 6 | C2S12,06 | C2S12-X1 | 1756-IF16-6 | AI | 4 - 20 mA | FT-60262FE | 0 | Feed Slurry Flow Transmitter for Nozzle #5 (AMTV-11B) | FT-60262FE_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
533 | C2 | 12 | 7 | C2S12,07 | C2S12-X1 | 1756-IF16-7 | AI | 4 - 20 mA | FT-60262FF | 0 | Feed Slurry Flow Transmitter for Nozzle #6 (AMTV-11B) | FT-60262FF_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
534 | C2 | 12 | 8 | C2S12,08 | C2S12-X1 | 1756-IF16-8 | AI | 4 - 20 mA | FT-60262FG | 0 | Feed Slurry Flow Transmitter for Nozzle #7 (AMTV-11B) | FT-60262FG_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
535 | C2 | 12 | 9 | C2S12,09 | C2S12-X1 | 1756-IF16-9 | AI | 4 - 20 mA | FT-60262FH | 0 | Feed Slurry Flow Transmitter for Nozzle #8 (AMTV-11B) | FT-60262FH_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
536 | C2 | 12 | 10 | C2S12,10 | C2S12-X1 | 1756-IF16-10 | AI | 4 - 20 mA | FT-60263FJ | 0 | Feed Slurry Flow Transmitter for Nozzle #9 (AMTV-11C) | FT-60263FJ_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
537 | C2 | 12 | 11 | C2S12,11 | C2S12-X1 | 1756-IF16-11 | AI | 4 - 20 mA | FT-60263FK | 0 | Feed Slurry Flow Transmitter for Nozzle #10 (AMTV-11C) | FT-60263FK_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
538 | C2 | 12 | 12 | C2S12,12 | C2S12-X1 | 1756-IF16-12 | AI | 4 - 20 mA | FT-60263FL | 0 | Feed Slurry Flow Transmitter for Nozzle #11 (AMTV-11C) | FT-60263FL_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
539 | C2 | 12 | 13 | C2S12,13 | C2S12-X1 | 1756-IF16-13 | AI | 4 - 20 mA | FT-60263FM | 0 | Feed Slurry Flow Transmitter for Nozzle #12 (AMTV-11C) | FT-60263FM_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
540 | C2 | 12 | 14 | C2S12,14 | C2S12-X1 | 1756-IF16-14 | AI | 4 - 20 mA | FT-60264FN | 0 | Feed Slurry Flow Transmitter for Nozzle #13 (AMTV-11D) | FT-60264FN_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
541 | C2 | 12 | 15 | C2S12,15 | C2S12-X1 | 1756-IF16-15 | AI | 4 - 20 mA | FT-60264FP | 0 | Feed Slurry Flow Transmitter for Nozzle #14 (AMTV-11D) | FT-60264FP_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
542 | C2 | 13 | 0 | C2S13,00 | C2S13-X1 | 1756-IF16-0 | AI | 4 - 20 mA | FT-60264FQ | 0 | Feed Slurry Flow Transmitter for Nozzle #15 (AMTV-11D) | FT-60264FQ_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
543 | C2 | 13 | 1 | C2S13,01 | C2S13-X1 | 1756-IF16-1 | AI | 4 - 20 mA | FT-60264FR | 0 | Feed Slurry Flow Transmitter for Nozzle #16 (AMTV-11D) | FT-60264FR_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
544 | C2 | 13 | 2 | C2S13,02 | C2S13-X1 | 1756-IF16-2 | AI | 4 - 20 mA | PT-60201 | Pressure Transmitter | Steam feed to Spray dryer | PT-60201_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
545 | C2 | 13 | 3 | C2S13,03 | C2S13-X1 | 1756-IF16-3 | AI | 4 - 20 mA | PT-60207 | Pressure Transmitter | Instr. Air Pressure Transmitter for Camera #4 (ACAM-21) | PT-60207_AI_1 | 3-25-01-602-PD-07 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
546 | C2 | 13 | 4 | C2S13,04 | C2S13-X1 | 1756-IF16-4 | AI | 4 - 20 mA | PT-60221 | Pressure Transmitter | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25) | PT-60221_AI_1 | 3-25-01-602-PD-04 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
547 | C2 | 13 | 5 | C2S13,05 | C2S13-X1 | 1756-IF16-5 | AI | 4 - 20 mA | PT-60221 | Pressure Transmitter | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25) | PT-60221_AI_1 | 3-25-01-602-PD-04 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
548 | C2 | 13 | 6 | C2S13,06 | C2S13-X1 | 1756-IF16-6 | AI | 4 - 20 mA | TI-FH-60210 | 0 | Gas Burner Firing Rate Temp Signal to AHTR-21 | TI-FH-60210_AI_1 | 325-01-600-PD-06 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
549 | C2 | 13 | 7 | C2S13,07 | C2S13-X1 | 1756-IF16-7 | AI | 4 - 20 mA | TT-60201 | 0 | Steam feed to Spray dryer | TT-60201_AI_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
550 | C2 | 13 | 8 | C2S13,08 | C2S13-X1 | 1756-IF16-8 | AI | 4 - 20 mA | TT-60202 | 0 | Compress air temp to camera | TT-60202_AI_1 | 3-25-01-602-PD-07 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
551 | C2 | 13 | 9 | C2S13,09 | C2S13-X1 | 1756-IF16-9 | AI | 4 - 20 mA | TT-60207 | 0 | Instr. Air Temperature Transmitter for Air Manifold - Camera #4 (ACAM-21) | TT-60207_AI_1 | 3-25-01-602-PD-07 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
552 | C2 | 13 | 10 | C2S13,10 | C2S13-X1 | 1756-IF16-10 | AI | 4 - 20 mA | UY-FH-60210A | 0 | Comb fan VFD Speed Control | UY-FH-60210A_AI_1 | 325-01-600-PD-06 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
553 | C2 | 13 | 11 | C2S13,11 | C2S13-X1 | 1756-IF16-11 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
554 | C2 | 13 | 12 | C2S13,12 | C2S13-X1 | 1756-IF16-12 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
555 | C2 | 13 | 13 | C2S13,13 | C2S13-X1 | 1756-IF16-13 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
556 | C2 | 13 | 14 | C2S13,14 | C2S13-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
557 | C2 | 13 | 15 | C2S13,15 | C2S13-X1 | 1756-IF16-15 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
558 | C3 | 1 | 0 | C3S01,00 | C3S01-X1 | 1756-IB32-0 | DI | - | AT-40201 | - | - | AT-40201_DI_1 | - | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 3rd | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
559 | C3 | 1 | 1 | C3S01,01 | C3S01-X1 | 1756-IB32-1 | DI | - | AT-40202 | - | - | AT-40202_DI_1 | - | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 3rd | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
560 | C3 | 1 | 2 | C3S01,02 | C3S01-X1 | 1756-IB32-2 | DI | - | AT-40203 | - | - | AT-40203_DI_1 | - | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 3rd | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
561 | C3 | 1 | 3 | C3S01,03 | C3S01-X1 | 1756-IB32-3 | DI | Dry Contact | LSH-60230 | 0 | Powder Level Switch High for Cyclone (CYCL-21) | LSH-60230_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 1st | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
562 | C3 | 1 | 4 | C3S01,04 | C3S01-X1 | 1756-IB32-4 | DI | Dry Contact | LSH-60231 | 0 | Powder Level Switch High for Cyclone (CYCL-22) | LSH-60231_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 1st | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
563 | C3 | 1 | 5 | C3S01,05 | C3S01-X1 | 1756-IB32-5 | DI | Dry Contact | LSH-60240 | 0 | Powder Level Switch High for Bag House (BGHS-21) | LSH-60240_DI_1 | 3-25-01-602-PD-05 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 1st | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
564 | C3 | 1 | 6 | C3S01,06 | C3S01-X1 | 1756-IB32-6 | DI | - | PD-60202 | - | - | PD-60202_DI_1 | - | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 3rd | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
565 | C3 | 1 | 7 | C3S01,07 | C3S01-X1 | 1756-IB32-7 | DI | - | RV-60204 | - | - | RV-60204_DI_1 | - | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 3rd | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
566 | C3 | 1 | 8 | C3S01,08 | C3S01-X1 | 1756-IB32-8 | DI | Dry Contact | ZS-60201C | 0 | Limit Switch for CHAM-21 (Spray Chamber) | ZS-60201C_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
567 | C3 | 1 | 9 | C3S01,09 | C3S01-X1 | 1756-IB32-9 | DI | Dry Contact | ZS-60201D | 0 | Limit Switch for CHAM-21 (Spray Chamber) | ZS-60201D_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
568 | C3 | 1 | 10 | C3S01,10 | C3S01-X1 | 1756-IB32-10 | DI | Dry Contact | ZS-60201E | 0 | Limit Switch for CHAM-21 (Spray Chamber) | ZS-60201E_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 1st | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
569 | C3 | 1 | 11 | C3S01,11 | C3S01-X1 | 1756-IB32-11 | DI | Dry Contact | ZS-60229 | 0 | Limit Switch for CY-60230 (Door Service) | ZS-60229_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
570 | C3 | 1 | 12 | C3S01,12 | C3S01-X1 | 1756-IB32-12 | DI | Dry Contact | ZS-60230 | 0 | Limit Switch for CY-60231 (Door Service) | ZS-60230_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
571 | C3 | 1 | 13 | C3S01,13 | C3S01-X1 | 1756-IB32-13 | DI | Dry Contact | ZS-60231A | 0 | Gas Limit Switch for DTEX-21 (Bag House Face Spectacle Inserted) | ZS-60231A_DI_1 | 3-25-01-602-PD-05 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
572 | C3 | 1 | 14 | C3S01,14 | C3S01-X1 | 1756-IB32-14 | DI | Dry Contact | ZS-60231B | 0 | Gas Limit Switch for DTEX-21 (Bag House Face Blind Inserted) | ZS-60231B_DI_1 | 3-25-01-602-PD-05 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
573 | C3 | 1 | 15 | C3S01,15 | C3S01-X1 | 1756-IB32-15 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-603 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
574 | C3 | 1 | 16 | C3S01,16 | C3S01-X2 | 1756-IB32-16 | DI | 24 VDC energized | DV-61301 | 0 | On/Off Valve for Diverter Valve DV-61301 | DV-61301_DI_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
575 | C3 | 1 | 17 | C3S01,17 | C3S01-X2 | 1756-IB32-17 | DI | 24 VDC energized | DV-61301 | 0 | On/Off Valve for Diverter Valve DV-61301 | DV-61301_DI_2 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
576 | C3 | 1 | 18 | C3S01,18 | C3S01-X2 | 1756-IB32-18 | DI | 24 VDC energized | DV-61302 | 0 | On/Off Valve for Diverter Valve DV-61302 | DV-61302_DI_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
577 | C3 | 1 | 19 | C3S01,19 | C3S01-X2 | 1756-IB32-19 | DI | 24 VDC energized | DV-61302 | 0 | On/Off Valve for Diverter Valve DV-61302 | DV-61302_DI_2 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
578 | C3 | 1 | 20 | C3S01,20 | C3S01-X2 | 1756-IB32-20 | DI | Dry Contact | LS-61303 | 0 | Level switch | LS-61303_DI_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 7th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
579 | C3 | 1 | 21 | C3S01,21 | C3S01-X2 | 1756-IB32-21 | DI | Dry Contact | PSL-61301 | 0 | Pressure alarm low | PSL-61301_DI_1 | 325-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
580 | C3 | 1 | 22 | C3S01,22 | C3S01-X2 | 1756-IB32-22 | DI | Dry Contact | PSL-61302 | 0 | Pressure alarm low | PSL-61302_DI_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
581 | C3 | 1 | 28 | C3S01,28 | C3S01-X2 | 1756-IB32-28 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-618 | Packing Tower 8th Floor | Packing Tower | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
582 | C3 | 1 | 29 | C3S01,29 | C3S01-X2 | 1756-IB32-29 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-618 | Packing Tower 8th Floor | Packing Tower | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
583 | C3 | 1 | 30 | C3S01,30 | C3S01-X2 | 1756-IB32-30 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-618 | Packing Tower 8th Floor | Packing Tower | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
584 | C3 | 1 | 31 | C3S01,31 | C3S01-X2 | 1756-IB32-31 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-618 | Packing Tower 8th Floor | Packing Tower | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
585 | C3 | 2 | 0 | C3S02,00 | C3S02-X1 | 1756-IB32-0 | DI | - | ISV-61301 | - | - | ISV-61301_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
586 | C3 | 2 | 1 | C3S02,01 | C3S02-X1 | 1756-IB32-1 | DI | Dry Contact | LSH-61301 | 0 | Level alarm high | LSH-61301_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 7th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
587 | C3 | 2 | 2 | C3S02,02 | C3S02-X1 | 1756-IB32-2 | DI | - | LSH-61303 | - | - | LSH-61303_DI_1 | 325-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 7th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
588 | C3 | 2 | 3 | C3S02,03 | C3S02-X1 | 1756-IB32-3 | DI | Dry Contact | LSH-61306 | 0 | Level alarm high | LSH-61306_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
589 | C3 | 2 | 4 | C3S02,04 | C3S02-X1 | 1756-IB32-4 | DI | Dry Contact | LSH-61308 | 0 | High Level alarm Cooling cyclone | LSH-61308_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
590 | C3 | 2 | 5 | C3S02,05 | C3S02-X1 | 1756-IB32-5 | DI | Dry Contact | LSL-61302 | 0 | Level alarm low | LSL-61302_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 6th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
591 | C3 | 2 | 6 | C3S02,06 | C3S02-X1 | 1756-IB32-6 | DI | Dry Contact | PSE-61300 | 0 | Explosion Vent PSE-61300 | PSE-61300_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
592 | C3 | 2 | 7 | C3S02,07 | C3S02-X1 | 1756-IB32-7 | DI | Dry Contact | PSE-61301 | 0 | Explosion Vent PSE-61301 | PSE-61301_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
593 | C3 | 2 | 8 | C3S02,08 | C3S02-X1 | 1756-IB32-8 | DI | Dry Contact | PSE-61304 | 0 | Explosion Vent PSE-61304 | PSE-61304_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
594 | C3 | 2 | 9 | C3S02,09 | C3S02-X1 | 1756-IB32-9 | DI | - | PSV-61301A | - | - | PSV-61301A_DI_1 | 325-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
595 | C3 | 2 | 10 | C3S02,10 | C3S02-X1 | 1756-IB32-10 | DI | - | PSV-61301B | - | - | PSV-61301B_DI_1 | 325-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
596 | C3 | 2 | 11 | C3S02,11 | C3S02-X1 | 1756-IB32-11 | DI | Dry Contact | ZS-61310 | 0 | Position Magnet Door | ZS-61310_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
597 | C3 | 2 | 12 | C3S02,12 | C3S02-X1 | 1756-IB32-12 | DI | Dry Contact | ZS-61311 | 0 | Position Magnet Door | ZS-61311_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
598 | C3 | 2 | 13 | C3S02,13 | C3S02-X1 | 1756-IB32-13 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
599 | C3 | 2 | 14 | C3S02,14 | C3S02-X1 | 1756-IB32-14 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
600 | C3 | 2 | 15 | C3S02,15 | C3S02-X1 | 1756-IB32-15 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
601 | C3 | 2 | 16 | C3S02,16 | C3S02-X2 | 1756-IB32-16 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
602 | C3 | 2 | 17 | C3S02,17 | C3S02-X2 | 1756-IB32-17 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
603 | C3 | 2 | 18 | C3S02,18 | C3S02-X2 | 1756-IB32-18 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
604 | C3 | 2 | 19 | C3S02,19 | C3S02-X2 | 1756-IB32-19 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
605 | C3 | 2 | 20 | C3S02,20 | C3S02-X2 | 1756-IB32-20 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
606 | C3 | 2 | 21 | C3S02,21 | C3S02-X2 | 1756-IB32-21 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
607 | C3 | 2 | 22 | C3S02,22 | C3S02-X2 | 1756-IB32-22 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
608 | C3 | 2 | 23 | C3S02,23 | C3S02-X2 | 1756-IB32-23 | DI | Dry Contact | PSL-61311 | 0 | Pressure alarm low | PSL-61311_DI_1 | 3-25-01-613-PD-04 | JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
609 | C3 | 2 | 23 | C3S02,23 | C3S02-X2 | 1756-IB32-23 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
610 | C3 | 2 | 24 | C3S02,24 | C3S02-X2 | 1756-IB32-24 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
611 | C3 | 2 | 24 | C3S02,24 | C3S02-X2 | 1756-IB32-24 | DI | 24 VDC energized | SV-61304 | 0 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) | SV-61304_DI_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
612 | C3 | 2 | 25 | C3S02,25 | C3S02-X2 | 1756-IB32-25 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
613 | C3 | 2 | 25 | C3S02,25 | C3S02-X2 | 1756-IB32-25 | DI | 24 VDC energized | SV-61304 | 0 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) | SV-61304_DI_2 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
614 | C3 | 2 | 26 | C3S02,26 | C3S02-X2 | 1756-IB32-26 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
615 | C3 | 2 | 26 | C3S02,26 | C3S02-X2 | 1756-IB32-26 | DI | 24 VDC energized | XV-61301 | 0 | Product feed-out Packing silo | XV-61301_DI_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
616 | C3 | 2 | 27 | C3S02,27 | C3S02-X2 | 1756-IB32-27 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
617 | C3 | 2 | 27 | C3S02,27 | C3S02-X2 | 1756-IB32-27 | DI | 24 VDC energized | XV-61301 | 0 | Product feed-out Packing silo | XV-61301_DI_2 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
618 | C3 | 2 | 28 | C3S02,28 | C3S02-X2 | 1756-IB32-28 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
619 | C3 | 2 | 29 | C3S02,29 | C3S02-X2 | 1756-IB32-29 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
620 | C3 | 2 | 30 | C3S02,30 | C3S02-X2 | 1756-IB32-30 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
621 | C3 | 2 | 31 | C3S02,31 | C3S02-X2 | 1756-IB32-31 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
622 | C3 | 3 | 0 | C3S03,00 | C3S03-X1 | 1756-OB32-0 | DO | 24 VDC energized | DV-61301 | 0 | On/Off Valve for Diverter Valve DV-61301 | DV-61301_DO_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
623 | C3 | 3 | 1 | C3S03,01 | C3S03-X1 | 1756-OB32-1 | DO | 24 VDC energized | DV-61302 | 0 | On/Off Valve for Diverter Valve DV-61302 | DV-61302_DO_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
624 | C3 | 3 | 2 | C3S03,02 | C3S03-X1 | 1756-OB32-2 | DO | 24 VDC energized | SV-61301 | 0 | Timer compress air pluse solenoid valve | SV-61301_DO_1 | 325-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
625 | C3 | 3 | 3 | C3S03,03 | C3S03-X1 | 1756-OB32-3 | DO | 24 VDC energized | SV-61302 | 0 | Air service | SV-61302_DO_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 7th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
626 | C3 | 3 | 4 | C3S03,04 | C3S03-X1 | 1756-OB32-4 | DO | 24 VDC energized | SV-61303 | 0 | Timer compress air pluse solenoid valve | SV-61303_DO_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
627 | C3 | 3 | 5 | C3S03,05 | C3S03-X1 | 1756-OB32-5 | DO | 24 VDC energized | SV-61304 | 0 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) | SV-61304_DO_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
628 | C3 | 3 | 6 | C3S03,06 | C3S03-X1 | 1756-OB32-6 | DO | 24 VDC energized | SV-61305 | 0 | Air service | SV-61305_DO_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
629 | C3 | 3 | 7 | C3S03,07 | C3S03-X1 | 1756-OB32-7 | DO | - | SV-61306 | - | - | SV-61306_DO_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
630 | C3 | 3 | 8 | C3S03,08 | C3S03-X1 | 1756-OB32-8 | DO | 24 VDC energized | XV-61301 | 0 | Product feed-out Packing silo | XV-61301_DO_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 5th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
631 | C3 | 3 | 9 | C3S03,09 | C3S03-X1 | 1756-OB32-9 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
632 | C3 | 3 | 10 | C3S03,10 | C3S03-X1 | 1756-OB32-10 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
633 | C3 | 3 | 11 | C3S03,11 | C3S03-X1 | 1756-OB32-11 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
634 | C3 | 3 | 12 | C3S03,12 | C3S03-X1 | 1756-OB32-12 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
635 | C3 | 3 | 13 | C3S03,13 | C3S03-X1 | 1756-OB32-13 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
636 | C3 | 3 | 14 | C3S03,14 | C3S03-X1 | 1756-OB32-14 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
637 | C3 | 3 | 15 | C3S03,15 | C3S03-X1 | 1756-OB32-15 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
638 | C3 | 3 | 16 | C3S03,16 | C3S03-X2 | 1756-OB32-16 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
639 | C3 | 3 | 17 | C3S03,17 | C3S03-X2 | 1756-OB32-17 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
640 | C3 | 3 | 18 | C3S03,18 | C3S03-X2 | 1756-OB32-18 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
641 | C3 | 3 | 19 | C3S03,19 | C3S03-X2 | 1756-OB32-19 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
642 | C3 | 3 | 20 | C3S03,20 | C3S03-X2 | 1756-OB32-20 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
643 | C3 | 3 | 21 | C3S03,21 | C3S03-X2 | 1756-OB32-21 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
644 | C3 | 3 | 22 | C3S03,22 | C3S03-X2 | 1756-OB32-22 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
645 | C3 | 3 | 23 | C3S03,23 | C3S03-X2 | 1756-OB32-23 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
646 | C3 | 3 | 24 | C3S03,24 | C3S03-X2 | 1756-OB32-24 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
647 | C3 | 3 | 25 | C3S03,25 | C3S03-X2 | 1756-OB32-25 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
648 | C3 | 3 | 26 | C3S03,26 | C3S03-X2 | 1756-OB32-26 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
649 | C3 | 3 | 27 | C3S03,27 | C3S03-X2 | 1756-OB32-27 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
650 | C3 | 3 | 28 | C3S03,28 | C3S03-X2 | 1756-OB32-28 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
651 | C3 | 3 | 29 | C3S03,29 | C3S03-X2 | 1756-OB32-29 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
652 | C3 | 3 | 30 | C3S03,30 | C3S03-X2 | 1756-OB32-30 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
653 | C3 | 3 | 31 | C3S03,31 | C3S03-X2 | 1756-OB32-31 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
654 | C3 | 4 | 0 | C3S04,00 | C3S04-X1 | 1756-IF16-0 | AI | 4 - 20 mA | PT-60230 | Pressure Transmitter | Gas Pressure Transmitter for Conveying Duct (DTCO-21) | PT-60230_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
655 | C3 | 4 | 1 | C3S04,01 | C3S04-X1 | 1756-IF16-1 | AI | 4 - 20 mA | PT-60231 | Pressure Transmitter | Gas Pressure Transmitter for Cyclone Exhaust Duct (DTCE-21) | PT-60231_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
656 | C3 | 4 | 2 | C3S04,02 | C3S04-X1 | 1756-IF16-2 | AI | 4 - 20 mA | TT-60224 | 0 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | TT-60224_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 4th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
657 | C3 | 4 | 3 | C3S04,03 | C3S04-X1 | 1756-IF16-3 | AI | 4 - 20 mA | TT-60225 | 0 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | TT-60225_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 3rd | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
658 | C3 | 4 | 4 | C3S04,04 | C3S04-X1 | 1756-IF16-4 | AI | 4 - 20 mA | TT-60226 | 0 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | TT-60226_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 2nd | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
659 | C3 | 4 | 5 | C3S04,05 | C3S04-X1 | 1756-IF16-5 | AI | 4 - 20 mA | TT-60227 | 0 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | TT-60227_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 1st | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
660 | C3 | 4 | 6 | C3S04,06 | C3S04-X1 | 1756-IF16-6 | AI | 4 - 20 mA | TT-60230 | 0 | Gas and Powder Temperature Transmitter for Conveying Duct (DTCO-21) | TT-60230_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | Spray Dryer 3rd Floor | Spray Dryer | 3rd | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
661 | C3 | 4 | 7 | C3S04,07 | C3S04-X1 | 1756-IF16-7 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-603 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
662 | C3 | 4 | 8 | C3S04,08 | C3S04-X1 | 1756-IF16-8 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-603 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
663 | C3 | 4 | 9 | C3S04,09 | C3S04-X1 | 1756-IF16-9 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-603 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
664 | C3 | 4 | 10 | C3S04,10 | C3S04-X1 | 1756-IF16-10 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-603 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
665 | C3 | 4 | 11 | C3S04,11 | C3S04-X1 | 1756-IF16-11 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-603 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
666 | C3 | 4 | 12 | C3S04,12 | C3S04-X1 | 1756-IF16-12 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-603 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
667 | C3 | 4 | 13 | C3S04,13 | C3S04-X1 | 1756-IF16-13 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-603 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
668 | C3 | 4 | 14 | C3S04,14 | C3S04-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-603 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
669 | C3 | 4 | 15 | C3S04,15 | C3S04-X1 | 1756-IF16-15 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-603 | Spray Dryer 3rd Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
670 | C3 | 5 | 0 | C3S05,00 | C3S05-X1 | 1756-IF16-0 | AI | 4 - 20 mA | PT-61303 | Pressure Transmitter | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) | PT-61303_AI_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
671 | C3 | 5 | 1 | C3S05,01 | C3S05-X1 | 1756-IF16-1 | AI | - | PT-61306 | - | - | PT-61306_AI_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
672 | C3 | 5 | 2 | C3S05,02 | C3S05-X1 | 1756-IF16-2 | AI | - | TT-61303 | - | - | TT-61303_AI_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
673 | C3 | 5 | 3 | C3S05,03 | C3S05-X1 | 1756-IF16-3 | AI | - | TT-61304 | - | - | TT-61304_AI_1 | 3-25-01-613-PD-01 | JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
674 | C3 | 5 | 4 | C3S05,04 | C3S05-X1 | 1756-IF16-4 | AI | 4 - 20 mA | DPT-61301 | Differential Pressure Transmitte | Vent filter pressure | DPT-61301_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
675 | C3 | 5 | 5 | C3S05,05 | C3S05-X1 | 1756-IF16-5 | AI | 4 - 20 mA | DPT-61302 | Differential Pressure Transmitte | Vent filter pressure | DPT-61302_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
676 | C3 | 5 | 6 | C3S05,06 | C3S05-X1 | 1756-IF16-6 | AI | 4 - 20 mA | LT-61301 | Level Transmitter | Level powder in silo | LT-61301_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
677 | C3 | 5 | 7 | C3S05,07 | C3S05-X1 | 1756-IF16-7 | AI | 4 - 20 mA | PT-61301 | Pressure Transmitter | Pressure in silo | PT-61301_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
678 | C3 | 5 | 8 | C3S05,08 | C3S05-X1 | 1756-IF16-8 | AI | 4 - 20 mA | PT-61303 | Pressure Transmitter | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) | PT-61303_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 8th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
679 | C3 | 5 | 9 | C3S05,09 | C3S05-X1 | 1756-IF16-9 | AI | 4 - 20 mA | PT-61304 | Pressure Transmitter | Gas Pressure Transmitter for Storage Bin Cyclone Inlet Duct (CYCL-31) | PT-61304_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
680 | C3 | 5 | 10 | C3S05,10 | C3S05-X1 | 1756-IF16-10 | AI | 4 - 20 mA | PT-61305 | Pressure Transmitter | Gas Pressure Transmitter for Exhaust Duct (DTEX-31) | PT-61305_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
681 | C3 | 5 | 11 | C3S05,11 | C3S05-X1 | 1756-IF16-11 | AI | 4 - 20 mA | TT-61301 | 0 | Gas Temperature Transmitter for Cold Air Duct (DTCA-32) | TT-61301_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
682 | C3 | 5 | 12 | C3S05,12 | C3S05-X1 | 1756-IF16-12 | AI | 4 - 20 mA | TT-61302 | 0 | Gas and Powder Temperature Transmitter for Cooling Cyclone (CYCL-31) | TT-61302_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | Packing Tower 8th Floor | Packing Tower | 9th | =CA1+MCP-M3 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
683 | C3 | 5 | 13 | C3S05,13 | C3S05-X1 | 1756-IF16-13 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
684 | C3 | 5 | 14 | C3S05,14 | C3S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
685 | C3 | 5 | 15 | C3S05,15 | C3S05-X1 | 1756-IF16-15 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-618 | Packing Tower 8th Floor | - | - | =CA1+MCP-M3 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
686 | C3 | 13 | 0 | C3S13,00 | C3S13-X1 | 1756-OF8-0 | AO | 4 - 20 mA | TCV-40222 | 0 | Jet Cooker | TCV-40222_AO_1 | 325-01-402-PD-02 | JB-402 | Jet Cooker 2nd Floor | Jet Cooker | 2nd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0
687 | C3 | 13 | 1 | C3S13,01 | C3S13-X1 | 1756-OF8-1 | AO | - | TV-60202 | - | - | TV-60202_AO_1 | 3-25-01-602-PD-07 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 3rd | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0
688 | C3 | 13 | 2 | C3S13,02 | C3S13-X1 | 1756-OF8-2 | AO | - | TV-60214 | - | - | TV-60214_AO_1 | 3-25-01-602-PD-03 | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | 5th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0
689 | C3 | 13 | 3 | C3S13,03 | C3S13-X1 | 1756-OF8-3 | AO | - | PV-60201 | - | - | PV-60201_AO_1 | 3-25-01-602-PD-02 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0
690 | C3 | 13 | 4 | C3S13,04 | C3S13-X1 | 1756-OF8-4 | AO | 4 - 20 mA | UY-FH-60210B | 0 | Demand Signal | UY-FH-60210B_AO_1 | 325-01-600-PD-06 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | =CA1+MCP-M2 | ACTIVE | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0
691 | C3 | 13 | 5 | C3S13,05 | C3S13-X1 | 1756-OF8-5 | AO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0
692 | C3 | 13 | 6 | C3S13,06 | C3S13-X1 | 1756-OF8-6 | AO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0
693 | C3 | 13 | 7 | C3S13,07 | C3S13-X1 | 1756-OF8-7 | AO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AO_0 | - | JB-607 | Spray Dryer 7th Floor | - | - | =CA1+MCP-M2 | SPARE | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0
694 | C4 | 1 | 0 | C4S01,00 | C4S01-X1 | 1756-IB32-0 | DI | 4 - 20 mA | FT-60203 | 0 | Culinary steam feed to Spray dryer | FT-60203_DI_1 | 3-25-01-602-PD-09 | JB-606 | Spray Dryer 6th Floor | Spray Dryer | 6th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0
695 | C4 | 1 | 1 | C4S01,01 | C4S01-X1 | 1756-IB32-1 | DI | Dry Contact | LSH-60250 | 0 | Water Level Switch High for Fire Deluge Pipe (FWDP-21) | LSH-60250_DI_1 | 3-25-01-602-PD-05 | JB-606 | Spray Dryer 6th Floor | Spray Dryer | 6th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
696 | C4 | 1 | 2 | C4S01,02 | C4S01-X1 | 1756-IB32-2 | DI | Dry Contact | XA-60261 | 0 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | XA-60261_DI_1 | 325-01-600-PD-05 | JB-606 | Spray Dryer 6th Floor | Spray Dryer | 6th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
697 | C4 | 1 | 3 | C4S01,03 | C4S01-X1 | 1756-IB32-3 | DI | Dry Contact | XA-60262 | 0 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | XA-60262_DI_1 | 325-01-600-PD-05 | JB-606 | Spray Dryer 6th Floor | Spray Dryer | 6th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
698 | C4 | 1 | 4 | C4S01,04 | C4S01-X1 | 1756-IB32-4 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-606 | Spray Dryer 6th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
699 | C4 | 1 | 5 | C4S01,05 | C4S01-X1 | 1756-IB32-5 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-606 | Spray Dryer 6th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
700 | C4 | 1 | 6 | C4S01,06 | C4S01-X1 | 1756-IB32-6 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-606 | Spray Dryer 6th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
701 | C4 | 1 | 7 | C4S01,07 | C4S01-X1 | 1756-IB32-7 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-606 | Spray Dryer 6th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
702 | C4 | 1 | 8 | C4S01,08 | C4S01-X1 | 1756-IB32-8 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-606 | Spray Dryer 6th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
703 | C4 | 1 | 9 | C4S01,09 | C4S01-X1 | 1756-IB32-9 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-606 | Spray Dryer 6th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
704 | C4 | 1 | 10 | C4S01,10 | C4S01-X1 | 1756-IB32-10 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-606 | Spray Dryer 6th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
705 | C4 | 1 | 11 | C4S01,11 | C4S01-X1 | 1756-IB32-11 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-606 | Spray Dryer 6th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
706 | C4 | 1 | 12 | C4S01,12 | C4S01-X1 | 1756-IB32-12 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-606 | Spray Dryer 6th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
707 | C4 | 1 | 13 | C4S01,13 | C4S01-X1 | 1756-IB32-13 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-606 | Spray Dryer 6th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
708 | C4 | 1 | 14 | C4S01,14 | C4S01-X1 | 1756-IB32-14 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-606 | Spray Dryer 6th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
709 | C4 | 1 | 15 | C4S01,15 | C4S01-X1 | 1756-IB32-15 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-606 | Spray Dryer 6th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
710 | C4 | 1 | 16 | C4S01,16 | C4S01-X2 | 1756-IB32-16 | DI | Dry Contact | ZS-60201A | 0 | Limit Switch for CHAM-21 (Spray Chamber) | ZS-60201A_DI_1 | 3-25-01-602-PD-04 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 6th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
711 | C4 | 1 | 17 | C4S01,17 | C4S01-X2 | 1756-IB32-17 | DI | Dry Contact | ZS-60201B | 0 | Limit Switch for CHAM-21 (Spray Chamber) | ZS-60201B_DI_1 | 3-25-01-602-PD-04 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 6th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
712 | C4 | 1 | 18 | C4S01,18 | C4S01-X2 | 1756-IB32-18 | DI | Dry Contact | ZS-60231C | 0 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Spool Inserted) | ZS-60231C_DI_1 | 3-25-01-602-PD-04 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 5th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
713 | C4 | 1 | 19 | C4S01,19 | C4S01-X2 | 1756-IB32-19 | DI | Dry Contact | ZS-60231D | 0 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Blind Inserted) | ZS-60231D_DI_1 | 3-25-01-602-PD-04 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 5th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
714 | C4 | 1 | 20 | C4S01,20 | C4S01-X2 | 1756-IB32-20 | DI | Dry Contact | ZS-60231E | 0 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Spool Inserted) | ZS-60231E_DI_1 | 3-25-01-602-PD-05 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 5th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
715 | C4 | 1 | 21 | C4S01,21 | C4S01-X2 | 1756-IB32-21 | DI | Dry Contact | ZS-60231F | 0 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Blind Inserted) | ZS-60231F_DI_1 | 3-25-01-602-PD-05 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 5th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
716 | C4 | 1 | 22 | C4S01,22 | C4S01-X2 | 1756-IB32-22 | DI | Dry Contact | ZS-60240 | 0 | Limit Switch for FA-60240 (Door Service) | ZS-60240_DI_1 | 3-25-01-602-PD-05 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 6th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
717 | C4 | 1 | 23 | C4S01,23 | C4S01-X2 | 1756-IB32-23 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
718 | C4 | 1 | 24 | C4S01,24 | C4S01-X2 | 1756-IB32-24 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
719 | C4 | 1 | 25 | C4S01,25 | C4S01-X2 | 1756-IB32-25 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
720 | C4 | 1 | 26 | C4S01,26 | C4S01-X2 | 1756-IB32-26 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
721 | C4 | 1 | 27 | C4S01,27 | C4S01-X2 | 1756-IB32-27 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
722 | C4 | 1 | 28 | C4S01,28 | C4S01-X2 | 1756-IB32-28 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
723 | C4 | 1 | 29 | C4S01,29 | C4S01-X2 | 1756-IB32-29 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
724 | C4 | 1 | 30 | C4S01,30 | C4S01-X2 | 1756-IB32-30 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
725 | C4 | 1 | 31 | C4S01,31 | C4S01-X2 | 1756-IB32-31 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
726 | C4 | 2 | 0 | C4S02,00 | C4S02-X1 | 1756-IB32-0 | DI | Dry Contact | PSL-61305 | 0 | Pressure alarm low | PSL-61305_DI_1 | 3-25-01-613-PD-03 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
727 | C4 | 2 | 1 | C4S02,01 | C4S02-X1 | 1756-IB32-1 | DI | Dry Contact | PSL-61306 | 0 | Pressure alarm low | PSL-61306_DI_1 | 3-25-01-613-PD-05 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
728 | C4 | 2 | 2 | C4S02,02 | C4S02-X1 | 1756-IB32-2 | DI | - | PVM-61301 | - | - | PVM-61301_DI_1 | 325-01-613-PD-03 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
729 | C4 | 2 | 3 | C4S02,03 | C4S02-X1 | 1756-IB32-3 | DI | - | PVM-61301 | - | - | PVM-61301_DI_2 | 325-01-613-PD-03 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
730 | C4 | 2 | 4 | C4S02,04 | C4S02-X1 | 1756-IB32-4 | DI | Dry Contact | XA-61301A | 0 | Request filter plant | XA-61301A_DI_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
731 | C4 | 2 | 5 | C4S02,05 | C4S02-X1 | 1756-IB32-5 | DI | Dry Contact | XA-61301B | 0 | Request material transport | XA-61301B_DI_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
732 | C4 | 2 | 6 | C4S02,06 | C4S02-X1 | 1756-IB32-6 | DI | Dry Contact | XA-61301C | 0 | Request belt plant | XA-61301C_DI_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
733 | C4 | 2 | 7 | C4S02,07 | C4S02-X1 | 1756-IB32-7 | DI | Dry Contact | XA-61301D | 0 | Machine in operation | XA-61301D_DI_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
734 | C4 | 2 | 8 | C4S02,08 | C4S02-X1 | 1756-IB32-8 | DI | Dry Contact | XA-61301E | 0 | General Fault | XA-61301E_DI_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
735 | C4 | 2 | 9 | C4S02,09 | C4S02-X1 | 1756-IB32-9 | DI | Dry Contact | XA-61301F | 0 | Machine is ready | XA-61301F_DI_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
736 | C4 | 2 | 10 | C4S02,10 | C4S02-X1 | 1756-IB32-10 | DI | Dry Contact | XA-61301G | 0 | Emergency stop activated | XA-61301G_DI_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
737 | C4 | 2 | 11 | C4S02,11 | C4S02-X1 | 1756-IB32-11 | DI | Dry Contact | XA-61301H | 0 | Silo minimum | XA-61301H_DI_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
738 | C4 | 2 | 12 | C4S02,12 | C4S02-X1 | 1756-IB32-12 | DI | Dry Contact | XA-61301J | 0 | Silo maximum | XA-61301J_DI_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
739 | C4 | 2 | 13 | C4S02,13 | C4S02-X1 | 1756-IB32-13 | DI | 24 VDC energized | XV-61302 | 0 | Dust collector feed vent | XV-61302_DI_1 | 3-25-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
740 | C4 | 2 | 14 | C4S02,14 | C4S02-X1 | 1756-IB32-14 | DI | 24 VDC energized | XV-61302 | 0 | Dust collector feed vent | XV-61302_DI_2 | 3-25-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
741 | C4 | 2 | 15 | C4S02,15 | C4S02-X1 | 1756-IB32-15 | DI | 24 VDC energized | XV-61303 | 0 | Dust collector feed from packer | XV-61303_DI_1 | 3-25-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
742 | C4 | 2 | 16 | C4S02,16 | C4S02-X2 | 1756-IB32-16 | DI | 24 VDC energized | XV-61303 | 0 | Dust collector feed from packer | XV-61303_DI_2 | 3-25-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
743 | C4 | 2 | 17 | C4S02,17 | C4S02-X2 | 1756-IB32-17 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
744 | C4 | 2 | 18 | C4S02,18 | C4S02-X2 | 1756-IB32-18 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
745 | C4 | 2 | 19 | C4S02,19 | C4S02-X2 | 1756-IB32-19 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
746 | C4 | 2 | 20 | C4S02,20 | C4S02-X2 | 1756-IB32-20 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
747 | C4 | 2 | 21 | C4S02,21 | C4S02-X2 | 1756-IB32-21 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
748 | C4 | 2 | 22 | C4S02,22 | C4S02-X2 | 1756-IB32-22 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
749 | C4 | 2 | 23 | C4S02,23 | C4S02-X2 | 1756-IB32-23 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
750 | C4 | 2 | 24 | C4S02,24 | C4S02-X2 | 1756-IB32-24 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
751 | C4 | 2 | 25 | C4S02,25 | C4S02-X2 | 1756-IB32-25 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
752 | C4 | 2 | 26 | C4S02,26 | C4S02-X2 | 1756-IB32-26 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
753 | C4 | 2 | 27 | C4S02,27 | C4S02-X2 | 1756-IB32-27 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
754 | C4 | 2 | 28 | C4S02,28 | C4S02-X2 | 1756-IB32-28 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
755 | C4 | 2 | 29 | C4S02,29 | C4S02-X2 | 1756-IB32-29 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
756 | C4 | 2 | 30 | C4S02,30 | C4S02-X2 | 1756-IB32-30 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
757 | C4 | 2 | 31 | C4S02,31 | C4S02-X2 | 1756-IB32-31 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
758 | C4 | 3 | 0 | C4S03,00 | C4S03-X1 | 1756-IB32-0 | DI | Dry Contact | ISV-61303 | 0 | Explosion isolation flap valve ISV-61303 | ISV-61303_DI_1 | 3-25-01-613-PD-03 | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
759 | C4 | 3 | 1 | C4S03,01 | C4S03-X1 | 1756-IB32-1 | DI | Dry Contact | ISV-61304 | 0 | Explosion isolation flap valve ISV-61304 | ISV-61304_DI_1 | 3-25-01-613-PD-05 | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
760 | C4 | 3 | 2 | C4S03,02 | C4S03-X1 | 1756-IB32-2 | DI | Dry Contact | LSH-61304 | 0 | Big bag level alarm high | LSH-61304_DI_1 | 3-25-01-613-PD-03 | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
761 | C4 | 3 | 3 | C4S03,03 | C4S03-X1 | 1756-IB32-3 | DI | Dry Contact | LSH-61305 | 0 | Big bag level alarm high | LSH-61305_DI_1 | 3-25-01-613-PD-05 | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
762 | C4 | 3 | 4 | C4S03,04 | C4S03-X1 | 1756-IB32-4 | DI | Dry Contact | LSH-61307 | 0 | High Level alarm reject screen | LSH-61307_DI_1 | 3-25-01-613-PD-01 | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
763 | C4 | 3 | 5 | C4S03,05 | C4S03-X1 | 1756-IB32-5 | DI | Dry Contact | LSH-61312 | 0 | Level alarm high | LSH-61312_DI_1 | 3-25-01-613-PD-05 | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
764 | C4 | 3 | 6 | C4S03,06 | C4S03-X1 | 1756-IB32-6 | DI | Dry Contact | PSE-61302 | 0 | Explosion Vent PSE-61302 | PSE-61302_DI_1 | 3-25-01-613-PD-03 | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
765 | C4 | 3 | 7 | C4S03,07 | C4S03-X1 | 1756-IB32-7 | DI | Dry Contact | PSE-61303 | 0 | Explosion Vent PSE-61303 | PSE-61303_DI_1 | 3-25-01-613-PD-05 | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
766 | C4 | 3 | 9 | C4S03,09 | C4S03-X1 | 1756-IB32-9 | DI | - | RV-61301 | - | - | RV-61301_DI_1 | - | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
767 | C4 | 3 | 10 | C4S03,10 | C4S03-X1 | 1756-IB32-10 | DI | - | RV-61304 | - | - | RV-61304_DI_1 | - | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
768 | C4 | 3 | 11 | C4S03,11 | C4S03-X1 | 1756-IB32-11 | DI | - | RV-61305 | - | - | RV-61305_DI_1 | - | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
769 | C4 | 3 | 12 | C4S03,12 | C4S03-X1 | 1756-IB32-12 | DI | - | SC-61301 | - | - | SC-61301_DI_1 | - | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
770 | C4 | 3 | 13 | C4S03,13 | C4S03-X1 | 1756-IB32-13 | DI | - | SC-61302 | - | - | SC-61302_DI_1 | - | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
771 | C4 | 3 | 14 | C4S03,14 | C4S03-X1 | 1756-IB32-14 | DI | Dry Contact | ZS-61312 | 0 | Position Magnet Door | ZS-61312_DI_1 | 3-25-01-613-PD-01 | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 3rd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
772 | C4 | 3 | 15 | C4S03,15 | C4S03-X1 | 1756-IB32-15 | DI | Dry Contact | ZS-61313 | 0 | Position Magnet Door | ZS-61313_DI_1 | 3-25-01-613-PD-01 | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 3rd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
773 | C4 | 3 | 16 | C4S03,16 | C4S03-X2 | 1756-IB32-16 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
774 | C4 | 3 | 17 | C4S03,17 | C4S03-X2 | 1756-IB32-17 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
775 | C4 | 3 | 18 | C4S03,18 | C4S03-X2 | 1756-IB32-18 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
776 | C4 | 3 | 19 | C4S03,19 | C4S03-X2 | 1756-IB32-19 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
777 | C4 | 3 | 20 | C4S03,20 | C4S03-X2 | 1756-IB32-20 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
778 | C4 | 3 | 21 | C4S03,21 | C4S03-X2 | 1756-IB32-21 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
779 | C4 | 3 | 22 | C4S03,22 | C4S03-X2 | 1756-IB32-22 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
780 | C4 | 3 | 23 | C4S03,23 | C4S03-X2 | 1756-IB32-23 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
781 | C4 | 3 | 24 | C4S03,24 | C4S03-X2 | 1756-IB32-24 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
782 | C4 | 3 | 25 | C4S03,25 | C4S03-X2 | 1756-IB32-25 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
783 | C4 | 3 | 26 | C4S03,26 | C4S03-X2 | 1756-IB32-26 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
784 | C4 | 3 | 27 | C4S03,27 | C4S03-X2 | 1756-IB32-27 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
785 | C4 | 3 | 28 | C4S03,28 | C4S03-X2 | 1756-IB32-28 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
786 | C4 | 3 | 29 | C4S03,29 | C4S03-X2 | 1756-IB32-29 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
787 | C4 | 3 | 30 | C4S03,30 | C4S03-X2 | 1756-IB32-30 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
788 | C4 | 3 | 31 | C4S03,31 | C4S03-X2 | 1756-IB32-31 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
789 | C4 | 4 | 0 | C4S04,00 | C4S04-X1 | 1756-OB32-0 | DO | 24 VDC energized | SV-60220 | 0 | PA On/Off Valve for Chamber PSE purge air (CHAM-21) | SV-60220_DO_1 | 3-25-01-602-PD-04 | JB-606 | Spray Dryer 6th Floor | Spray Dryer | 6th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
790 | C4 | 4 | 1 | C4S04,01 | C4S04-X1 | 1756-OB32-1 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-606 | Spray Dryer 6th Floor | Spray Dryer | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
791 | C4 | 4 | 2 | C4S04,02 | C4S04-X1 | 1756-OB32-2 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-606 | Spray Dryer 6th Floor | Spray Dryer | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
792 | C4 | 4 | 3 | C4S04,03 | C4S04-X1 | 1756-OB32-3 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-606 | Spray Dryer 6th Floor | Spray Dryer | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
793 | C4 | 4 | 4 | C4S04,04 | C4S04-X1 | 1756-OB32-4 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-606 | Spray Dryer 6th Floor | Spray Dryer | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
794 | C4 | 4 | 5 | C4S04,05 | C4S04-X1 | 1756-OB32-5 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-606 | Spray Dryer 6th Floor | Spray Dryer | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
795 | C4 | 4 | 6 | C4S04,06 | C4S04-X1 | 1756-OB32-6 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-606 | Spray Dryer 6th Floor | Spray Dryer | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
796 | C4 | 4 | 7 | C4S04,07 | C4S04-X1 | 1756-OB32-7 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-606 | Spray Dryer 6th Floor | Spray Dryer | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
797 | C4 | 4 | 8 | C4S04,08 | C4S04-X1 | 1756-OB32-8 | DO | 4 - 20 mA | XA-60201 | 0 | LEL gas Buzzer Alarm | XA-60201_DO_1 | 3-25-01-602-PD-03 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 5th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
798 | C4 | 4 | 9 | C4S04,09 | C4S04-X1 | 1756-OB32-9 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
799 | C4 | 4 | 10 | C4S04,10 | C4S04-X1 | 1756-OB32-10 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
800 | C4 | 4 | 11 | C4S04,11 | C4S04-X1 | 1756-OB32-11 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
801 | C4 | 4 | 12 | C4S04,12 | C4S04-X1 | 1756-OB32-12 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
802 | C4 | 4 | 13 | C4S04,13 | C4S04-X1 | 1756-OB32-13 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
803 | C4 | 4 | 14 | C4S04,14 | C4S04-X1 | 1756-OB32-14 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
804 | C4 | 4 | 15 | C4S04,15 | C4S04-X1 | 1756-OB32-15 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
805 | C4 | 4 | 16 | C4S04,16 | C4S04-X2 | 1756-OB32-16 | DO | - | PVM-61301 | - | - | PVM-61301_DO_1 | 325-01-613-PD-03 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
806 | C4 | 4 | 17 | C4S04,17 | C4S04-X2 | 1756-OB32-17 | DO | - | PVM-61301 | - | - | PVM-61301_DO_2 | 325-01-613-PD-03 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
807 | C4 | 4 | 18 | C4S04,18 | C4S04-X2 | 1756-OB32-18 | DO | - | SV-61307 | - | - | SV-61307_DO_1 | 3-25-01-613-PD-01 | JB-612 | Packing Tower 2th Floor | Packing Tower | 3rd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
808 | C4 | 4 | 19 | C4S04,19 | C4S04-X2 | 1756-OB32-19 | DO | 24 VDC energized | SV-61308 | 0 | Timer compress air pluse solenoid valve | SV-61308_DO_1 | 325-01-613-PD-03 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
809 | C4 | 4 | 20 | C4S04,20 | C4S04-X2 | 1756-OB32-20 | DO | 24 VDC energized | SV-61309 | 0 | Air service | SV-61309_DO_1 | 3-25-01-613-PD-03 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
810 | C4 | 4 | 21 | C4S04,21 | C4S04-X2 | 1756-OB32-21 | DO | 24 VDC energized | SV-61310 | 0 | Timer compress air pluse solenoid valve | SV-61310_DO_1 | 325-01-613-PD-05 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
811 | C4 | 4 | 22 | C4S04,22 | C4S04-X2 | 1756-OB32-22 | DO | 24 VDC energized | SV-61311 | 0 | Air service | SV-61311_DO_1 | 3-25-01-613-PD-05 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
812 | C4 | 4 | 23 | C4S04,23 | C4S04-X2 | 1756-OB32-23 | DO | 24 VDC energized | XS-61301A | 0 | Filter plant in operation | XS-61301A_DO_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
813 | C4 | 4 | 24 | C4S04,24 | C4S04-X2 | 1756-OB32-24 | DO | 24 VDC energized | XS-61301B | 0 | Material transport in operation | XS-61301B_DO_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
814 | C4 | 4 | 25 | C4S04,25 | C4S04-X2 | 1756-OB32-25 | DO | 24 VDC energized | XS-61301C | 0 | Belt plant in operation | XS-61301C_DO_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
815 | C4 | 4 | 26 | C4S04,26 | C4S04-X2 | 1756-OB32-26 | DO | 24 VDC energized | XS-61301D | 0 | Sequence Stop | XS-61301D_DO_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
816 | C4 | 4 | 27 | C4S04,27 | C4S04-X2 | 1756-OB32-27 | DO | 24 VDC energized | XS-61301E | 0 | Status from Customer Emergency stop | XS-61301E_DO_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
817 | C4 | 4 | 28 | C4S04,28 | C4S04-X2 | 1756-OB32-28 | DO | 24 VDC energized | XS-61301F | 0 | Operation Release | XS-61301F_DO_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
818 | C4 | 4 | 29 | C4S04,29 | C4S04-X2 | 1756-OB32-29 | DO | 24 VDC energized | XV-61302 | 0 | Dust collector feed vent | XV-61302_DO_1 | 3-25-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
819 | C4 | 4 | 30 | C4S04,30 | C4S04-X2 | 1756-OB32-30 | DO | 24 VDC energized | XV-61303 | 0 | Dust collector feed from packer | XV-61303_DO_1 | 3-25-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
820 | C4 | 4 | 31 | C4S04,31 | C4S04-X2 | 1756-OB32-31 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | JB-612 | Packing Tower 2th Floor | Packing Tower | - | =CA1+MCP-M4 | SPARE | Require I/O DI= ,DO=,AI=,AO=,Bus=
821 | C4 | 5 | 0 | C4S05,00 | C4S05-X1 | 1756-IF16-0 | AI | 4 - 20 mA | DPT-60201 | Differential Pressure Transmitte | Steam filter pressure | DPT-60201_AI_1 | 3-25-01-602-PD-09 | JB-606 | Spray Dryer 6th Floor | Spray Dryer | 6th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
822 | C4 | 5 | 1 | C4S05,01 | C4S05-X1 | 1756-IF16-1 | AI | 4 - 20 mA | FT-60203 | 0 | Culinary steam feed to Spray dryer | FT-60203_AI_1 | 3-25-01-602-PD-09 | JB-606 | Spray Dryer 6th Floor | Spray Dryer | 6th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0
823 | C4 | 5 | 2 | C4S05,02 | C4S05-X1 | 1756-IF16-2 | AI | 4 - 20 mA | TT-60245 | 0 | Gas Temperature Transmitter for Exhaust Stack (DTXS-21) | TT-60245_AI_1 | 3-25-01-602-PD-05 | JB-608 | Spray Dryer 8th Floor | Spray Dryer | 8th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
824 | C4 | 5 | 3 | C4S05,03 | C4S05-X1 | 1756-IF16-3 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
825 | C4 | 5 | 4 | C4S05,04 | C4S05-X1 | 1756-IF16-4 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
826 | C4 | 5 | 5 | C4S05,05 | C4S05-X1 | 1756-IF16-5 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
827 | C4 | 5 | 6 | C4S05,06 | C4S05-X1 | 1756-IF16-6 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
828 | C4 | 5 | 6 | C4S05,06 | C4S05-X1 | 1756-IF16-6 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
829 | C4 | 5 | 7 | C4S05,07 | C4S05-X1 | 1756-IF16-7 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
830 | C4 | 5 | 7 | C4S05,07 | C4S05-X1 | 1756-IF16-7 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-608 | Spray Dryer 8th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
831 | C4 | 5 | 8 | C4S05,08 | C4S05-X1 | 1756-IF16-8 | AI | 4 - 20 mA | PT-61302 | Pressure Transmitter | Pressure in vacuum line | PT-61302_AI_1 | 3-25-01-613-PD-03 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
832 | C4 | 5 | 9 | C4S05,09 | C4S05-X1 | 1756-IF16-9 | AI | 4 - 20 mA | PT-61309 | Pressure Transmitter | Pressure transmitter | PT-61309_AI_1 | 3-25-01-613-PD-04 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
833 | C4 | 5 | 10 | C4S05,10 | C4S05-X1 | 1756-IF16-10 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
834 | C4 | 5 | 11 | C4S05,11 | C4S05-X1 | 1756-IF16-11 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
835 | C4 | 5 | 12 | C4S05,12 | C4S05-X1 | 1756-IF16-12 | AI | 4 - 20 mA | PT-61302 | Pressure Transmitter | Pressure in vacuum line | PT-61302_AI_1 | 3-25-01-613-PD-03 | JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
836 | C4 | 5 | 13 | C4S05,13 | C4S05-X1 | 1756-IF16-13 | AI | 4 - 20 mA | PT-61309 | Pressure Transmitter | Pressure transmitter | PT-61309_AI_1 | 3-25-01-613-PD-04 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
837 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
838 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
839 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
840 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
841 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
842 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
843 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
844 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
845 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | IS-JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
846 | C4 | 5 | 15 | C4S05,15 | C4S05-X1 | 1756-IF16-15 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | JB-612 | Packing Tower 2th Floor | - | - | =CA1+MCP-M4 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
847 | C4 | 6 | 0 | C4S06,00 | C4S06-X1 | 1756-IF16-0 | AI | 4 - 20 mA | PT-60220 | Pressure Transmitter | Gas Pressure Transmitter for Chamber (CHAM-21) | PT-60220_AI_1 | 3-25-01-602-PD-04 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 6th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
848 | C4 | 6 | 1 | C4S06,01 | C4S06-X1 | 1756-IF16-1 | AI | 4 - 20 mA | TT-60220 | 0 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | TT-60220_AI_1 | 3-25-01-602-PD-04 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 6th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
849 | C4 | 6 | 2 | C4S06,02 | C4S06-X1 | 1756-IF16-2 | AI | 4 - 20 mA | TT-60221 | 0 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | TT-60221_AI_1 | 3-25-01-602-PD-04 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 6th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
850 | C4 | 6 | 3 | C4S06,03 | C4S06-X1 | 1756-IF16-3 | AI | 4 - 20 mA | TT-60222 | 0 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | TT-60222_AI_1 | 3-25-01-602-PD-04 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 5th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
851 | C4 | 6 | 4 | C4S06,04 | C4S06-X1 | 1756-IF16-4 | AI | 4 - 20 mA | TT-60223 | 0 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | TT-60223_AI_1 | 3-25-01-602-PD-04 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 5th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
852 | C4 | 6 | 5 | C4S06,05 | C4S06-X1 | 1756-IF16-5 | AI | 4 - 20 mA | XT-60201 | 0 | LEL gas analyzer | XT-60201_AI_1 | 3-25-01-602-PD-03 | IS-JB-608 | Spray Dryer 8th Floor | Spray Dryer | 5th | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
853 | C4 | 6 | 6 | C4S06,06 | C4S06-X1 | 1756-IF16-6 | AI | 4 - 20 mA | DPT-61310 | Differential Pressure Transmitte | Vent filter pressure | DPT-61310_AI_1 | 3-25-01-613-PD-03 | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
854 | C4 | 6 | 7 | C4S06,07 | C4S06-X1 | 1756-IF16-7 | AI | - | DPT-61312 | - | - | DPT-61312_AI_1 | 3-25-01-613-PD-05 | IS-JB-612 | Packing Tower 2th Floor | Packing Tower | 2nd | =CA1+MCP-M4 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
855 | C5 | 1 | 0 | C5S01,00 | C5S01-X1 | 1756-IB32-0 | DI | - | FS-20201 | - | - | FS-20201_DI_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
856 | C5 | 1 | 1 | C5S01,01 | C5S01-X1 | 1756-IB32-1 | DI | 4 - 20 mA,Pulse | FT-913201 | 0 | Flow outlet LPG line | FT-913201_DI_1 | 3-25-01-913-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0
857 | C5 | 1 | 2 | C5S01,02 | C5S01-X1 | 1756-IB32-2 | DI | 4 - 20 mA,Pulse | FT-936201 | 0 | Process Water | FT-936201_DI_1 | 3-25-01-930-PD-08 | RIO-200 | Slurry - Out Building 2nd Floor | Process Water | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0
858 | C5 | 1 | 3 | C5S01,03 | C5S01-X1 | 1756-IB32-3 | DI | 4 - 20 mA,Pulse | FT-936202 | 0 | Process Water | FT-936202_DI_1 | 3-25-01-930-PD-07 | RIO-200 | Slurry - Out Building 2nd Floor | Process Water | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0
859 | C5 | 1 | 4 | C5S01,04 | C5S01-X1 | 1756-IB32-4 | DI | Dry Contact | LSL-814201 | 0 | Low Level alarm | LSL-814201_DI_1 | 3-25-01-814-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | CIP Water System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
860 | C5 | 1 | 5 | C5S01,05 | C5S01-X1 | 1756-IB32-5 | DI | - | PK-913201 | - | - | PK-913201_DI_1 | - | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
861 | C5 | 1 | 6 | C5S01,06 | C5S01-X1 | 1756-IB32-6 | DI | - | PK-913202 | - | - | PK-913202_DI_1 | - | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
862 | C5 | 1 | 7 | C5S01,07 | C5S01-X1 | 1756-IB32-7 | DI | Dry Contact | HV-20204 | Manual Valve With Position Switch | Slurry Drain line | HV-20204_DI_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
863 | C5 | 1 | 8 | C5S01,08 | C5S01-X1 | 1756-IB32-8 | DI | Dry Contact | HV-20205 | Manual Valve With Position Switch | Slurry Drain line | HV-20205_DI_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
864 | C5 | 1 | 9 | C5S01,09 | C5S01-X1 | 1756-IB32-9 | DI | Dry Contact | HV-20206 | Manual Valve With Position Switch | Slurry Drain line | HV-20206_DI_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
865 | C5 | 1 | 10 | C5S01,10 | C5S01-X1 | 1756-IB32-10 | DI | Dry Contact | HV-20207 | Manual Valve With Position Switch | Slurry Drain line | HV-20207_DI_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
866 | C5 | 1 | 11 | C5S01,11 | C5S01-X1 | 1756-IB32-11 | DI | Dry Contact | HV-20208 | Manual Valve With Position Switch | Slurry Drain line | HV-20208_DI_1 | 3-25-01-202-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
867 | C5 | 1 | 12 | C5S01,12 | C5S01-X1 | 1756-IB32-12 | DI | Dry Contact | HV-20209 | Manual Valve With Position Switch | Slurry Drain line | HV-20209_DI_1 | 3-25-01-202-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
868 | C5 | 1 | 13 | C5S01,13 | C5S01-X1 | 1756-IB32-13 | DI | Dry Contact | HV-20210 | Manual Valve With Position Switch | Slurry Drain line | HV-20210_DI_1 | 3-25-01-202-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
869 | C5 | 1 | 14 | C5S01,14 | C5S01-X1 | 1756-IB32-14 | DI | Dry Contact | XA-80305A | 0 | Gas Vaporizer 5 control status | XA-80305A_DI_1 | 325-01-803-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
870 | C5 | 1 | 15 | C5S01,15 | C5S01-X1 | 1756-IB32-15 | DI | Dry Contact | XA-80305B | 0 | Gas Vaporizer 5 control status | XA-80305B_DI_1 | 325-01-803-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
871 | C5 | 1 | 16 | C5S01,16 | C5S01-X2 | 1756-IB32-16 | DI | Dry Contact | XA-80305C | 0 | Gas Vaporizer 5 control status | XA-80305C_DI_1 | 325-01-803-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
872 | C5 | 1 | 17 | C5S01,17 | C5S01-X2 | 1756-IB32-17 | DI | Dry Contact | XA-80305D | 0 | Gas Vaporizer 5 control status | XA-80305D_DI_1 | 325-01-803-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
873 | C5 | 1 | 18 | C5S01,18 | C5S01-X2 | 1756-IB32-18 | DI | Dry Contact | XA-80305E | 0 | Gas Vaporizer 5 control status | XA-80305E_DI_1 | 325-01-803-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
874 | C5 | 1 | 19 | C5S01,19 | C5S01-X2 | 1756-IB32-19 | DI | Dry Contact | XA-80305F | 0 | Gas Vaporizer 5 control status | XA-80305F_DI_1 | 325-01-803-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
875 | C5 | 1 | 20 | C5S01,20 | C5S01-X2 | 1756-IB32-20 | DI | Dry Contact | XA-80306A | 0 | Gas Vaporizer 6 control status | XA-80306A_DI_1 | 325-01-803-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
876 | C5 | 1 | 21 | C5S01,21 | C5S01-X2 | 1756-IB32-21 | DI | Dry Contact | XA-80306B | 0 | Gas Vaporizer 6 control status | XA-80306B_DI_1 | 325-01-803-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
877 | C5 | 1 | 22 | C5S01,22 | C5S01-X2 | 1756-IB32-22 | DI | Dry Contact | XA-80306C | 0 | Gas Vaporizer 6 control status | XA-80306C_DI_1 | 325-01-803-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
878 | C5 | 1 | 23 | C5S01,23 | C5S01-X2 | 1756-IB32-23 | DI | Dry Contact | XA-80306D | 0 | Gas Vaporizer 6 control status | XA-80306D_DI_1 | 325-01-803-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
879 | C5 | 1 | 24 | C5S01,24 | C5S01-X2 | 1756-IB32-24 | DI | Dry Contact | XA-80306E | 0 | Gas Vaporizer 6 control status | XA-80306E_DI_1 | 325-01-803-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
880 | C5 | 1 | 25 | C5S01,25 | C5S01-X2 | 1756-IB32-25 | DI | Dry Contact | XA-80306F | 0 | Gas Vaporizer 6 control status | XA-80306F_DI_1 | 325-01-803-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
881 | C5 | 1 | 26 | C5S01,26 | C5S01-X2 | 1756-IB32-26 | DI | 24 VDC energized | XV-20201 | 0 | Slurry Preparation Tank 1 | XV-20201_DI_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
882 | C5 | 1 | 27 | C5S01,27 | C5S01-X2 | 1756-IB32-27 | DI | 24 VDC energized | XV-20201 | 0 | Slurry Preparation Tank 1 | XV-20201_DI_2 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
883 | C5 | 1 | 28 | C5S01,28 | C5S01-X2 | 1756-IB32-28 | DI | 24 VDC energized | XV-20202 | 0 | Slurry Preparation Tank 1 | XV-20202_DI_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
884 | C5 | 1 | 29 | C5S01,29 | C5S01-X2 | 1756-IB32-29 | DI | 24 VDC energized | XV-20202 | 0 | Slurry Preparation Tank 1 | XV-20202_DI_2 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
885 | C5 | 1 | 30 | C5S01,30 | C5S01-X2 | 1756-IB32-30 | DI | 24 VDC energized | XV-20203 | 0 | Slurry Preparation Tank 1 | XV-20203_DI_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
886 | C5 | 1 | 31 | C5S01,31 | C5S01-X2 | 1756-IB32-31 | DI | 24 VDC energized | XV-20203 | 0 | Slurry Preparation Tank 1 | XV-20203_DI_2 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
887 | C5 | 2 | 0 | C5S02,00 | C5S02-X1 | 1756-IB32-0 | DI | 24 VDC energized | XV-20211 | 0 | Slurry Preparation Tank 2 | XV-20211_DI_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
888 | C5 | 2 | 1 | C5S02,01 | C5S02-X1 | 1756-IB32-1 | DI | 24 VDC energized | XV-20211 | 0 | Slurry Preparation Tank 2 | XV-20211_DI_2 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
889 | C5 | 2 | 2 | C5S02,02 | C5S02-X1 | 1756-IB32-2 | DI | 24 VDC energized | XV-20212 | 0 | Slurry Preparation Tank 2 | XV-20212_DI_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
890 | C5 | 2 | 3 | C5S02,03 | C5S02-X1 | 1756-IB32-3 | DI | 24 VDC energized | XV-20212 | 0 | Slurry Preparation Tank 2 | XV-20212_DI_2 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
891 | C5 | 2 | 4 | C5S02,04 | C5S02-X1 | 1756-IB32-4 | DI | 24 VDC energized | XV-20213 | 0 | Slurry Preparation Tank 2 | XV-20213_DI_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
892 | C5 | 2 | 5 | C5S02,05 | C5S02-X1 | 1756-IB32-5 | DI | 24 VDC energized | XV-20213 | 0 | Slurry Preparation Tank 2 | XV-20213_DI_2 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
893 | C5 | 2 | 6 | C5S02,06 | C5S02-X1 | 1756-IB32-6 | DI | 24 VDC energized | XV-913201 | 0 | Outlet LPG line | XV-913201_DI_1 | 3-25-01-913-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=1,AO=0,Bus=0
894 | C5 | 2 | 7 | C5S02,07 | C5S02-X1 | 1756-IB32-7 | DI | 24 VDC energized | XV-913201 | 0 | Outlet LPG line | XV-913201_DI_1 | 3-25-01-913-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=1,AO=0,Bus=0
895 | C5 | 2 | 8 | C5S02,08 | C5S02-X1 | 1756-IB32-8 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
896 | C5 | 2 | 9 | C5S02,09 | C5S02-X1 | 1756-IB32-9 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
897 | C5 | 2 | 10 | C5S02,10 | C5S02-X1 | 1756-IB32-10 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
898 | C5 | 2 | 11 | C5S02,11 | C5S02-X1 | 1756-IB32-11 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
899 | C5 | 2 | 12 | C5S02,12 | C5S02-X1 | 1756-IB32-12 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
900 | C5 | 2 | 13 | C5S02,13 | C5S02-X1 | 1756-IB32-13 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
901 | C5 | 2 | 14 | C5S02,14 | C5S02-X1 | 1756-IB32-14 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
902 | C5 | 2 | 15 | C5S02,15 | C5S02-X1 | 1756-IB32-15 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
903 | C5 | 2 | 16 | C5S02,16 | C5S02-X2 | 1756-IB32-16 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
904 | C5 | 2 | 17 | C5S02,17 | C5S02-X2 | 1756-IB32-17 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
905 | C5 | 2 | 18 | C5S02,18 | C5S02-X2 | 1756-IB32-18 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
906 | C5 | 2 | 19 | C5S02,19 | C5S02-X2 | 1756-IB32-19 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
907 | C5 | 2 | 20 | C5S02,20 | C5S02-X2 | 1756-IB32-20 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
908 | C5 | 2 | 21 | C5S02,21 | C5S02-X2 | 1756-IB32-21 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
909 | C5 | 2 | 22 | C5S02,22 | C5S02-X2 | 1756-IB32-22 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
910 | C5 | 2 | 23 | C5S02,23 | C5S02-X2 | 1756-IB32-23 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
911 | C5 | 2 | 24 | C5S02,24 | C5S02-X2 | 1756-IB32-24 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
912 | C5 | 2 | 25 | C5S02,25 | C5S02-X2 | 1756-IB32-25 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
913 | C5 | 2 | 26 | C5S02,26 | C5S02-X2 | 1756-IB32-26 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
914 | C5 | 2 | 27 | C5S02,27 | C5S02-X2 | 1756-IB32-27 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
915 | C5 | 2 | 28 | C5S02,28 | C5S02-X2 | 1756-IB32-28 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
916 | C5 | 2 | 29 | C5S02,29 | C5S02-X2 | 1756-IB32-29 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
917 | C5 | 2 | 30 | C5S02,30 | C5S02-X2 | 1756-IB32-30 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
918 | C5 | 2 | 31 | C5S02,31 | C5S02-X2 | 1756-IB32-31 | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
919 | C5 | 3 | 0 | C5S03,00 | C5S03-X1 | 1756-OB32-0 | DO | 4 - 20 mA | XA-92201 | 0 | LEL gas Buzzer Alarm | XA-92201_DO_1 | 3-25-01-922-PD-03 | RIO-200 | Slurry - Out Building 2nd Floor | Boiler System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
920 | C5 | 3 | 1 | C5S03,01 | C5S03-X1 | 1756-OB32-1 | DO | 24 VDC energized | XV-20201 | 0 | Slurry Preparation Tank 1 | XV-20201_DO_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
921 | C5 | 3 | 2 | C5S03,02 | C5S03-X1 | 1756-OB32-2 | DO | 24 VDC energized | XV-20202 | 0 | Slurry Preparation Tank 1 | XV-20202_DO_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
922 | C5 | 3 | 3 | C5S03,03 | C5S03-X1 | 1756-OB32-3 | DO | 24 VDC energized | XV-20203 | 0 | Slurry Preparation Tank 1 | XV-20203_DO_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
923 | C5 | 3 | 4 | C5S03,04 | C5S03-X1 | 1756-OB32-4 | DO | 24 VDC energized | XV-20211 | 0 | Slurry Preparation Tank 2 | XV-20211_DO_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
924 | C5 | 3 | 5 | C5S03,05 | C5S03-X1 | 1756-OB32-5 | DO | 24 VDC energized | XV-20212 | 0 | Slurry Preparation Tank 2 | XV-20212_DO_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
925 | C5 | 3 | 6 | C5S03,06 | C5S03-X1 | 1756-OB32-6 | DO | 24 VDC energized | XV-20213 | 0 | Slurry Preparation Tank 2 | XV-20213_DO_1 | 3-25-01-202-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | Slurry - Out Building | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0
926 | C5 | 3 | 7 | C5S03,07 | C5S03-X1 | 1756-OB32-7 | DO | 24 VDC energized | XV-913201 | 0 | Outlet LPG line | XV-913201_DO_1 | 3-25-01-913-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 2,DO=1,AI=1,AO=0,Bus=0
927 | C5 | 3 | 8 | C5S03,08 | C5S03-X1 | 1756-OB32-8 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
928 | C5 | 3 | 9 | C5S03,09 | C5S03-X1 | 1756-OB32-9 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
929 | C5 | 3 | 10 | C5S03,10 | C5S03-X1 | 1756-OB32-10 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
930 | C5 | 3 | 11 | C5S03,11 | C5S03-X1 | 1756-OB32-11 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
931 | C5 | 3 | 12 | C5S03,12 | C5S03-X1 | 1756-OB32-12 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
932 | C5 | 3 | 13 | C5S03,13 | C5S03-X1 | 1756-OB32-13 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
933 | C5 | 3 | 14 | C5S03,14 | C5S03-X1 | 1756-OB32-14 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
934 | C5 | 3 | 15 | C5S03,15 | C5S03-X1 | 1756-OB32-15 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
935 | C5 | 3 | 16 | C5S03,16 | C5S03-X2 | 1756-OB32-16 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
936 | C5 | 3 | 17 | C5S03,17 | C5S03-X2 | 1756-OB32-17 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
937 | C5 | 3 | 18 | C5S03,18 | C5S03-X2 | 1756-OB32-18 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
938 | C5 | 3 | 19 | C5S03,19 | C5S03-X2 | 1756-OB32-19 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
939 | C5 | 3 | 20 | C5S03,20 | C5S03-X2 | 1756-OB32-20 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
940 | C5 | 3 | 21 | C5S03,21 | C5S03-X2 | 1756-OB32-21 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
941 | C5 | 3 | 22 | C5S03,22 | C5S03-X2 | 1756-OB32-22 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
942 | C5 | 3 | 23 | C5S03,23 | C5S03-X2 | 1756-OB32-23 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
943 | C5 | 3 | 24 | C5S03,24 | C5S03-X2 | 1756-OB32-24 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
944 | C5 | 3 | 25 | C5S03,25 | C5S03-X2 | 1756-OB32-25 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
945 | C5 | 3 | 26 | C5S03,26 | C5S03-X2 | 1756-OB32-26 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
946 | C5 | 3 | 27 | C5S03,27 | C5S03-X2 | 1756-OB32-27 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
947 | C5 | 3 | 28 | C5S03,28 | C5S03-X2 | 1756-OB32-28 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
948 | C5 | 3 | 29 | C5S03,29 | C5S03-X2 | 1756-OB32-29 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
949 | C5 | 3 | 30 | C5S03,30 | C5S03-X2 | 1756-OB32-30 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
950 | C5 | 3 | 31 | C5S03,31 | C5S03-X2 | 1756-OB32-31 | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
951 | C5 | 4 | 0 | C5S04,00 | C5S04-X1 | 1756-IF16-0 | AI | - | EXT-BIILER | - | - | EXT-BIILER_AI_1 | External Remote Setpoint | RIO-200 | Slurry - Out Building 2nd Floor | Boiler System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
952 | C5 | 4 | 1 | C5S04,01 | C5S04-X1 | 1756-IF16-1 | AI | 4 - 20 mA,Pulse | FT-913201 | 0 | Flow outlet LPG line | FT-913201_AI_1 | 3-25-01-913-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0
953 | C5 | 4 | 2 | C5S04,02 | C5S04-X1 | 1756-IF16-2 | AI | 4 - 20 mA,Pulse | FT-913201 | 0 | Flow outlet LPG line | FT-913201_AI_2 | 3-25-01-913-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0
954 | C5 | 4 | 3 | C5S04,03 | C5S04-X1 | 1756-IF16-3 | AI | 4 - 20 mA,Pulse | FT-936201 | 0 | Process Water | FT-936201_AI_1 | 3-25-01-930-PD-08 | RIO-200 | Slurry - Out Building 2nd Floor | Process Water | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0
955 | C5 | 4 | 4 | C5S04,04 | C5S04-X1 | 1756-IF16-4 | AI | 4 - 20 mA,Pulse | FT-936202 | 0 | Process Water | FT-936202_AI_1 | 3-25-01-930-PD-07 | RIO-200 | Slurry - Out Building 2nd Floor | Process Water | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0
956 | C5 | 4 | 5 | C5S04,05 | C5S04-X1 | 1756-IF16-5 | AI | 4 - 20 mA | LT-913201 | Level Transmitter | Level LPG in storage | LT-913201_AI_1 | 3-25-01-913-PD-01 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
957 | C5 | 4 | 6 | C5S04,06 | C5S04-X1 | 1756-IF16-6 | AI | 4 - 20 mA | PT-913201 | Pressure Transmitter | Pressure outlet LPG line | PT-913201_AI_1 | 3-25-01-913-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
958 | C5 | 4 | 7 | C5S04,07 | C5S04-X1 | 1756-IF16-7 | AI | 4 - 20 mA | XT-92201 | 0 | LEL gas analyzer | XT-92201_AI_1 | 3-25-01-922-PD-03 | RIO-200 | Slurry - Out Building 2nd Floor | Boiler System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
959 | C5 | 4 | 8 | C5S04,08 | C5S04-X1 | 1756-IF16-8 | AI | 24 VDC energized | XV-913201 | 0 | Outlet LPG line | XV-913201_AI_1 | 3-25-01-913-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | ACTIVE | Require I/O DI= 0,DO=0,AI=0,AO=0,Bus=0
960 | C5 | 4 | 9 | C5S04,09 | C5S04-X1 | 1756-IF16-9 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | 3-25-01-913-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
961 | C5 | 4 | 10 | C5S04,10 | C5S04-X1 | 1756-IF16-10 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | 3-25-01-913-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
962 | C5 | 4 | 11 | C5S04,11 | C5S04-X1 | 1756-IF16-11 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | 3-25-01-913-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
963 | C5 | 4 | 12 | C5S04,12 | C5S04-X1 | 1756-IF16-12 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | 3-25-01-913-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
964 | C5 | 4 | 13 | C5S04,13 | C5S04-X1 | 1756-IF16-13 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | 3-25-01-913-PD-02 | RIO-200 | Slurry - Out Building 2nd Floor | LPG System | 1st | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
965 | C5 | 4 | 14 | C5S04,14 | C5S04-X1 | 1756-IF16-14 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
966 | C5 | 4 | 15 | C5S04,15 | C5S04-X1 | 1756-IF16-15 | AI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_AI_0 | - | RIO-200 | Slurry - Out Building 2nd Floor | - | - | =CA1+MCP-M5 | SPARE | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0
967 | C6 | 5 | 0 | C6S05,00 | C6S05- | - | DO | - | PCM-2030 | - | - | PCM-2030_DO_1 | 3-25-01-202-PD-01 | MCC | MCC Room | Slurry - Out Building | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
968 | C6 | 5 | 1 | C6S05,01 | C6S05- | - | DO | - | PCM-2030 | - | - | PCM-2030_DO_2 | 3-25-01-202-PD-01 | MCC | MCC Room | Slurry - Out Building | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
969 | C6 | 5 | 2 | C6S05,02 | C6S05- | - | DO | 24 VDC energized | PCM-2031 | 0 | Start / Stop Command for FVNR PC-2031 | PCM-2031_DO_1 | 3-25-01-202-PD-01 | MCC | MCC Room | Slurry - Out Building | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
970 | C6 | 5 | 3 | C6S05,03 | C6S05- | - | DO | 24 VDC energized | PCM-2031 | 0 | Start / Stop Command for FVNR PC-2031 | PCM-2031_DO_2 | 3-25-01-202-PD-01 | MCC | MCC Room | Slurry - Out Building | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
971 | C6 | 5 | 4 | C6S05,04 | C6S05- | - | DO | 24 VDC energized | PCY-814201 | PUMP | Start / Stop Command to VSD PC-81001 | PCY-814201_DO_1 | 3-25-01-810-PD-01 | MCC | MCC Room | CIP Water System | 2nd | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
972 | C6 | 5 | 5 | C6S05,05 | C6S05- | - | DO | 24 VDC energized | PCY-814202 | PUMP | Start / Stop Command to VSD PC-81002 | PCY-814202_DO_1 | 3-25-01-810-PD-01 | MCC | MCC Room | CIP Water System | 2nd | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
973 | C6 | 5 | 6 | C6S05,06 | C6S05- | - | DO | 24 VDC energized | XS-80305 | 0 | Start / Stop Command for Gas Vaporizer 5 | XS-80305_DO_1 | 325-01-803-PD-02 | MCC | MCC Room | LPG System | 1st | MCC | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
974 | C6 | 5 | 7 | C6S05,07 | C6S05- | - | DO | 24 VDC energized | XS-80306 | Pressure Transmitter | Start / Stop Command for Gas Vaporizer 6 | XS-80306_DO_1 | 325-01-803-PD-02 | MCC | MCC Room | LPG System | 1st | MCC | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
975 | C6 | 6 | 0 | C6S06,00 | C6S06- | - | DI | - | PCM-2030 | - | - | PCM-2030_DI_1 | 3-25-01-202-PD-01 | MCC | MCC Room | Slurry - Out Building | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
976 | C6 | 6 | 1 | C6S06,01 | C6S06- | - | DI | - | PCM-2030 | - | - | PCM-2030_DI_2 | 3-25-01-202-PD-01 | MCC | MCC Room | Slurry - Out Building | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
977 | C6 | 6 | 2 | C6S06,02 | C6S06- | - | DI | 24 VDC energized | PCM-2031 | 0 | Start / Stop Command for FVNR PC-2031 | PCM-2031_DI_1 | 3-25-01-202-PD-01 | MCC | MCC Room | Slurry - Out Building | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
978 | C6 | 6 | 3 | C6S06,03 | C6S06- | - | DI | 24 VDC energized | PCM-2031 | 0 | Start / Stop Command for FVNR PC-2031 | PCM-2031_DI_2 | 3-25-01-202-PD-01 | MCC | MCC Room | Slurry - Out Building | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
979 | C6 | 6 | 4 | C6S06,04 | C6S06- | - | DI | 24 VDC energized | PCY-814201 | PUMP | Start / Stop Command to VSD PC-81001 | PCY-814201_DI_1 | 3-25-01-810-PD-01 | MCC | MCC Room | CIP Water System | 2nd | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
980 | C6 | 6 | 5 | C6S06,05 | C6S06- | - | DI | 24 VDC energized | PCY-814201 | PUMP | Start / Stop Command to VSD PC-81001 | PCY-814201_DI_2 | 3-25-01-810-PD-01 | MCC | MCC Room | CIP Water System | 2nd | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
981 | C6 | 6 | 6 | C6S06,06 | C6S06- | - | DI | 24 VDC energized | PCY-814201 | PUMP | Start / Stop Command to VSD PC-81001 | PCY-814201_DI_3 | 3-25-01-810-PD-01 | MCC | MCC Room | CIP Water System | 2nd | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
982 | C6 | 6 | 7 | C6S06,07 | C6S06- | - | DI | 24 VDC energized | PCY-814202 | PUMP | Start / Stop Command to VSD PC-81002 | PCY-814202_DI_1 | 3-25-01-810-PD-01 | MCC | MCC Room | CIP Water System | 2nd | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
983 | C6 | 6 | 8 | C6S06,08 | C6S06- | - | DI | 24 VDC energized | PCY-814202 | PUMP | Start / Stop Command to VSD PC-81002 | PCY-814202_DI_2 | 3-25-01-810-PD-01 | MCC | MCC Room | CIP Water System | 2nd | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
984 | C6 | 6 | 9 | C6S06,09 | C6S06- | - | DI | 24 VDC energized | PCY-814202 | PUMP | Start / Stop Command to VSD PC-81002 | PCY-814202_DI_3 | 3-25-01-810-PD-01 | MCC | MCC Room | CIP Water System | 2nd | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
985 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | ATY-40201 | Tank Agitator | Start / Stop Command for VSD AT-40201 | ATY-40201_BUS_1 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
986 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | ATY-40202 | Tank Agitator | Start / Stop Command for VSD AT-40202 | ATY-40202_BUS_1 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
987 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | ATY-40203 | Tank Agitator | Start / Stop Command for VSD AT-40203 | ATY-40203_BUS_1 | 3-25-01-402-PD-02 | MCC | MCC Room | Infeed Tank | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
988 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60206 | 0 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) | BFY-60206_BUS_1 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
989 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60210 | 0 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) | BFY-60210_BUS_1 | 325-01-600-PD-03 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
990 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60211 | 0 | Start / Stop Command for VSD FANC-21 (Combustion Fan) | BFY-60211_BUS_1 | 325-01-600-PD-03 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
991 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60220 | 0 | Start / Stop Command for VSD FANS-22 (Cooling Fan) | BFY-60220_BUS_1 | 325-01-600-PD-04 | MCC | MCC Room | Spray Dryer | 7th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
992 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60240 | 0 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) | BFY-60240_BUS_1 | 325-01-600-PD-05 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
993 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-61301 | 0 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) | BFY-61301_BUS_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 8th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
994 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-61302 | 0 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) | BFY-61302_BUS_1 | 325-01-613-PD-05 | MCC | MCC Room | Packing Tower | 2nd | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
995 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-61303 | 0 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) | BFY-61303_BUS_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
996 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | COM-FH-60210B | 0 | Communication Signal | COM-FH-60210B_BUS_1 | 325-01-600-PD-06 | JB-607 | Spray Dryer 7th Floor | Spray Dryer | 7th | MCC | ACTIVE | Require I/O DI= 0,DO=0,AI=0,AO=0,Bus=1
997 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | Communication Signal | - | - | Communication Signal_BUS_1 | 325-01-613-PD-02 | JB-612 | Packing Tower 2th Floor | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 0,DO=0,AI=0,AO=0,Bus=1
998 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-40201 | PUMP | Start / Stop Command for VSD PC-40201 | PCY-40201_BUS_1 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
999 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-40202 | PUMP | Start / Stop Command for VSD PC-40202 | PCY-40202_BUS_1 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1000 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-40203 | PUMP | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) | PCY-40203_BUS_1 | 3-25-01-402-PD-02 | MCC | MCC Room | Infeed Tank | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1001 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-60205 | - | - | PCY-60205_BUS_1 | 325-01-600-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1002 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-60215 | PUMP | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) | PCY-60215_BUS_1 | 325-01-600-PD-03 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1003 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-814201 | PUMP | Start / Stop Command to VSD PC-81001 | PCY-814201_BUS_1 | 3-25-01-810-PD-01 | MCC | MCC Room | CIP Water System | 2nd | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1004 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-814202 | PUMP | Start / Stop Command to VSD PC-81002 | PCY-814202_BUS_1 | 3-25-01-810-PD-01 | MCC | MCC Room | CIP Water System | 2nd | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1005 | C7 | 1 | 0 | C7S01,00 | C7S01- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1006 | C7 | 1 | 1 | C7S01,01 | C7S01- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1007 | C7 | 1 | 2 | C7S01,02 | C7S01- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1008 | C7 | 1 | 3 | C7S01,03 | C7S01- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1009 | C7 | 1 | 4 | C7S01,04 | C7S01- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1010 | C7 | 1 | 5 | C7S01,05 | C7S01- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1011 | C7 | 1 | 6 | C7S01,06 | C7S01- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1012 | C7 | 1 | 7 | C7S01,07 | C7S01- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1013 | C7 | 1 | 8 | C7S01,08 | C7S01- | - | DI | 24 VDC energized | ATY-40201 | Tank Agitator | Start / Stop Command for VSD AT-40201 | ATY-40201_DI_1 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1014 | C7 | 1 | 9 | C7S01,09 | C7S01- | - | DI | 24 VDC energized | ATY-40201 | Tank Agitator | Start / Stop Command for VSD AT-40201 | ATY-40201_DI_2 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1015 | C7 | 1 | 10 | C7S01,10 | C7S01- | - | DI | 24 VDC energized | ATY-40201 | Tank Agitator | Start / Stop Command for VSD AT-40201 | ATY-40201_DI_3 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1016 | C7 | 1 | 11 | C7S01,11 | C7S01- | - | DI | 24 VDC energized | ATY-40202 | Tank Agitator | Start / Stop Command for VSD AT-40202 | ATY-40202_DI_1 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1017 | C7 | 1 | 12 | C7S01,12 | C7S01- | - | DI | 24 VDC energized | ATY-40202 | Tank Agitator | Start / Stop Command for VSD AT-40202 | ATY-40202_DI_2 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1018 | C7 | 1 | 13 | C7S01,13 | C7S01- | - | DI | 24 VDC energized | ATY-40202 | Tank Agitator | Start / Stop Command for VSD AT-40202 | ATY-40202_DI_3 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1019 | C7 | 1 | 14 | C7S01,14 | C7S01- | - | DI | 24 VDC energized | ATY-40203 | Tank Agitator | Start / Stop Command for VSD AT-40203 | ATY-40203_DI_1 | 3-25-01-402-PD-02 | MCC | MCC Room | Infeed Tank | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1020 | C7 | 1 | 15 | C7S01,15 | C7S01- | - | DI | 24 VDC energized | ATY-40203 | Tank Agitator | Start / Stop Command for VSD AT-40203 | ATY-40203_DI_2 | 3-25-01-402-PD-02 | MCC | MCC Room | Infeed Tank | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1021 | C7 | 1 | 16 | C7S01,16 | C7S01- | - | DI | 24 VDC energized | ATY-40203 | Tank Agitator | Start / Stop Command for VSD AT-40203 | ATY-40203_DI_3 | 3-25-01-402-PD-02 | MCC | MCC Room | Infeed Tank | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1022 | C7 | 1 | 17 | C7S01,17 | C7S01- | - | DI | 24 VDC energized | PCY-40201 | PUMP | Start / Stop Command for VSD PC-40201 | PCY-40201_DI_1 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1023 | C7 | 1 | 18 | C7S01,18 | C7S01- | - | DI | 24 VDC energized | PCY-40201 | PUMP | Start / Stop Command for VSD PC-40201 | PCY-40201_DI_2 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1024 | C7 | 1 | 19 | C7S01,19 | C7S01- | - | DI | 24 VDC energized | PCY-40201 | PUMP | Start / Stop Command for VSD PC-40201 | PCY-40201_DI_3 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1025 | C7 | 1 | 20 | C7S01,20 | C7S01- | - | DI | 24 VDC energized | PCY-40202 | PUMP | Start / Stop Command for VSD PC-40202 | PCY-40202_DI_1 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1026 | C7 | 1 | 21 | C7S01,21 | C7S01- | - | DI | 24 VDC energized | PCY-40202 | PUMP | Start / Stop Command for VSD PC-40202 | PCY-40202_DI_2 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1027 | C7 | 1 | 22 | C7S01,22 | C7S01- | - | DI | 24 VDC energized | PCY-40202 | PUMP | Start / Stop Command for VSD PC-40202 | PCY-40202_DI_3 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1028 | C7 | 1 | 23 | C7S01,23 | C7S01- | - | DI | 24 VDC energized | PCY-40203 | PUMP | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) | PCY-40203_DI_1 | 3-25-01-402-PD-02 | MCC | MCC Room | Infeed Tank | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1029 | C7 | 1 | 24 | C7S01,24 | C7S01- | - | DI | 24 VDC energized | PCY-40203 | PUMP | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) | PCY-40203_DI_2 | 3-25-01-402-PD-02 | MCC | MCC Room | Infeed Tank | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1030 | C7 | 1 | 25 | C7S01,25 | C7S01- | - | DI | 24 VDC energized | PCY-40203 | PUMP | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) | PCY-40203_DI_3 | 3-25-01-402-PD-02 | MCC | MCC Room | Infeed Tank | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1031 | C7 | 1 | 26 | C7S01,26 | C7S01- | - | DI | 24 VDC energized | BFY-60206 | 0 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) | BFY-60206_DI_1 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1032 | C7 | 1 | 27 | C7S01,27 | C7S01- | - | DI | - | PCM-60205-2 | - | - | PCM-60205-2_DI_1 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1033 | C7 | 1 | 28 | C7S01,28 | C7S01- | - | DI | - | PCM-60205-2 | - | - | PCM-60205-2_DI_2 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1034 | C7 | 1 | 29 | C7S01,29 | C7S01- | - | DI | - | PCM-60205-3 | - | - | PCM-60205-3_DI_1 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1035 | C7 | 1 | 30 | C7S01,30 | C7S01- | - | DI | - | PCM-60205-3 | - | - | PCM-60205-3_DI_2 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1036 | C7 | 1 | 31 | C7S01,31 | C7S01- | - | DI | - | PCM-60205-4 | - | - | PCM-60205-4_DI_1 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1037 | C7 | 2 | 0 | C7S02,00 | C7S02- | - | DI | - | PCM-60205-4 | - | - | PCM-60205-4_DI_2 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1038 | C7 | 2 | 1 | C7S02,01 | C7S02- | - | DI | - | PCM-60205-5 | - | - | PCM-60205-5_DI_1 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1039 | C7 | 2 | 2 | C7S02,02 | C7S02- | - | DI | - | PCM-60205-5 | - | - | PCM-60205-5_DI_2 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1040 | C7 | 2 | 3 | C7S02,03 | C7S02- | - | DI | - | PCY-60205 | - | - | PCY-60205_DI_1 | 325-01-600-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1041 | C7 | 2 | 4 | C7S02,04 | C7S02- | - | DI | - | PCY-60205 | - | - | PCY-60205_DI_2 | 325-01-600-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1042 | C7 | 2 | 5 | C7S02,05 | C7S02- | - | DI | 24 VDC energized | RVM-60201 | 0 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) | RVM-60201_DI_1 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1043 | C7 | 2 | 6 | C7S02,06 | C7S02- | - | DI | 24 VDC energized | RVM-60201 | 0 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) | RVM-60201_DI_2 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1044 | C7 | 2 | 7 | C7S02,07 | C7S02- | - | DI | 24 VDC energized | RVM-60202 | 0 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) | RVM-60202_DI_1 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1045 | C7 | 2 | 8 | C7S02,08 | C7S02- | - | DI | 24 VDC energized | RVM-60202 | 0 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) | RVM-60202_DI_2 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1046 | C7 | 2 | 9 | C7S02,09 | C7S02- | - | DI | 24 VDC energized | RVM-60203 | 0 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) | RVM-60203_DI_1 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1047 | C7 | 2 | 10 | C7S02,10 | C7S02- | - | DI | 24 VDC energized | RVM-60203 | 0 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) | RVM-60203_DI_2 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1048 | C7 | 2 | 11 | C7S02,11 | C7S02- | - | DI | 24 VDC energized | BFY-60210 | 0 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) | BFY-60210_DI_1 | 325-01-600-PD-03 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1049 | C7 | 2 | 12 | C7S02,12 | C7S02- | - | DI | 24 VDC energized | BFY-60211 | 0 | Start / Stop Command for VSD FANC-21 (Combustion Fan) | BFY-60211_DI_1 | 325-01-600-PD-03 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1050 | C7 | 2 | 13 | C7S02,13 | C7S02- | - | DI | 24 VDC energized | BFY-60240 | 0 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) | BFY-60240_DI_1 | 325-01-600-PD-05 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1051 | C7 | 2 | 14 | C7S02,14 | C7S02- | - | DI | 24 VDC energized | PCY-60215 | PUMP | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) | PCY-60215_DI_1 | 325-01-600-PD-03 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1052 | C7 | 2 | 15 | C7S02,15 | C7S02- | - | DI | 24 VDC energized | PCY-60215 | PUMP | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) | PCY-60215_DI_2 | 325-01-600-PD-03 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1053 | C7 | 2 | 16 | C7S02,16 | C7S02- | - | DI | 24 VDC energized | PCY-60215 | PUMP | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) | PCY-60215_DI_3 | 325-01-600-PD-03 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1054 | C7 | 2 | 17 | C7S02,17 | C7S02- | - | DI | 24 VDC energized | BFY-60220 | 0 | Start / Stop Command for VSD FANS-22 (Cooling Fan) | BFY-60220_DI_1 | 325-01-600-PD-04 | MCC | MCC Room | Spray Dryer | 7th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1055 | C7 | 2 | 18 | C7S02,18 | C7S02- | - | DI | 24 VDC energized | BFY-61302 | 0 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) | BFY-61302_DI_1 | 325-01-613-PD-05 | MCC | MCC Room | Packing Tower | 2nd | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1056 | C7 | 2 | 19 | C7S02,19 | C7S02- | - | DI | Dry Contact | HS-61307F | 0 | Start/Stop | HS-61307F_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 4th | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1057 | C7 | 2 | 20 | C7S02,20 | C7S02- | - | DI | Dry Contact | HS-61307G | 0 | Start/Stop | HS-61307G_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 3rd | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1058 | C7 | 2 | 21 | C7S02,21 | C7S02- | - | DI | Dry Contact | HS-61307H | 0 | Start/Stop | HS-61307H_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 3rd | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1059 | C7 | 2 | 22 | C7S02,22 | C7S02- | - | DI | Dry Contact | HS-61307I | 0 | Start/Stop | HS-61307I_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1060 | C7 | 2 | 23 | C7S02,23 | C7S02- | - | DI | Dry Contact | HS-61307J | 0 | Start/Stop | HS-61307J_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1061 | C7 | 2 | 24 | C7S02,24 | C7S02- | - | DI | Dry Contact | HS-61307K | 0 | Start/Stop | HS-61307K_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1062 | C7 | 2 | 25 | C7S02,25 | C7S02- | - | DI | Dry Contact | HS-61307L | 0 | Start/Stop | HS-61307L_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1063 | C7 | 2 | 26 | C7S02,26 | C7S02- | - | DI | Dry Contact | HS-61307M | 0 | Start/Stop | HS-61307M_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1064 | C7 | 2 | 27 | C7S02,27 | C7S02- | - | DI | Dry Contact | HS-61307N | 0 | Start/Stop | HS-61307N_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1065 | C7 | 2 | 28 | C7S02,28 | C7S02- | - | DI | Dry Contact | HS-61307O | 0 | Start/Stop | HS-61307O_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1066 | C7 | 2 | 29 | C7S02,29 | C7S02- | - | DI | Dry Contact | HS-61307P | 0 | Start/Stop | HS-61307P_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1067 | C7 | 2 | 30 | C7S02,30 | C7S02- | - | DI | Dry Contact | HS-61307Q | 0 | Start/Stop | HS-61307Q_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1068 | C7 | 2 | 31 | C7S02,31 | C7S02- | - | DI | Dry Contact | HS-61307R | 0 | Start/Stop | HS-61307R_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1069 | C7 | 3 | 0 | C7S03,00 | C7S03- | - | DI | 24 VDC energized | RVM-61302 | 0 | Start / Stop Command for FVNR RV-61302 | RVM-61302_DI_1 | 325-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1070 | C7 | 3 | 1 | C7S03,01 | C7S03- | - | DI | 24 VDC energized | RVM-61302 | 0 | Start / Stop Command for FVNR RV-61302 | RVM-61302_DI_2 | 325-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1071 | C7 | 3 | 2 | C7S03,02 | C7S03- | - | DI | 24 VDC energized | RVM-61303 | 0 | Start / Stop Command for FVNR RV-61303 | RVM-61303_DI_1 | 325-01-613-PD-05 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1072 | C7 | 3 | 3 | C7S03,03 | C7S03- | - | DI | 24 VDC energized | RVM-61303 | 0 | Start / Stop Command for FVNR RV-61303 | RVM-61303_DI_2 | 325-01-613-PD-05 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1073 | C7 | 3 | 4 | C7S03,04 | C7S03- | - | DI | 24 VDC energized | SCM-61301 | 0 | Start / Stop Command for FVNR SC-61301 (Sifter ) | SCM-61301_DI_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 4th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1074 | C7 | 3 | 5 | C7S03,05 | C7S03- | - | DI | 24 VDC energized | SCM-61301 | 0 | Start / Stop Command for FVNR SC-61301 (Sifter ) | SCM-61301_DI_2 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 4th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1075 | C7 | 3 | 6 | C7S03,06 | C7S03- | - | DI | 24 VDC energized | SCM-61302 | 0 | Start / Stop Command for FVNR SC-61302 (Sifter ) | SCM-61302_DI_2 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 4th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1076 | C7 | 3 | 7 | C7S03,07 | C7S03- | - | DI | 24 VDC energized | SCM-61302 | 0 | Start / Stop Command for FVNR SC-61302 (Sifter ) | SCM-61302_DI_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 4th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1077 | C7 | 3 | 8 | C7S03,08 | C7S03- | - | DI | 24 VDC energized | BFY-61301 | 0 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) | BFY-61301_DI_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 8th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1078 | C7 | 3 | 9 | C7S03,09 | C7S03- | - | DI | 24 VDC energized | BFY-61303 | 0 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) | BFY-61303_DI_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1079 | C7 | 3 | 10 | C7S03,10 | C7S03- | - | DI | 24 VDC energized | BLM-61302 | 0 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | BLM-61302_DI_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 5th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1080 | C7 | 3 | 11 | C7S03,11 | C7S03- | - | DI | 24 VDC energized | BLM-61302 | 0 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | BLM-61302_DI_2 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 5th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1081 | C7 | 3 | 12 | C7S03,12 | C7S03- | - | DI | Dry Contact | HS-61307A | 0 | Start/Stop | HS-61307A_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 8th | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1082 | C7 | 3 | 13 | C7S03,13 | C7S03- | - | DI | Dry Contact | HS-61307B | 0 | Start/Stop | HS-61307B_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 8th | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1083 | C7 | 3 | 14 | C7S03,14 | C7S03- | - | DI | Dry Contact | HS-61307C | 0 | Start/Stop | HS-61307C_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 7th | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1084 | C7 | 3 | 15 | C7S03,15 | C7S03- | - | DI | Dry Contact | HS-61307D | 0 | Start/Stop | HS-61307D_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 5th | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1085 | C7 | 3 | 16 | C7S03,16 | C7S03- | - | DI | Dry Contact | HS-61307E | 0 | Start/Stop | HS-61307E_DI_1 | 3-25-01-613-PD-03 | MCC | MCC Room | Packing Tower | 5th | MCC | ACTIVE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1086 | C7 | 3 | 17 | C7S03,17 | C7S03- | - | DI | 24 VDC energized | RVM-60204 | 0 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) | RVM-60204_DI_1 | 325-01-600-PD-08 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1087 | C7 | 3 | 18 | C7S03,18 | C7S03- | - | DI | 24 VDC energized | RVM-60204 | 0 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) | RVM-60204_DI_2 | 325-01-600-PD-08 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1088 | C7 | 3 | 19 | C7S03,19 | C7S03- | - | DI | 24 VDC energized | RVM-61301 | 0 | Start / Stop Command for FVNR RV-61301 | RVM-61301_DI_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 6th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1089 | C7 | 3 | 20 | C7S03,20 | C7S03- | - | DI | 24 VDC energized | RVM-61301 | 0 | Start / Stop Command for FVNR RV-61301 | RVM-61301_DI_2 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 6th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1090 | C7 | 3 | 21 | C7S03,21 | C7S03- | - | DI | 24 VDC energized | RVM-61304 | 0 | Start / Stop Command for FVNR RV-61304 | RVM-61304_DI_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1091 | C7 | 3 | 22 | C7S03,22 | C7S03- | - | DI | 24 VDC energized | RVM-61304 | 0 | Start / Stop Command for FVNR RV-61304 | RVM-61304_DI_2 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1092 | C7 | 3 | 23 | C7S03,23 | C7S03- | - | DI | 24 VDC energized | RVM-61305 | 0 | Start / Stop Command for FVNR RV-61305 | RVM-61305_DI_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1093 | C7 | 3 | 24 | C7S03,24 | C7S03- | - | DI | 24 VDC energized | RVM-61305 | 0 | Start / Stop Command for FVNR RV-61305 | RVM-61305_DI_2 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1094 | C7 | 3 | 25 | C7S03,25 | C7S03- | - | DI | - | PCY-60205 | - | - | PCY-60205_DI_3 | 325-01-600-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1095 | C7 | 4 | 4 | C7S04,04 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1096 | C7 | 4 | 5 | C7S04,05 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1097 | C7 | 4 | 6 | C7S04,06 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1098 | C7 | 4 | 7 | C7S04,07 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1099 | C7 | 4 | 8 | C7S04,08 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1100 | C7 | 4 | 9 | C7S04,09 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1101 | C7 | 4 | 10 | C7S04,10 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1102 | C7 | 4 | 11 | C7S04,11 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1103 | C7 | 4 | 12 | C7S04,12 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1104 | C7 | 4 | 13 | C7S04,13 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1105 | C7 | 4 | 14 | C7S04,14 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1106 | C7 | 4 | 15 | C7S04,15 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1107 | C7 | 4 | 16 | C7S04,16 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1108 | C7 | 4 | 17 | C7S04,17 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1109 | C7 | 4 | 18 | C7S04,18 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1110 | C7 | 4 | 19 | C7S04,19 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1111 | C7 | 4 | 20 | C7S04,20 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1112 | C7 | 4 | 21 | C7S04,21 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1113 | C7 | 4 | 22 | C7S04,22 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1114 | C7 | 4 | 23 | C7S04,23 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1115 | C7 | 4 | 24 | C7S04,24 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1116 | C7 | 4 | 25 | C7S04,25 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1117 | C7 | 4 | 26 | C7S04,26 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1118 | C7 | 4 | 27 | C7S04,27 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1119 | C7 | 4 | 28 | C7S04,28 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1120 | C7 | 4 | 29 | C7S04,29 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1121 | C7 | 4 | 30 | C7S04,30 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1122 | C7 | 4 | 31 | C7S04,31 | C7S04- | - | DI | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DI_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0
1123 | C7 | 5 | 0 | C7S05,00 | C7S05- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1124 | C7 | 5 | 1 | C7S05,01 | C7S05- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1125 | C7 | 5 | 2 | C7S05,02 | C7S05- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1126 | C7 | 5 | 3 | C7S05,03 | C7S05- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1127 | C7 | 5 | 4 | C7S05,04 | C7S05- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1128 | C7 | 5 | 5 | C7S05,05 | C7S05- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1129 | C7 | 5 | 6 | C7S05,06 | C7S05- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1130 | C7 | 5 | 7 | C7S05,07 | C7S05- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1131 | C7 | 5 | 8 | C7S05,08 | C7S05- | - | DO | 24 VDC energized | ATY-40201 | Tank Agitator | Start / Stop Command for VSD AT-40201 | ATY-40201_DO_1 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1132 | C7 | 5 | 9 | C7S05,09 | C7S05- | - | DO | 24 VDC energized | ATY-40202 | Tank Agitator | Start / Stop Command for VSD AT-40202 | ATY-40202_DO_1 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1133 | C7 | 5 | 10 | C7S05,10 | C7S05- | - | DO | 24 VDC energized | ATY-40203 | Tank Agitator | Start / Stop Command for VSD AT-40203 | ATY-40203_DO_1 | 3-25-01-402-PD-02 | MCC | MCC Room | Infeed Tank | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1134 | C7 | 5 | 11 | C7S05,11 | C7S05- | - | DO | 24 VDC energized | PCY-40201 | PUMP | Start / Stop Command for VSD PC-40201 | PCY-40201_DO_1 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1135 | C7 | 5 | 12 | C7S05,12 | C7S05- | - | DO | 24 VDC energized | PCY-40202 | PUMP | Start / Stop Command for VSD PC-40202 | PCY-40202_DO_1 | 3-25-01-402-PD-01 | MCC | MCC Room | PH Adjustment | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1136 | C7 | 5 | 13 | C7S05,13 | C7S05- | - | DO | 24 VDC energized | PCY-40203 | PUMP | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) | PCY-40203_DO_1 | 3-25-01-402-PD-02 | MCC | MCC Room | Infeed Tank | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1137 | C7 | 5 | 14 | C7S05,14 | C7S05- | - | DO | 24 VDC energized | BFY-60206 | 0 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) | BFY-60206_DO_1 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1138 | C7 | 5 | 15 | C7S05,15 | C7S05- | - | DO | - | PCM-60205-2 | - | - | PCM-60205-2_DO_1 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1139 | C7 | 5 | 16 | C7S05,16 | C7S05- | - | DO | - | PCM-60205-2 | - | - | PCM-60205-2_DO_2 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1140 | C7 | 5 | 17 | C7S05,17 | C7S05- | - | DO | - | PCM-60205-3 | - | - | PCM-60205-3_DO_1 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1141 | C7 | 5 | 18 | C7S05,18 | C7S05- | - | DO | - | PCM-60205-3 | - | - | PCM-60205-3_DO_2 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1142 | C7 | 5 | 19 | C7S05,19 | C7S05- | - | DO | - | PCM-60205-4 | - | - | PCM-60205-4_DO_1 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1143 | C7 | 5 | 20 | C7S05,20 | C7S05- | - | DO | - | PCM-60205-4 | - | - | PCM-60205-4_DO_2 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1144 | C7 | 5 | 21 | C7S05,21 | C7S05- | - | DO | - | PCM-60205-5 | - | - | PCM-60205-5_DO_1 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1145 | C7 | 5 | 22 | C7S05,22 | C7S05- | - | DO | - | PCM-60205-5 | - | - | PCM-60205-5_DO_2 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1146 | C7 | 5 | 23 | C7S05,23 | C7S05- | - | DO | 24 VDC energized | RVM-60201 | 0 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) | RVM-60201_DO_1 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1147 | C7 | 5 | 24 | C7S05,24 | C7S05- | - | DO | 24 VDC energized | RVM-60201 | 0 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) | RVM-60201_DO_2 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1148 | C7 | 5 | 25 | C7S05,25 | C7S05- | - | DO | 24 VDC energized | RVM-60202 | 0 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) | RVM-60202_DO_1 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1149 | C7 | 5 | 26 | C7S05,26 | C7S05- | - | DO | 24 VDC energized | RVM-60202 | 0 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) | RVM-60202_DO_2 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1150 | C7 | 5 | 27 | C7S05,27 | C7S05- | - | DO | 24 VDC energized | RVM-60203 | 0 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) | RVM-60203_DO_1 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1151 | C7 | 5 | 28 | C7S05,28 | C7S05- | - | DO | 24 VDC energized | RVM-60203 | 0 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) | RVM-60203_DO_2 | 325-01-600-PD-08 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1152 | C7 | 5 | 29 | C7S05,29 | C7S05- | - | DO | 0 | XS-60205 | 0 | Start / Stop Command for PUPD-11 (Positive Displacement Pump ) | XS-60205_DO_1 | 325-01-600-PD-01 | MCC | MCC Room | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1153 | C7 | 5 | 30 | C7S05,30 | C7S05- | - | DO | 24 VDC energized | BFY-60210 | 0 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) | BFY-60210_DO_1 | 325-01-600-PD-03 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1154 | C7 | 5 | 31 | C7S05,31 | C7S05- | - | DO | 24 VDC energized | BFY-60211 | 0 | Start / Stop Command for VSD FANC-21 (Combustion Fan) | BFY-60211_DO_1 | 325-01-600-PD-03 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1155 | C7 | 6 | 0 | C7S06,00 | C7S06- | - | DO | 24 VDC energized | BFY-60240 | 0 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) | BFY-60240_DO_1 | 325-01-600-PD-05 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1156 | C7 | 6 | 1 | C7S06,01 | C7S06- | - | DO | 24 VDC energized | PCY-60215 | PUMP | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) | PCY-60215_DO_1 | 325-01-600-PD-03 | MCC | MCC Room | Spray Dryer | 5th | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1157 | C7 | 6 | 2 | C7S06,02 | C7S06- | - | DO | Dry Contact | XS-60240A | 0 | Start / Stop Command for BGHS-21 (Bag House Air Pulsing) | XS-60240A_DO_1 | 325-01-600-PD-05 | MCC | MCC Room | Spray Dryer | 4th | MCC | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1158 | C7 | 6 | 3 | C7S06,03 | C7S06- | - | DO | Dry Contact | XS-60241A | 0 | Start / Stop Command for HTRE-21 (Heater Control Panel) | XS-60241A_DO_1 | 325-01-600-PD-05 | MCC | MCC Room | Spray Dryer | 4th | MCC | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1159 | C7 | 6 | 4 | C7S06,04 | C7S06- | - | DO | Dry Contact | XS-60242A | 0 | Start / Stop Command for HTRE-21 (Heater Control Panel) | XS-60242A_DO_1 | 325-01-600-PD-05 | MCC | MCC Room | Spray Dryer | 3rd | MCC | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1160 | C7 | 6 | 4 | C7S06,04 | C7S06- | - | DO | Dry Contact | XS-60243A | 0 | Start / Stop Command for HTRE-21 (Heater Control Panel) | XS-60243A_DO_1 | 325-01-600-PD-05 | MCC | MCC Room | Spray Dryer | 4th | MCC | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1161 | C7 | 6 | 6 | C7S06,06 | C7S06- | - | DO | 24 VDC energized | XS-60260 | 0 | Start / Stop Command for FWDP-21 (Fire Deluge) | XS-60260_DO_1 | 325-01-600-PD-05 | MCC | MCC Room | Spray Dryer | 6th | MCC | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1162 | C7 | 6 | 7 | C7S06,07 | C7S06- | - | DO | 24 VDC energized | BFY-60220 | 0 | Start / Stop Command for VSD FANS-22 (Cooling Fan) | BFY-60220_DO_1 | 325-01-600-PD-04 | MCC | MCC Room | Spray Dryer | 7th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1163 | C7 | 6 | 8 | C7S06,08 | C7S06- | - | DO | Dry Contact | XS-FH-60210A | 0 | Start / Stop Command Burner Remote Start for AHTR-21 | XS-FH-60210A_DO_1 | 325-01-600-PD-06 | MCC | MCC Room | Spray Dryer | 7th | MCC | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1164 | C7 | 6 | 9 | C7S06,09 | C7S06- | - | DO | Dry Contact | XS-FH-60210B | 0 | Start / Stop Command Dryer Interlocks for AHTR-21 | XS-FH-60210B_DO_1 | 325-01-600-PD-06 | MCC | MCC Room | Spray Dryer | 7th | MCC | ACTIVE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1165 | C7 | 6 | 10 | C7S06,10 | C7S06- | - | DO | 24 VDC energized | BFY-61302 | 0 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) | BFY-61302_DO_1 | 325-01-613-PD-05 | MCC | MCC Room | Packing Tower | 2nd | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1166 | C7 | 6 | 11 | C7S06,11 | C7S06- | - | DO | 24 VDC energized | RVM-61302 | 0 | Start / Stop Command for FVNR RV-61302 | RVM-61302_DO_1 | 325-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1167 | C7 | 6 | 12 | C7S06,12 | C7S06- | - | DO | 24 VDC energized | RVM-61302 | 0 | Start / Stop Command for FVNR RV-61302 | RVM-61302_DO_2 | 325-01-613-PD-03 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1168 | C7 | 6 | 13 | C7S06,13 | C7S06- | - | DO | 24 VDC energized | RVM-61303 | 0 | Start / Stop Command for FVNR RV-61303 | RVM-61303_DO_1 | 325-01-613-PD-05 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1169 | C7 | 6 | 14 | C7S06,14 | C7S06- | - | DO | 24 VDC energized | RVM-61303 | 0 | Start / Stop Command for FVNR RV-61303 | RVM-61303_DO_2 | 325-01-613-PD-05 | MCC | MCC Room | Packing Tower | 1st | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1170 | C7 | 6 | 15 | C7S06,15 | C7S06- | - | DO | 24 VDC energized | SCM-61301 | 0 | Start / Stop Command for FVNR SC-61301 (Sifter ) | SCM-61301_DO_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 4th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1171 | C7 | 6 | 16 | C7S06,16 | C7S06- | - | DO | 24 VDC energized | SCM-61301 | 0 | Start / Stop Command for FVNR SC-61301 (Sifter ) | SCM-61301_DO_2 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 4th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1172 | C7 | 6 | 17 | C7S06,17 | C7S06- | - | DO | 24 VDC energized | SCM-61302 | 0 | Start / Stop Command for FVNR SC-61302 (Sifter ) | SCM-61302_DO_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 4th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1173 | C7 | 6 | 18 | C7S06,18 | C7S06- | - | DO | 24 VDC energized | SCM-61302 | 0 | Start / Stop Command for FVNR SC-61302 (Sifter ) | SCM-61302_DO_2 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 4th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1174 | C7 | 6 | 19 | C7S06,19 | C7S06- | - | DO | 24 VDC energized | BFY-61301 | 0 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) | BFY-61301_DO_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 8th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1175 | C7 | 6 | 20 | C7S06,20 | C7S06- | - | DO | 24 VDC energized | BFY-61303 | 0 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) | BFY-61303_DO_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1
1176 | C7 | 6 | 21 | C7S06,21 | C7S06- | - | DO | 24 VDC energized | BLM-61302 | 0 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | BLM-61302_DO_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 5th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1177 | C7 | 6 | 22 | C7S06,22 | C7S06- | - | DO | 24 VDC energized | BLM-61302 | 0 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | BLM-61302_DO_2 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 5th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1178 | C7 | 6 | 23 | C7S06,23 | C7S06- | - | DO | 24 VDC energized | RVM-60204 | 0 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) | RVM-60204_DO_1 | 325-01-600-PD-08 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1179 | C7 | 6 | 24 | C7S06,24 | C7S06- | - | DO | 24 VDC energized | RVM-60204 | 0 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) | RVM-60204_DO_2 | 325-01-600-PD-08 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1180 | C7 | 6 | 25 | C7S06,25 | C7S06- | - | DO | 24 VDC energized | RVM-61301 | 0 | Start / Stop Command for FVNR RV-61301 | RVM-61301_DO_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 6th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1181 | C7 | 6 | 26 | C7S06,26 | C7S06- | - | DO | 24 VDC energized | RVM-61301 | 0 | Start / Stop Command for FVNR RV-61301 | RVM-61301_DO_2 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 6th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1182 | C7 | 6 | 27 | C7S06,27 | C7S06- | - | DO | 24 VDC energized | RVM-61304 | 0 | Start / Stop Command for FVNR RV-61304 | RVM-61304_DO_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1183 | C7 | 6 | 28 | C7S06,28 | C7S06- | - | DO | 24 VDC energized | RVM-61304 | 0 | Start / Stop Command for FVNR RV-61304 | RVM-61304_DO_2 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1184 | C7 | 6 | 29 | C7S06,29 | C7S06- | - | DO | 24 VDC energized | RVM-61305 | 0 | Start / Stop Command for FVNR RV-61305 | RVM-61305_DO_1 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1185 | C7 | 6 | 30 | C7S06,30 | C7S06- | - | DO | 24 VDC energized | RVM-61305 | 0 | Start / Stop Command for FVNR RV-61305 | RVM-61305_DO_2 | 325-01-613-PD-01 | MCC | MCC Room | Packing Tower | 9th | MCC | ACTIVE | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0
1186 | C7 | 6 | 31 | C7S06,31 | C7S06- | - | DO | - | PCY-60205 | - | - | PCY-60205_DO_1 | 325-01-600-PD-01 | JB-601 | Spray Dryer 1st Floor | Spray Dryer | 1st | MCC | ACTIVE | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1
1187 | C7 | 7 | 8 | C7S07,08 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1188 | C7 | 7 | 9 | C7S07,09 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1189 | C7 | 7 | 10 | C7S07,10 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1190 | C7 | 7 | 11 | C7S07,11 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1191 | C7 | 7 | 12 | C7S07,12 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1192 | C7 | 7 | 13 | C7S07,13 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1193 | C7 | 7 | 14 | C7S07,14 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1194 | C7 | 7 | 15 | C7S07,15 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1195 | C7 | 7 | 16 | C7S07,16 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1196 | C7 | 7 | 17 | C7S07,17 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1197 | C7 | 7 | 18 | C7S07,18 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1198 | C7 | 7 | 19 | C7S07,19 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1199 | C7 | 7 | 20 | C7S07,20 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1200 | C7 | 7 | 21 | C7S07,21 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1201 | C7 | 7 | 22 | C7S07,22 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1202 | C7 | 7 | 23 | C7S07,23 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1203 | C7 | 7 | 24 | C7S07,24 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1204 | C7 | 7 | 25 | C7S07,25 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1205 | C7 | 7 | 26 | C7S07,26 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1206 | C7 | 7 | 27 | C7S07,27 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1207 | C7 | 7 | 28 | C7S07,28 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1208 | C7 | 7 | 29 | C7S07,29 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1209 | C7 | 7 | 30 | C7S07,30 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0
1210 | C7 | 7 | 31 | C7S07,31 | C7S07- | - | DO | - | Spare | Spare Channel | Unused Spare Point for Future Expansion | Spare_DO_0 | - | MCC | MCC Room | - | - | MCC | SPARE | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0

## IO_List_Raw_Columns_Sorted
Reference Designation | Destination | Column7 | Column5 | Column52 | Terminal | Column6 | Terminal Label | Junction Box Location | Master Zone | Zone | Instruement Tag | Instruement_Description | Floor | P&ID No. 3.3 | P&ID No. 3.5 | Control Description | Column1 | Require IO | Column2 | PLC_Tag | I/O Type | IO_ID | IO-Point (Instruement) | Column23 | Column22 | Column3 | Card | Signal Type | Column4 | Column332 | Chassis | Slot | Point | Terminal2 | DI | DO | AI | AO | Bus | Bus Address | Signal Type2
=CA1+MCP-M1 | CA1 | C1S03,00 | 1756-IB32-0 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI00 | C1S03,00 | 1756-IB32-0 |  | x | DI | C1 | 3 | 0 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,01 | 1756-IB32-1 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI01 | C1S03,01 | 1756-IB32-1 |  | x | DI | C1 | 3 | 1 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,02 | 1756-IB32-2 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI02 | C1S03,02 | 1756-IB32-2 |  | x | DI | C1 | 3 | 2 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,03 | 1756-IB32-3 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI03 | C1S03,03 | 1756-IB32-3 |  | x | DI | C1 | 3 | 3 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,04 | 1756-IB32-4 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI04 | C1S03,04 | 1756-IB32-4 |  | x | DI | C1 | 3 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,05 | 1756-IB32-5 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI05 | C1S03,05 | 1756-IB32-5 |  | x | DI | C1 | 3 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,06 | 1756-IB32-6 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI06 | C1S03,06 | 1756-IB32-6 |  | x | DI | C1 | 3 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,07 | 1756-IB32-7 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI07 | C1S03,07 | 1756-IB32-7 |  | x | DI | C1 | 3 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,08 | 1756-IB32-8 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI08 | C1S03,08 | 1756-IB32-8 |  | x | DI | C1 | 3 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,09 | 1756-IB32-9 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI09 | C1S03,09 | 1756-IB32-9 |  | x | DI | C1 | 3 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,10 | 1756-IB32-10 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI10 | C1S03,10 | 1756-IB32-10 |  | x | DI | C1 | 3 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,11 | 1756-IB32-11 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI11 | C1S03,11 | 1756-IB32-11 |  | x | DI | C1 | 3 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,12 | 1756-IB32-12 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI12 | C1S03,12 | 1756-IB32-12 |  | x | DI | C1 | 3 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,13 | 1756-IB32-13 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI13 | C1S03,13 | 1756-IB32-13 |  | x | DI | C1 | 3 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,14 | 1756-IB32-14 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI14 | C1S03,14 | 1756-IB32-14 |  | x | DI | C1 | 3 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S03,15 | 1756-IB32-15 | X1 | C1S03-X1 | Spare_DI_0 |  | Main Control Cabinet | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S03 | C1S03DI15 | C1S03,15 | 1756-IB32-15 |  | x | DI | C1 | 3 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S03,16 | 1756-IB32-16 | X2 | C1S03-X2 | FSL-40201_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | FSL-40201 | Flow Switch | 1st | - | 3-25-01-402-PD-01 | Slurry low flow |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | FSL-40201_DI_1 | DI | 1 | 1 | C1S03 | C1S03DI16 | C1S03,16 | 1756-IB32-16 |  | x | DI | C1 | 3 | 16 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-401 | C1S03,17 | 1756-IB32-17 | X2 | C1S03-X2 | FSL-40202_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | FSL-40202 | Flow Switch | 1st | - | 3-25-01-402-PD-01 | Slurry low flow |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | FSL-40202_DI_1 | DI | 1 | 1 | C1S03 | C1S03DI17 | C1S03,17 | 1756-IB32-17 |  | x | DI | C1 | 3 | 17 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-401 | C1S03,18 | 1756-IB32-18 | X2 | C1S03-X2 | FT-40201_DI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | FT-40201 | Coriolis Flow Transmitter | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Slurry flowrate & density check transfer line |  | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0 | xx | FT-40201_DI_1 | DI | 1 | 1 | C1S03 | C1S03DI18 | C1S03,18 | 1756-IB32-18 |  | x | DI | C1 | 3 | 18 |  | 1 | 0 | 2 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M1 | JB-401 | C1S03,19 | 1756-IB32-19 | X2 | C1S03-X2 | FT-40202_DI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | FT-40202 | Magnetic Flow Transmitter | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Feed Slurry Flow Transmitter for Pipe (PIPE) |  | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0 | xx | FT-40202_DI_1 | DI | 1 | 1 | C1S03 | C1S03DI19 | C1S03,19 | 1756-IB32-19 |  | x | DI | C1 | 3 | 19 |  | 1 | 0 | 1 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M1 | JB-401 | C1S03,20 | 1756-IB32-20 | X2 | C1S03-X2 | HV-40201_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | HV-40201 | Manual Valve With Position Switch | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry Drain line |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | HV-40201_DI_1 | DI | 1 | 1 | C1S03 | C1S03DI20 | C1S03,20 | 1756-IB32-20 |  | x | DI | C1 | 3 | 20 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-401 | C1S03,21 | 1756-IB32-21 | X2 | C1S03-X2 | HV-40202_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | HV-40202 | Manual Valve With Position Switch | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry Drain line |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | HV-40202_DI_1 | DI | 1 | 1 | C1S03 | C1S03DI21 | C1S03,21 | 1756-IB32-21 |  | x | DI | C1 | 3 | 21 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-401 | C1S03,22 | 1756-IB32-22 | X2 | C1S03-X2 | HV-40203_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | HV-40203 | Manual Valve With Position Switch | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry Drain tank TS-40201 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | HV-40203_DI_1 | DI | 1 | 1 | C1S03 | C1S03DI22 | C1S03,22 | 1756-IB32-22 |  | x | DI | C1 | 3 | 22 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-401 | C1S03,23 | 1756-IB32-23 | X2 | C1S03-X2 | HV-40204_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | HV-40204 | Manual Valve With Position Switch | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry Drain tank TS-40202 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | HV-40204_DI_1 | DI | 1 | 1 | C1S03 | C1S03DI23 | C1S03,23 | 1756-IB32-23 |  | x | DI | C1 | 3 | 23 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-401 | C1S03,24 | 1756-IB32-24 | X2 | C1S03-X2 | HV-40205_DI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | HV-40205 | Manual Valve With Position Switch | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-02 | Slurry Drain line |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | HV-40205_DI_1 | DI | 1 | 1 | C1S03 | C1S03DI24 | C1S03,24 | 1756-IB32-24 |  | x | DI | C1 | 3 | 24 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-401 | C1S03,25 | 1756-IB32-25 | X2 | C1S03-X2 | HV-40206_DI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | HV-40206 | Manual Valve With Position Switch | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-02 | Slurry Drain tank TS-40203 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | HV-40206_DI_1 | DI | 1 | 1 | C1S03 | C1S03DI25 | C1S03,25 | 1756-IB32-25 |  | x | DI | C1 | 3 | 25 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-401 | C1S03,26 | 1756-IB32-26 | X2 | C1S03-X2 | XV-40201A_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201A | 0 | 1st | - | 3-25-01-402-PD-01 | Slurry feed-in pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201A_DI_1 | DI | 1 | 1 | C1S03 | C1S03DI26 | C1S03,26 | 1756-IB32-26 |  | x | DI | C1 | 3 | 26 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S03,27 | 1756-IB32-27 | X2 | C1S03-X2 | XV-40201A_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201A | 0 | 1st | - | 3-25-01-402-PD-01 | Slurry feed-in pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201A_DI_2 | DI | 1 | 2 | C1S03 | C1S03DI27 | C1S03,27 | 1756-IB32-27 |  | x | DI | C1 | 3 | 27 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S03,28 | 1756-IB32-28 | X2 | C1S03-X2 | XV-40201B_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201B | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201B_DI_1 | DI | 1 | 1 | C1S03 | C1S03DI28 | C1S03,28 | 1756-IB32-28 |  | x | DI | C1 | 3 | 28 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S03,29 | 1756-IB32-29 | X2 | C1S03-X2 | XV-40201B_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201B | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201B_DI_2 | DI | 1 | 2 | C1S03 | C1S03DI29 | C1S03,29 | 1756-IB32-29 |  | x | DI | C1 | 3 | 29 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S03,30 | 1756-IB32-30 | X2 | C1S03-X2 | XV-40201C_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201C | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201C_DI_1 | DI | 1 | 1 | C1S03 | C1S03DI30 | C1S03,30 | 1756-IB32-30 |  | x | DI | C1 | 3 | 30 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S03,31 | 1756-IB32-31 | X2 | C1S03-X2 | XV-40201C_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201C | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201C_DI_2 | DI | 1 | 2 | C1S03 | C1S03DI31 | C1S03,31 | 1756-IB32-31 |  | x | DI | C1 | 3 | 31 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,00 | 1756-IB32-0 | X1 | C1S04-X1 | XV-40201D_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201D | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry circulation pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201D_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI00 | C1S04,00 | 1756-IB32-0 |  | x | DI | C1 | 4 | 0 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,01 | 1756-IB32-1 | X1 | C1S04-X1 | XV-40201D_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201D | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry circulation pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201D_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI01 | C1S04,01 | 1756-IB32-1 |  | x | DI | C1 | 4 | 1 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,02 | 1756-IB32-2 | X1 | C1S04-X1 | XV-40201E_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201E | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201E_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI02 | C1S04,02 | 1756-IB32-2 |  | x | DI | C1 | 4 | 2 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,03 | 1756-IB32-3 | X1 | C1S04-X1 | XV-40201E_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201E | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201E_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI03 | C1S04,03 | 1756-IB32-3 |  | x | DI | C1 | 4 | 3 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,04 | 1756-IB32-4 | X1 | C1S04-X1 | XV-40201F_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201F | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-to spray dry tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201F_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI04 | C1S04,04 | 1756-IB32-4 |  | x | DI | C1 | 4 | 4 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,05 | 1756-IB32-5 | X1 | C1S04-X1 | XV-40201F_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201F | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-to spray dry tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201F_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI05 | C1S04,05 | 1756-IB32-5 |  | x | DI | C1 | 4 | 5 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,06 | 1756-IB32-6 | X1 | C1S04-X1 | XV-40201G_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201G | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | CIP water washing pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201G_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI06 | C1S04,06 | 1756-IB32-6 |  | x | DI | C1 | 4 | 6 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,07 | 1756-IB32-7 | X1 | C1S04-X1 | XV-40201G_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201G | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | CIP water washing pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201G_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI07 | C1S04,07 | 1756-IB32-7 |  | x | DI | C1 | 4 | 7 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,08 | 1756-IB32-8 | X1 | C1S04-X1 | XV-40201H_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201H | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201H_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI08 | C1S04,08 | 1756-IB32-8 |  | x | DI | C1 | 4 | 8 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,09 | 1756-IB32-9 | X1 | C1S04-X1 | XV-40201H_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201H | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201H_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI09 | C1S04,09 | 1756-IB32-9 |  | x | DI | C1 | 4 | 9 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,11 | 1756-IB32-11 | X1 | C1S04-X1 | XV-40202A_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202A | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-in pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202A_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI11 | C1S04,11 | 1756-IB32-11 |  | x | DI | C1 | 4 | 11 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,12 | 1756-IB32-12 | X1 | C1S04-X1 | XV-40202B_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202B | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-out pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202B_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI12 | C1S04,12 | 1756-IB32-12 |  | x | DI | C1 | 4 | 12 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,13 | 1756-IB32-13 | X1 | C1S04-X1 | XV-40202B_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202B | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-out pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202B_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI13 | C1S04,13 | 1756-IB32-13 |  | x | DI | C1 | 4 | 13 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,14 | 1756-IB32-14 | X1 | C1S04-X1 | XV-40202C_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202C | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Water washing line outlet pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202C_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI14 | C1S04,14 | 1756-IB32-14 |  | x | DI | C1 | 4 | 14 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,15 | 1756-IB32-15 | X1 | C1S04-X1 | XV-40202C_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202C | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Water washing line outlet pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202C_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI15 | C1S04,15 | 1756-IB32-15 |  | x | DI | C1 | 4 | 15 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,16 | 1756-IB32-16 | X2 | C1S04-X2 | XV-40202D_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202D | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry circulation pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202D_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI16 | C1S04,16 | 1756-IB32-16 |  | x | DI | C1 | 4 | 16 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,17 | 1756-IB32-17 | X2 | C1S04-X2 | XV-40202D_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202D | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry circulation pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202D_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI17 | C1S04,17 | 1756-IB32-17 |  | x | DI | C1 | 4 | 17 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,18 | 1756-IB32-18 | X2 | C1S04-X2 | XV-40202E_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202E | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202E_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI18 | C1S04,18 | 1756-IB32-18 |  | x | DI | C1 | 4 | 18 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,19 | 1756-IB32-19 | X2 | C1S04-X2 | XV-40202A_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202A | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-in pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202A_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI19 | C1S04,19 | 1756-IB32-19 |  | x | DI | C1 | 4 | 19 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,19 | 1756-IB32-19 | X2 | C1S04-X2 | XV-40202E_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202E | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202E_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI19 | C1S04,19 | 1756-IB32-19 |  | x | DI | C1 | 4 | 19 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,20 | 1756-IB32-20 | X2 | C1S04-X2 | XV-40202F_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202F | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-to spray dry tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202F_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI20 | C1S04,20 | 1756-IB32-20 |  | x | DI | C1 | 4 | 20 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,21 | 1756-IB32-21 | X2 | C1S04-X2 | XV-40202F_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202F | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-to spray dry tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202F_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI21 | C1S04,21 | 1756-IB32-21 |  | x | DI | C1 | 4 | 21 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,22 | 1756-IB32-22 | X2 | C1S04-X2 | XV-40202G_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202G | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | CIP water washing pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202G_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI22 | C1S04,22 | 1756-IB32-22 |  | x | DI | C1 | 4 | 22 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,23 | 1756-IB32-23 | X2 | C1S04-X2 | XV-40202G_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202G | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | CIP water washing pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202G_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI23 | C1S04,23 | 1756-IB32-23 |  | x | DI | C1 | 4 | 23 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,24 | 1756-IB32-24 | X2 | C1S04-X2 | XV-40202H_DI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202H | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202H_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI24 | C1S04,24 | 1756-IB32-24 |  | x | DI | C1 | 4 | 24 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,25 | 1756-IB32-25 | X2 | C1S04-X2 | XV-40202H_DI_2 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202H | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202H_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI25 | C1S04,25 | 1756-IB32-25 |  | x | DI | C1 | 4 | 25 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,26 | 1756-IB32-26 | X2 | C1S04-X2 | XV-40203B_DI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | XV-40203B | 0 | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Slurry feed-out Spray dryer infeed tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203B_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI26 | C1S04,26 | 1756-IB32-26 |  | x | DI | C1 | 4 | 26 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,27 | 1756-IB32-27 | X2 | C1S04-X2 | XV-40203B_DI_2 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | XV-40203B | 0 | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Slurry feed-out Spray dryer infeed tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203B_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI27 | C1S04,27 | 1756-IB32-27 |  | x | DI | C1 | 4 | 27 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,28 | 1756-IB32-28 | X2 | C1S04-X2 | XV-40203C_DI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | XV-40203C | 0 | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Water washing line outlet Spray dryer infeed tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203C_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI28 | C1S04,28 | 1756-IB32-28 |  | x | DI | C1 | 4 | 28 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,29 | 1756-IB32-29 | X2 | C1S04-X2 | XV-40203C_DI_2 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | XV-40203C | 0 | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Water washing line outlet Spray dryer infeed tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203C_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI29 | C1S04,29 | 1756-IB32-29 |  | x | DI | C1 | 4 | 29 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,30 | 1756-IB32-30 | X2 | C1S04-X2 | XV-40203D_DI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | XV-40203D | 0 | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | CIP water washing Spray dryer infeed tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203D_DI_1 | DI | 1 | 1 | C1S04 | C1S04DI30 | C1S04,30 | 1756-IB32-30 |  | x | DI | C1 | 4 | 30 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S04,31 | 1756-IB32-31 | X2 | C1S04-X2 | XV-40203D_DI_2 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | XV-40203D | 0 | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | CIP water washing Spray dryer infeed tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203D_DI_2 | DI | 1 | 2 | C1S04 | C1S04DI31 | C1S04,31 | 1756-IB32-31 |  | x | DI | C1 | 4 | 31 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S05,00 | 1756-IB32-0 | X1 | C1S05-X1 | XV-40203E_DI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | XV-40203E | 0 | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | CIP hight pressure water washing Spray dryer infeed tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203E_DI_1 | DI | 1 | 1 | C1S05 | C1S05DI00 | C1S05,00 | 1756-IB32-0 |  | x | DI | C1 | 5 | 0 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S05,01 | 1756-IB32-1 | X1 | C1S05-X1 | XV-40203E_DI_2 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | XV-40203E | 0 | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | CIP hight pressure water washing Spray dryer infeed tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203E_DI_2 | DI | 1 | 2 | C1S05 | C1S05DI01 | C1S05,01 | 1756-IB32-1 |  | x | DI | C1 | 5 | 1 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S05,02 | 1756-IB32-2 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI02 | C1S05,02 | 1756-IB32-2 |  | x | DI | C1 | 5 | 2 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S05,03 | 1756-IB32-3 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI03 | C1S05,03 | 1756-IB32-3 |  | x | DI | C1 | 5 | 3 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S05,04 | 1756-IB32-4 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI04 | C1S05,04 | 1756-IB32-4 |  | x | DI | C1 | 5 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S05,05 | 1756-IB32-5 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI05 | C1S05,05 | 1756-IB32-5 |  | x | DI | C1 | 5 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S05,06 | 1756-IB32-6 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI06 | C1S05,06 | 1756-IB32-6 |  | x | DI | C1 | 5 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S05,07 | 1756-IB32-7 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI07 | C1S05,07 | 1756-IB32-7 |  | x | DI | C1 | 5 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S05,08 | 1756-IB32-8 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI08 | C1S05,08 | 1756-IB32-8 |  | x | DI | C1 | 5 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S05,09 | 1756-IB32-9 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI09 | C1S05,09 | 1756-IB32-9 |  | x | DI | C1 | 5 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S05,10 | 1756-IB32-10 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI10 | C1S05,10 | 1756-IB32-10 |  | x | DI | C1 | 5 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S05,11 | 1756-IB32-11 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI11 | C1S05,11 | 1756-IB32-11 |  | x | DI | C1 | 5 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S05,12 | 1756-IB32-12 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI12 | C1S05,12 | 1756-IB32-12 |  | x | DI | C1 | 5 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S05,13 | 1756-IB32-13 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI13 | C1S05,13 | 1756-IB32-13 |  | x | DI | C1 | 5 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S05,14 | 1756-IB32-14 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI14 | C1S05,14 | 1756-IB32-14 |  | x | DI | C1 | 5 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S05,15 | 1756-IB32-15 | X1 | C1S05-X1 | Spare_DI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI15 | C1S05,15 | 1756-IB32-15 |  | x | DI | C1 | 5 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S05,16 | 1756-IB32-16 | X2 | C1S05-X2 | ES-60202_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | ES-60202 | 0 | 1st | 325-01-600-PD-01 | - | E-Stop for PUPD-11 (Positive Displacement Pump ) | x | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | ES-60202_DI_1 | DI | 1 | 1 | C1S05 | C1S05DI16 | C1S05,16 | 1756-IB32-16 |  | x | DI | C1 | 5 | 16 |  | 1 | 0 | 0 | 0 | 0 |  | 0
=CA1+MCP-M1 | JB-601 | C1S05,17 | 1756-IB32-17 | X2 | C1S05-X2 | FS-60205_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | FS-60205 | Flow Switch | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 | Cooling Water Return Flow Switch for Positive Displacement Pump (PUPD-11) | x | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | FS-60205_DI_1 | DI | 1 | 1 | C1S05 | C1S05DI17 | C1S05,17 | 1756-IB32-17 |  | x | DI | C1 | 5 | 17 |  | 1 | 0 | 0 | 0 | 0 |  | 0
=CA1+MCP-M1 | JB-601 | C1S05,18 | 1756-IB32-18 | X2 | C1S05-X2 | LSL-60201_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | LSL-60201 | 0 | 1st | 325-01-600-PD-11 | 3-25-01-602-PD-11 | Level low switch |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | LSL-60201_DI_1 | DI | 1 | 1 | C1S05 | C1S05DI18 | C1S05,18 | 1756-IB32-18 |  | x | DI | C1 | 5 | 18 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S05,19 | 1756-IB32-19 | X2 | C1S05-X2 | SV-60201_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60201 | 0 | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60201_DI_1 | DI | 1 | 1 | C1S05 | C1S05DI19 | C1S05,19 | 1756-IB32-19 |  | x | DI | C1 | 5 | 19 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S05,20 | 1756-IB32-20 | X2 | C1S05-X2 | SV-60201_DI_2 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60201 | 0 | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60201_DI_2 | DI | 1 | 2 | C1S05 | C1S05DI20 | C1S05,20 | 1756-IB32-20 |  | x | DI | C1 | 5 | 20 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S05,21 | 1756-IB32-21 | X2 | C1S05-X2 | SV-60202_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60202 | 0 | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60202_DI_1 | DI | 1 | 1 | C1S05 | C1S05DI21 | C1S05,21 | 1756-IB32-21 |  | x | DI | C1 | 5 | 21 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S05,22 | 1756-IB32-22 | X2 | C1S05-X2 | SV-60202_DI_2 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60202 | 0 | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60202_DI_2 | DI | 1 | 2 | C1S05 | C1S05DI22 | C1S05,22 | 1756-IB32-22 |  | x | DI | C1 | 5 | 22 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S05,23 | 1756-IB32-23 | X2 | C1S05-X2 | SV-60203_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60203 | 0 | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60203_DI_1 | DI | 1 | 1 | C1S05 | C1S05DI23 | C1S05,23 | 1756-IB32-23 |  | x | DI | C1 | 5 | 23 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S05,24 | 1756-IB32-24 | X2 | C1S05-X2 | SV-60203_DI_2 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60203 | 0 | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60203_DI_2 | DI | 1 | 2 | C1S05 | C1S05DI24 | C1S05,24 | 1756-IB32-24 |  | x | DI | C1 | 5 | 24 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S05,25 | 1756-IB32-25 | X2 | C1S05-X2 | VS-60205_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | VS-60205 | Vibration Switch | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 | Vibration Gear Box Vibration Switch for Switch Vibration for PUPD-11 (PUPD-11) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | VS-60205_DI_1 | DI | 1 | 1 | C1S05 | C1S05DI25 | C1S05,25 | 1756-IB32-25 |  | x | DI | C1 | 5 | 25 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S05,26 | 1756-IB32-26 | X2 | C1S05-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI26 | C1S05,26 | 1756-IB32-26 |  | x | DI | C1 | 5 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S05,27 | 1756-IB32-27 | X2 | C1S05-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI27 | C1S05,27 | 1756-IB32-27 |  | x | DI | C1 | 5 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S05,28 | 1756-IB32-28 | X2 | C1S05-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI28 | C1S05,28 | 1756-IB32-28 |  | x | DI | C1 | 5 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S05,29 | 1756-IB32-29 | X2 | C1S05-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI29 | C1S05,29 | 1756-IB32-29 |  | x | DI | C1 | 5 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S05,30 | 1756-IB32-30 | X2 | C1S05-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI30 | C1S05,30 | 1756-IB32-30 |  | x | DI | C1 | 5 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S05,31 | 1756-IB32-31 | X2 | C1S05-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S05 | C1S05DI31 | C1S05,31 | 1756-IB32-31 |  | x | DI | C1 | 5 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,00 | 1756-IB32-0 | X1 | C1S06-X1 | XA-60202A_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XA-60202A | 0 | 1st | 325-01-600-PD-08 | - | General Alarm Emergency Stop Actuation for XSUP-5601 (Supression Panel) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60202A_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI00 | C1S06,00 | 1756-IB32-0 |  | x | DI | C1 | 6 | 0 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,01 | 1756-IB32-1 | X1 | C1S06-X1 | XA-60202B_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XA-60202B | 0 | 1st | 325-01-600-PD-08 | - | General Fault Controlled Stop for XSUP-5601 (Supression Panel) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60202B_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI01 | C1S06,01 | 1756-IB32-1 |  | x | DI | C1 | 6 | 1 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,02 | 1756-IB32-2 | X1 | C1S06-X1 | XA-60202C_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XA-60202C | 0 | 1st | 325-01-600-PD-08 | - | General Armed Status Indicator for XSUP-5601 (Supression Panel) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60202C_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI02 | C1S06,02 | 1756-IB32-2 |  | x | DI | C1 | 6 | 2 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,03 | 1756-IB32-3 | X1 | C1S06-X1 | XA-60202D_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XA-60202D | 0 | 1st | 325-01-600-PD-08 | - | Power Fault Status Indicator for XSUP-5601 (Supression Panel) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60202D_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI03 | C1S06,03 | 1756-IB32-3 |  | x | DI | C1 | 6 | 3 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,04 | 1756-IB32-4 | X1 | C1S06-X1 | XA-60202E_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XA-60202E | 0 | 1st | 325-01-600-PD-08 | - | Dryer CHAM-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60202E_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI04 | C1S06,04 | 1756-IB32-4 |  | x | DI | C1 | 6 | 4 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,05 | 1756-IB32-5 | X1 | C1S06-X1 | XA-60202F_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XA-60202F | 0 | 1st | 325-01-600-PD-08 | - | CHAM-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60202F_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI05 | C1S06,05 | 1756-IB32-5 |  | x | DI | C1 | 6 | 5 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,06 | 1756-IB32-6 | X1 | C1S06-X1 | XA-60202G_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XA-60202G | 0 | 1st | 325-01-600-PD-08 | - | CYCL-21/22 Emergency Stop Actuation for XSUP-5601 (Supression Panel) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60202G_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI06 | C1S06,06 | 1756-IB32-6 |  | x | DI | C1 | 6 | 6 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,07 | 1756-IB32-7 | X1 | C1S06-X1 | XA-60202H_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XA-60202H | 0 | 1st | 325-01-600-PD-08 | - | CYCL-21/22 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60202H_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI07 | C1S06,07 | 1756-IB32-7 |  | x | DI | C1 | 6 | 7 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,08 | 1756-IB32-8 | X1 | C1S06-X1 | XA-60202I_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XA-60202I |  | 1st | 325-01-600-PD-08 | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60202I_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI08 | C1S06,08 | 1756-IB32-8 |  | x | DI | C1 | 6 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,09 | 1756-IB32-9 | X1 | C1S06-X1 | XA-60202J_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XA-60202J | 0 | 1st | 325-01-600-PD-08 | - | BGHS-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60202J_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI09 | C1S06,09 | 1756-IB32-9 |  | x | DI | C1 | 6 | 9 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,10 | 1756-IB32-10 | X1 | C1S06-X1 | XA-60202K_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XA-60202K | 0 | 1st | 325-01-600-PD-08 | - | BGHS-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60202K_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI10 | C1S06,10 | 1756-IB32-10 |  | x | DI | C1 | 6 | 10 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,11 | 1756-IB32-11 | X1 | C1S06-X1 | XA-60202L_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XA-60202L | 0 | 1st | 325-01-600-PD-08 | - | CYCL-31 Emergency Stop Actuation for XSUP-5601 (Supression Panel) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60202L_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI11 | C1S06,11 | 1756-IB32-11 |  | x | DI | C1 | 6 | 11 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,12 | 1756-IB32-12 | X1 | C1S06-X1 | XA-60202M_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XA-60202M | 0 | 1st | 325-01-600-PD-08 | - | CYCL-31 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60202M_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI12 | C1S06,12 | 1756-IB32-12 |  | x | DI | C1 | 6 | 12 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,13 | 1756-IB32-13 | X1 | C1S06-X1 | XV-60202_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XV-60202 | 0 | 1st | 325-01-600-PD-11 | 3-25-01-602-PD-11 | High Pressure Water On/Off Valve for Drain Pipe |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60202_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI13 | C1S06,13 | 1756-IB32-13 |  | x | DI | C1 | 6 | 13 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S06,14 | 1756-IB32-14 | X1 | C1S06-X1 | XV-60202_DI_2 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XV-60202 | 0 | 1st | 325-01-600-PD-11 | 3-25-01-602-PD-11 | High Pressure Water On/Off Valve for Drain Pipe |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60202_DI_2 | DI | 1 | 2 | C1S06 | C1S06DI14 | C1S06,14 | 1756-IB32-14 |  | x | DI | C1 | 6 | 14 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S06,15 | 1756-IB32-15 | X1 | C1S06-X1 | XV-60205A_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XV-60205A | 0 | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60205A_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI15 | C1S06,15 | 1756-IB32-15 |  | x | DI | C1 | 6 | 15 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,16 | 1756-IB32-16 | X2 | C1S06-X2 | XV-60205A_DI_2 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XV-60205A | 0 | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60205A_DI_2 | DI | 1 | 2 | C1S06 | C1S06DI16 | C1S06,16 | 1756-IB32-16 |  | x | DI | C1 | 6 | 16 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M1 | JB-601 | C1S06,17 | 1756-IB32-17 | X2 | C1S06-X2 | XV-60240D_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XV-60240D |  | 1st | 325-01-600-PD-05 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60240D_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI17 | C1S06,17 | 1756-IB32-17 |  | x | DI | C1 | 6 | 17 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,18 | 1756-IB32-18 | X2 | C1S06-X2 | XV-60240D_DI_2 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XV-60240D |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-05 |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60240D_DI_2 | DI | 1 | 2 | C1S06 | C1S06DI18 | C1S06,18 | 1756-IB32-18 |  | x | DI | C1 | 6 | 18 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,19 | 1756-IB32-19 | X2 | C1S06-X2 | XV-60240D_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XV-60240D |  | 1st | 325-01-600-PD-05 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60240D_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI19 | C1S06,19 | 1756-IB32-19 |  | x | DI | C1 | 6 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,20 | 1756-IB32-20 | X2 | C1S06-X2 | XV-60240D_DI_2 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XV-60240D |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-05 |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60240D_DI_2 | DI | 1 | 2 | C1S06 | C1S06DI20 | C1S06,20 | 1756-IB32-20 |  | x | DI | C1 | 6 | 20 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,21 | 1756-IB32-21 | X2 | C1S06-X2 | YA-60205_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | YA-60205 | 0 | 1st | 325-01-600-PD-01 | - | Fault Command |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | YA-60205_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI21 | C1S06,21 | 1756-IB32-21 |  | x | DI | C1 | 6 | 21 |  | 1 | 0 | 0 | 0 | 0 |  | 0
=CA1+MCP-M1 | JB-601 | C1S06,22 | 1756-IB32-22 | X2 | C1S06-X2 | YI-60205_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | YI-60205 | 0 | 1st | 325-01-600-PD-01 | - | Run Command |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | YI-60205_DI_1 | DI | 1 | 1 | C1S06 | C1S06DI22 | C1S06,22 | 1756-IB32-22 |  | x | DI | C1 | 6 | 22 |  | 1 | 0 | 0 | 0 | 0 |  | 0
=CA1+MCP-M1 | JB-601 | C1S06,23 | 1756-IB32-23 | X2 | C1S06-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S06 | C1S06DI23 | C1S06,23 | 1756-IB32-23 |  | x | DI | C1 | 6 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,24 | 1756-IB32-24 | X2 | C1S06-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S06 | C1S06DI24 | C1S06,24 | 1756-IB32-24 |  | x | DI | C1 | 6 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,25 | 1756-IB32-25 | X2 | C1S06-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S06 | C1S06DI25 | C1S06,25 | 1756-IB32-25 |  | x | DI | C1 | 6 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,26 | 1756-IB32-26 | X2 | C1S06-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S06 | C1S06DI26 | C1S06,26 | 1756-IB32-26 |  | x | DI | C1 | 6 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,27 | 1756-IB32-27 | X2 | C1S06-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S06 | C1S06DI27 | C1S06,27 | 1756-IB32-27 |  | x | DI | C1 | 6 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,28 | 1756-IB32-28 | X2 | C1S06-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S06 | C1S06DI28 | C1S06,28 | 1756-IB32-28 |  | x | DI | C1 | 6 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,29 | 1756-IB32-29 | X2 | C1S06-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S06 | C1S06DI29 | C1S06,29 | 1756-IB32-29 |  | x | DI | C1 | 6 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,30 | 1756-IB32-30 | X2 | C1S06-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S06 | C1S06DI30 | C1S06,30 | 1756-IB32-30 |  | x | DI | C1 | 6 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S06,31 | 1756-IB32-31 | X2 | C1S06-X2 | Spare_DI_0 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C1S06 | C1S06DI31 | C1S06,31 | 1756-IB32-31 |  | x | DI | C1 | 6 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,00 | 1756-OB32-0 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO00 | C1S07,00 | 1756-OB32-0 |  | x | DO | C1 | 7 | 0 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,01 | 1756-OB32-1 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO01 | C1S07,01 | 1756-OB32-1 |  | x | DO | C1 | 7 | 1 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,02 | 1756-OB32-2 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO02 | C1S07,02 | 1756-OB32-2 |  | x | DO | C1 | 7 | 2 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,03 | 1756-OB32-3 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO03 | C1S07,03 | 1756-OB32-3 |  | x | DO | C1 | 7 | 3 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,04 | 1756-OB32-4 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO04 | C1S07,04 | 1756-OB32-4 |  | x | DO | C1 | 7 | 4 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,05 | 1756-OB32-5 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO05 | C1S07,05 | 1756-OB32-5 |  | x | DO | C1 | 7 | 5 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,06 | 1756-OB32-6 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO06 | C1S07,06 | 1756-OB32-6 |  | x | DO | C1 | 7 | 6 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,07 | 1756-OB32-7 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO07 | C1S07,07 | 1756-OB32-7 |  | x | DO | C1 | 7 | 7 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,08 | 1756-OB32-8 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO08 | C1S07,08 | 1756-OB32-8 |  | x | DO | C1 | 7 | 8 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,09 | 1756-OB32-9 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO09 | C1S07,09 | 1756-OB32-9 |  | x | DO | C1 | 7 | 9 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,10 | 1756-OB32-10 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO10 | C1S07,10 | 1756-OB32-10 |  | x | DO | C1 | 7 | 10 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,11 | 1756-OB32-11 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO11 | C1S07,11 | 1756-OB32-11 |  | x | DO | C1 | 7 | 11 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,12 | 1756-OB32-12 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO12 | C1S07,12 | 1756-OB32-12 |  | x | DO | C1 | 7 | 12 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,13 | 1756-OB32-13 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO13 | C1S07,13 | 1756-OB32-13 |  | x | DO | C1 | 7 | 13 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,14 | 1756-OB32-14 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO14 | C1S07,14 | 1756-OB32-14 |  | x | DO | C1 | 7 | 14 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 | C1S07,15 | 1756-OB32-15 | X1 | C1S07-X1 | Spare_DO_0 |  | Main Control Cabinet |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S07 | C1S07DO15 | C1S07,15 | 1756-OB32-15 |  | x | DO | C1 | 7 | 15 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S07,16 | 1756-OB32-16 | X2 | C1S07-X2 | XV-40202E_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202E | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 |  | XV-40202E_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO16 | C1S07,16 | 1756-OB32-16 |  | x | DO | C1 | 7 | 16 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,17 | 1756-OB32-17 | X2 | C1S07-X2 | XV-40202F_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202F | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-to spray dry tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202F_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO17 | C1S07,17 | 1756-OB32-17 |  | x | DO | C1 | 7 | 17 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,18 | 1756-OB32-18 | X2 | C1S07-X2 | XV-40202G_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202G | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | CIP water washing pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202G_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO18 | C1S07,18 | 1756-OB32-18 |  | x | DO | C1 | 7 | 18 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,19 | 1756-OB32-19 | X2 | C1S07-X2 | XV-40202H_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202H | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202H_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO19 | C1S07,19 | 1756-OB32-19 |  | x | DO | C1 | 7 | 19 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,20 | 1756-OB32-20 | X2 | C1S07-X2 | XV-40203B_DO_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | XV-40203B | 0 | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Slurry feed-out Spray dryer infeed tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203B_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO20 | C1S07,20 | 1756-OB32-20 |  | x | DO | C1 | 7 | 20 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,21 | 1756-OB32-21 | X2 | C1S07-X2 | XV-40203C_DO_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | XV-40203C | 0 | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Water washing line outlet Spray dryer infeed tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203C_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO21 | C1S07,21 | 1756-OB32-21 |  | x | DO | C1 | 7 | 21 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,22 | 1756-OB32-22 | X2 | C1S07-X2 | XV-40203D_DO_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | XV-40203D | 0 | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | CIP water washing Spray dryer infeed tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203D_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO22 | C1S07,22 | 1756-OB32-22 |  | x | DO | C1 | 7 | 22 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,23 | 1756-OB32-23 | X2 | C1S07-X2 | XV-40203E_DO_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | XV-40203E | 0 | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | CIP hight pressure water washing Spray dryer infeed tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203E_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO23 | C1S07,23 | 1756-OB32-23 |  | x | DO | C1 | 7 | 23 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,24 | 1756-OB32-24 | X2 | C1S07-X2 | SV-40201_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | SV-40201 | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 1 |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | SV-40201_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO24 | C1S07,24 | 1756-OB32-24 |  | x | DO | C1 | 7 | 24 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,25 | 1756-OB32-25 | X2 | C1S07-X2 | SV-40202_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | SV-40202 | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 2 |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | SV-40202_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO25 | C1S07,25 | 1756-OB32-25 |  | x | DO | C1 | 7 | 25 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,26 | 1756-OB32-26 | X2 | C1S07-X2 | SV-40203_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | SV-40203 | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 1 |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | SV-40203_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO26 | C1S07,26 | 1756-OB32-26 |  | x | DO | C1 | 7 | 26 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,27 | 1756-OB32-27 | X2 | C1S07-X2 | SV-40204_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | SV-40204 | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 2 |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | SV-40204_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO27 | C1S07,27 | 1756-OB32-27 |  | x | DO | C1 | 7 | 27 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,28 | 1756-OB32-28 | X2 | C1S07-X2 | XV-40201A_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201A | 0 | 1st | - | 3-25-01-402-PD-01 | Slurry feed-in pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201A_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO28 | C1S07,28 | 1756-OB32-28 |  | x | DO | C1 | 7 | 28 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,29 | 1756-OB32-29 | X2 | C1S07-X2 | XV-40201B_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201B | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201B_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO29 | C1S07,29 | 1756-OB32-29 |  | x | DO | C1 | 7 | 29 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,30 | 1756-OB32-30 | X2 | C1S07-X2 | XV-40201C_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201C | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201C_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO30 | C1S07,30 | 1756-OB32-30 |  | x | DO | C1 | 7 | 30 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S07,31 | 1756-OB32-31 | X2 | C1S07-X2 | XV-40201D_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201D | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry circulation pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201D_DO_1 | DO | 2 | 1 | C1S07 | C1S07DO31 | C1S07,31 | 1756-OB32-31 |  | x | DO | C1 | 7 | 31 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S08,00 | 1756-OB32-0 | X1 | C1S08-X1 | XV-40201E_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201E | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201E_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO00 | C1S08,00 | 1756-OB32-0 |  | x | DO | C1 | 8 | 0 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S08,01 | 1756-OB32-1 | X1 | C1S08-X1 | XV-40201F_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201F | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-to spray dry tank |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201F_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO01 | C1S08,01 | 1756-OB32-1 |  | x | DO | C1 | 8 | 1 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S08,02 | 1756-OB32-2 | X1 | C1S08-X1 | XV-40201G_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201G | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | CIP water washing pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201G_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO02 | C1S08,02 | 1756-OB32-2 |  | x | DO | C1 | 8 | 2 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S08,03 | 1756-OB32-3 | X1 | C1S08-X1 | XV-40201H_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40201H | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40201H_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO03 | C1S08,03 | 1756-OB32-3 |  | x | DO | C1 | 8 | 3 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S08,04 | 1756-OB32-4 | X1 | C1S08-X1 | XV-40202A_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202A | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-in pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202A_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO04 | C1S08,04 | 1756-OB32-4 |  | x | DO | C1 | 8 | 4 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S08,05 | 1756-OB32-5 | X1 | C1S08-X1 | XV-40202B_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202B | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry feed-out pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202B_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO05 | C1S08,05 | 1756-OB32-5 |  | x | DO | C1 | 8 | 5 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S08,06 | 1756-OB32-6 | X1 | C1S08-X1 | XV-40202C_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202C | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Water washing line outlet pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202C_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO06 | C1S08,06 | 1756-OB32-6 |  | x | DO | C1 | 8 | 6 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S08,07 | 1756-OB32-7 | X1 | C1S08-X1 | XV-40202D_DO_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | XV-40202D | 0 | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Slurry circulation pH Adjustment tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40202D_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO07 | C1S08,07 | 1756-OB32-7 |  | x | DO | C1 | 8 | 7 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-401 | C1S08,08 | 1756-OB32-8 | X1 | C1S08-X1 | Spare_DO_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S08 | C1S08DO08 | C1S08,08 | 1756-OB32-8 |  | x | DO | C1 | 8 | 8 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S08,09 | 1756-OB32-9 | X1 | C1S08-X1 | Spare_DO_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S08 | C1S08DO09 | C1S08,09 | 1756-OB32-9 |  | x | DO | C1 | 8 | 9 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S08,10 | 1756-OB32-10 | X1 | C1S08-X1 | Spare_DO_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S08 | C1S08DO10 | C1S08,10 | 1756-OB32-10 |  | x | DO | C1 | 8 | 10 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S08,11 | 1756-OB32-11 | X1 | C1S08-X1 | Spare_DO_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S08 | C1S08DO11 | C1S08,11 | 1756-OB32-11 |  | x | DO | C1 | 8 | 11 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S08,12 | 1756-OB32-12 | X1 | C1S08-X1 | Spare_DO_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S08 | C1S08DO12 | C1S08,12 | 1756-OB32-12 |  | x | DO | C1 | 8 | 12 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S08,13 | 1756-OB32-13 | X1 | C1S08-X1 | Spare_DO_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S08 | C1S08DO13 | C1S08,13 | 1756-OB32-13 |  | x | DO | C1 | 8 | 13 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S08,14 | 1756-OB32-14 | X1 | C1S08-X1 | Spare_DO_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S08 | C1S08DO14 | C1S08,14 | 1756-OB32-14 |  | x | DO | C1 | 8 | 14 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S08,15 | 1756-OB32-15 | X1 | C1S08-X1 | Spare_DO_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S08 | C1S08DO15 | C1S08,15 | 1756-OB32-15 |  | x | DO | C1 | 8 | 15 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S08,16 | 1756-OB32-16 | X2 | C1S08-X2 | SV-60201_DO_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60201 | 0 | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60201_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO16 | C1S08,16 | 1756-OB32-16 |  | x | DO | C1 | 8 | 16 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S08,17 | 1756-OB32-17 | X2 | C1S08-X2 | SV-60202_DO_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60202 | 0 | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60202_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO17 | C1S08,17 | 1756-OB32-17 |  | x | DO | C1 | 8 | 17 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S08,18 | 1756-OB32-18 | X2 | C1S08-X2 | SV-60230_DO_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60230 | 0 | 1st | 325-01-600-PD-04 | 3-25-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 27 (CYCL-21) |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60230_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO18 | C1S08,18 | 1756-OB32-18 |  | x | DO | C1 | 8 | 18 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S08,19 | 1756-OB32-19 | X2 | C1S08-X2 | SV-60203_DO_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60203 | 0 | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60203_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO19 | C1S08,19 | 1756-OB32-19 |  | x | DO | C1 | 8 | 19 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S08,20 | 1756-OB32-20 | X2 | C1S08-X2 | SV-60240A_DO_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60240A | 0 | 1st | 325-01-600-PD-05 | 3-25-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29A (BGHS-21) |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60240A_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO20 | C1S08,20 | 1756-OB32-20 |  | x | DO | C1 | 8 | 20 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S08,21 | 1756-OB32-21 | X2 | C1S08-X2 | SV-60231_DO_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60231 | 0 | 1st | 325-01-600-PD-04 | 3-25-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 28 (CYCL-22) |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60231_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO21 | C1S08,21 | 1756-OB32-21 |  | x | DO | C1 | 8 | 21 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S08,22 | 1756-OB32-22 | X2 | C1S08-X2 | SV-60240B_DO_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60240B | 0 | 1st | 325-01-600-PD-05 | 3-25-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29B (BGHS-21) |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60240B_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO22 | C1S08,22 | 1756-OB32-22 |  | x | DO | C1 | 8 | 22 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S08,23 | 1756-OB32-23 | X2 | C1S08-X2 | SV-60240C_DO_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | SV-60240C | 0 | 1st | 325-01-600-PD-05 | 3-25-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29C (BGHS-21) |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60240C_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO23 | C1S08,23 | 1756-OB32-23 |  | x | DO | C1 | 8 | 23 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S08,24 | 1756-OB32-24 | X2 | C1S08-X2 | XV-60240D_DO_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XV-60240D |  | 1st | 325-01-600-PD-05 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60240D_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO24 | C1S08,24 | 1756-OB32-24 |  | x | DO | C1 | 8 | 24 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S08,25 | 1756-OB32-25 | X2 | C1S08-X2 | XV-60251_DO_1 |  | Spray Dryer 1st Floor | JB-601 | Infeed Tank | XV-60251 | 0 | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 | Liquid On/Off Valve for Drain Pipe (PIPE) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60251_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO25 | C1S08,25 | 1756-OB32-25 |  | x | DO | C1 | 8 | 25 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S08,26 | 1756-OB32-26 | X2 | C1S08-X2 | XV-60202_DO_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XV-60202 | 0 | 1st | 325-01-600-PD-11 | 3-25-01-602-PD-11 | High Pressure Water On/Off Valve for Drain Pipe |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60202_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO26 | C1S08,26 | 1756-OB32-26 |  | x | DO | C1 | 8 | 26 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M1 | JB-601 | C1S08,27 | 1756-OB32-27 | X2 | C1S08-X2 | XV-60205A_DO_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | XV-60205A | 0 | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60205A_DO_1 | DO | 2 | 1 | C1S08 | C1S08DO27 | C1S08,27 | 1756-OB32-27 |  | x | DO | C1 | 8 | 27 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M1 | JB-601 | C1S08,28 | 1756-OB32-28 | X2 | C1S08-X2 | Spare_DO_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S08 | C1S08DO28 | C1S08,28 | 1756-OB32-28 |  | x | DO | C1 | 8 | 28 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S08,29 | 1756-OB32-29 | X2 | C1S08-X2 | Spare_DO_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S08 | C1S08DO29 | C1S08,29 | 1756-OB32-29 |  | x | DO | C1 | 8 | 29 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S08,30 | 1756-OB32-30 | X2 | C1S08-X2 | Spare_DO_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S08 | C1S08DO30 | C1S08,30 | 1756-OB32-30 |  | x | DO | C1 | 8 | 30 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S08,31 | 1756-OB32-31 | X2 | C1S08-X2 | Spare_DO_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C1S08 | C1S08DO31 | C1S08,31 | 1756-OB32-31 |  | x | DO | C1 | 8 | 31 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S09,00 | 1756-IF16-0 | X1 | C1S09-X1 | FT-40201_AI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | FT-40201 | Coriolis Flow Transmitter | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Slurry flowrate & density check transfer line |  | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0 | xx | FT-40201_AI_1 | AI | 3 | 1 | C1S09 | C1S09AI00 | C1S09,00 | 1756-IF16-0 |  | x | AI | C1 | 9 | 0 |  | 1 | 0 | 2 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M1 | JB-401 | C1S09,01 | 1756-IF16-1 | X1 | C1S09-X1 | FT-40201_AI_2 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | FT-40201 | Coriolis Flow Transmitter | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Slurry flowrate & density check transfer line |  | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0 | xx | FT-40201_AI_2 | AI | 3 | 2 | C1S09 | C1S09AI01 | C1S09,01 | 1756-IF16-1 |  | x | AI | C1 | 9 | 1 |  | 1 | 0 | 2 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M1 | JB-401 | C1S09,02 | 1756-IF16-2 | X1 | C1S09-X1 | FT-40202_AI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | FT-40202 | Magnetic Flow Transmitter | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Feed Slurry Flow Transmitter for Pipe (PIPE) |  | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0 | xx | FT-40202_AI_1 | AI | 3 | 1 | C1S09 | C1S09AI02 | C1S09,02 | 1756-IF16-2 |  | x | AI | C1 | 9 | 2 |  | 1 | 0 | 1 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M1 | JB-401 | C1S09,03 | 1756-IF16-3 | X1 | C1S09-X1 | LT-40203_AI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | LT-40203 | Level Transmitter | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Level transmitter in Spray dryer infeed tank | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | LT-40203_AI_1 | AI | 3 | 1 | C1S09 | C1S09AI03 | C1S09,03 | 1756-IF16-3 |  | x | AI | C1 | 9 | 3 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-401 | C1S09,04 | 1756-IF16-4 | X1 | C1S09-X1 | LT-40201_AI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | LT-40201 | Level Transmitter | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Level transmitter in pH Adjustment tank 1 | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | LT-40201_AI_1 | AI | 3 | 1 | C1S09 | C1S09AI04 | C1S09,04 | 1756-IF16-4 |  | x | AI | C1 | 9 | 4 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-401 | C1S09,05 | 1756-IF16-5 | X1 | C1S09-X1 | LT-40202_AI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | LT-40202 | Level Transmitter | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Level transmitter in pH Adjustment tank 2 | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | LT-40202_AI_1 | AI | 3 | 1 | C1S09 | C1S09AI05 | C1S09,05 | 1756-IF16-5 |  | x | AI | C1 | 9 | 5 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-401 | C1S09,06 | 1756-IF16-6 | X1 | C1S09-X1 | pHT-40201_AI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | pHT-40201 | PH Transmitter | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | pH analyzer in pH Adjustment tank 1 | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | pHT-40201_AI_1 | AI | 3 | 1 | C1S09 | C1S09AI06 | C1S09,06 | 1756-IF16-6 |  | x | AI | C1 | 9 | 6 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-401 | C1S09,07 | 1756-IF16-7 | X1 | C1S09-X1 | pHT-40202_AI_1 |  | Infeed 2nd Floor | JB-401 | PH Adjustment | pHT-40202 | PH Transmitter | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | pH analyzer in pH Adjustment tank 2 | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | pHT-40202_AI_1 | AI | 3 | 1 | C1S09 | C1S09AI07 | C1S09,07 | 1756-IF16-7 |  | x | AI | C1 | 9 | 7 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-401 | C1S09,08 | 1756-IF16-8 | X1 | C1S09-X1 | PT-40201_AI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | PT-40201 | Pressure Transmitter | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Pressure Transmitter for Inlet Filter Strainer (FSTR-11) | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-40201_AI_1 | AI | 3 | 1 | C1S09 | C1S09AI08 | C1S09,08 | 1756-IF16-8 |  | x | AI | C1 | 9 | 8 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-401 | C1S09,09 | 1756-IF16-9 | X1 | C1S09-X1 | PT-40202_AI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | PT-40202 | Pressure Transmitter | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Feed Slurry Pressure Transmitter for Pipe (PIPE) | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-40202_AI_1 | AI | 3 | 1 | C1S09 | C1S09AI09 | C1S09,09 | 1756-IF16-9 |  | x | AI | C1 | 9 | 9 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-401 | C1S09,10 | 1756-IF16-10 | X1 | C1S09-X1 | PT-60202_AI_1 |  | Infeed 2nd Floor | JB-401 | Infeed Tank | PT-60202 | Pressure Transmitter | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-60202_AI_1 | AI | 3 | 1 | C1S09 | C1S09AI10 | C1S09,10 | 1756-IF16-10 |  | x | AI | C1 | 9 | 10 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-401 | C1S09,11 | 1756-IF16-11 | X1 | C1S09-X1 | Spare_AI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C1S09 | C1S09AI11 | C1S09,11 | 1756-IF16-11 |  | x | AI | C1 | 9 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S09,12 | 1756-IF16-12 | X1 | C1S09-X1 | Spare_AI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C1S09 | C1S09AI12 | C1S09,12 | 1756-IF16-12 |  | x | AI | C1 | 9 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S09,13 | 1756-IF16-13 | X1 | C1S09-X1 | Spare_AI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C1S09 | C1S09AI13 | C1S09,13 | 1756-IF16-13 |  | x | AI | C1 | 9 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S09,14 | 1756-IF16-14 | X1 | C1S09-X1 | Spare_AI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C1S09 | C1S09AI14 | C1S09,14 | 1756-IF16-14 |  | x | AI | C1 | 9 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 | C1S09,15 | 1756-IF16-15 | X1 | C1S09-X1 | Spare_AI_0 |  | Infeed 2nd Floor | JB-401 |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C1S09 | C1S09AI15 | C1S09,15 | 1756-IF16-15 |  | x | AI | C1 | 9 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S10,00 | 1756-IF16-0 | X1 | C1S10-X1 | DPI-60240_AI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | DPI-60240 | 0 | 1st | 325-01-600-PD-05 | - | Gas Pressure Differntial Pressure (Bag House Air Pulsing) | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | DPI-60240_AI_1 | AI | 3 | 1 | C1S10 | C1S10AI00 | C1S10,00 | 1756-IF16-0 |  | x | AI | C1 | 10 | 0 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-601 | C1S10,01 | 1756-IF16-1 | X1 | C1S10-X1 | DPT-60202_AI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | DPT-60202 | Differential Pressure Transmitte | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 | Gas Pressure Differential Transmitter for Air Filter (FICA-31) | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | DPT-60202_AI_1 | AI | 3 | 1 | C1S10 | C1S10AI01 | C1S10,01 | 1756-IF16-1 |  | x | AI | C1 | 10 | 1 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-601 | C1S10,02 | 1756-IF16-2 | X1 | C1S10-X1 | FT-60201_AI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | FT-60201 | 0 | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 | Gas Flow Transmitter for Cooling Conveying Cold Air Duct (DTCA-32) | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60201_AI_1 | AI | 3 | 1 | C1S10 | C1S10AI02 | C1S10,02 | 1756-IF16-2 |  | x | AI | C1 | 10 | 2 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-601 | C1S10,03 | 1756-IF16-3 | X1 | C1S10-X1 | FT-60204_AI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | FT-60204 | 0 | 1st | 325-01-600-PD-10 | 3-25-01-602-PD-10 | Compressed air Flow | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60204_AI_1 | AI | 3 | 1 | C1S10 | C1S10AI03 | C1S10,03 | 1756-IF16-3 |  | x | AI | C1 | 10 | 3 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-601 | C1S10,04 | 1756-IF16-4 | X1 | C1S10-X1 | FT-61307_AI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | FT-61307 | 0 | 1st | - | 3-25-01-613-PD-04 | Compressed air Flow | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-61307_AI_1 | AI | 3 | 1 | C1S10 | C1S10AI04 | C1S10,04 | 1756-IF16-4 |  | x | AI | C1 | 10 | 4 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-601 | C1S10,05 | 1756-IF16-5 | X1 | C1S10-X1 | PT-60203_AI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | PT-60203 | Pressure Transmitter | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 | Gas Pressure Transmitter for Cool Air Duct (DTCA-32) | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-60203_AI_1 | AI | 3 | 1 | C1S10 | C1S10AI05 | C1S10,05 | 1756-IF16-5 |  | x | AI | C1 | 10 | 5 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-601 | C1S10,06 | 1756-IF16-6 | X1 | C1S10-X1 | PT-60204_AI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | PT-60204 | Pressure Transmitter | 1st | 325-01-600-PD-10 | 3-25-01-602-PD-10 | Pressure transmitter | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-60204_AI_1 | AI | 3 | 1 | C1S10 | C1S10AI06 | C1S10,06 | 1756-IF16-6 |  | x | AI | C1 | 10 | 6 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-601 | C1S10,07 | 1756-IF16-7 | X1 | C1S10-X1 | PT-60205_AI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | PT-60205 | Pressure Transmitter | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | x | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-60205_AI_1 | AI | 3 | 1 | C1S10 | C1S10AI07 | C1S10,07 | 1756-IF16-7 |  | x | AI | C1 | 10 | 7 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M1 | JB-601 | C1S10,08 | 1756-IF16-8 | X1 | C1S10-X1 | Spare_AI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C1S10 | C1S10AI08 | C1S10,08 | 1756-IF16-8 |  | x | AI | C1 | 10 | 8 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S10,09 | 1756-IF16-9 | X1 | C1S10-X1 | Spare_AI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C1S10 | C1S10AI09 | C1S10,09 | 1756-IF16-9 |  | x | AI | C1 | 10 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S10,10 | 1756-IF16-10 | X1 | C1S10-X1 | Spare_AI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C1S10 | C1S10AI10 | C1S10,10 | 1756-IF16-10 |  | x | AI | C1 | 10 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S10,11 | 1756-IF16-11 | X1 | C1S10-X1 | Spare_AI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C1S10 | C1S10AI11 | C1S10,11 | 1756-IF16-11 |  | x | AI | C1 | 10 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S10,12 | 1756-IF16-12 | X1 | C1S10-X1 | Spare_AI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C1S10 | C1S10AI12 | C1S10,12 | 1756-IF16-12 |  | x | AI | C1 | 10 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S10,13 | 1756-IF16-13 | X1 | C1S10-X1 | Spare_AI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C1S10 | C1S10AI13 | C1S10,13 | 1756-IF16-13 |  | x | AI | C1 | 10 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S10,14 | 1756-IF16-14 | X1 | C1S10-X1 | Spare_AI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C1S10 | C1S10AI14 | C1S10,14 | 1756-IF16-14 |  | x | AI | C1 | 10 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 | C1S10,15 | 1756-IF16-15 | X1 | C1S10-X1 | Spare_AI_0 |  | Spray Dryer 1st Floor | JB-601 |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C1S10 | C1S10AI15 | C1S10,15 | 1756-IF16-15 |  | x | AI | C1 | 10 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S01,00 | 1756-IB32-0 | X1 | C2S01-X1 | FS-40204_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | FS-40204 | Flow Switch | 2nd | - | 325-01-402-PD-01 | Jet Cooker |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | FS-40204_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI00 | C2S01,00 | 1756-IB32-0 |  |  | DI | C2 | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-402 | C2S01,01 | 1756-IB32-1 | X1 | C2S01-X1 | FS-40205_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | FS-40205 | Flow Switch | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | FS-40205_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI01 | C2S01,01 | 1756-IB32-1 |  |  | DI | C2 | 1 | 1 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-402 | C2S01,02 | 1756-IB32-2 | X1 | C2S01-X1 | FT-40221_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | FT-40221 | Coriolis Flow Transmitter | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0 | xx | FT-40221_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI02 | C2S01,02 | 1756-IB32-2 |  |  | DI | C2 | 1 | 2 |  | 1 | 0 | 2 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M2 | JB-402 | C2S01,03 | 1756-IB32-3 | X1 | C2S01-X1 | FT-40222_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | FT-40222 | Coriolis Flow Transmitter | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0 | xx | FT-40222_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI03 | C2S01,03 | 1756-IB32-3 |  |  | DI | C2 | 1 | 3 |  | 1 | 0 | 2 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M2 | JB-402 | C2S01,04 | 1756-IB32-4 | X1 | C2S01-X1 | HV-40207_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | HV-40207 | Manual Valve With Position Switch | 2nd | - | 325-01-402-PD-01 | Jet Cooker |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | HV-40207_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI04 | C2S01,04 | 1756-IB32-4 |  |  | DI | C2 | 1 | 4 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-402 | C2S01,05 | 1756-IB32-5 | X1 | C2S01-X1 | HV-40208_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | HV-40208 | Manual Valve With Position Switch | 2nd | - | 325-01-402-PD-01 | Jet Cooker |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | HV-40208_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI05 | C2S01,05 | 1756-IB32-5 |  |  | DI | C2 | 1 | 5 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-402 | C2S01,06 | 1756-IB32-6 | X1 | C2S01-X1 | XV-40203F_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40203F | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203F_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI06 | C2S01,06 | 1756-IB32-6 |  |  | DI | C2 | 1 | 6 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,07 | 1756-IB32-7 | X1 | C2S01-X1 | XV-40203F_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40203F | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203F_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI07 | C2S01,07 | 1756-IB32-7 |  |  | DI | C2 | 1 | 7 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,08 | 1756-IB32-8 | X1 | C2S01-X1 | XV-40204B_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40204B | 0 | 2nd | - | 325-01-402-PD-01 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40204B_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI08 | C2S01,08 | 1756-IB32-8 |  |  | DI | C2 | 1 | 8 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,09 | 1756-IB32-9 | X1 | C2S01-X1 | XV-40204B_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40204B | 0 | 2nd | - | 325-01-402-PD-01 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40204B_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI09 | C2S01,09 | 1756-IB32-9 |  |  | DI | C2 | 1 | 9 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,10 | 1756-IB32-10 | X1 | C2S01-X1 | XV-40204C_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40204C | 0 | 2nd | - | 325-01-402-PD-01 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40204C_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI10 | C2S01,10 | 1756-IB32-10 |  |  | DI | C2 | 1 | 10 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,11 | 1756-IB32-11 | X1 | C2S01-X1 | XV-40204C_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40204C | 0 | 2nd | - | 325-01-402-PD-01 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40204C_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI11 | C2S01,11 | 1756-IB32-11 |  |  | DI | C2 | 1 | 11 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,12 | 1756-IB32-12 | X1 | C2S01-X1 | XV-40205A_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205A | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205A_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI12 | C2S01,12 | 1756-IB32-12 |  |  | DI | C2 | 1 | 12 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,13 | 1756-IB32-13 | X1 | C2S01-X1 | XV-40205A_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205A | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205A_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI13 | C2S01,13 | 1756-IB32-13 |  |  | DI | C2 | 1 | 13 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,14 | 1756-IB32-14 | X1 | C2S01-X1 | XV-40205B_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205B | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205B_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI14 | C2S01,14 | 1756-IB32-14 |  |  | DI | C2 | 1 | 14 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,15 | 1756-IB32-15 | X1 | C2S01-X1 | XV-40205B_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205B | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205B_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI15 | C2S01,15 | 1756-IB32-15 |  |  | DI | C2 | 1 | 15 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,16 | 1756-IB32-16 | X2 | C2S01-X2 | XV-40205C_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205C | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205C_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI16 | C2S01,16 | 1756-IB32-16 |  |  | DI | C2 | 1 | 16 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,17 | 1756-IB32-17 | X2 | C2S01-X2 | XV-40205C_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205C | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205C_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI17 | C2S01,17 | 1756-IB32-17 |  |  | DI | C2 | 1 | 17 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,18 | 1756-IB32-18 | X2 | C2S01-X2 | XV-40205D_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205D | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205D_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI18 | C2S01,18 | 1756-IB32-18 |  |  | DI | C2 | 1 | 18 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,19 | 1756-IB32-19 | X2 | C2S01-X2 | XV-40205D_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205D | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205D_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI19 | C2S01,19 | 1756-IB32-19 |  |  | DI | C2 | 1 | 19 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,20 | 1756-IB32-20 | X2 | C2S01-X2 | XV-40205F_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205F | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205F_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI20 | C2S01,20 | 1756-IB32-20 |  |  | DI | C2 | 1 | 20 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,21 | 1756-IB32-21 | X2 | C2S01-X2 | XV-40205F_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205F | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205F_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI21 | C2S01,21 | 1756-IB32-21 |  |  | DI | C2 | 1 | 21 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,22 | 1756-IB32-22 | X2 | C2S01-X2 | XV-40222_DI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40222 | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40222_DI_1 | DI | 1 | 1 | C2S01 | C2S01DI22 | C2S01,22 | 1756-IB32-22 |  |  | DI | C2 | 1 | 22 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,23 | 1756-IB32-23 | X2 | C2S01-X2 | XV-40222_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40222 | 0 | 2nd | - | - | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40222_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI23 | C2S01,23 | 1756-IB32-23 |  |  | DI | C2 | 1 | 23 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S01,24 | 1756-IB32-24 | X2 | C2S01-X2 | Spare_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | Spare |  | 2nd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI24 | C2S01,24 | 1756-IB32-24 |  |  | DI | C2 | 1 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S01,25 | 1756-IB32-25 | X2 | C2S01-X2 | Spare_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | Spare |  | 2nd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI25 | C2S01,25 | 1756-IB32-25 |  |  | DI | C2 | 1 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S01,26 | 1756-IB32-26 | X2 | C2S01-X2 | Spare_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | Spare |  | 2nd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI26 | C2S01,26 | 1756-IB32-26 |  |  | DI | C2 | 1 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S01,27 | 1756-IB32-27 | X2 | C2S01-X2 | Spare_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | Spare |  | 2nd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI27 | C2S01,27 | 1756-IB32-27 |  |  | DI | C2 | 1 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S01,28 | 1756-IB32-28 | X2 | C2S01-X2 | Spare_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | Spare |  | 2nd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI28 | C2S01,28 | 1756-IB32-28 |  |  | DI | C2 | 1 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S01,29 | 1756-IB32-29 | X2 | C2S01-X2 | Spare_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | Spare |  | 2nd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI29 | C2S01,29 | 1756-IB32-29 |  |  | DI | C2 | 1 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S01,30 | 1756-IB32-30 | X2 | C2S01-X2 | Spare_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | Spare |  | 2nd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI30 | C2S01,30 | 1756-IB32-30 |  |  | DI | C2 | 1 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S01,31 | 1756-IB32-31 | X2 | C2S01-X2 | Spare_DI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | Spare |  | 2nd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_2 | DI | 1 | 2 | C2S01 | C2S01DI31 | C2S01,31 | 1756-IB32-31 |  |  | DI | C2 | 1 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S02,00 | 1756-IB32-0 | X1 | C2S02-X1 | FT-60202_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | FT-60202 | 0 | 5th | 325-01-600-PD-09 | 3-25-01-602-PD-09 | Steam feed to Spray dryer |  | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60202_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI00 | C2S02,00 | 1756-IB32-0 |  |  | DI | C2 | 2 | 0 |  | 1 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S02,01 | 1756-IB32-1 | X1 | C2S02-X1 | LSH-60251_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | LSH-60251 | 0 | 4th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Water Level Switch High for Fire Deluge Pipe (FWDP-22) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | LSH-60251_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI01 | C2S02,01 | 1756-IB32-1 |  |  | DI | C2 | 2 | 1 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,02 | 1756-IB32-2 | X1 | C2S02-X1 | PSL-60220_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | PSL-60220 | 0 | 5th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas Pressure Switch Low for Spray Chamber (CHAM-21) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | PSL-60220_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI02 | C2S02,02 | 1756-IB32-2 |  |  | DI | C2 | 2 | 2 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,03 | 1756-IB32-3 | X1 | C2S02-X1 | TSH-60230_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TSH-60230 | 0 | 3rd | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | TSH-60230_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI03 | C2S02,03 | 1756-IB32-3 |  |  | DI | C2 | 2 | 3 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,04 | 1756-IB32-4 | X1 | C2S02-X1 | TSH-60240_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TSH-60240 | 0 | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | TSH-60240_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI04 | C2S02,04 | 1756-IB32-4 |  |  | DI | C2 | 2 | 4 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,05 | 1756-IB32-5 | X1 | C2S02-X1 | TSH-60241A_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TSH-60241A | 0 | 4th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | TSH-60241A_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI05 | C2S02,05 | 1756-IB32-5 |  |  | DI | C2 | 2 | 5 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,06 | 1756-IB32-6 | X1 | C2S02-X1 | TSH-60242A_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TSH-60242A | 0 | 3rd | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | TSH-60242A_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI06 | C2S02,06 | 1756-IB32-6 |  |  | DI | C2 | 2 | 6 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,07 | 1756-IB32-7 | X1 | C2S02-X1 | TSH-60243A_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TSH-60243A | 0 | 4th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | TSH-60243A_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI07 | C2S02,07 | 1756-IB32-7 |  |  | DI | C2 | 2 | 7 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,08 | 1756-IB32-8 | X1 | C2S02-X1 | TSL-60241B_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TSL-60241B | 0 | 4th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | TSL-60241B_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI08 | C2S02,08 | 1756-IB32-8 |  |  | DI | C2 | 2 | 8 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,09 | 1756-IB32-9 | X1 | C2S02-X1 | TSL-60242B_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TSL-60242B | 0 | 3rd | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | TSL-60242B_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI09 | C2S02,09 | 1756-IB32-9 |  |  | DI | C2 | 2 | 9 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,10 | 1756-IB32-10 | X1 | C2S02-X1 | TSL-60243B_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TSL-60243B | 0 | 4th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | TSL-60243B_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI10 | C2S02,10 | 1756-IB32-10 |  |  | DI | C2 | 2 | 10 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,11 | 1756-IB32-11 | X1 | C2S02-X1 | XA-60240A_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XA-60240A | 0 | 4th | 325-01-600-PD-05 | - | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60240A_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI11 | C2S02,11 | 1756-IB32-11 |  |  | DI | C2 | 2 | 11 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,12 | 1756-IB32-12 | X1 | C2S02-X1 | XA-60240B_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XA-60240B | 0 | 4th | 325-01-600-PD-05 | - | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60240B_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI12 | C2S02,12 | 1756-IB32-12 |  |  | DI | C2 | 2 | 12 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,13 | 1756-IB32-13 | X1 | C2S02-X1 | XA-60241A_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XA-60241A | 0 | 4th | 325-01-600-PD-05 | - | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60241A_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI13 | C2S02,13 | 1756-IB32-13 |  |  | DI | C2 | 2 | 13 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,14 | 1756-IB32-14 | X1 | C2S02-X1 | XA-60241B_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XA-60241B | 0 | 4th | 325-01-600-PD-05 | - | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60241B_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI14 | C2S02,14 | 1756-IB32-14 |  |  | DI | C2 | 2 | 14 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,15 | 1756-IB32-15 | X1 | C2S02-X1 | XA-60242A_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XA-60242A | 0 | 3rd | 325-01-600-PD-05 | - | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60242A_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI15 | C2S02,15 | 1756-IB32-15 |  |  | DI | C2 | 2 | 15 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,16 | 1756-IB32-16 | X2 | C2S02-X2 | XA-60242B_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XA-60242B | 0 | 3rd | 325-01-600-PD-05 | - | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60242B_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI16 | C2S02,16 | 1756-IB32-16 |  |  | DI | C2 | 2 | 16 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,17 | 1756-IB32-17 | X2 | C2S02-X2 | XA-60243A_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XA-60243A | 0 | 4th | 325-01-600-PD-05 | - | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60243A_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI17 | C2S02,17 | 1756-IB32-17 |  |  | DI | C2 | 2 | 17 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,18 | 1756-IB32-18 | X2 | C2S02-X2 | XA-60243B_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XA-60243B | 0 | 4th | 325-01-600-PD-05 | - | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-60243B_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI18 | C2S02,18 | 1756-IB32-18 |  |  | DI | C2 | 2 | 18 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,19 | 1756-IB32-19 | X2 | C2S02-X2 | XV-60214_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XV-60214 | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Steam feed to Spray dryer |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60214_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI19 | C2S02,19 | 1756-IB32-19 |  |  | DI | C2 | 2 | 19 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-602 | C2S02,20 | 1756-IB32-20 | X2 | C2S02-X2 | XV-60214_DI_2 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XV-60214 | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Steam feed to Spray dryer |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60214_DI_2 | DI | 1 | 2 | C2S02 | C2S02DI20 | C2S02,20 | 1756-IB32-20 |  |  | DI | C2 | 2 | 20 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-602 | C2S02,21 | 1756-IB32-21 | X2 | C2S02-X2 | XV-60241_DI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XV-60241 | 0 | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60241_DI_1 | DI | 1 | 1 | C2S02 | C2S02DI21 | C2S02,21 | 1756-IB32-21 |  |  | DI | C2 | 2 | 21 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,22 | 1756-IB32-22 | X2 | C2S02-X2 | XV-60241_DI_2 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XV-60241 | 0 | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60241_DI_2 | DI | 1 | 2 | C2S02 | C2S02DI22 | C2S02,22 | 1756-IB32-22 |  |  | DI | C2 | 2 | 22 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-602 | C2S02,23 | 1756-IB32-23 | X2 | C2S02-X2 | Spare_DI_0 |  | Spray Dryer 3rd Floor | JB-602 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C2S02 | C2S02DI23 | C2S02,23 | 1756-IB32-23 |  |  | DI | C2 | 2 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S02,24 | 1756-IB32-24 | X2 | C2S02-X2 | Spare_DI_0 |  | Spray Dryer 3rd Floor | JB-602 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C2S02 | C2S02DI24 | C2S02,24 | 1756-IB32-24 |  |  | DI | C2 | 2 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S02,25 | 1756-IB32-25 | X2 | C2S02-X2 | Spare_DI_0 |  | Spray Dryer 3rd Floor | JB-602 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C2S02 | C2S02DI25 | C2S02,25 | 1756-IB32-25 |  |  | DI | C2 | 2 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S02,26 | 1756-IB32-26 | X2 | C2S02-X2 | Spare_DI_0 |  | Spray Dryer 3rd Floor | JB-602 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C2S02 | C2S02DI26 | C2S02,26 | 1756-IB32-26 |  |  | DI | C2 | 2 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S02,27 | 1756-IB32-27 | X2 | C2S02-X2 | Spare_DI_0 |  | Spray Dryer 3rd Floor | JB-602 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C2S02 | C2S02DI27 | C2S02,27 | 1756-IB32-27 |  |  | DI | C2 | 2 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S02,28 | 1756-IB32-28 | X2 | C2S02-X2 | Spare_DI_0 |  | Spray Dryer 3rd Floor | JB-602 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C2S02 | C2S02DI28 | C2S02,28 | 1756-IB32-28 |  |  | DI | C2 | 2 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S02,29 | 1756-IB32-29 | X2 | C2S02-X2 | Spare_DI_0 |  | Spray Dryer 3rd Floor | JB-602 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C2S02 | C2S02DI29 | C2S02,29 | 1756-IB32-29 |  |  | DI | C2 | 2 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S02,30 | 1756-IB32-30 | X2 | C2S02-X2 | Spare_DI_0 |  | Spray Dryer 3rd Floor | JB-602 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C2S02 | C2S02DI30 | C2S02,30 | 1756-IB32-30 |  |  | DI | C2 | 2 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S02,31 | 1756-IB32-31 | X2 | C2S02-X2 | Spare_DI_0 |  | Spray Dryer 3rd Floor | JB-602 |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | Spare_DI_0 | DI | 1 | 0 | C2S02 | C2S02DI31 | C2S02,31 | 1756-IB32-31 |  |  | DI | C2 | 2 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S03,00 | 1756-IB32-0 | X1 | C2S03-X1 | XA-FH-60210A_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XA-FH-60210A | 0 | 7th | 325-01-600-PD-06 | - | BMS PANEL POWER ON for AHTR-21 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-FH-60210A_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI00 | C2S03,00 | 1756-IB32-0 |  |  | DI | C2 | 3 | 0 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,01 | 1756-IB32-1 | X1 | C2S03-X1 | XA-FH-60210B_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XA-FH-60210B | 0 | 7th | 325-01-600-PD-06 | - | BMS Burner High Fire Purge for AHTR-21 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-FH-60210B_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI01 | C2S03,01 | 1756-IB32-1 |  |  | DI | C2 | 3 | 1 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,02 | 1756-IB32-2 | X1 | C2S03-X1 | XA-FH-60210C_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XA-FH-60210C | 0 | 7th | 325-01-600-PD-06 | - | BMS Burner On for AHTR-21 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-FH-60210C_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI02 | C2S03,02 | 1756-IB32-2 |  |  | DI | C2 | 3 | 2 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,03 | 1756-IB32-3 | X1 | C2S03-X1 | XA-FH-60210D_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XA-FH-60210D | 0 | 7th | 325-01-600-PD-06 | - | BMS BMS Lockout for AHTR-21 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-FH-60210D_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI03 | C2S03,03 | 1756-IB32-3 |  |  | DI | C2 | 3 | 3 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,04 | 1756-IB32-4 | X1 | C2S03-X1 | XA-FH-60210E_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XA-FH-60210E | 0 | 7th | 325-01-600-PD-06 | - | BMS Remote Modet for AHTR-21 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 | xx | XA-FH-60210E_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI04 | C2S03,04 | 1756-IB32-4 |  |  | DI | C2 | 3 | 4 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,08 | 1756-IB32-8 | X1 | C2S03-X1 | SV-60207_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | SV-60207 | 0 | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60207_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI08 | C2S03,08 | 1756-IB32-8 |  |  | DI | C2 | 3 | 8 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-607 | C2S03,09 | 1756-IB32-9 | X1 | C2S03-X1 | SV-60207_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | SV-60207 | 0 | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60207_DI_2 | DI | 1 | 2 | C2S03 | C2S03DI09 | C2S03,09 | 1756-IB32-9 |  |  | DI | C2 | 3 | 9 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-607 | C2S03,10 | 1756-IB32-10 | X1 | C2S03-X1 | XV-60264_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264 |  | 7th | 325-01-600-PD-02 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI10 | C2S03,10 | 1756-IB32-10 |  |  | DI | C2 | 3 | 10 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S03,11 | 1756-IB32-11 | X1 | C2S03-X1 | XV-60264_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264 |  | 7th | 325-01-600-PD-02 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264_DI_2 | DI | 1 | 2 | C2S03 | C2S03DI11 | C2S03,11 | 1756-IB32-11 |  |  | DI | C2 | 3 | 11 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S03,12 | 1756-IB32-12 | X1 | C2S03-X1 | XV-60264FN_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264FN | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264FN_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI12 | C2S03,12 | 1756-IB32-12 |  |  | DI | C2 | 3 | 12 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,13 | 1756-IB32-13 | X1 | C2S03-X1 | XV-60264FN_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264FN | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264FN_DI_2 | DI | 1 | 2 | C2S03 | C2S03DI13 | C2S03,13 | 1756-IB32-13 |  |  | DI | C2 | 3 | 13 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,14 | 1756-IB32-14 | X1 | C2S03-X1 | XV-60264FP_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264FP | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264FP_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI14 | C2S03,14 | 1756-IB32-14 |  |  | DI | C2 | 3 | 14 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,15 | 1756-IB32-15 | X1 | C2S03-X1 | XV-60264FP_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264FP | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264FP_DI_2 | DI | 1 | 2 | C2S03 | C2S03DI15 | C2S03,15 | 1756-IB32-15 |  |  | DI | C2 | 3 | 15 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,16 | 1756-IB32-16 | X2 | C2S03-X2 | XV-60201_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60201 | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam feed to Spray dryer |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60201_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI16 | C2S03,16 | 1756-IB32-16 |  |  | DI | C2 | 3 | 16 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-607 | C2S03,17 | 1756-IB32-17 | X2 | C2S03-X2 | XV-60201_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60201 | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam feed to Spray dryer |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60201_DI_2 | DI | 1 | 2 | C2S03 | C2S03DI17 | C2S03,17 | 1756-IB32-17 |  |  | DI | C2 | 3 | 17 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-607 | C2S03,18 | 1756-IB32-18 | X2 | C2S03-X2 | XV-60264FQ_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264FQ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264FQ_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI18 | C2S03,18 | 1756-IB32-18 |  |  | DI | C2 | 3 | 18 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,19 | 1756-IB32-19 | X2 | C2S03-X2 | XV-60264FQ_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264FQ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264FQ_DI_2 | DI | 1 | 2 | C2S03 | C2S03DI19 | C2S03,19 | 1756-IB32-19 |  |  | DI | C2 | 3 | 19 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,20 | 1756-IB32-20 | X2 | C2S03-X2 | XV-60261_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261 |  | 7th | 325-01-600-PD-02 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI20 | C2S03,20 | 1756-IB32-20 |  |  | DI | C2 | 3 | 20 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S03,21 | 1756-IB32-21 | X2 | C2S03-X2 | XV-60261_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261 |  | 7th | 325-01-600-PD-02 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261_DI_2 | DI | 1 | 2 | C2S03 | C2S03DI21 | C2S03,21 | 1756-IB32-21 |  |  | DI | C2 | 3 | 21 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S03,22 | 1756-IB32-22 | X2 | C2S03-X2 | XV-60264FR_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264FR | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264FR_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI22 | C2S03,22 | 1756-IB32-22 |  |  | DI | C2 | 3 | 22 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,23 | 1756-IB32-23 | X2 | C2S03-X2 | XV-60264FR_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264FR | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264FR_DI_2 | DI | 1 | 2 | C2S03 | C2S03DI23 | C2S03,23 | 1756-IB32-23 |  |  | DI | C2 | 3 | 23 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,24 | 1756-IB32-24 | X2 | C2S03-X2 | XV-60261FA_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261FA | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261FA_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI24 | C2S03,24 | 1756-IB32-24 |  |  | DI | C2 | 3 | 24 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,25 | 1756-IB32-25 | X2 | C2S03-X2 | XV-60261FA_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261FA | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261FA_DI_2 | DI | 1 | 2 | C2S03 | C2S03DI25 | C2S03,25 | 1756-IB32-25 |  |  | DI | C2 | 3 | 25 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,26 | 1756-IB32-26 | X2 | C2S03-X2 | XV-60264SN_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264SN | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #13 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264SN_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI26 | C2S03,26 | 1756-IB32-26 |  |  | DI | C2 | 3 | 26 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,27 | 1756-IB32-27 | X2 | C2S03-X2 | XV-60264SN_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264SN | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #13 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264SN_DI_2 | DI | 1 | 2 | C2S03 | C2S03DI27 | C2S03,27 | 1756-IB32-27 |  |  | DI | C2 | 3 | 27 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,28 | 1756-IB32-28 | X2 | C2S03-X2 | XV-60261FB_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261FB | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261FB_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI28 | C2S03,28 | 1756-IB32-28 |  |  | DI | C2 | 3 | 28 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,29 | 1756-IB32-29 | X2 | C2S03-X2 | XV-60261FB_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261FB | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261FB_DI_2 | DI | 1 | 2 | C2S03 | C2S03DI29 | C2S03,29 | 1756-IB32-29 |  |  | DI | C2 | 3 | 29 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,30 | 1756-IB32-30 | X2 | C2S03-X2 | XV-60264SP_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264SP | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #14 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264SP_DI_1 | DI | 1 | 1 | C2S03 | C2S03DI30 | C2S03,30 | 1756-IB32-30 |  |  | DI | C2 | 3 | 30 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S03,31 | 1756-IB32-31 | X2 | C2S03-X2 | XV-60264SP_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264SP | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #14 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264SP_DI_2 | DI | 1 | 2 | C2S03 | C2S03DI31 | C2S03,31 | 1756-IB32-31 |  |  | DI | C2 | 3 | 31 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,00 | 1756-IB32-0 | X1 | C2S04-X1 | XV-60261FC_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261FC | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261FC_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI00 | C2S04,00 | 1756-IB32-0 |  |  | DI | C2 | 4 | 0 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,01 | 1756-IB32-1 | X1 | C2S04-X1 | XV-60261FC_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261FC | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261FC_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI01 | C2S04,01 | 1756-IB32-1 |  |  | DI | C2 | 4 | 1 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,02 | 1756-IB32-2 | X1 | C2S04-X1 | XV-60264SQ_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264SQ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #15 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264SQ_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI02 | C2S04,02 | 1756-IB32-2 |  |  | DI | C2 | 4 | 2 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,03 | 1756-IB32-3 | X1 | C2S04-X1 | XV-60264SQ_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264SQ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #15 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264SQ_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI03 | C2S04,03 | 1756-IB32-3 |  |  | DI | C2 | 4 | 3 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,04 | 1756-IB32-4 | X1 | C2S04-X1 | XV-60261FD_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261FD | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261FD_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI04 | C2S04,04 | 1756-IB32-4 |  |  | DI | C2 | 4 | 4 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,05 | 1756-IB32-5 | X1 | C2S04-X1 | XV-60261FD_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261FD | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261FD_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI05 | C2S04,05 | 1756-IB32-5 |  |  | DI | C2 | 4 | 5 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,06 | 1756-IB32-6 | X1 | C2S04-X1 | XV-60264SR_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264SR | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #16 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264SR_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI06 | C2S04,06 | 1756-IB32-6 |  |  | DI | C2 | 4 | 6 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,07 | 1756-IB32-7 | X1 | C2S04-X1 | XV-60264SR_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264SR | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #16 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264SR_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI07 | C2S04,07 | 1756-IB32-7 |  |  | DI | C2 | 4 | 7 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,08 | 1756-IB32-8 | X1 | C2S04-X1 | XV-60261SA_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261SA | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #1 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261SA_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI08 | C2S04,08 | 1756-IB32-8 |  |  | DI | C2 | 4 | 8 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,09 | 1756-IB32-9 | X1 | C2S04-X1 | XV-60261SA_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261SA | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #1 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261SA_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI09 | C2S04,09 | 1756-IB32-9 |  |  | DI | C2 | 4 | 9 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,10 | 1756-IB32-10 | X1 | C2S04-X1 | XV-60261SB_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261SB | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #2 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261SB_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI10 | C2S04,10 | 1756-IB32-10 |  |  | DI | C2 | 4 | 10 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,11 | 1756-IB32-11 | X1 | C2S04-X1 | XV-60261SB_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261SB | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #2 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261SB_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI11 | C2S04,11 | 1756-IB32-11 |  |  | DI | C2 | 4 | 11 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,12 | 1756-IB32-12 | X1 | C2S04-X1 | XV-60261SC_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261SC | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #3 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261SC_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI12 | C2S04,12 | 1756-IB32-12 |  |  | DI | C2 | 4 | 12 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,13 | 1756-IB32-13 | X1 | C2S04-X1 | XV-60261SC_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261SC | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #3 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261SC_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI13 | C2S04,13 | 1756-IB32-13 |  |  | DI | C2 | 4 | 13 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,14 | 1756-IB32-14 | X1 | C2S04-X1 | XV-60261SD_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261SD | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #4 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261SD_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI14 | C2S04,14 | 1756-IB32-14 |  |  | DI | C2 | 4 | 14 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,15 | 1756-IB32-15 | X1 | C2S04-X1 | XV-60261SD_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261SD | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #4 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261SD_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI15 | C2S04,15 | 1756-IB32-15 |  |  | DI | C2 | 4 | 15 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,16 | 1756-IB32-16 | X2 | C2S04-X2 | XV-60262_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262 |  | 7th | 325-01-600-PD-02 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI16 | C2S04,16 | 1756-IB32-16 |  |  | DI | C2 | 4 | 16 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S04,17 | 1756-IB32-17 | X2 | C2S04-X2 | XV-60262_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262 |  | 7th | 325-01-600-PD-02 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI17 | C2S04,17 | 1756-IB32-17 |  |  | DI | C2 | 4 | 17 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S04,18 | 1756-IB32-18 | X2 | C2S04-X2 | XV-60262FE_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262FE | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262FE_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI18 | C2S04,18 | 1756-IB32-18 |  |  | DI | C2 | 4 | 18 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,19 | 1756-IB32-19 | X2 | C2S04-X2 | XV-60262FE_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262FE | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262FE_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI19 | C2S04,19 | 1756-IB32-19 |  |  | DI | C2 | 4 | 19 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,20 | 1756-IB32-20 | X2 | C2S04-X2 | XV-60262FF_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262FF | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262FF_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI20 | C2S04,20 | 1756-IB32-20 |  |  | DI | C2 | 4 | 20 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,21 | 1756-IB32-21 | X2 | C2S04-X2 | XV-60262FF_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262FF | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262FF_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI21 | C2S04,21 | 1756-IB32-21 |  |  | DI | C2 | 4 | 21 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,22 | 1756-IB32-22 | X2 | C2S04-X2 | XV-60262FG_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262FG | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262FG_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI22 | C2S04,22 | 1756-IB32-22 |  |  | DI | C2 | 4 | 22 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,23 | 1756-IB32-23 | X2 | C2S04-X2 | XV-60262FG_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262FG | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262FG_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI23 | C2S04,23 | 1756-IB32-23 |  |  | DI | C2 | 4 | 23 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,24 | 1756-IB32-24 | X2 | C2S04-X2 | XV-60262FH_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262FH | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262FH_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI24 | C2S04,24 | 1756-IB32-24 |  |  | DI | C2 | 4 | 24 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,25 | 1756-IB32-25 | X2 | C2S04-X2 | XV-60262FH_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262FH | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262FH_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI25 | C2S04,25 | 1756-IB32-25 |  |  | DI | C2 | 4 | 25 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,26 | 1756-IB32-26 | X2 | C2S04-X2 | XV-60262SE_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262SE | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #5 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262SE_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI26 | C2S04,26 | 1756-IB32-26 |  |  | DI | C2 | 4 | 26 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,27 | 1756-IB32-27 | X2 | C2S04-X2 | XV-60262SE_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262SE | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #5 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262SE_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI27 | C2S04,27 | 1756-IB32-27 |  |  | DI | C2 | 4 | 27 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,28 | 1756-IB32-28 | X2 | C2S04-X2 | XV-60262SF_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262SF | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #6 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262SF_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI28 | C2S04,28 | 1756-IB32-28 |  |  | DI | C2 | 4 | 28 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,29 | 1756-IB32-29 | X2 | C2S04-X2 | XV-60262SF_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262SF | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #6 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262SF_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI29 | C2S04,29 | 1756-IB32-29 |  |  | DI | C2 | 4 | 29 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,30 | 1756-IB32-30 | X2 | C2S04-X2 | XV-60262SG_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262SG | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #7 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262SG_DI_1 | DI | 1 | 1 | C2S04 | C2S04DI30 | C2S04,30 | 1756-IB32-30 |  |  | DI | C2 | 4 | 30 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S04,31 | 1756-IB32-31 | X2 | C2S04-X2 | XV-60262SG_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262SG | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #7 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262SG_DI_2 | DI | 1 | 2 | C2S04 | C2S04DI31 | C2S04,31 | 1756-IB32-31 |  |  | DI | C2 | 4 | 31 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,00 | 1756-IB32-0 | X1 | C2S05-X1 | XV-60262SH_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262SH | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #8 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262SH_DI_1 | DI | 1 | 1 | C2S05 | C2S05DI00 | C2S05,00 | 1756-IB32-0 |  |  | DI | C2 | 5 | 0 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,01 | 1756-IB32-1 | X1 | C2S05-X1 | XV-60262SH_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262SH | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #8 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262SH_DI_2 | DI | 1 | 2 | C2S05 | C2S05DI01 | C2S05,01 | 1756-IB32-1 |  |  | DI | C2 | 5 | 1 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,02 | 1756-IB32-2 | X1 | C2S05-X1 | XV-60263_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263 |  | 7th | 325-01-600-PD-02 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263_DI_1 | DI | 1 | 1 | C2S05 | C2S05DI02 | C2S05,02 | 1756-IB32-2 |  |  | DI | C2 | 5 | 2 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S05,03 | 1756-IB32-3 | X1 | C2S05-X1 | XV-60263_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263 |  | 7th | 325-01-600-PD-02 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263_DI_2 | DI | 1 | 2 | C2S05 | C2S05DI03 | C2S05,03 | 1756-IB32-3 |  |  | DI | C2 | 5 | 3 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S05,04 | 1756-IB32-4 | X1 | C2S05-X1 | XV-60263FJ_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263FJ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263FJ_DI_1 | DI | 1 | 1 | C2S05 | C2S05DI04 | C2S05,04 | 1756-IB32-4 |  |  | DI | C2 | 5 | 4 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,05 | 1756-IB32-5 | X1 | C2S05-X1 | XV-60263FJ_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263FJ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263FJ_DI_2 | DI | 1 | 2 | C2S05 | C2S05DI05 | C2S05,05 | 1756-IB32-5 |  |  | DI | C2 | 5 | 5 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,06 | 1756-IB32-6 | X1 | C2S05-X1 | XV-60263FK_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263FK | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263FK_DI_1 | DI | 1 | 1 | C2S05 | C2S05DI06 | C2S05,06 | 1756-IB32-6 |  |  | DI | C2 | 5 | 6 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,07 | 1756-IB32-7 | X1 | C2S05-X1 | XV-60263FK_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263FK | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263FK_DI_2 | DI | 1 | 2 | C2S05 | C2S05DI07 | C2S05,07 | 1756-IB32-7 |  |  | DI | C2 | 5 | 7 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,08 | 1756-IB32-8 | X1 | C2S05-X1 | XV-60263FL_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263FL | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263FL_DI_1 | DI | 1 | 1 | C2S05 | C2S05DI08 | C2S05,08 | 1756-IB32-8 |  |  | DI | C2 | 5 | 8 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,09 | 1756-IB32-9 | X1 | C2S05-X1 | XV-60263FL_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263FL | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263FL_DI_2 | DI | 1 | 2 | C2S05 | C2S05DI09 | C2S05,09 | 1756-IB32-9 |  |  | DI | C2 | 5 | 9 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,10 | 1756-IB32-10 | X1 | C2S05-X1 | XV-60263FM_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263FM | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263FM_DI_1 | DI | 1 | 1 | C2S05 | C2S05DI10 | C2S05,10 | 1756-IB32-10 |  |  | DI | C2 | 5 | 10 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,11 | 1756-IB32-11 | X1 | C2S05-X1 | XV-60263FM_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263FM | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263FM_DI_2 | DI | 1 | 2 | C2S05 | C2S05DI11 | C2S05,11 | 1756-IB32-11 |  |  | DI | C2 | 5 | 11 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,12 | 1756-IB32-12 | X1 | C2S05-X1 | XV-60263SJ_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263SJ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #9 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263SJ_DI_1 | DI | 1 | 1 | C2S05 | C2S05DI12 | C2S05,12 | 1756-IB32-12 |  |  | DI | C2 | 5 | 12 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,13 | 1756-IB32-13 | X1 | C2S05-X1 | XV-60263SJ_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263SJ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #9 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263SJ_DI_2 | DI | 1 | 2 | C2S05 | C2S05DI13 | C2S05,13 | 1756-IB32-13 |  |  | DI | C2 | 5 | 13 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,14 | 1756-IB32-14 | X1 | C2S05-X1 | XV-60263SK_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263SK | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #10 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263SK_DI_1 | DI | 1 | 1 | C2S05 | C2S05DI14 | C2S05,14 | 1756-IB32-14 |  |  | DI | C2 | 5 | 14 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,15 | 1756-IB32-15 | X1 | C2S05-X1 | XV-60263SK_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263SK | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #10 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263SK_DI_2 | DI | 1 | 2 | C2S05 | C2S05DI15 | C2S05,15 | 1756-IB32-15 |  |  | DI | C2 | 5 | 15 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,16 | 1756-IB32-16 | X2 | C2S05-X2 | XV-60263SL_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263SL | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #11 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263SL_DI_1 | DI | 1 | 1 | C2S05 | C2S05DI16 | C2S05,16 | 1756-IB32-16 |  |  | DI | C2 | 5 | 16 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,17 | 1756-IB32-17 | X2 | C2S05-X2 | XV-60263SL_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263SL | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #11 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263SL_DI_2 | DI | 1 | 2 | C2S05 | C2S05DI17 | C2S05,17 | 1756-IB32-17 |  |  | DI | C2 | 5 | 17 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,18 | 1756-IB32-18 | X2 | C2S05-X2 | XV-60263SM_DI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263SM | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #12 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263SM_DI_1 | DI | 1 | 1 | C2S05 | C2S05DI18 | C2S05,18 | 1756-IB32-18 |  |  | DI | C2 | 5 | 18 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,19 | 1756-IB32-19 | X2 | C2S05-X2 | XV-60263SM_DI_2 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263SM | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #12 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263SM_DI_2 | DI | 1 | 2 | C2S05 | C2S05DI19 | C2S05,19 | 1756-IB32-19 |  |  | DI | C2 | 5 | 19 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S05,20 | 1756-IB32-20 | X2 | C2S05-X2 | Spare_DI_0 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | Spare |  | - | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C2S05 | C2S05DI20 | C2S05,20 | 1756-IB32-20 |  |  | DI | C2 | 5 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S05,21 | 1756-IB32-21 | X2 | C2S05-X2 | Spare_DI_0 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | Spare |  | - | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C2S05 | C2S05DI21 | C2S05,21 | 1756-IB32-21 |  |  | DI | C2 | 5 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S05,22 | 1756-IB32-22 | X2 | C2S05-X2 | Spare_DI_0 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | Spare |  | - | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C2S05 | C2S05DI22 | C2S05,22 | 1756-IB32-22 |  |  | DI | C2 | 5 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S05,23 | 1756-IB32-23 | X2 | C2S05-X2 | Spare_DI_0 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | Spare |  | - | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C2S05 | C2S05DI23 | C2S05,23 | 1756-IB32-23 |  |  | DI | C2 | 5 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S05,24 | 1756-IB32-24 | X2 | C2S05-X2 | Spare_DI_0 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | Spare |  | - | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C2S05 | C2S05DI24 | C2S05,24 | 1756-IB32-24 |  |  | DI | C2 | 5 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S05,25 | 1756-IB32-25 | X2 | C2S05-X2 | Spare_DI_0 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | Spare |  | - | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C2S05 | C2S05DI25 | C2S05,25 | 1756-IB32-25 |  |  | DI | C2 | 5 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S05,26 | 1756-IB32-26 | X2 | C2S05-X2 | Spare_DI_0 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | Spare |  | - | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C2S05 | C2S05DI26 | C2S05,26 | 1756-IB32-26 |  |  | DI | C2 | 5 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S05,27 | 1756-IB32-27 | X2 | C2S05-X2 | Spare_DI_0 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | Spare |  | - | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C2S05 | C2S05DI27 | C2S05,27 | 1756-IB32-27 |  |  | DI | C2 | 5 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S05,28 | 1756-IB32-28 | X2 | C2S05-X2 | Spare_DI_0 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | Spare |  | - | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C2S05 | C2S05DI28 | C2S05,28 | 1756-IB32-28 |  |  | DI | C2 | 5 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S05,29 | 1756-IB32-29 | X2 | C2S05-X2 | Spare_DI_0 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | Spare |  | - | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C2S05 | C2S05DI29 | C2S05,29 | 1756-IB32-29 |  |  | DI | C2 | 5 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S05,30 | 1756-IB32-30 | X2 | C2S05-X2 | Spare_DI_0 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | Spare |  | - | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C2S05 | C2S05DI30 | C2S05,30 | 1756-IB32-30 |  |  | DI | C2 | 5 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S05,31 | 1756-IB32-31 | X2 | C2S05-X2 | Spare_DI_0 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | Spare |  | - | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C2S05 | C2S05DI31 | C2S05,31 | 1756-IB32-31 |  |  | DI | C2 | 5 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S06,00 | 1756-OB32-0 | X1 | C2S06-X1 | XV-40203F_DO_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40203F | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40203F_DO_1 | DO | 2 | 1 | C2S06 | C2S06DO00 | C2S06,00 | 1756-OB32-0 |  |  | DO | C2 | 6 | 0 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S06,01 | 1756-OB32-1 | X1 | C2S06-X1 | XV-40204B_DO_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40204B | 0 | 2nd | - | 325-01-402-PD-01 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40204B_DO_1 | DO | 2 | 1 | C2S06 | C2S06DO01 | C2S06,01 | 1756-OB32-1 |  |  | DO | C2 | 6 | 1 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S06,02 | 1756-OB32-2 | X1 | C2S06-X1 | XV-40204C_DO_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40204C | 0 | 2nd | - | 325-01-402-PD-01 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40204C_DO_1 | DO | 2 | 1 | C2S06 | C2S06DO02 | C2S06,02 | 1756-OB32-2 |  |  | DO | C2 | 6 | 2 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S06,03 | 1756-OB32-3 | X1 | C2S06-X1 | XV-40205A_DO_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205A | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205A_DO_1 | DO | 2 | 1 | C2S06 | C2S06DO03 | C2S06,03 | 1756-OB32-3 |  |  | DO | C2 | 6 | 3 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S06,04 | 1756-OB32-4 | X1 | C2S06-X1 | XV-40205B_DO_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205B | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205B_DO_1 | DO | 2 | 1 | C2S06 | C2S06DO04 | C2S06,04 | 1756-OB32-4 |  |  | DO | C2 | 6 | 4 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S06,05 | 1756-OB32-5 | X1 | C2S06-X1 | XV-40205C_DO_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205C | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205C_DO_1 | DO | 2 | 1 | C2S06 | C2S06DO05 | C2S06,05 | 1756-OB32-5 |  |  | DO | C2 | 6 | 5 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S06,06 | 1756-OB32-6 | X1 | C2S06-X1 | XV-40205D_DO_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205D | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205D_DO_1 | DO | 2 | 1 | C2S06 | C2S06DO06 | C2S06,06 | 1756-OB32-6 |  |  | DO | C2 | 6 | 6 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S06,07 | 1756-OB32-7 | X1 | C2S06-X1 | XV-40205F_DO_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40205F | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40205F_DO_1 | DO | 2 | 1 | C2S06 | C2S06DO07 | C2S06,07 | 1756-OB32-7 |  |  | DO | C2 | 6 | 7 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S06,08 | 1756-OB32-8 | X1 | C2S06-X1 | XV-40222_DO_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | XV-40222 | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-40222_DO_1 | DO | 2 | 1 | C2S06 | C2S06DO08 | C2S06,08 | 1756-OB32-8 |  |  | DO | C2 | 6 | 8 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-402 | C2S06,09 | 1756-OB32-9 | X1 | C2S06-X1 | Spare_DO_0 |  | Jet Cooker 2nd Floor | JB-402 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO09 | C2S06,09 | 1756-OB32-9 |  |  | DO | C2 | 6 | 9 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S06,10 | 1756-OB32-10 | X1 | C2S06-X1 | Spare_DO_0 |  | Jet Cooker 2nd Floor | JB-402 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO10 | C2S06,10 | 1756-OB32-10 |  |  | DO | C2 | 6 | 10 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S06,11 | 1756-OB32-11 | X1 | C2S06-X1 | Spare_DO_0 |  | Jet Cooker 2nd Floor | JB-402 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO11 | C2S06,11 | 1756-OB32-11 |  |  | DO | C2 | 6 | 11 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S06,12 | 1756-OB32-12 | X1 | C2S06-X1 | Spare_DO_0 |  | Jet Cooker 2nd Floor | JB-402 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO12 | C2S06,12 | 1756-OB32-12 |  |  | DO | C2 | 6 | 12 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S06,13 | 1756-OB32-13 | X1 | C2S06-X1 | Spare_DO_0 |  | Jet Cooker 2nd Floor | JB-402 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO13 | C2S06,13 | 1756-OB32-13 |  |  | DO | C2 | 6 | 13 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S06,14 | 1756-OB32-14 | X1 | C2S06-X1 | Spare_DO_0 |  | Jet Cooker 2nd Floor | JB-402 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO14 | C2S06,14 | 1756-OB32-14 |  |  | DO | C2 | 6 | 14 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S06,15 | 1756-OB32-15 | X1 | C2S06-X1 | Spare_DO_0 |  | Jet Cooker 2nd Floor | JB-402 |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO15 | C2S06,15 | 1756-OB32-15 |  |  | DO | C2 | 6 | 15 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S06,16 | 1756-OB32-16 | X2 | C2S06-X2 | XS-60240B_DO_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XS-60240B | 0 | 4th | 325-01-600-PD-05 | - | Fan Command for BGHS-21 (Bag House Air Pulsing) |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | XS-60240B_DO_1 | DO | 2 | 1 | C2S06 | C2S06DO16 | C2S06,16 | 1756-OB32-16 |  |  | DO | C2 | 6 | 16 |  | 0 | 1 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-602 | C2S06,17 | 1756-OB32-17 | X2 | C2S06-X2 | XV-60214_DO_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XV-60214 | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Steam feed to Spray dryer |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60214_DO_1 | DO | 2 | 1 | C2S06 | C2S06DO17 | C2S06,17 | 1756-OB32-17 |  |  | DO | C2 | 6 | 17 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-602 | C2S06,18 | 1756-OB32-18 | X2 | C2S06-X2 | XV-60241_DO_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | XV-60241 | 0 | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60241_DO_1 | DO | 2 | 1 | C2S06 | C2S06DO18 | C2S06,18 | 1756-OB32-18 |  |  | DO | C2 | 6 | 18 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-602 | C2S06,19 | 1756-OB32-19 | X2 | C2S06-X2 | Spare_DO_0 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO19 | C2S06,19 | 1756-OB32-19 |  |  | DO | C2 | 6 | 19 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S06,20 | 1756-OB32-20 | X2 | C2S06-X2 | Spare_DO_0 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO20 | C2S06,20 | 1756-OB32-20 |  |  | DO | C2 | 6 | 20 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S06,21 | 1756-OB32-21 | X2 | C2S06-X2 | Spare_DO_0 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO21 | C2S06,21 | 1756-OB32-21 |  |  | DO | C2 | 6 | 21 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S06,22 | 1756-OB32-22 | X2 | C2S06-X2 | Spare_DO_0 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO22 | C2S06,22 | 1756-OB32-22 |  |  | DO | C2 | 6 | 22 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S06,23 | 1756-OB32-23 | X2 | C2S06-X2 | Spare_DO_0 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO23 | C2S06,23 | 1756-OB32-23 |  |  | DO | C2 | 6 | 23 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S06,24 | 1756-OB32-24 | X2 | C2S06-X2 | Spare_DO_0 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO24 | C2S06,24 | 1756-OB32-24 |  |  | DO | C2 | 6 | 24 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S06,25 | 1756-OB32-25 | X2 | C2S06-X2 | Spare_DO_0 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO25 | C2S06,25 | 1756-OB32-25 |  |  | DO | C2 | 6 | 25 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S06,26 | 1756-OB32-26 | X2 | C2S06-X2 | Spare_DO_0 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO26 | C2S06,26 | 1756-OB32-26 |  |  | DO | C2 | 6 | 26 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S06,27 | 1756-OB32-27 | X2 | C2S06-X2 | Spare_DO_0 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO27 | C2S06,27 | 1756-OB32-27 |  |  | DO | C2 | 6 | 27 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S06,28 | 1756-OB32-28 | X2 | C2S06-X2 | Spare_DO_0 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO28 | C2S06,28 | 1756-OB32-28 |  |  | DO | C2 | 6 | 28 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S06,29 | 1756-OB32-29 | X2 | C2S06-X2 | Spare_DO_0 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO29 | C2S06,29 | 1756-OB32-29 |  |  | DO | C2 | 6 | 29 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S06,30 | 1756-OB32-30 | X2 | C2S06-X2 | Spare_DO_0 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO30 | C2S06,30 | 1756-OB32-30 |  |  | DO | C2 | 6 | 30 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S06,31 | 1756-OB32-31 | X2 | C2S06-X2 | Spare_DO_0 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S06 | C2S06DO31 | C2S06,31 | 1756-OB32-31 |  |  | DO | C2 | 6 | 31 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S07,00 | 1756-OB32-0 | X1 | C2S07-X1 | SV-60207_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | SV-60207 | 0 | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-60207_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO00 | C2S07,00 | 1756-OB32-0 |  |  | DO | C2 | 7 | 0 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-607 | C2S07,01 | 1756-OB32-1 | X1 | C2S07-X1 | XS-FH-60210C_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XS-FH-60210C | 0 | 7th | 325-01-600-PD-06 | - | Command Remote Reset for AHTR-21 |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | XS-FH-60210C_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO01 | C2S07,01 | 1756-OB32-1 |  |  | DO | C2 | 7 | 1 |  | 0 | 1 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,02 | 1756-OB32-2 | X1 | C2S07-X1 | XS-FH-60210D_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XS-FH-60210D | 0 | 7th | 325-01-600-PD-06 | - | Spare |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | XS-FH-60210D_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO02 | C2S07,02 | 1756-OB32-2 |  |  | DO | C2 | 7 | 2 |  | 0 | 1 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,03 | 1756-OB32-3 | X1 | C2S07-X1 | XV-60201_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60201 | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam feed to Spray dryer |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60201_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO03 | C2S07,03 | 1756-OB32-3 |  |  | DO | C2 | 7 | 3 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M2 | JB-607 | C2S07,04 | 1756-OB32-4 | X1 | C2S07-X1 | XV-60261_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261 |  | 7th | 325-01-600-PD-02 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO04 | C2S07,04 | 1756-OB32-4 |  |  | DO | C2 | 7 | 4 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S07,05 | 1756-OB32-5 | X1 | C2S07-X1 | XV-60261FA_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261FA | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261FA_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO05 | C2S07,05 | 1756-OB32-5 |  |  | DO | C2 | 7 | 5 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,06 | 1756-OB32-6 | X1 | C2S07-X1 | XV-60261FB_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261FB | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261FB_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO06 | C2S07,06 | 1756-OB32-6 |  |  | DO | C2 | 7 | 6 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,07 | 1756-OB32-7 | X1 | C2S07-X1 | XV-60261FC_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261FC | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261FC_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO07 | C2S07,07 | 1756-OB32-7 |  |  | DO | C2 | 7 | 7 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,08 | 1756-OB32-8 | X1 | C2S07-X1 | XV-60261FD_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261FD | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261FD_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO08 | C2S07,08 | 1756-OB32-8 |  |  | DO | C2 | 7 | 8 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,09 | 1756-OB32-9 | X1 | C2S07-X1 | XV-60261SA_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261SA | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #1 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261SA_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO09 | C2S07,09 | 1756-OB32-9 |  |  | DO | C2 | 7 | 9 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,10 | 1756-OB32-10 | X1 | C2S07-X1 | XV-60261SB_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261SB | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #2 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261SB_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO10 | C2S07,10 | 1756-OB32-10 |  |  | DO | C2 | 7 | 10 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,11 | 1756-OB32-11 | X1 | C2S07-X1 | XV-60261SC_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261SC | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #3 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261SC_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO11 | C2S07,11 | 1756-OB32-11 |  |  | DO | C2 | 7 | 11 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,12 | 1756-OB32-12 | X1 | C2S07-X1 | XV-60261SD_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60261SD | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #4 (ATVM-11A) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60261SD_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO12 | C2S07,12 | 1756-OB32-12 |  |  | DO | C2 | 7 | 12 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,13 | 1756-OB32-13 | X1 | C2S07-X1 | XV-60262_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262 |  | 7th | 325-01-600-PD-02 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO13 | C2S07,13 | 1756-OB32-13 |  |  | DO | C2 | 7 | 13 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S07,14 | 1756-OB32-14 | X1 | C2S07-X1 | XV-60262FE_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262FE | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262FE_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO14 | C2S07,14 | 1756-OB32-14 |  |  | DO | C2 | 7 | 14 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,15 | 1756-OB32-15 | X1 | C2S07-X1 | XV-60262FF_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262FF | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262FF_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO15 | C2S07,15 | 1756-OB32-15 |  |  | DO | C2 | 7 | 15 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,16 | 1756-OB32-16 | X2 | C2S07-X2 | XV-60262FG_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262FG | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262FG_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO16 | C2S07,16 | 1756-OB32-16 |  |  | DO | C2 | 7 | 16 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,17 | 1756-OB32-17 | X2 | C2S07-X2 | XV-60262FH_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262FH | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262FH_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO17 | C2S07,17 | 1756-OB32-17 |  |  | DO | C2 | 7 | 17 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,18 | 1756-OB32-18 | X2 | C2S07-X2 | XV-60262SE_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262SE | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #5 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262SE_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO18 | C2S07,18 | 1756-OB32-18 |  |  | DO | C2 | 7 | 18 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,19 | 1756-OB32-19 | X2 | C2S07-X2 | XV-60262SF_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262SF | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #6 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262SF_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO19 | C2S07,19 | 1756-OB32-19 |  |  | DO | C2 | 7 | 19 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,20 | 1756-OB32-20 | X2 | C2S07-X2 | XV-60262SG_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262SG | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #7 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262SG_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO20 | C2S07,20 | 1756-OB32-20 |  |  | DO | C2 | 7 | 20 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,21 | 1756-OB32-21 | X2 | C2S07-X2 | XV-60262SH_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60262SH | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #8 (ATVM-11B) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60262SH_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO21 | C2S07,21 | 1756-OB32-21 |  |  | DO | C2 | 7 | 21 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,22 | 1756-OB32-22 | X2 | C2S07-X2 | XV-60263_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263 |  | 7th | 325-01-600-PD-02 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO22 | C2S07,22 | 1756-OB32-22 |  |  | DO | C2 | 7 | 22 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S07,23 | 1756-OB32-23 | X2 | C2S07-X2 | XV-60263FJ_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263FJ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263FJ_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO23 | C2S07,23 | 1756-OB32-23 |  |  | DO | C2 | 7 | 23 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,24 | 1756-OB32-24 | X2 | C2S07-X2 | XV-60263FK_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263FK | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263FK_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO24 | C2S07,24 | 1756-OB32-24 |  |  | DO | C2 | 7 | 24 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,25 | 1756-OB32-25 | X2 | C2S07-X2 | XV-60263FL_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263FL | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263FL_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO25 | C2S07,25 | 1756-OB32-25 |  |  | DO | C2 | 7 | 25 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,26 | 1756-OB32-26 | X2 | C2S07-X2 | XV-60263FM_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263FM | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263FM_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO26 | C2S07,26 | 1756-OB32-26 |  |  | DO | C2 | 7 | 26 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,27 | 1756-OB32-27 | X2 | C2S07-X2 | XV-60263SJ_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263SJ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #9 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263SJ_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO27 | C2S07,27 | 1756-OB32-27 |  |  | DO | C2 | 7 | 27 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,28 | 1756-OB32-28 | X2 | C2S07-X2 | XV-60263SK_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263SK | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #10 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263SK_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO28 | C2S07,28 | 1756-OB32-28 |  |  | DO | C2 | 7 | 28 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,29 | 1756-OB32-29 | X2 | C2S07-X2 | XV-60263SL_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263SL | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #11 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263SL_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO29 | C2S07,29 | 1756-OB32-29 |  |  | DO | C2 | 7 | 29 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,30 | 1756-OB32-30 | X2 | C2S07-X2 | XV-60263SM_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60263SM | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #12 (ATVM-11C) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60263SM_DO_1 | DO | 2 | 1 | C2S07 | C2S07DO30 | C2S07,30 | 1756-OB32-30 |  |  | DO | C2 | 7 | 30 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S07,31 | 1756-OB32-31 | X2 | C2S07-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S07 | C2S07DO31 | C2S07,31 | 1756-OB32-31 |  |  | DO | C2 | 7 | 31 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,00 | 1756-OB32-0 | X1 | C2S08-X1 | XV-60264_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264 |  | 7th | 325-01-600-PD-02 | - |  |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264_DO_1 | DO | 2 | 1 | C2S08 | C2S08DO00 | C2S08,00 | 1756-OB32-0 |  |  | DO | C2 | 8 | 0 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,01 | 1756-OB32-1 | X1 | C2S08-X1 | XV-60264FN_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264FN | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264FN_DO_1 | DO | 2 | 1 | C2S08 | C2S08DO01 | C2S08,01 | 1756-OB32-1 |  |  | DO | C2 | 8 | 1 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S08,02 | 1756-OB32-2 | X1 | C2S08-X1 | XV-60264FP_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264FP | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264FP_DO_1 | DO | 2 | 1 | C2S08 | C2S08DO02 | C2S08,02 | 1756-OB32-2 |  |  | DO | C2 | 8 | 2 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S08,03 | 1756-OB32-3 | X1 | C2S08-X1 | XV-60264FQ_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264FQ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264FQ_DO_1 | DO | 2 | 1 | C2S08 | C2S08DO03 | C2S08,03 | 1756-OB32-3 |  |  | DO | C2 | 8 | 3 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S08,04 | 1756-OB32-4 | X1 | C2S08-X1 | XV-60264FR_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264FR | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264FR_DO_1 | DO | 2 | 1 | C2S08 | C2S08DO04 | C2S08,04 | 1756-OB32-4 |  |  | DO | C2 | 8 | 4 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S08,05 | 1756-OB32-5 | X1 | C2S08-X1 | XV-60264SN_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264SN | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #13 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264SN_DO_1 | DO | 2 | 1 | C2S08 | C2S08DO05 | C2S08,05 | 1756-OB32-5 |  |  | DO | C2 | 8 | 5 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S08,06 | 1756-OB32-6 | X1 | C2S08-X1 | XV-60264SP_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264SP | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #14 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264SP_DO_1 | DO | 2 | 1 | C2S08 | C2S08DO06 | C2S08,06 | 1756-OB32-6 |  |  | DO | C2 | 8 | 6 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S08,07 | 1756-OB32-7 | X1 | C2S08-X1 | XV-60264SQ_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264SQ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #15 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264SQ_DO_1 | DO | 2 | 1 | C2S08 | C2S08DO07 | C2S08,07 | 1756-OB32-7 |  |  | DO | C2 | 8 | 7 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S08,08 | 1756-OB32-8 | X1 | C2S08-X1 | XV-60264SR_DO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | XV-60264SR | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam On/Off Valve for Nozzle #16 (ATVM-11D) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-60264SR_DO_1 | DO | 2 | 1 | C2S08 | C2S08DO08 | C2S08,08 | 1756-OB32-8 |  |  | DO | C2 | 8 | 8 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized,Dry Contact
=CA1+MCP-M2 | JB-607 | C2S08,09 | 1756-OB32-9 | X1 | C2S08-X1 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO09 | C2S08,09 | 1756-OB32-9 |  |  | DO | C2 | 8 | 9 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,10 | 1756-OB32-10 | X1 | C2S08-X1 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO10 | C2S08,10 | 1756-OB32-10 |  |  | DO | C2 | 8 | 10 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,11 | 1756-OB32-11 | X1 | C2S08-X1 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO11 | C2S08,11 | 1756-OB32-11 |  |  | DO | C2 | 8 | 11 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,12 | 1756-OB32-12 | X1 | C2S08-X1 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO12 | C2S08,12 | 1756-OB32-12 |  |  | DO | C2 | 8 | 12 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,13 | 1756-OB32-13 | X1 | C2S08-X1 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO13 | C2S08,13 | 1756-OB32-13 |  |  | DO | C2 | 8 | 13 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,14 | 1756-OB32-14 | X1 | C2S08-X1 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO14 | C2S08,14 | 1756-OB32-14 |  |  | DO | C2 | 8 | 14 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,15 | 1756-OB32-15 | X1 | C2S08-X1 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO15 | C2S08,15 | 1756-OB32-15 |  |  | DO | C2 | 8 | 15 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,16 | 1756-OB32-16 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO16 | C2S08,16 | 1756-OB32-16 |  |  | DO | C2 | 8 | 16 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,17 | 1756-OB32-17 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO17 | C2S08,17 | 1756-OB32-17 |  |  | DO | C2 | 8 | 17 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,18 | 1756-OB32-18 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO18 | C2S08,18 | 1756-OB32-18 |  |  | DO | C2 | 8 | 18 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,19 | 1756-OB32-19 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO19 | C2S08,19 | 1756-OB32-19 |  |  | DO | C2 | 8 | 19 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,20 | 1756-OB32-20 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO20 | C2S08,20 | 1756-OB32-20 |  |  | DO | C2 | 8 | 20 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,21 | 1756-OB32-21 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO21 | C2S08,21 | 1756-OB32-21 |  |  | DO | C2 | 8 | 21 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,22 | 1756-OB32-22 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO22 | C2S08,22 | 1756-OB32-22 |  |  | DO | C2 | 8 | 22 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,23 | 1756-OB32-23 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO23 | C2S08,23 | 1756-OB32-23 |  |  | DO | C2 | 8 | 23 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,24 | 1756-OB32-24 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO24 | C2S08,24 | 1756-OB32-24 |  |  | DO | C2 | 8 | 24 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,25 | 1756-OB32-25 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO25 | C2S08,25 | 1756-OB32-25 |  |  | DO | C2 | 8 | 25 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,26 | 1756-OB32-26 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO26 | C2S08,26 | 1756-OB32-26 |  |  | DO | C2 | 8 | 26 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,27 | 1756-OB32-27 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO27 | C2S08,27 | 1756-OB32-27 |  |  | DO | C2 | 8 | 27 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,28 | 1756-OB32-28 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO28 | C2S08,28 | 1756-OB32-28 |  |  | DO | C2 | 8 | 28 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,29 | 1756-OB32-29 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO29 | C2S08,29 | 1756-OB32-29 |  |  | DO | C2 | 8 | 29 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,30 | 1756-OB32-30 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO30 | C2S08,30 | 1756-OB32-30 |  |  | DO | C2 | 8 | 30 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S08,31 | 1756-OB32-31 | X2 | C2S08-X2 | Spare_DO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 | xx | Spare_DO_0 | DO | 2 | 0 | C2S08 | C2S08DO31 | C2S08,31 | 1756-OB32-31 |  |  | DO | C2 | 8 | 31 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S09,00 | 1756-IF16-0 | X1 | C2S09-X1 | FT-40221_AI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | FT-40221 | Coriolis Flow Transmitter | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0 | xx | FT-40221_AI_1 | AI | 3 | 1 | C2S09 | C2S09AI00 | C2S09,00 | 1756-IF16-0 |  |  | AI | C2 | 9 | 0 |  | 1 | 0 | 2 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M2 | JB-402 | C2S09,01 | 1756-IF16-1 | X1 | C2S09-X1 | FT-40221_AI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | FT-40221 | Coriolis Flow Transmitter | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0 | xx | FT-40221_AI_2 | AI | 3 | 2 | C2S09 | C2S09AI01 | C2S09,01 | 1756-IF16-1 |  |  | AI | C2 | 9 | 1 |  | 1 | 0 | 2 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M2 | JB-402 | C2S09,02 | 1756-IF16-2 | X1 | C2S09-X1 | FT-40222_AI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | FT-40222 | Coriolis Flow Transmitter | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0 | xx | FT-40222_AI_1 | AI | 3 | 1 | C2S09 | C2S09AI02 | C2S09,02 | 1756-IF16-2 |  |  | AI | C2 | 9 | 2 |  | 1 | 0 | 2 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M2 | JB-402 | C2S09,03 | 1756-IF16-3 | X1 | C2S09-X1 | FT-40222_AI_2 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | FT-40222 | Coriolis Flow Transmitter | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0 | xx | FT-40222_AI_2 | AI | 3 | 2 | C2S09 | C2S09AI03 | C2S09,03 | 1756-IF16-3 |  |  | AI | C2 | 9 | 3 |  | 1 | 0 | 2 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M2 | JB-402 | C2S09,04 | 1756-IF16-4 | X1 | C2S09-X1 | PT-40222_AI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | PT-40222 | Pressure Transmitter | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-40222_AI_1 | AI | 3 | 1 | C2S09 | C2S09AI04 | C2S09,04 | 1756-IF16-4 |  |  | AI | C2 | 9 | 4 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-402 | C2S09,05 | 1756-IF16-5 | X1 | C2S09-X1 | TT-40221_AI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | TT-40221 | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-40221_AI_1 | AI | 3 | 1 | C2S09 | C2S09AI05 | C2S09,05 | 1756-IF16-5 |  |  | AI | C2 | 9 | 5 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-402 | C2S09,06 | 1756-IF16-6 | X1 | C2S09-X1 | TT-40222_AI_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | TT-40222 | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-40222_AI_1 | AI | 3 | 1 | C2S09 | C2S09AI06 | C2S09,06 | 1756-IF16-6 |  |  | AI | C2 | 9 | 6 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-402 | C2S09,07 | 1756-IF16-7 | X1 | C2S09-X1 | Spare_AI_0 |  | Jet Cooker 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S09 | C2S09AI07 | C2S09,07 | 1756-IF16-7 |  |  | AI | C2 | 9 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S09,08 | 1756-IF16-8 | X1 | C2S09-X1 | Spare_AI_0 |  | Jet Cooker 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S09 | C2S09AI08 | C2S09,08 | 1756-IF16-8 |  |  | AI | C2 | 9 | 8 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S09,09 | 1756-IF16-9 | X1 | C2S09-X1 | Spare_AI_0 |  | Jet Cooker 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S09 | C2S09AI09 | C2S09,09 | 1756-IF16-9 |  |  | AI | C2 | 9 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S09,10 | 1756-IF16-10 | X1 | C2S09-X1 | Spare_AI_0 |  | Jet Cooker 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S09 | C2S09AI10 | C2S09,10 | 1756-IF16-10 |  |  | AI | C2 | 9 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S09,11 | 1756-IF16-11 | X1 | C2S09-X1 | Spare_AI_0 |  | Jet Cooker 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S09 | C2S09AI11 | C2S09,11 | 1756-IF16-11 |  |  | AI | C2 | 9 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S09,12 | 1756-IF16-12 | X1 | C2S09-X1 | Spare_AI_0 |  | Jet Cooker 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S09 | C2S09AI12 | C2S09,12 | 1756-IF16-12 |  |  | AI | C2 | 9 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S09,13 | 1756-IF16-13 | X1 | C2S09-X1 | Spare_AI_0 |  | Jet Cooker 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S09 | C2S09AI13 | C2S09,13 | 1756-IF16-13 |  |  | AI | C2 | 9 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S09,14 | 1756-IF16-14 | X1 | C2S09-X1 | Spare_AI_0 |  | Jet Cooker 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S09 | C2S09AI14 | C2S09,14 | 1756-IF16-14 |  |  | AI | C2 | 9 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 | C2S09,15 | 1756-IF16-15 | X1 | C2S09-X1 | Spare_AI_0 |  | Jet Cooker 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S09 | C2S09AI15 | C2S09,15 | 1756-IF16-15 |  |  | AI | C2 | 9 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S10,00 | 1756-IF16-0 | X1 | C2S10-X1 | AT-60241_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | AT-60241 | Dust Analyzer Transmitter | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Dust Analyzer Transmitter for Exhaust Duct (DTEX-22) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | AT-60241_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI00 | C2S10,00 | 1756-IF16-0 |  |  | AI | C2 | 10 | 0 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S10,01 | 1756-IF16-1 | X1 | C2S10-X1 | DPT-60203_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | DPT-60203 | Differential Pressure Transmitte | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Gas Pressure Differential Transmitter for Air Filter (FICA-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | DPT-60203_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI01 | C2S10,01 | 1756-IF16-1 |  |  | AI | C2 | 10 | 1 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S10,02 | 1756-IF16-2 | X1 | C2S10-X1 | FT-60202_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | FT-60202 | 0 | 5th | 325-01-600-PD-09 | 3-25-01-602-PD-09 | Steam feed to Spray dryer |  | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60202_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI02 | C2S10,02 | 1756-IF16-2 |  |  | AI | C2 | 10 | 2 |  | 1 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S10,03 | 1756-IF16-3 | X1 | C2S10-X1 | PT-60210_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | PT-60210 | Pressure Transmitter | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Gas Pressure Transmitter for Hot Air Duct (DTHA-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-60210_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI03 | C2S10,03 | 1756-IF16-3 |  |  | AI | C2 | 10 | 3 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S10,04 | 1756-IF16-4 | X1 | C2S10-X1 | PT-60215_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | PT-60215 | Pressure Transmitter | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | 15% Polypropylene Glycol Pressure Indicator Transmitter for Heat Recovery Pumping Skid (PUCF-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-60215_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI04 | C2S10,04 | 1756-IF16-4 |  |  | AI | C2 | 10 | 4 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S10,05 | 1756-IF16-5 | X1 | C2S10-X1 | PT-60216_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | PT-60216 | Pressure Transmitter | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Gas Pressure Transmitter for Combustion Air Burner Duct (DTCB-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-60216_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI05 | C2S10,05 | 1756-IF16-5 |  |  | AI | C2 | 10 | 5 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S10,06 | 1756-IF16-6 | X1 | C2S10-X1 | PT-60240_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | PT-60240 | Pressure Transmitter | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Gas Pressure Transmitter for Bag House Exhaust Duct (DTEX-22) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-60240_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI06 | C2S10,06 | 1756-IF16-6 |  |  | AI | C2 | 10 | 6 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S10,07 | 1756-IF16-7 | X1 | C2S10-X1 | PT-60241_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | PT-60241 | Pressure Transmitter | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Gas Pressure Transmitter for Exhaust Fan (FANE-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-60241_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI07 | C2S10,07 | 1756-IF16-7 |  |  | AI | C2 | 10 | 7 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S10,08 | 1756-IF16-8 | X1 | C2S10-X1 | TT-60210_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TT-60210 | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60210_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI08 | C2S10,08 | 1756-IF16-8 |  |  | AI | C2 | 10 | 8 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S10,09 | 1756-IF16-9 | X1 | C2S10-X1 | TT-60210A_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TT-60210A |  | 5th | 325-01-600-PD-03 | - |  |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60210A_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI09 | C2S10,09 | 1756-IF16-9 |  |  | AI | C2 | 10 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S10,10 | 1756-IF16-10 | X1 | C2S10-X1 | TT-60210B_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TT-60210B |  | 5th | 325-01-600-PD-03 | - |  |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60210B_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI10 | C2S10,10 | 1756-IF16-10 |  |  | AI | C2 | 10 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S10,11 | 1756-IF16-11 | X1 | C2S10-X1 | TT-60211_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TT-60211 | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60211_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI11 | C2S10,11 | 1756-IF16-11 |  |  | AI | C2 | 10 | 11 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S10,12 | 1756-IF16-12 | X1 | C2S10-X1 | TT-60212A_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TT-60212A | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60212A_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI12 | C2S10,12 | 1756-IF16-12 |  |  | AI | C2 | 10 | 12 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S10,13 | 1756-IF16-13 | X1 | C2S10-X1 | TT-60212B_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TT-60212B | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60212B_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI13 | C2S10,13 | 1756-IF16-13 |  |  | AI | C2 | 10 | 13 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S10,14 | 1756-IF16-14 | X1 | C2S10-X1 | TT-60214_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TT-60214 | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Steam Temperature Transmitter for Cold Air Duct (DTCA-23) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60214_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI14 | C2S10,14 | 1756-IF16-14 |  |  | AI | C2 | 10 | 14 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S10,15 | 1756-IF16-15 | X1 | C2S10-X1 | TT-60215A_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TT-60215A | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60215A_AI_1 | AI | 3 | 1 | C2S10 | C2S10AI15 | C2S10,15 | 1756-IF16-15 |  |  | AI | C2 | 10 | 15 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,00 | 1756-IF16-0 | X1 | C2S11-X1 | TT-60215B_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TT-60215B | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60215B_AI_1 | AI | 3 | 1 | C2S11 | C2S11AI00 | C2S11,00 | 1756-IF16-0 |  |  | AI | C2 | 11 | 0 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,01 | 1756-IF16-1 | X1 | C2S11-X1 | TT-60216_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TT-60216 | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Gas Temperature Transmitter for Combustion Air Burner Duct (DTCB-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60216_AI_1 | AI | 3 | 1 | C2S11 | C2S11AI01 | C2S11,01 | 1756-IF16-1 |  |  | AI | C2 | 11 | 1 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,02 | 1756-IF16-2 | X1 | C2S11-X1 | TT-60240_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TT-60240 | 0 | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Fan (FANE-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60240_AI_1 | AI | 3 | 1 | C2S11 | C2S11AI02 | C2S11,02 | 1756-IF16-2 |  |  | AI | C2 | 11 | 2 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,03 | 1756-IF16-3 | X1 | C2S11-X1 | TT-60241A_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TT-60241A | 0 | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60241A_AI_1 | AI | 3 | 1 | C2S11 | C2S11AI03 | C2S11,03 | 1756-IF16-3 |  |  | AI | C2 | 11 | 3 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,04 | 1756-IF16-4 | X1 | C2S11-X1 | TT-60241B_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TT-60241B | 0 | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60241B_AI_1 | AI | 3 | 1 | C2S11 | C2S11AI04 | C2S11,04 | 1756-IF16-4 |  |  | AI | C2 | 11 | 4 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,05 | 1756-IF16-5 | X1 | C2S11-X1 | VT-60210A_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | VT-60210A | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | VT-60210A_AI_1 | AI | 3 | 1 | C2S11 | C2S11AI05 | C2S11,05 | 1756-IF16-5 |  |  | AI | C2 | 11 | 5 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,06 | 1756-IF16-6 | X1 | C2S11-X1 | VT-60210B_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | VT-60210B | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | VT-60210B_AI_1 | AI | 3 | 1 | C2S11 | C2S11AI06 | C2S11,06 | 1756-IF16-6 |  |  | AI | C2 | 11 | 6 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,07 | 1756-IF16-7 | X1 | C2S11-X1 | VT-60241A_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | VT-60241A | 0 | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | VT-60241A_AI_1 | AI | 3 | 1 | C2S11 | C2S11AI07 | C2S11,07 | 1756-IF16-7 |  |  | AI | C2 | 11 | 7 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,08 | 1756-IF16-8 | X1 | C2S11-X1 | VT-60241B_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | VT-60241B | 0 | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | VT-60241B_AI_1 | AI | 3 | 1 | C2S11 | C2S11AI08 | C2S11,08 | 1756-IF16-8 |  |  | AI | C2 | 11 | 8 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,09 | 1756-IF16-9 | X1 | C2S11-X1 | FT-60210_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | FT-60210 | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) |  | Require I/O DI= 0,DO=0,AI=2,AO=0,Bus=0 | xx | FT-60210_AI_1 | AI | 3 | 1 | C2S11 | C2S11AI09 | C2S11,09 | 1756-IF16-9 |  |  | AI | C2 | 11 | 9 |  | 0 | 0 | 2 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,10 | 1756-IF16-10 | X1 | C2S11-X1 | FT-60211_AI_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | FT-60211 | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) |  | Require I/O DI= 0,DO=0,AI=2,AO=0,Bus=0 | xx | FT-60211_AI_1 | AI | 3 | 1 | C2S11 | C2S11AI10 | C2S11,10 | 1756-IF16-10 |  |  | AI | C2 | 11 | 10 |  | 0 | 0 | 2 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,11 | 1756-IF16-11 | X1 | C2S11-X1 | FT-60210_AI_2 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | FT-60210 | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) |  | Require I/O DI= 0,DO=0,AI=2,AO=0,Bus=0 | xx | FT-60210_AI_2 | AI | 3 | 2 | C2S11 | C2S11AI11 | C2S11,11 | 1756-IF16-11 |  |  | AI | C2 | 11 | 11 |  | 0 | 0 | 2 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,12 | 1756-IF16-12 | X1 | C2S11-X1 | FT-60211_AI_2 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | FT-60211 | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) |  | Require I/O DI= 0,DO=0,AI=2,AO=0,Bus=0 | xx | FT-60211_AI_2 | AI | 3 | 2 | C2S11 | C2S11AI12 | C2S11,12 | 1756-IF16-12 |  |  | AI | C2 | 11 | 12 |  | 0 | 0 | 2 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C2S11,13 | 1756-IF16-13 | X1 | C2S11-X1 | Spare_AI_0 |  | Spray Dryer 3rd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S11 | C2S11AI13 | C2S11,13 | 1756-IF16-13 |  |  | AI | C2 | 11 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S11,14 | 1756-IF16-14 | X1 | C2S11-X1 | Spare_AI_0 |  | Spray Dryer 3rd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S11 | C2S11AI14 | C2S11,14 | 1756-IF16-14 |  |  | AI | C2 | 11 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 | C2S11,15 | 1756-IF16-15 | X1 | C2S11-X1 | Spare_AI_0 |  | Spray Dryer 3rd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S11 | C2S11AI15 | C2S11,15 | 1756-IF16-15 |  |  | AI | C2 | 11 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S12,00 | 1756-IF16-0 | X1 | C2S12-X1 | FT-60207_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60207 | 0 | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 | Instr. Air Flow Transmitter for Camera #4 (ACAM-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60207_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI00 | C2S12,00 | 1756-IF16-0 |  |  | AI | C2 | 12 | 0 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,01 | 1756-IF16-1 | X1 | C2S12-X1 | FT-60221_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60221 | 0 | 7th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Cool air Flow |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60221_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI01 | C2S12,01 | 1756-IF16-1 |  |  | AI | C2 | 12 | 1 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,02 | 1756-IF16-2 | X1 | C2S12-X1 | FT-60261FA_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60261FA | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #1 (AMTV-11A) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60261FA_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI02 | C2S12,02 | 1756-IF16-2 |  |  | AI | C2 | 12 | 2 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,03 | 1756-IF16-3 | X1 | C2S12-X1 | FT-60261FB_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60261FB | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #2 (AMTV-11A) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60261FB_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI03 | C2S12,03 | 1756-IF16-3 |  |  | AI | C2 | 12 | 3 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,04 | 1756-IF16-4 | X1 | C2S12-X1 | FT-60261FC_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60261FC | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #3 (AMTV-11A) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60261FC_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI04 | C2S12,04 | 1756-IF16-4 |  |  | AI | C2 | 12 | 4 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,05 | 1756-IF16-5 | X1 | C2S12-X1 | FT-60261FD_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60261FD | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #4 (AMTV-11A) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60261FD_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI05 | C2S12,05 | 1756-IF16-5 |  |  | AI | C2 | 12 | 5 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,06 | 1756-IF16-6 | X1 | C2S12-X1 | FT-60262FE_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60262FE | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #5 (AMTV-11B) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60262FE_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI06 | C2S12,06 | 1756-IF16-6 |  |  | AI | C2 | 12 | 6 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,07 | 1756-IF16-7 | X1 | C2S12-X1 | FT-60262FF_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60262FF | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #6 (AMTV-11B) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60262FF_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI07 | C2S12,07 | 1756-IF16-7 |  |  | AI | C2 | 12 | 7 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,08 | 1756-IF16-8 | X1 | C2S12-X1 | FT-60262FG_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60262FG | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #7 (AMTV-11B) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60262FG_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI08 | C2S12,08 | 1756-IF16-8 |  |  | AI | C2 | 12 | 8 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,09 | 1756-IF16-9 | X1 | C2S12-X1 | FT-60262FH_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60262FH | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #8 (AMTV-11B) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60262FH_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI09 | C2S12,09 | 1756-IF16-9 |  |  | AI | C2 | 12 | 9 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,10 | 1756-IF16-10 | X1 | C2S12-X1 | FT-60263FJ_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60263FJ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #9 (AMTV-11C) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60263FJ_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI10 | C2S12,10 | 1756-IF16-10 |  |  | AI | C2 | 12 | 10 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,11 | 1756-IF16-11 | X1 | C2S12-X1 | FT-60263FK_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60263FK | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #10 (AMTV-11C) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60263FK_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI11 | C2S12,11 | 1756-IF16-11 |  |  | AI | C2 | 12 | 11 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,12 | 1756-IF16-12 | X1 | C2S12-X1 | FT-60263FL_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60263FL | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #11 (AMTV-11C) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60263FL_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI12 | C2S12,12 | 1756-IF16-12 |  |  | AI | C2 | 12 | 12 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,13 | 1756-IF16-13 | X1 | C2S12-X1 | FT-60263FM_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60263FM | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #12 (AMTV-11C) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60263FM_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI13 | C2S12,13 | 1756-IF16-13 |  |  | AI | C2 | 12 | 13 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,14 | 1756-IF16-14 | X1 | C2S12-X1 | FT-60264FN_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60264FN | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #13 (AMTV-11D) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60264FN_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI14 | C2S12,14 | 1756-IF16-14 |  |  | AI | C2 | 12 | 14 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S12,15 | 1756-IF16-15 | X1 | C2S12-X1 | FT-60264FP_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60264FP | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #14 (AMTV-11D) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60264FP_AI_1 | AI | 3 | 1 | C2S12 | C2S12AI15 | C2S12,15 | 1756-IF16-15 |  |  | AI | C2 | 12 | 15 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S13,00 | 1756-IF16-0 | X1 | C2S13-X1 | FT-60264FQ_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60264FQ | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #15 (AMTV-11D) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60264FQ_AI_1 | AI | 3 | 1 | C2S13 | C2S13AI00 | C2S13,00 | 1756-IF16-0 |  |  | AI | C2 | 13 | 0 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S13,01 | 1756-IF16-1 | X1 | C2S13-X1 | FT-60264FR_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | FT-60264FR | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #16 (AMTV-11D) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | FT-60264FR_AI_1 | AI | 3 | 1 | C2S13 | C2S13AI01 | C2S13,01 | 1756-IF16-1 |  |  | AI | C2 | 13 | 1 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S13,02 | 1756-IF16-2 | X1 | C2S13-X1 | PT-60201_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | PT-60201 | Pressure Transmitter | 7th | - | 3-25-01-602-PD-02 | Steam feed to Spray dryer |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-60201_AI_1 | AI | 3 | 1 | C2S13 | C2S13AI02 | C2S13,02 | 1756-IF16-2 |  |  | AI | C2 | 13 | 2 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S13,03 | 1756-IF16-3 | X1 | C2S13-X1 | PT-60207_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | PT-60207 | Pressure Transmitter | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 | Instr. Air Pressure Transmitter for Camera #4 (ACAM-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-60207_AI_1 | AI | 3 | 1 | C2S13 | C2S13AI03 | C2S13,03 | 1756-IF16-3 |  |  | AI | C2 | 13 | 3 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S13,04 | 1756-IF16-4 | X1 | C2S13-X1 | PT-60221_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | PT-60221 | Pressure Transmitter | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-04 | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-60221_AI_1 | AI | 3 | 1 | C2S13 | C2S13AI04 | C2S13,04 | 1756-IF16-4 |  |  | AI | C2 | 13 | 4 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S13,05 | 1756-IF16-5 | X1 | C2S13-X1 | PT-60221_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | PT-60221 | Pressure Transmitter | 7th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | PT-60221_AI_1 | AI | 3 | 1 | C2S13 | C2S13AI05 | C2S13,05 | 1756-IF16-5 |  |  | AI | C2 | 13 | 5 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S13,06 | 1756-IF16-6 | X1 | C2S13-X1 | TI-FH-60210_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | TI-FH-60210 | 0 | 7th | 325-01-600-PD-06 | - | Gas Burner Firing Rate Temp Signal to AHTR-21 |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TI-FH-60210_AI_1 | AI | 3 | 1 | C2S13 | C2S13AI06 | C2S13,06 | 1756-IF16-6 |  |  | AI | C2 | 13 | 6 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S13,07 | 1756-IF16-7 | X1 | C2S13-X1 | TT-60201_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | TT-60201 | 0 | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 | Steam feed to Spray dryer |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60201_AI_1 | AI | 3 | 1 | C2S13 | C2S13AI07 | C2S13,07 | 1756-IF16-7 |  |  | AI | C2 | 13 | 7 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S13,08 | 1756-IF16-8 | X1 | C2S13-X1 | TT-60202_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | TT-60202 | 0 | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 | Compress air temp to camera |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60202_AI_1 | AI | 3 | 1 | C2S13 | C2S13AI08 | C2S13,08 | 1756-IF16-8 |  |  | AI | C2 | 13 | 8 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S13,09 | 1756-IF16-9 | X1 | C2S13-X1 | TT-60207_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | TT-60207 | 0 | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 | Instr. Air Temperature Transmitter for Air Manifold - Camera #4 (ACAM-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | TT-60207_AI_1 | AI | 3 | 1 | C2S13 | C2S13AI09 | C2S13,09 | 1756-IF16-9 |  |  | AI | C2 | 13 | 9 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S13,10 | 1756-IF16-10 | X1 | C2S13-X1 | UY-FH-60210A_AI_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | UY-FH-60210A | 0 | 7th | 325-01-600-PD-06 | - | Comb fan VFD Speed Control |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | UY-FH-60210A_AI_1 | AI | 3 | 1 | C2S13 | C2S13AI10 | C2S13,10 | 1756-IF16-10 |  |  | AI | C2 | 13 | 10 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C2S13,11 | 1756-IF16-11 | X1 | C2S13-X1 | Spare_AI_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S13 | C2S13AI11 | C2S13,11 | 1756-IF16-11 |  |  | AI | C2 | 13 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S13,12 | 1756-IF16-12 | X1 | C2S13-X1 | Spare_AI_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S13 | C2S13AI12 | C2S13,12 | 1756-IF16-12 |  |  | AI | C2 | 13 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S13,13 | 1756-IF16-13 | X1 | C2S13-X1 | Spare_AI_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S13 | C2S13AI13 | C2S13,13 | 1756-IF16-13 |  |  | AI | C2 | 13 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S13,14 | 1756-IF16-14 | X1 | C2S13-X1 | Spare_AI_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S13 | C2S13AI14 | C2S13,14 | 1756-IF16-14 |  |  | AI | C2 | 13 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 | C2S13,15 | 1756-IF16-15 | X1 | C2S13-X1 | Spare_AI_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 | xx | Spare_AI_0 | AI | 3 | 0 | C2S13 | C2S13AI15 | C2S13,15 | 1756-IF16-15 |  |  | AI | C2 | 13 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S01,00 | 1756-IB32-0 | X1 | C3S01-X1 | AT-40201_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | AT-40201 |  | 3rd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | AT-40201_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI00 | C3S01,00 | 1756-IB32-0 |  |  | DI | C3 | 1 | 0 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S01,01 | 1756-IB32-1 | X1 | C3S01-X1 | AT-40202_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | AT-40202 |  | 3rd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | AT-40202_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI01 | C3S01,01 | 1756-IB32-1 |  |  | DI | C3 | 1 | 1 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S01,02 | 1756-IB32-2 | X1 | C3S01-X1 | AT-40203_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | AT-40203 |  | 3rd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | AT-40203_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI02 | C3S01,02 | 1756-IB32-2 |  |  | DI | C3 | 1 | 2 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S01,03 | 1756-IB32-3 | X1 | C3S01-X1 | LSH-60230_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | LSH-60230 | 0 | 1st | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-21) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSH-60230_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI03 | C3S01,03 | 1756-IB32-3 |  |  | DI | C3 | 1 | 3 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-603 | C3S01,04 | 1756-IB32-4 | X1 | C3S01-X1 | LSH-60231_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | LSH-60231 | 0 | 1st | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-22) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSH-60231_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI04 | C3S01,04 | 1756-IB32-4 |  |  | DI | C3 | 1 | 4 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-603 | C3S01,05 | 1756-IB32-5 | X1 | C3S01-X1 | LSH-60240_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | LSH-60240 | 0 | 1st | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Powder Level Switch High for Bag House (BGHS-21) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSH-60240_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI05 | C3S01,05 | 1756-IB32-5 |  |  | DI | C3 | 1 | 5 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-603 | C3S01,06 | 1756-IB32-6 | X1 | C3S01-X1 | PD-60202_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | PD-60202 |  | 3rd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PD-60202_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI06 | C3S01,06 | 1756-IB32-6 |  |  | DI | C3 | 1 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S01,07 | 1756-IB32-7 | X1 | C3S01-X1 | RV-60204_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | RV-60204 |  | 3rd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | RV-60204_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI07 | C3S01,07 | 1756-IB32-7 |  |  | DI | C3 | 1 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S01,08 | 1756-IB32-8 | X1 | C3S01-X1 | ZS-60201C_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | ZS-60201C | 0 | 4th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60201C_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI08 | C3S01,08 | 1756-IB32-8 |  |  | DI | C3 | 1 | 8 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-603 | C3S01,09 | 1756-IB32-9 | X1 | C3S01-X1 | ZS-60201D_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | ZS-60201D | 0 | 4th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60201D_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI09 | C3S01,09 | 1756-IB32-9 |  |  | DI | C3 | 1 | 9 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-603 | C3S01,10 | 1756-IB32-10 | X1 | C3S01-X1 | ZS-60201E_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | ZS-60201E | 0 | 1st | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60201E_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI10 | C3S01,10 | 1756-IB32-10 |  |  | DI | C3 | 1 | 10 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-603 | C3S01,11 | 1756-IB32-11 | X1 | C3S01-X1 | ZS-60229_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | ZS-60229 | 0 | 4th | - | 3-25-01-602-PD-04 | Limit Switch for CY-60230 (Door Service) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60229_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI11 | C3S01,11 | 1756-IB32-11 |  |  | DI | C3 | 1 | 11 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-603 | C3S01,12 | 1756-IB32-12 | X1 | C3S01-X1 | ZS-60230_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | ZS-60230 | 0 | 4th | - | 3-25-01-602-PD-04 | Limit Switch for CY-60231 (Door Service) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60230_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI12 | C3S01,12 | 1756-IB32-12 |  |  | DI | C3 | 1 | 12 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-603 | C3S01,13 | 1756-IB32-13 | X1 | C3S01-X1 | ZS-60231A_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | ZS-60231A | 0 | 4th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Spectacle Inserted) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60231A_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI13 | C3S01,13 | 1756-IB32-13 |  |  | DI | C3 | 1 | 13 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-603 | C3S01,14 | 1756-IB32-14 | X1 | C3S01-X1 | ZS-60231B_DI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | ZS-60231B | 0 | 4th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Blind Inserted) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60231B_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI14 | C3S01,14 | 1756-IB32-14 |  |  | DI | C3 | 1 | 14 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-603 | C3S01,15 | 1756-IB32-15 | X1 | C3S01-X1 | Spare_DI_0 |  | Spray Dryer 3rd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S01 | C3S01DI15 | C3S01,15 | 1756-IB32-15 |  |  | DI | C3 | 1 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S01,16 | 1756-IB32-16 | X2 | C3S01-X2 | DV-61301_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | DV-61301 | 0 | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61301 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | DV-61301_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI16 | C3S01,16 | 1756-IB32-16 |  |  | DI | C3 | 1 | 16 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | JB-618 | C3S01,17 | 1756-IB32-17 | X2 | C3S01-X2 | DV-61301_DI_2 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | DV-61301 | 0 | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61301 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | DV-61301_DI_2 | DI | 1 | 2 | C3S01 | C3S01DI17 | C3S01,17 | 1756-IB32-17 |  |  | DI | C3 | 1 | 17 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | JB-618 | C3S01,18 | 1756-IB32-18 | X2 | C3S01-X2 | DV-61302_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | DV-61302 | 0 | 9th | - | 3-25-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61302 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | DV-61302_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI18 | C3S01,18 | 1756-IB32-18 |  |  | DI | C3 | 1 | 18 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | JB-618 | C3S01,19 | 1756-IB32-19 | X2 | C3S01-X2 | DV-61302_DI_2 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | DV-61302 | 0 | 9th | - | 3-25-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61302 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | DV-61302_DI_2 | DI | 1 | 2 | C3S01 | C3S01DI19 | C3S01,19 | 1756-IB32-19 |  |  | DI | C3 | 1 | 19 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | JB-618 | C3S01,20 | 1756-IB32-20 | X2 | C3S01-X2 | LS-61303_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | LS-61303 | 0 | 7th | - | 3-25-01-613-PD-01 | Level switch |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LS-61303_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI20 | C3S01,20 | 1756-IB32-20 |  |  | DI | C3 | 1 | 20 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | JB-618 | C3S01,21 | 1756-IB32-21 | X2 | C3S01-X2 | PSL-61301_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PSL-61301 | 0 | 5th | 325-01-613-PD-01 | - | Pressure alarm low |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PSL-61301_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI21 | C3S01,21 | 1756-IB32-21 |  |  | DI | C3 | 1 | 21 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | JB-618 | C3S01,22 | 1756-IB32-22 | X2 | C3S01-X2 | PSL-61302_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PSL-61302 | 0 | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Pressure alarm low |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PSL-61302_DI_1 | DI | 1 | 1 | C3S01 | C3S01DI22 | C3S01,22 | 1756-IB32-22 |  |  | DI | C3 | 1 | 22 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | JB-618 | C3S01,28 | 1756-IB32-28 | X2 | C3S01-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S01 | C3S01DI28 | C3S01,28 | 1756-IB32-28 |  |  | DI | C3 | 1 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S01,29 | 1756-IB32-29 | X2 | C3S01-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S01 | C3S01DI29 | C3S01,29 | 1756-IB32-29 |  |  | DI | C3 | 1 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S01,30 | 1756-IB32-30 | X2 | C3S01-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S01 | C3S01DI30 | C3S01,30 | 1756-IB32-30 |  |  | DI | C3 | 1 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S01,31 | 1756-IB32-31 | X2 | C3S01-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  |  | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S01 | C3S01DI31 | C3S01,31 | 1756-IB32-31 |  |  | DI | C3 | 1 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,00 | 1756-IB32-0 | X1 | C3S02-X1 | ISV-61301_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | ISV-61301 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ISV-61301_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI00 | C3S02,00 | 1756-IB32-0 |  |  | DI | C3 | 2 | 0 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,01 | 1756-IB32-1 | X1 | C3S02-X1 | LSH-61301_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | LSH-61301 | 0 | 7th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Level alarm high |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSH-61301_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI01 | C3S02,01 | 1756-IB32-1 |  |  | DI | C3 | 2 | 1 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-618 | C3S02,02 | 1756-IB32-2 | X1 | C3S02-X1 | LSH-61303_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | LSH-61303 |  | 7th | 325-01-613-PD-01 | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSH-61303_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI02 | C3S02,02 | 1756-IB32-2 |  |  | DI | C3 | 2 | 2 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,03 | 1756-IB32-3 | X1 | C3S02-X1 | LSH-61306_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | LSH-61306 | 0 | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Level alarm high |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSH-61306_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI03 | C3S02,03 | 1756-IB32-3 |  |  | DI | C3 | 2 | 3 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-618 | C3S02,04 | 1756-IB32-4 | X1 | C3S02-X1 | LSH-61308_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | LSH-61308 | 0 | 8th | - | 3-25-01-613-PD-01 | High Level alarm Cooling cyclone |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSH-61308_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI04 | C3S02,04 | 1756-IB32-4 |  |  | DI | C3 | 2 | 4 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-618 | C3S02,05 | 1756-IB32-5 | X1 | C3S02-X1 | LSL-61302_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | LSL-61302 | 0 | 6th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Level alarm low |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSL-61302_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI05 | C3S02,05 | 1756-IB32-5 |  |  | DI | C3 | 2 | 5 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-618 | C3S02,06 | 1756-IB32-6 | X1 | C3S02-X1 | PSE-61300_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PSE-61300 | 0 | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Explosion Vent PSE-61300 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PSE-61300_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI06 | C3S02,06 | 1756-IB32-6 |  |  | DI | C3 | 2 | 6 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-618 | C3S02,07 | 1756-IB32-7 | X1 | C3S02-X1 | PSE-61301_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PSE-61301 | 0 | 8th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Explosion Vent PSE-61301 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PSE-61301_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI07 | C3S02,07 | 1756-IB32-7 |  |  | DI | C3 | 2 | 7 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-618 | C3S02,08 | 1756-IB32-8 | X1 | C3S02-X1 | PSE-61304_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PSE-61304 | 0 | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Explosion Vent PSE-61304 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PSE-61304_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI08 | C3S02,08 | 1756-IB32-8 |  |  | DI | C3 | 2 | 8 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-618 | C3S02,09 | 1756-IB32-9 | X1 | C3S02-X1 | PSV-61301A_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PSV-61301A |  | 8th | 325-01-613-PD-01 | 325-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PSV-61301A_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI09 | C3S02,09 | 1756-IB32-9 |  |  | DI | C3 | 2 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,10 | 1756-IB32-10 | X1 | C3S02-X1 | PSV-61301B_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PSV-61301B |  | 8th | 325-01-613-PD-01 | 325-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PSV-61301B_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI10 | C3S02,10 | 1756-IB32-10 |  |  | DI | C3 | 2 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,11 | 1756-IB32-11 | X1 | C3S02-X1 | ZS-61310_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | ZS-61310 | 0 | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Position Magnet Door |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-61310_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI11 | C3S02,11 | 1756-IB32-11 |  |  | DI | C3 | 2 | 11 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-618 | C3S02,12 | 1756-IB32-12 | X1 | C3S02-X1 | ZS-61311_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | ZS-61311 | 0 | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Position Magnet Door |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-61311_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI12 | C3S02,12 | 1756-IB32-12 |  |  | DI | C3 | 2 | 12 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-618 | C3S02,13 | 1756-IB32-13 | X1 | C3S02-X1 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI13 | C3S02,13 | 1756-IB32-13 |  |  | DI | C3 | 2 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,14 | 1756-IB32-14 | X1 | C3S02-X1 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI14 | C3S02,14 | 1756-IB32-14 |  |  | DI | C3 | 2 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,15 | 1756-IB32-15 | X1 | C3S02-X1 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI15 | C3S02,15 | 1756-IB32-15 |  |  | DI | C3 | 2 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,16 | 1756-IB32-16 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI16 | C3S02,16 | 1756-IB32-16 |  |  | DI | C3 | 2 | 16 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,17 | 1756-IB32-17 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI17 | C3S02,17 | 1756-IB32-17 |  |  | DI | C3 | 2 | 17 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,18 | 1756-IB32-18 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI18 | C3S02,18 | 1756-IB32-18 |  |  | DI | C3 | 2 | 18 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,19 | 1756-IB32-19 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI19 | C3S02,19 | 1756-IB32-19 |  |  | DI | C3 | 2 | 19 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,20 | 1756-IB32-20 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI20 | C3S02,20 | 1756-IB32-20 |  |  | DI | C3 | 2 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,21 | 1756-IB32-21 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI21 | C3S02,21 | 1756-IB32-21 |  |  | DI | C3 | 2 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,22 | 1756-IB32-22 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI22 | C3S02,22 | 1756-IB32-22 |  |  | DI | C3 | 2 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S02,23 | 1756-IB32-23 | X2 | C3S02-X2 | PSL-61311_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PSL-61311 | 0 | 8th | 325-01-613-PD-04 | 3-25-01-613-PD-04 | Pressure alarm low |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PSL-61311_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI23 | C3S02,23 | 1756-IB32-23 |  |  | DI | C3 | 2 | 23 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M3 | IS-JB-618 | C3S02,23 | 1756-IB32-23 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI23 | C3S02,23 | 1756-IB32-23 |  |  | DI | C3 | 2 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,24 | 1756-IB32-24 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI24 | C3S02,24 | 1756-IB32-24 |  |  | DI | C3 | 2 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S02,24 | 1756-IB32-24 | X2 | C3S02-X2 | SV-61304_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | SV-61304 | 0 | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-61304_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI24 | C3S02,24 | 1756-IB32-24 |  |  | DI | C3 | 2 | 24 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | IS-JB-618 | C3S02,25 | 1756-IB32-25 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI25 | C3S02,25 | 1756-IB32-25 |  |  | DI | C3 | 2 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S02,25 | 1756-IB32-25 | X2 | C3S02-X2 | SV-61304_DI_2 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | SV-61304 | 0 | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-61304_DI_2 | DI | 1 | 2 | C3S02 | C3S02DI25 | C3S02,25 | 1756-IB32-25 |  |  | DI | C3 | 2 | 25 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | IS-JB-618 | C3S02,26 | 1756-IB32-26 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI26 | C3S02,26 | 1756-IB32-26 |  |  | DI | C3 | 2 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S02,26 | 1756-IB32-26 | X2 | C3S02-X2 | XV-61301_DI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | XV-61301 | 0 | 5th | - | 3-25-01-613-PD-01 | Product feed-out Packing silo |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-61301_DI_1 | DI | 1 | 1 | C3S02 | C3S02DI26 | C3S02,26 | 1756-IB32-26 |  |  | DI | C3 | 2 | 26 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | IS-JB-618 | C3S02,27 | 1756-IB32-27 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI27 | C3S02,27 | 1756-IB32-27 |  |  | DI | C3 | 2 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S02,27 | 1756-IB32-27 | X2 | C3S02-X2 | XV-61301_DI_2 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | XV-61301 | 0 | 5th | - | 3-25-01-613-PD-01 | Product feed-out Packing silo |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-61301_DI_2 | DI | 1 | 2 | C3S02 | C3S02DI27 | C3S02,27 | 1756-IB32-27 |  |  | DI | C3 | 2 | 27 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | IS-JB-618 | C3S02,28 | 1756-IB32-28 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI28 | C3S02,28 | 1756-IB32-28 |  |  | DI | C3 | 2 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,29 | 1756-IB32-29 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI29 | C3S02,29 | 1756-IB32-29 |  |  | DI | C3 | 2 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,30 | 1756-IB32-30 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI30 | C3S02,30 | 1756-IB32-30 |  |  | DI | C3 | 2 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S02,31 | 1756-IB32-31 | X2 | C3S02-X2 | Spare_DI_0 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C3S02 | C3S02DI31 | C3S02,31 | 1756-IB32-31 |  |  | DI | C3 | 2 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,00 | 1756-OB32-0 | X1 | C3S03-X1 | DV-61301_DO_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | DV-61301 | 0 | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61301 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | DV-61301_DO_1 | DO | 2 | 1 | C3S03 | C3S03DO00 | C3S03,00 | 1756-OB32-0 |  |  | DO | C3 | 3 | 0 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | JB-618 | C3S03,01 | 1756-OB32-1 | X1 | C3S03-X1 | DV-61302_DO_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | DV-61302 | 0 | 9th | - | 3-25-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61302 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | DV-61302_DO_1 | DO | 2 | 1 | C3S03 | C3S03DO01 | C3S03,01 | 1756-OB32-1 |  |  | DO | C3 | 3 | 1 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | JB-618 | C3S03,02 | 1756-OB32-2 | X1 | C3S03-X1 | SV-61301_DO_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | SV-61301 | 0 | 8th | 325-01-613-PD-01 | - | Timer compress air pluse solenoid valve |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | SV-61301_DO_1 | DO | 2 | 1 | C3S03 | C3S03DO02 | C3S03,02 | 1756-OB32-2 |  |  | DO | C3 | 3 | 2 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | JB-618 | C3S03,03 | 1756-OB32-3 | X1 | C3S03-X1 | SV-61302_DO_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | SV-61302 | 0 | 7th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Air service |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | SV-61302_DO_1 | DO | 2 | 1 | C3S03 | C3S03DO03 | C3S03,03 | 1756-OB32-3 |  |  | DO | C3 | 3 | 3 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | JB-618 | C3S03,04 | 1756-OB32-4 | X1 | C3S03-X1 | SV-61303_DO_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | SV-61303 | 0 | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Timer compress air pluse solenoid valve |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | SV-61303_DO_1 | DO | 2 | 1 | C3S03 | C3S03DO04 | C3S03,04 | 1756-OB32-4 |  |  | DO | C3 | 3 | 4 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | JB-618 | C3S03,05 | 1756-OB32-5 | X1 | C3S03-X1 | SV-61304_DO_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | SV-61304 | 0 | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | SV-61304_DO_1 | DO | 2 | 1 | C3S03 | C3S03DO05 | C3S03,05 | 1756-OB32-5 |  |  | DO | C3 | 3 | 5 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | JB-618 | C3S03,06 | 1756-OB32-6 | X1 | C3S03-X1 | SV-61305_DO_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | SV-61305 | 0 | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Air service |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | SV-61305_DO_1 | DO | 2 | 1 | C3S03 | C3S03DO06 | C3S03,06 | 1756-OB32-6 |  |  | DO | C3 | 3 | 6 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | JB-618 | C3S03,07 | 1756-OB32-7 | X1 | C3S03-X1 | SV-61306_DO_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | SV-61306 |  | 5th | - | 3-25-01-613-PD-01 |  |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | SV-61306_DO_1 | DO | 2 | 1 | C3S03 | C3S03DO07 | C3S03,07 | 1756-OB32-7 |  |  | DO | C3 | 3 | 7 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,08 | 1756-OB32-8 | X1 | C3S03-X1 | XV-61301_DO_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | XV-61301 | 0 | 5th | - | 3-25-01-613-PD-01 | Product feed-out Packing silo |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-61301_DO_1 | DO | 2 | 1 | C3S03 | C3S03DO08 | C3S03,08 | 1756-OB32-8 |  |  | DO | C3 | 3 | 8 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M3 | JB-618 | C3S03,09 | 1756-OB32-9 | X1 | C3S03-X1 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO09 | C3S03,09 | 1756-OB32-9 |  |  | DO | C3 | 3 | 9 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,10 | 1756-OB32-10 | X1 | C3S03-X1 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO10 | C3S03,10 | 1756-OB32-10 |  |  | DO | C3 | 3 | 10 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,11 | 1756-OB32-11 | X1 | C3S03-X1 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO11 | C3S03,11 | 1756-OB32-11 |  |  | DO | C3 | 3 | 11 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,12 | 1756-OB32-12 | X1 | C3S03-X1 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO12 | C3S03,12 | 1756-OB32-12 |  |  | DO | C3 | 3 | 12 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,13 | 1756-OB32-13 | X1 | C3S03-X1 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO13 | C3S03,13 | 1756-OB32-13 |  |  | DO | C3 | 3 | 13 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,14 | 1756-OB32-14 | X1 | C3S03-X1 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO14 | C3S03,14 | 1756-OB32-14 |  |  | DO | C3 | 3 | 14 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,15 | 1756-OB32-15 | X1 | C3S03-X1 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO15 | C3S03,15 | 1756-OB32-15 |  |  | DO | C3 | 3 | 15 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,16 | 1756-OB32-16 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO16 | C3S03,16 | 1756-OB32-16 |  |  | DO | C3 | 3 | 16 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,17 | 1756-OB32-17 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO17 | C3S03,17 | 1756-OB32-17 |  |  | DO | C3 | 3 | 17 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,18 | 1756-OB32-18 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO18 | C3S03,18 | 1756-OB32-18 |  |  | DO | C3 | 3 | 18 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,19 | 1756-OB32-19 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO19 | C3S03,19 | 1756-OB32-19 |  |  | DO | C3 | 3 | 19 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,20 | 1756-OB32-20 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO20 | C3S03,20 | 1756-OB32-20 |  |  | DO | C3 | 3 | 20 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,21 | 1756-OB32-21 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO21 | C3S03,21 | 1756-OB32-21 |  |  | DO | C3 | 3 | 21 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,22 | 1756-OB32-22 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO22 | C3S03,22 | 1756-OB32-22 |  |  | DO | C3 | 3 | 22 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,23 | 1756-OB32-23 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO23 | C3S03,23 | 1756-OB32-23 |  |  | DO | C3 | 3 | 23 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,24 | 1756-OB32-24 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO24 | C3S03,24 | 1756-OB32-24 |  |  | DO | C3 | 3 | 24 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,25 | 1756-OB32-25 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO25 | C3S03,25 | 1756-OB32-25 |  |  | DO | C3 | 3 | 25 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,26 | 1756-OB32-26 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO26 | C3S03,26 | 1756-OB32-26 |  |  | DO | C3 | 3 | 26 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,27 | 1756-OB32-27 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO27 | C3S03,27 | 1756-OB32-27 |  |  | DO | C3 | 3 | 27 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,28 | 1756-OB32-28 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO28 | C3S03,28 | 1756-OB32-28 |  |  | DO | C3 | 3 | 28 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,29 | 1756-OB32-29 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO29 | C3S03,29 | 1756-OB32-29 |  |  | DO | C3 | 3 | 29 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,30 | 1756-OB32-30 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO30 | C3S03,30 | 1756-OB32-30 |  |  | DO | C3 | 3 | 30 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S03,31 | 1756-OB32-31 | X2 | C3S03-X2 | Spare_DO_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C3S03 | C3S03DO31 | C3S03,31 | 1756-OB32-31 |  |  | DO | C3 | 3 | 31 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S04,00 | 1756-IF16-0 | X1 | C3S04-X1 | PT-60230_AI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | PT-60230 | Pressure Transmitter | 4th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas Pressure Transmitter for Conveying Duct (DTCO-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-60230_AI_1 | AI | 3 | 1 | C3S04 | C3S04AI00 | C3S04,00 | 1756-IF16-0 |  |  | AI | C3 | 4 | 0 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-603 | C3S04,01 | 1756-IF16-1 | X1 | C3S04-X1 | PT-60231_AI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | PT-60231 | Pressure Transmitter | 4th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas Pressure Transmitter for Cyclone Exhaust Duct (DTCE-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-60231_AI_1 | AI | 3 | 1 | C3S04 | C3S04AI01 | C3S04,01 | 1756-IF16-1 |  |  | AI | C3 | 4 | 1 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-603 | C3S04,02 | 1756-IF16-2 | X1 | C3S04-X1 | TT-60224_AI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | TT-60224 | 0 | 4th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-60224_AI_1 | AI | 3 | 1 | C3S04 | C3S04AI02 | C3S04,02 | 1756-IF16-2 |  |  | AI | C3 | 4 | 2 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-603 | C3S04,03 | 1756-IF16-3 | X1 | C3S04-X1 | TT-60225_AI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | TT-60225 | 0 | 3rd | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-60225_AI_1 | AI | 3 | 1 | C3S04 | C3S04AI03 | C3S04,03 | 1756-IF16-3 |  |  | AI | C3 | 4 | 3 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-603 | C3S04,04 | 1756-IF16-4 | X1 | C3S04-X1 | TT-60226_AI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | TT-60226 | 0 | 2nd | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-60226_AI_1 | AI | 3 | 1 | C3S04 | C3S04AI04 | C3S04,04 | 1756-IF16-4 |  |  | AI | C3 | 4 | 4 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-603 | C3S04,05 | 1756-IF16-5 | X1 | C3S04-X1 | TT-60227_AI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | TT-60227 | 0 | 1st | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-60227_AI_1 | AI | 3 | 1 | C3S04 | C3S04AI05 | C3S04,05 | 1756-IF16-5 |  |  | AI | C3 | 4 | 5 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-603 | C3S04,06 | 1756-IF16-6 | X1 | C3S04-X1 | TT-60230_AI_1 |  | Spray Dryer 3rd Floor | JB-603 | Spray Dryer | TT-60230 | 0 | 3rd | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Conveying Duct (DTCO-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-60230_AI_1 | AI | 3 | 1 | C3S04 | C3S04AI06 | C3S04,06 | 1756-IF16-6 |  |  | AI | C3 | 4 | 6 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-603 | C3S04,07 | 1756-IF16-7 | X1 | C3S04-X1 | Spare_AI_0 |  | Spray Dryer 3rd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C3S04 | C3S04AI07 | C3S04,07 | 1756-IF16-7 |  |  | AI | C3 | 4 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S04,08 | 1756-IF16-8 | X1 | C3S04-X1 | Spare_AI_0 |  | Spray Dryer 3rd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C3S04 | C3S04AI08 | C3S04,08 | 1756-IF16-8 |  |  | AI | C3 | 4 | 8 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S04,09 | 1756-IF16-9 | X1 | C3S04-X1 | Spare_AI_0 |  | Spray Dryer 3rd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C3S04 | C3S04AI09 | C3S04,09 | 1756-IF16-9 |  |  | AI | C3 | 4 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S04,10 | 1756-IF16-10 | X1 | C3S04-X1 | Spare_AI_0 |  | Spray Dryer 3rd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C3S04 | C3S04AI10 | C3S04,10 | 1756-IF16-10 |  |  | AI | C3 | 4 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S04,11 | 1756-IF16-11 | X1 | C3S04-X1 | Spare_AI_0 |  | Spray Dryer 3rd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C3S04 | C3S04AI11 | C3S04,11 | 1756-IF16-11 |  |  | AI | C3 | 4 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S04,12 | 1756-IF16-12 | X1 | C3S04-X1 | Spare_AI_0 |  | Spray Dryer 3rd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C3S04 | C3S04AI12 | C3S04,12 | 1756-IF16-12 |  |  | AI | C3 | 4 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S04,13 | 1756-IF16-13 | X1 | C3S04-X1 | Spare_AI_0 |  | Spray Dryer 3rd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C3S04 | C3S04AI13 | C3S04,13 | 1756-IF16-13 |  |  | AI | C3 | 4 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S04,14 | 1756-IF16-14 | X1 | C3S04-X1 | Spare_AI_0 |  | Spray Dryer 3rd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C3S04 | C3S04AI14 | C3S04,14 | 1756-IF16-14 |  |  | AI | C3 | 4 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 | C3S04,15 | 1756-IF16-15 | X1 | C3S04-X1 | Spare_AI_0 |  | Spray Dryer 3rd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C3S04 | C3S04AI15 | C3S04,15 | 1756-IF16-15 |  |  | AI | C3 | 4 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S05,00 | 1756-IF16-0 | X1 | C3S05-X1 | PT-61303_AI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PT-61303 | Pressure Transmitter | 8th | - | 3-25-01-613-PD-01 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-61303_AI_1 | AI | 3 | 1 | C3S05 | C3S05AI00 | C3S05,00 | 1756-IF16-0 |  |  | AI | C3 | 5 | 0 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | JB-618 | C3S05,01 | 1756-IF16-1 | X1 | C3S05-X1 | PT-61306_AI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PT-61306 |  | 8th | - | 3-25-01-613-PD-01 |  |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-61306_AI_1 | AI | 3 | 1 | C3S05 | C3S05AI01 | C3S05,01 | 1756-IF16-1 |  |  | AI | C3 | 5 | 1 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S05,02 | 1756-IF16-2 | X1 | C3S05-X1 | TT-61303_AI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | TT-61303 |  | 8th | - | 3-25-01-613-PD-01 |  |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-61303_AI_1 | AI | 3 | 1 | C3S05 | C3S05AI02 | C3S05,02 | 1756-IF16-2 |  |  | AI | C3 | 5 | 2 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | JB-618 | C3S05,03 | 1756-IF16-3 | X1 | C3S05-X1 | TT-61304_AI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | TT-61304 |  | 8th | - | 3-25-01-613-PD-01 |  |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-61304_AI_1 | AI | 3 | 1 | C3S05 | C3S05AI03 | C3S05,03 | 1756-IF16-3 |  |  | AI | C3 | 5 | 3 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S05,04 | 1756-IF16-4 | X1 | C3S05-X1 | DPT-61301_AI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | DPT-61301 | Differential Pressure Transmitte | 8th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Vent filter pressure |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | DPT-61301_AI_1 | AI | 3 | 1 | C3S05 | C3S05AI04 | C3S05,04 | 1756-IF16-4 |  |  | AI | C3 | 5 | 4 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-618 | C3S05,05 | 1756-IF16-5 | X1 | C3S05-X1 | DPT-61302_AI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | DPT-61302 | Differential Pressure Transmitte | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Vent filter pressure |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | DPT-61302_AI_1 | AI | 3 | 1 | C3S05 | C3S05AI05 | C3S05,05 | 1756-IF16-5 |  |  | AI | C3 | 5 | 5 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-618 | C3S05,06 | 1756-IF16-6 | X1 | C3S05-X1 | LT-61301_AI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | LT-61301 | Level Transmitter | 8th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Level powder in silo |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | LT-61301_AI_1 | AI | 3 | 1 | C3S05 | C3S05AI06 | C3S05,06 | 1756-IF16-6 |  |  | AI | C3 | 5 | 6 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-618 | C3S05,07 | 1756-IF16-7 | X1 | C3S05-X1 | PT-61301_AI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PT-61301 | Pressure Transmitter | 8th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Pressure in silo |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-61301_AI_1 | AI | 3 | 1 | C3S05 | C3S05AI07 | C3S05,07 | 1756-IF16-7 |  |  | AI | C3 | 5 | 7 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-618 | C3S05,08 | 1756-IF16-8 | X1 | C3S05-X1 | PT-61303_AI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PT-61303 | Pressure Transmitter | 8th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-61303_AI_1 | AI | 3 | 1 | C3S05 | C3S05AI08 | C3S05,08 | 1756-IF16-8 |  |  | AI | C3 | 5 | 8 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-618 | C3S05,09 | 1756-IF16-9 | X1 | C3S05-X1 | PT-61304_AI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PT-61304 | Pressure Transmitter | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Gas Pressure Transmitter for Storage Bin Cyclone Inlet Duct (CYCL-31) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-61304_AI_1 | AI | 3 | 1 | C3S05 | C3S05AI09 | C3S05,09 | 1756-IF16-9 |  |  | AI | C3 | 5 | 9 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-618 | C3S05,10 | 1756-IF16-10 | X1 | C3S05-X1 | PT-61305_AI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | PT-61305 | Pressure Transmitter | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Gas Pressure Transmitter for Exhaust Duct (DTEX-31) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-61305_AI_1 | AI | 3 | 1 | C3S05 | C3S05AI10 | C3S05,10 | 1756-IF16-10 |  |  | AI | C3 | 5 | 10 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-618 | C3S05,11 | 1756-IF16-11 | X1 | C3S05-X1 | TT-61301_AI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | TT-61301 | 0 | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Gas Temperature Transmitter for Cold Air Duct (DTCA-32) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-61301_AI_1 | AI | 3 | 1 | C3S05 | C3S05AI11 | C3S05,11 | 1756-IF16-11 |  |  | AI | C3 | 5 | 11 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-618 | C3S05,12 | 1756-IF16-12 | X1 | C3S05-X1 | TT-61302_AI_1 |  | Packing Tower 8th Floor | JB-618 | Packing Tower | TT-61302 | 0 | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Gas and Powder Temperature Transmitter for Cooling Cyclone (CYCL-31) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-61302_AI_1 | AI | 3 | 1 | C3S05 | C3S05AI12 | C3S05,12 | 1756-IF16-12 |  |  | AI | C3 | 5 | 12 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M3 | IS-JB-618 | C3S05,13 | 1756-IF16-13 | X1 | C3S05-X1 | Spare_AI_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C3S05 | C3S05AI13 | C3S05,13 | 1756-IF16-13 |  |  | AI | C3 | 5 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S05,14 | 1756-IF16-14 | X1 | C3S05-X1 | Spare_AI_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C3S05 | C3S05AI14 | C3S05,14 | 1756-IF16-14 |  |  | AI | C3 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 | C3S05,15 | 1756-IF16-15 | X1 | C3S05-X1 | Spare_AI_0 |  | Packing Tower 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C3S05 | C3S05AI15 | C3S05,15 | 1756-IF16-15 |  |  | AI | C3 | 5 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 | C3S13,00 | 1756-OF8-0 | X1 | C3S13-X1 | TCV-40222_AO_1 |  | Jet Cooker 2nd Floor | JB-402 | Jet Cooker | TCV-40222 | 0 | 2nd | - | 325-01-402-PD-02 | Jet Cooker |  | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0 | xx | TCV-40222_AO_1 | AO | 4 | 1 | C3S13 | C3S13AO00 | C3S13,00 | 1756-OF8-0 |  |  | AO | C3 | 13 | 0 |  | 0 | 0 | 0 | 1 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-602 | C3S13,01 | 1756-OF8-1 | X1 | C3S13-X1 | TV-60202_AO_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TV-60202 |  | 3rd | 325-01-600-PD-07 | 3-25-01-602-PD-07 |  |  | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0 | xx | TV-60202_AO_1 | AO | 4 | 1 | C3S13 | C3S13AO01 | C3S13,01 | 1756-OF8-1 |  |  | AO | C3 | 13 | 1 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M2 | JB-602 | C3S13,02 | 1756-OF8-2 | X1 | C3S13-X1 | TV-60214_AO_1 |  | Spray Dryer 3rd Floor | JB-602 | Spray Dryer | TV-60214 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0 | xx | TV-60214_AO_1 | AO | 4 | 1 | C3S13 | C3S13AO02 | C3S13,02 | 1756-OF8-2 |  |  | AO | C3 | 13 | 2 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M2 | JB-607 | C3S13,03 | 1756-OF8-3 | X1 | C3S13-X1 | PV-60201_AO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | PV-60201 |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0 | xx | PV-60201_AO_1 | AO | 4 | 1 | C3S13 | C3S13AO03 | C3S13,03 | 1756-OF8-3 |  |  | AO | C3 | 13 | 3 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M2 | JB-607 | C3S13,04 | 1756-OF8-4 | X1 | C3S13-X1 | UY-FH-60210B_AO_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | UY-FH-60210B | 0 | 7th | 325-01-600-PD-06 | - | Demand Signal |  | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0 | xx | UY-FH-60210B_AO_1 | AO | 4 | 1 | C3S13 | C3S13AO04 | C3S13,04 | 1756-OF8-4 |  |  | AO | C3 | 13 | 4 |  | 0 | 0 | 0 | 1 | 0 |  | 4 - 20 mA
=CA1+MCP-M2 | JB-607 | C3S13,05 | 1756-OF8-5 | X1 | C3S13-X1 | Spare_AO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0 | xx | Spare_AO_0 | AO | 4 | 0 | C3S13 | C3S13AO05 | C3S13,05 | 1756-OF8-5 |  |  | AO | C3 | 13 | 5 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M2 | JB-607 | C3S13,06 | 1756-OF8-6 | X1 | C3S13-X1 | Spare_AO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0 | xx | Spare_AO_0 | AO | 4 | 0 | C3S13 | C3S13AO06 | C3S13,06 | 1756-OF8-6 |  |  | AO | C3 | 13 | 6 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M2 | JB-607 | C3S13,07 | 1756-OF8-7 | X1 | C3S13-X1 | Spare_AO_0 |  | Spray Dryer 7th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=0,AO=1,Bus=0 | xx | Spare_AO_0 | AO | 4 | 0 | C3S13 | C3S13AO07 | C3S13,07 | 1756-OF8-7 |  |  | AO | C3 | 13 | 7 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M4 | JB-606 | C4S01,00 | 1756-IB32-0 | X1 | C4S01-X1 | FT-60203_DI_1 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | FT-60203 | 0 | 6th | 325-01-600-PD-09 | 3-25-01-602-PD-09 | Culinary steam feed to Spray dryer |  | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0 |  | FT-60203_DI_1 | DI | 1 | 1 | C4S01 | C4S01DI00 | C4S01,00 | 1756-IB32-0 |  |  | DI | C4 | 1 | 0 |  | 1 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | JB-606 | C4S01,01 | 1756-IB32-1 | X1 | C4S01-X1 | LSH-60250_DI_1 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | LSH-60250 | 0 | 6th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Water Level Switch High for Fire Deluge Pipe (FWDP-21) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSH-60250_DI_1 | DI | 1 | 1 | C4S01 | C4S01DI01 | C4S01,01 | 1756-IB32-1 |  |  | DI | C4 | 1 | 1 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-606 | C4S01,02 | 1756-IB32-2 | X1 | C4S01-X1 | XA-60261_DI_1 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | XA-60261 | 0 | 6th | 325-01-600-PD-05 | - | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-60261_DI_1 | DI | 1 | 1 | C4S01 | C4S01DI02 | C4S01,02 | 1756-IB32-2 |  |  | DI | C4 | 1 | 2 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-606 | C4S01,03 | 1756-IB32-3 | X1 | C4S01-X1 | XA-60262_DI_1 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | XA-60262 | 0 | 6th | 325-01-600-PD-05 | - | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-60262_DI_1 | DI | 1 | 1 | C4S01 | C4S01DI03 | C4S01,03 | 1756-IB32-3 |  |  | DI | C4 | 1 | 3 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-606 | C4S01,04 | 1756-IB32-4 | X1 | C4S01-X1 | Spare_DI_0 |  | Spray Dryer 6th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI04 | C4S01,04 | 1756-IB32-4 |  |  | DI | C4 | 1 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 | C4S01,05 | 1756-IB32-5 | X1 | C4S01-X1 | Spare_DI_0 |  | Spray Dryer 6th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI05 | C4S01,05 | 1756-IB32-5 |  |  | DI | C4 | 1 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 | C4S01,06 | 1756-IB32-6 | X1 | C4S01-X1 | Spare_DI_0 |  | Spray Dryer 6th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI06 | C4S01,06 | 1756-IB32-6 |  |  | DI | C4 | 1 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 | C4S01,07 | 1756-IB32-7 | X1 | C4S01-X1 | Spare_DI_0 |  | Spray Dryer 6th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI07 | C4S01,07 | 1756-IB32-7 |  |  | DI | C4 | 1 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 | C4S01,08 | 1756-IB32-8 | X1 | C4S01-X1 | Spare_DI_0 |  | Spray Dryer 6th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI08 | C4S01,08 | 1756-IB32-8 |  |  | DI | C4 | 1 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 | C4S01,09 | 1756-IB32-9 | X1 | C4S01-X1 | Spare_DI_0 |  | Spray Dryer 6th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI09 | C4S01,09 | 1756-IB32-9 |  |  | DI | C4 | 1 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 | C4S01,10 | 1756-IB32-10 | X1 | C4S01-X1 | Spare_DI_0 |  | Spray Dryer 6th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI10 | C4S01,10 | 1756-IB32-10 |  |  | DI | C4 | 1 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 | C4S01,11 | 1756-IB32-11 | X1 | C4S01-X1 | Spare_DI_0 |  | Spray Dryer 6th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI11 | C4S01,11 | 1756-IB32-11 |  |  | DI | C4 | 1 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 | C4S01,12 | 1756-IB32-12 | X1 | C4S01-X1 | Spare_DI_0 |  | Spray Dryer 6th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI12 | C4S01,12 | 1756-IB32-12 |  |  | DI | C4 | 1 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 | C4S01,13 | 1756-IB32-13 | X1 | C4S01-X1 | Spare_DI_0 |  | Spray Dryer 6th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI13 | C4S01,13 | 1756-IB32-13 |  |  | DI | C4 | 1 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 | C4S01,14 | 1756-IB32-14 | X1 | C4S01-X1 | Spare_DI_0 |  | Spray Dryer 6th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI14 | C4S01,14 | 1756-IB32-14 |  |  | DI | C4 | 1 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 | C4S01,15 | 1756-IB32-15 | X1 | C4S01-X1 | Spare_DI_0 |  | Spray Dryer 6th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI15 | C4S01,15 | 1756-IB32-15 |  |  | DI | C4 | 1 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 | C4S01,16 | 1756-IB32-16 | X2 | C4S01-X2 | ZS-60201A_DI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | ZS-60201A | 0 | 6th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60201A_DI_1 | DI | 1 | 1 | C4S01 | C4S01DI16 | C4S01,16 | 1756-IB32-16 |  |  | DI | C4 | 1 | 16 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-608 | C4S01,17 | 1756-IB32-17 | X2 | C4S01-X2 | ZS-60201B_DI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | ZS-60201B | 0 | 6th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60201B_DI_1 | DI | 1 | 1 | C4S01 | C4S01DI17 | C4S01,17 | 1756-IB32-17 |  |  | DI | C4 | 1 | 17 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-608 | C4S01,18 | 1756-IB32-18 | X2 | C4S01-X2 | ZS-60231C_DI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | ZS-60231C | 0 | 5th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Spool Inserted) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60231C_DI_1 | DI | 1 | 1 | C4S01 | C4S01DI18 | C4S01,18 | 1756-IB32-18 |  |  | DI | C4 | 1 | 18 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-608 | C4S01,19 | 1756-IB32-19 | X2 | C4S01-X2 | ZS-60231D_DI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | ZS-60231D | 0 | 5th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Blind Inserted) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60231D_DI_1 | DI | 1 | 1 | C4S01 | C4S01DI19 | C4S01,19 | 1756-IB32-19 |  |  | DI | C4 | 1 | 19 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-608 | C4S01,20 | 1756-IB32-20 | X2 | C4S01-X2 | ZS-60231E_DI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | ZS-60231E | 0 | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Spool Inserted) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60231E_DI_1 | DI | 1 | 1 | C4S01 | C4S01DI20 | C4S01,20 | 1756-IB32-20 |  |  | DI | C4 | 1 | 20 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-608 | C4S01,21 | 1756-IB32-21 | X2 | C4S01-X2 | ZS-60231F_DI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | ZS-60231F | 0 | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Blind Inserted) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60231F_DI_1 | DI | 1 | 1 | C4S01 | C4S01DI21 | C4S01,21 | 1756-IB32-21 |  |  | DI | C4 | 1 | 21 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-608 | C4S01,22 | 1756-IB32-22 | X2 | C4S01-X2 | ZS-60240_DI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | ZS-60240 | 0 | 6th | - | 3-25-01-602-PD-05 | Limit Switch for FA-60240 (Door Service) |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-60240_DI_1 | DI | 1 | 1 | C4S01 | C4S01DI22 | C4S01,22 | 1756-IB32-22 |  |  | DI | C4 | 1 | 22 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-608 | C4S01,23 | 1756-IB32-23 | X2 | C4S01-X2 | Spare_DI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI23 | C4S01,23 | 1756-IB32-23 |  |  | DI | C4 | 1 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 | C4S01,24 | 1756-IB32-24 | X2 | C4S01-X2 | Spare_DI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI24 | C4S01,24 | 1756-IB32-24 |  |  | DI | C4 | 1 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 | C4S01,25 | 1756-IB32-25 | X2 | C4S01-X2 | Spare_DI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI25 | C4S01,25 | 1756-IB32-25 |  |  | DI | C4 | 1 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 | C4S01,26 | 1756-IB32-26 | X2 | C4S01-X2 | Spare_DI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI26 | C4S01,26 | 1756-IB32-26 |  |  | DI | C4 | 1 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 | C4S01,27 | 1756-IB32-27 | X2 | C4S01-X2 | Spare_DI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI27 | C4S01,27 | 1756-IB32-27 |  |  | DI | C4 | 1 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 | C4S01,28 | 1756-IB32-28 | X2 | C4S01-X2 | Spare_DI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI28 | C4S01,28 | 1756-IB32-28 |  |  | DI | C4 | 1 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 | C4S01,29 | 1756-IB32-29 | X2 | C4S01-X2 | Spare_DI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI29 | C4S01,29 | 1756-IB32-29 |  |  | DI | C4 | 1 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 | C4S01,30 | 1756-IB32-30 | X2 | C4S01-X2 | Spare_DI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI30 | C4S01,30 | 1756-IB32-30 |  |  | DI | C4 | 1 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 | C4S01,31 | 1756-IB32-31 | X2 | C4S01-X2 | Spare_DI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S01 | C4S01DI31 | C4S01,31 | 1756-IB32-31 |  |  | DI | C4 | 1 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,00 | 1756-IB32-0 | X1 | C4S02-X1 | PSL-61305_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | PSL-61305 | 0 | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Pressure alarm low |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PSL-61305_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI00 | C4S02,00 | 1756-IB32-0 |  |  | DI | C4 | 2 | 0 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-612 | C4S02,01 | 1756-IB32-1 | X1 | C4S02-X1 | PSL-61306_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | PSL-61306 | 0 | 1st | 325-01-613-PD-05 | 3-25-01-613-PD-05 | Pressure alarm low |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PSL-61306_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI01 | C4S02,01 | 1756-IB32-1 |  |  | DI | C4 | 2 | 1 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-612 | C4S02,02 | 1756-IB32-2 | X1 | C4S02-X1 | PVM-61301_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | PVM-61301 |  | 2nd | 325-01-613-PD-03 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 | xx | PVM-61301_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI02 | C4S02,02 | 1756-IB32-2 |  |  | DI | C4 | 2 | 2 |  | 2 | 2 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,03 | 1756-IB32-3 | X1 | C4S02-X1 | PVM-61301_DI_2 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | PVM-61301 |  | 2nd | 325-01-613-PD-03 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 | xx | PVM-61301_DI_2 | DI | 1 | 2 | C4S02 | C4S02DI03 | C4S02,03 | 1756-IB32-3 |  |  | DI | C4 | 2 | 3 |  | 2 | 2 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,04 | 1756-IB32-4 | X1 | C4S02-X1 | XA-61301A_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XA-61301A | 0 | 1st | 325-01-613-PD-02 | - | Request filter plant |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-61301A_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI04 | C4S02,04 | 1756-IB32-4 |  |  | DI | C4 | 2 | 4 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-612 | C4S02,05 | 1756-IB32-5 | X1 | C4S02-X1 | XA-61301B_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XA-61301B | 0 | 1st | 325-01-613-PD-02 | - | Request material transport |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-61301B_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI05 | C4S02,05 | 1756-IB32-5 |  |  | DI | C4 | 2 | 5 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-612 | C4S02,06 | 1756-IB32-6 | X1 | C4S02-X1 | XA-61301C_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XA-61301C | 0 | 1st | 325-01-613-PD-02 | - | Request belt plant |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-61301C_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI06 | C4S02,06 | 1756-IB32-6 |  |  | DI | C4 | 2 | 6 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-612 | C4S02,07 | 1756-IB32-7 | X1 | C4S02-X1 | XA-61301D_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XA-61301D | 0 | 1st | 325-01-613-PD-02 | - | Machine in operation |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-61301D_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI07 | C4S02,07 | 1756-IB32-7 |  |  | DI | C4 | 2 | 7 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-612 | C4S02,08 | 1756-IB32-8 | X1 | C4S02-X1 | XA-61301E_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XA-61301E | 0 | 1st | 325-01-613-PD-02 | - | General Fault |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-61301E_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI08 | C4S02,08 | 1756-IB32-8 |  |  | DI | C4 | 2 | 8 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-612 | C4S02,09 | 1756-IB32-9 | X1 | C4S02-X1 | XA-61301F_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XA-61301F | 0 | 1st | 325-01-613-PD-02 | - | Machine is ready |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-61301F_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI09 | C4S02,09 | 1756-IB32-9 |  |  | DI | C4 | 2 | 9 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-612 | C4S02,10 | 1756-IB32-10 | X1 | C4S02-X1 | XA-61301G_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XA-61301G | 0 | 1st | 325-01-613-PD-02 | - | Emergency stop activated |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-61301G_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI10 | C4S02,10 | 1756-IB32-10 |  |  | DI | C4 | 2 | 10 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-612 | C4S02,11 | 1756-IB32-11 | X1 | C4S02-X1 | XA-61301H_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XA-61301H | 0 | 1st | 325-01-613-PD-02 | - | Silo minimum |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-61301H_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI11 | C4S02,11 | 1756-IB32-11 |  |  | DI | C4 | 2 | 11 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-612 | C4S02,12 | 1756-IB32-12 | X1 | C4S02-X1 | XA-61301J_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XA-61301J | 0 | 1st | 325-01-613-PD-02 | - | Silo maximum |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-61301J_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI12 | C4S02,12 | 1756-IB32-12 |  |  | DI | C4 | 2 | 12 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | JB-612 | C4S02,13 | 1756-IB32-13 | X1 | C4S02-X1 | XV-61302_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XV-61302 | 0 | 2nd | 325-01-613-PD-02 | 3-25-01-613-PD-02 | Dust collector feed vent |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-61302_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI13 | C4S02,13 | 1756-IB32-13 |  |  | DI | C4 | 2 | 13 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S02,14 | 1756-IB32-14 | X1 | C4S02-X1 | XV-61302_DI_2 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XV-61302 | 0 | 2nd | 325-01-613-PD-02 | 3-25-01-613-PD-02 | Dust collector feed vent |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-61302_DI_2 | DI | 1 | 2 | C4S02 | C4S02DI14 | C4S02,14 | 1756-IB32-14 |  |  | DI | C4 | 2 | 14 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S02,15 | 1756-IB32-15 | X1 | C4S02-X1 | XV-61303_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XV-61303 | 0 | 2nd | 325-01-613-PD-02 | 3-25-01-613-PD-02 | Dust collector feed from packer |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-61303_DI_1 | DI | 1 | 1 | C4S02 | C4S02DI15 | C4S02,15 | 1756-IB32-15 |  |  | DI | C4 | 2 | 15 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S02,16 | 1756-IB32-16 | X2 | C4S02-X2 | XV-61303_DI_2 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XV-61303 | 0 | 2nd | 325-01-613-PD-02 | 3-25-01-613-PD-02 | Dust collector feed from packer |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-61303_DI_2 | DI | 1 | 2 | C4S02 | C4S02DI16 | C4S02,16 | 1756-IB32-16 |  |  | DI | C4 | 2 | 16 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S02,17 | 1756-IB32-17 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI17 | C4S02,17 | 1756-IB32-17 |  |  | DI | C4 | 2 | 17 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,18 | 1756-IB32-18 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI18 | C4S02,18 | 1756-IB32-18 |  |  | DI | C4 | 2 | 18 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,19 | 1756-IB32-19 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI19 | C4S02,19 | 1756-IB32-19 |  |  | DI | C4 | 2 | 19 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,20 | 1756-IB32-20 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI20 | C4S02,20 | 1756-IB32-20 |  |  | DI | C4 | 2 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,21 | 1756-IB32-21 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI21 | C4S02,21 | 1756-IB32-21 |  |  | DI | C4 | 2 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,22 | 1756-IB32-22 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI22 | C4S02,22 | 1756-IB32-22 |  |  | DI | C4 | 2 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,23 | 1756-IB32-23 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI23 | C4S02,23 | 1756-IB32-23 |  |  | DI | C4 | 2 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,24 | 1756-IB32-24 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI24 | C4S02,24 | 1756-IB32-24 |  |  | DI | C4 | 2 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,25 | 1756-IB32-25 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI25 | C4S02,25 | 1756-IB32-25 |  |  | DI | C4 | 2 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,26 | 1756-IB32-26 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI26 | C4S02,26 | 1756-IB32-26 |  |  | DI | C4 | 2 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,27 | 1756-IB32-27 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI27 | C4S02,27 | 1756-IB32-27 |  |  | DI | C4 | 2 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,28 | 1756-IB32-28 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI28 | C4S02,28 | 1756-IB32-28 |  |  | DI | C4 | 2 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,29 | 1756-IB32-29 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI29 | C4S02,29 | 1756-IB32-29 |  |  | DI | C4 | 2 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,30 | 1756-IB32-30 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI30 | C4S02,30 | 1756-IB32-30 |  |  | DI | C4 | 2 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S02,31 | 1756-IB32-31 | X2 | C4S02-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S02 | C4S02DI31 | C4S02,31 | 1756-IB32-31 |  |  | DI | C4 | 2 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,00 | 1756-IB32-0 | X1 | C4S03-X1 | ISV-61303_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | ISV-61303 | 0 | 2nd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Explosion isolation flap valve ISV-61303 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ISV-61303_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI00 | C4S03,00 | 1756-IB32-0 |  |  | DI | C4 | 3 | 0 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-612 | C4S03,01 | 1756-IB32-1 | X1 | C4S03-X1 | ISV-61304_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | ISV-61304 | 0 | 2nd | 325-01-613-PD-05 | 3-25-01-613-PD-05 | Explosion isolation flap valve ISV-61304 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ISV-61304_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI01 | C4S03,01 | 1756-IB32-1 |  |  | DI | C4 | 3 | 1 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-612 | C4S03,02 | 1756-IB32-2 | X1 | C4S03-X1 | LSH-61304_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | LSH-61304 | 0 | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Big bag level alarm high |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSH-61304_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI02 | C4S03,02 | 1756-IB32-2 |  |  | DI | C4 | 3 | 2 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-612 | C4S03,03 | 1756-IB32-3 | X1 | C4S03-X1 | LSH-61305_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | LSH-61305 | 0 | 1st | 325-01-613-PD-05 | 3-25-01-613-PD-05 | Big bag level alarm high |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSH-61305_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI03 | C4S03,03 | 1756-IB32-3 |  |  | DI | C4 | 3 | 3 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-612 | C4S03,04 | 1756-IB32-4 | X1 | C4S03-X1 | LSH-61307_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | LSH-61307 | 0 | 1st | - | 3-25-01-613-PD-01 | High Level alarm reject screen |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSH-61307_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI04 | C4S03,04 | 1756-IB32-4 |  |  | DI | C4 | 3 | 4 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-612 | C4S03,05 | 1756-IB32-5 | X1 | C4S03-X1 | LSH-61312_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | LSH-61312 | 0 | 2nd | 325-01-613-PD-05 | 3-25-01-613-PD-05 | Level alarm high |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSH-61312_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI05 | C4S03,05 | 1756-IB32-5 |  |  | DI | C4 | 3 | 5 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-612 | C4S03,06 | 1756-IB32-6 | X1 | C4S03-X1 | PSE-61302_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | PSE-61302 | 0 | 2nd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Explosion Vent PSE-61302 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PSE-61302_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI06 | C4S03,06 | 1756-IB32-6 |  |  | DI | C4 | 3 | 6 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-612 | C4S03,07 | 1756-IB32-7 | X1 | C4S03-X1 | PSE-61303_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | PSE-61303 | 0 | 2nd | 325-01-613-PD-05 | 3-25-01-613-PD-05 | Explosion Vent PSE-61303 |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PSE-61303_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI07 | C4S03,07 | 1756-IB32-7 |  |  | DI | C4 | 3 | 7 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-612 | C4S03,09 | 1756-IB32-9 | X1 | C4S03-X1 | RV-61301_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | RV-61301 |  | 2nd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | RV-61301_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI09 | C4S03,09 | 1756-IB32-9 |  |  | DI | C4 | 3 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,10 | 1756-IB32-10 | X1 | C4S03-X1 | RV-61304_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | RV-61304 |  | 2nd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | RV-61304_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI10 | C4S03,10 | 1756-IB32-10 |  |  | DI | C4 | 3 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,11 | 1756-IB32-11 | X1 | C4S03-X1 | RV-61305_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | RV-61305 |  | 2nd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | RV-61305_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI11 | C4S03,11 | 1756-IB32-11 |  |  | DI | C4 | 3 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,12 | 1756-IB32-12 | X1 | C4S03-X1 | SC-61301_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | SC-61301 |  | 2nd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | SC-61301_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI12 | C4S03,12 | 1756-IB32-12 |  |  | DI | C4 | 3 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,13 | 1756-IB32-13 | X1 | C4S03-X1 | SC-61302_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | SC-61302 |  | 2nd | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | SC-61302_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI13 | C4S03,13 | 1756-IB32-13 |  |  | DI | C4 | 3 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,14 | 1756-IB32-14 | X1 | C4S03-X1 | ZS-61312_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | ZS-61312 | 0 | 3rd | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Position Magnet Door |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-61312_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI14 | C4S03,14 | 1756-IB32-14 |  |  | DI | C4 | 3 | 14 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-612 | C4S03,15 | 1756-IB32-15 | X1 | C4S03-X1 | ZS-61313_DI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | ZS-61313 | 0 | 3rd | 325-01-613-PD-01 | 3-25-01-613-PD-01 | Position Magnet Door |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | ZS-61313_DI_1 | DI | 1 | 1 | C4S03 | C4S03DI15 | C4S03,15 | 1756-IB32-15 |  |  | DI | C4 | 3 | 15 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M4 | IS-JB-612 | C4S03,16 | 1756-IB32-16 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI16 | C4S03,16 | 1756-IB32-16 |  |  | DI | C4 | 3 | 16 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,17 | 1756-IB32-17 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI17 | C4S03,17 | 1756-IB32-17 |  |  | DI | C4 | 3 | 17 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,18 | 1756-IB32-18 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI18 | C4S03,18 | 1756-IB32-18 |  |  | DI | C4 | 3 | 18 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,19 | 1756-IB32-19 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI19 | C4S03,19 | 1756-IB32-19 |  |  | DI | C4 | 3 | 19 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,20 | 1756-IB32-20 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI20 | C4S03,20 | 1756-IB32-20 |  |  | DI | C4 | 3 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,21 | 1756-IB32-21 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI21 | C4S03,21 | 1756-IB32-21 |  |  | DI | C4 | 3 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,22 | 1756-IB32-22 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI22 | C4S03,22 | 1756-IB32-22 |  |  | DI | C4 | 3 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,23 | 1756-IB32-23 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI23 | C4S03,23 | 1756-IB32-23 |  |  | DI | C4 | 3 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,24 | 1756-IB32-24 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI24 | C4S03,24 | 1756-IB32-24 |  |  | DI | C4 | 3 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,25 | 1756-IB32-25 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI25 | C4S03,25 | 1756-IB32-25 |  |  | DI | C4 | 3 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,26 | 1756-IB32-26 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI26 | C4S03,26 | 1756-IB32-26 |  |  | DI | C4 | 3 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,27 | 1756-IB32-27 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI27 | C4S03,27 | 1756-IB32-27 |  |  | DI | C4 | 3 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,28 | 1756-IB32-28 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI28 | C4S03,28 | 1756-IB32-28 |  |  | DI | C4 | 3 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,29 | 1756-IB32-29 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI29 | C4S03,29 | 1756-IB32-29 |  |  | DI | C4 | 3 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,30 | 1756-IB32-30 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI30 | C4S03,30 | 1756-IB32-30 |  |  | DI | C4 | 3 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S03,31 | 1756-IB32-31 | X2 | C4S03-X2 | Spare_DI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C4S03 | C4S03DI31 | C4S03,31 | 1756-IB32-31 |  |  | DI | C4 | 3 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 | C4S04,00 | 1756-OB32-0 | X1 | C4S04-X1 | SV-60220_DO_1 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | SV-60220 | 0 | 6th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | PA On/Off Valve for Chamber PSE purge air (CHAM-21) |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | SV-60220_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO00 | C4S04,00 | 1756-OB32-0 |  |  | DO | C4 | 4 | 0 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-606 | C4S04,01 | 1756-OB32-1 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO01 | C4S04,01 | 1756-OB32-1 |  |  | DO | C4 | 4 | 1
=CA1+MCP-M4 | JB-606 | C4S04,02 | 1756-OB32-2 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO02 | C4S04,02 | 1756-OB32-2 |  |  | DO | C4 | 4 | 2
=CA1+MCP-M4 | JB-606 | C4S04,03 | 1756-OB32-3 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO03 | C4S04,03 | 1756-OB32-3 |  |  | DO | C4 | 4 | 3
=CA1+MCP-M4 | JB-606 | C4S04,04 | 1756-OB32-4 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO04 | C4S04,04 | 1756-OB32-4 |  |  | DO | C4 | 4 | 4
=CA1+MCP-M4 | JB-606 | C4S04,05 | 1756-OB32-5 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO05 | C4S04,05 | 1756-OB32-5 |  |  | DO | C4 | 4 | 5
=CA1+MCP-M4 | JB-606 | C4S04,06 | 1756-OB32-6 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO06 | C4S04,06 | 1756-OB32-6 |  |  | DO | C4 | 4 | 6
=CA1+MCP-M4 | JB-606 | C4S04,07 | 1756-OB32-7 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO07 | C4S04,07 | 1756-OB32-7 |  |  | DO | C4 | 4 | 7
=CA1+MCP-M4 | IS-JB-608 | C4S04,08 | 1756-OB32-8 | X1 | C4S04-X1 | XA-60201_DO_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | XA-60201 | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | LEL gas Buzzer Alarm |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XA-60201_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO08 | C4S04,08 | 1756-OB32-8 |  |  | DO | C4 | 4 | 8 |  | 0 | 1 | 0 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | IS-JB-608 | C4S04,09 | 1756-OB32-9 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO09 | C4S04,09 | 1756-OB32-9 |  |  | DO | C4 | 4 | 9
=CA1+MCP-M4 | IS-JB-608 | C4S04,10 | 1756-OB32-10 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO10 | C4S04,10 | 1756-OB32-10 |  |  | DO | C4 | 4 | 10
=CA1+MCP-M4 | IS-JB-608 | C4S04,11 | 1756-OB32-11 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO11 | C4S04,11 | 1756-OB32-11 |  |  | DO | C4 | 4 | 11
=CA1+MCP-M4 | IS-JB-608 | C4S04,12 | 1756-OB32-12 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO12 | C4S04,12 | 1756-OB32-12 |  |  | DO | C4 | 4 | 12
=CA1+MCP-M4 | IS-JB-608 | C4S04,13 | 1756-OB32-13 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO13 | C4S04,13 | 1756-OB32-13 |  |  | DO | C4 | 4 | 13
=CA1+MCP-M4 | IS-JB-608 | C4S04,14 | 1756-OB32-14 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO14 | C4S04,14 | 1756-OB32-14 |  |  | DO | C4 | 4 | 14
=CA1+MCP-M4 | IS-JB-608 | C4S04,15 | 1756-OB32-15 | X1 | C4S04-X1 | Spare_DO_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO15 | C4S04,15 | 1756-OB32-15 |  |  | DO | C4 | 4 | 15
=CA1+MCP-M4 | JB-612 | C4S04,16 | 1756-OB32-16 | X2 | C4S04-X2 | PVM-61301_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | PVM-61301 |  | 2nd | 325-01-613-PD-03 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 | xx | PVM-61301_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO16 | C4S04,16 | 1756-OB32-16 |  |  | DO | C4 | 4 | 16 |  | 2 | 2 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S04,17 | 1756-OB32-17 | X2 | C4S04-X2 | PVM-61301_DO_2 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | PVM-61301 |  | 2nd | 325-01-613-PD-03 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 | xx | PVM-61301_DO_2 | DO | 2 | 2 | C4S04 | C4S04DO17 | C4S04,17 | 1756-OB32-17 |  |  | DO | C4 | 4 | 17 |  | 2 | 2 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S04,18 | 1756-OB32-18 | X2 | C4S04-X2 | SV-61307_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | SV-61307 |  | 3rd | - | 3-25-01-613-PD-01 |  |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | SV-61307_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO18 | C4S04,18 | 1756-OB32-18 |  |  | DO | C4 | 4 | 18 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S04,19 | 1756-OB32-19 | X2 | C4S04-X2 | SV-61308_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | SV-61308 | 0 | 2nd | 325-01-613-PD-03 | - | Timer compress air pluse solenoid valve |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | SV-61308_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO19 | C4S04,19 | 1756-OB32-19 |  |  | DO | C4 | 4 | 19 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S04,20 | 1756-OB32-20 | X2 | C4S04-X2 | SV-61309_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | SV-61309 | 0 | 2nd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Air service |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | SV-61309_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO20 | C4S04,20 | 1756-OB32-20 |  |  | DO | C4 | 4 | 20 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S04,21 | 1756-OB32-21 | X2 | C4S04-X2 | SV-61310_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | SV-61310 | 0 | 2nd | 325-01-613-PD-05 | - | Timer compress air pluse solenoid valve |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | SV-61310_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO21 | C4S04,21 | 1756-OB32-21 |  |  | DO | C4 | 4 | 21 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S04,22 | 1756-OB32-22 | X2 | C4S04-X2 | SV-61311_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | SV-61311 | 0 | 1st | 325-01-613-PD-05 | 3-25-01-613-PD-05 | Air service |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | SV-61311_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO22 | C4S04,22 | 1756-OB32-22 |  |  | DO | C4 | 4 | 22 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S04,23 | 1756-OB32-23 | X2 | C4S04-X2 | XS-61301A_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XS-61301A | 0 | 1st | 325-01-613-PD-02 | - | Filter plant in operation |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-61301A_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO23 | C4S04,23 | 1756-OB32-23 |  |  | DO | C4 | 4 | 23 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S04,24 | 1756-OB32-24 | X2 | C4S04-X2 | XS-61301B_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XS-61301B | 0 | 1st | 325-01-613-PD-02 | - | Material transport in operation |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-61301B_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO24 | C4S04,24 | 1756-OB32-24 |  |  | DO | C4 | 4 | 24 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S04,25 | 1756-OB32-25 | X2 | C4S04-X2 | XS-61301C_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XS-61301C | 0 | 1st | 325-01-613-PD-02 | - | Belt plant in operation |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-61301C_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO25 | C4S04,25 | 1756-OB32-25 |  |  | DO | C4 | 4 | 25 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S04,26 | 1756-OB32-26 | X2 | C4S04-X2 | XS-61301D_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XS-61301D | 0 | 1st | 325-01-613-PD-02 | - | Sequence Stop |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-61301D_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO26 | C4S04,26 | 1756-OB32-26 |  |  | DO | C4 | 4 | 26 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S04,27 | 1756-OB32-27 | X2 | C4S04-X2 | XS-61301E_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XS-61301E | 0 | 1st | 325-01-613-PD-02 | - | Status from Customer Emergency stop |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-61301E_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO27 | C4S04,27 | 1756-OB32-27 |  |  | DO | C4 | 4 | 27 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S04,28 | 1756-OB32-28 | X2 | C4S04-X2 | XS-61301F_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XS-61301F | 0 | 1st | 325-01-613-PD-02 | - | Operation Release |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-61301F_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO28 | C4S04,28 | 1756-OB32-28 |  |  | DO | C4 | 4 | 28 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S04,29 | 1756-OB32-29 | X2 | C4S04-X2 | XV-61302_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XV-61302 | 0 | 2nd | 325-01-613-PD-02 | 3-25-01-613-PD-02 | Dust collector feed vent |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-61302_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO29 | C4S04,29 | 1756-OB32-29 |  |  | DO | C4 | 4 | 29 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S04,30 | 1756-OB32-30 | X2 | C4S04-X2 | XV-61303_DO_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | XV-61303 | 0 | 2nd | 325-01-613-PD-02 | 3-25-01-613-PD-02 | Dust collector feed from packer |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-61303_DO_1 | DO | 2 | 1 | C4S04 | C4S04DO30 | C4S04,30 | 1756-OB32-30 |  |  | DO | C4 | 4 | 30 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M4 | JB-612 | C4S04,31 | 1756-OB32-31 | X2 | C4S04-X2 | Spare_DO_0 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | Spare | [6 empty] | Require I/O DI= ,DO=,AI=,AO=,Bus= |  | Spare_DO_0 | DO | 2 | 0 | C4S04 | C4S04DO31 | C4S04,31 | 1756-OB32-31 |  |  | DO | C4 | 4 | 31
=CA1+MCP-M4 | JB-606 | C4S05,00 | 1756-IF16-0 | X1 | C4S05-X1 | DPT-60201_AI_1 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | DPT-60201 | Differential Pressure Transmitte | 6th | 325-01-600-PD-09 | 3-25-01-602-PD-09 | Steam filter pressure |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | DPT-60201_AI_1 | AI | 3 | 1 | C4S05 | C4S05AI00 | C4S05,00 | 1756-IF16-0 |  |  | AI | C4 | 5 | 0 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | JB-606 | C4S05,01 | 1756-IF16-1 | X1 | C4S05-X1 | FT-60203_AI_1 |  | Spray Dryer 6th Floor | JB-606 | Spray Dryer | FT-60203 | 0 | 6th | 325-01-600-PD-09 | 3-25-01-602-PD-09 | Culinary steam feed to Spray dryer |  | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0 |  | FT-60203_AI_1 | AI | 3 | 1 | C4S05 | C4S05AI01 | C4S05,01 | 1756-IF16-1 |  |  | AI | C4 | 5 | 1 |  | 1 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | JB-608 | C4S05,02 | 1756-IF16-2 | X1 | C4S05-X1 | TT-60245_AI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | TT-60245 | 0 | 8th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Stack (DTXS-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-60245_AI_1 | AI | 3 | 1 | C4S05 | C4S05AI02 | C4S05,02 | 1756-IF16-2 |  |  | AI | C4 | 5 | 2 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | JB-608 | C4S05,03 | 1756-IF16-3 | X1 | C4S05-X1 | Spare_AI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI03 | C4S05,03 | 1756-IF16-3 |  |  | AI | C4 | 5 | 3 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-608 | C4S05,04 | 1756-IF16-4 | X1 | C4S05-X1 | Spare_AI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI04 | C4S05,04 | 1756-IF16-4 |  |  | AI | C4 | 5 | 4 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-608 | C4S05,05 | 1756-IF16-5 | X1 | C4S05-X1 | Spare_AI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI05 | C4S05,05 | 1756-IF16-5 |  |  | AI | C4 | 5 | 5 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-608 | C4S05,06 | 1756-IF16-6 | X1 | C4S05-X1 | Spare_AI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI06 | C4S05,06 | 1756-IF16-6 |  |  | AI | C4 | 5 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 | C4S05,06 | 1756-IF16-6 | X1 | C4S05-X1 | Spare_AI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI06 | C4S05,06 | 1756-IF16-6 |  |  | AI | C4 | 5 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-608 | C4S05,07 | 1756-IF16-7 | X1 | C4S05-X1 | Spare_AI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI07 | C4S05,07 | 1756-IF16-7 |  |  | AI | C4 | 5 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 | C4S05,07 | 1756-IF16-7 | X1 | C4S05-X1 | Spare_AI_0 |  | Spray Dryer 8th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI07 | C4S05,07 | 1756-IF16-7 |  |  | AI | C4 | 5 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S05,08 | 1756-IF16-8 | X1 | C4S05-X1 | PT-61302_AI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | PT-61302 | Pressure Transmitter | 2nd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Pressure in vacuum line |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-61302_AI_1 | AI | 3 | 1 | C4S05 | C4S05AI08 | C4S05,08 | 1756-IF16-8 |  |  | AI | C4 | 5 | 8 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | JB-612 | C4S05,09 | 1756-IF16-9 | X1 | C4S05-X1 | PT-61309_AI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | PT-61309 | Pressure Transmitter | 1st | 325-01-613-PD-04 | 3-25-01-613-PD-04 | Pressure transmitter |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-61309_AI_1 | AI | 3 | 1 | C4S05 | C4S05AI09 | C4S05,09 | 1756-IF16-9 |  |  | AI | C4 | 5 | 9 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | JB-612 | C4S05,10 | 1756-IF16-10 | X1 | C4S05-X1 | Spare_AI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI10 | C4S05,10 | 1756-IF16-10 |  |  | AI | C4 | 5 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S05,11 | 1756-IF16-11 | X1 | C4S05-X1 | Spare_AI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI11 | C4S05,11 | 1756-IF16-11 |  |  | AI | C4 | 5 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S05,12 | 1756-IF16-12 | X1 | C4S05-X1 | PT-61302_AI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | PT-61302 | Pressure Transmitter | 2nd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Pressure in vacuum line |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-61302_AI_1 | AI | 3 | 1 | C4S05 | C4S05AI12 | C4S05,12 | 1756-IF16-12 |  |  | AI | C4 | 5 | 12 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | JB-612 | C4S05,13 | 1756-IF16-13 | X1 | C4S05-X1 | PT-61309_AI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | PT-61309 | Pressure Transmitter | 1st | 325-01-613-PD-04 | 3-25-01-613-PD-04 | Pressure transmitter |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-61309_AI_1 | AI | 3 | 1 | C4S05 | C4S05AI13 | C4S05,13 | 1756-IF16-13 |  |  | AI | C4 | 5 | 13 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | JB-612 | C4S05,14 | 1756-IF16-14 | X1 | C4S05-X1 | Spare_AI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI14 | C4S05,14 | 1756-IF16-14 |  |  | AI | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S05,14 | 1756-IF16-14 | X1 | C4S05-X1 | Spare_AI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI14 | C4S05,14 | 1756-IF16-14 |  |  | AI | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S05,14 | 1756-IF16-14 | X1 | C4S05-X1 | Spare_AI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI14 | C4S05,14 | 1756-IF16-14 |  |  | AI | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S05,14 | 1756-IF16-14 | X1 | C4S05-X1 | Spare_AI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI14 | C4S05,14 | 1756-IF16-14 |  |  | AI | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S05,14 | 1756-IF16-14 | X1 | C4S05-X1 | Spare_AI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI14 | C4S05,14 | 1756-IF16-14 |  |  | AI | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S05,14 | 1756-IF16-14 | X1 | C4S05-X1 | Spare_AI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI14 | C4S05,14 | 1756-IF16-14 |  |  | AI | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S05,14 | 1756-IF16-14 | X1 | C4S05-X1 | Spare_AI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI14 | C4S05,14 | 1756-IF16-14 |  |  | AI | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S05,14 | 1756-IF16-14 | X1 | C4S05-X1 | Spare_AI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI14 | C4S05,14 | 1756-IF16-14 |  |  | AI | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 | C4S05,14 | 1756-IF16-14 | X1 | C4S05-X1 | Spare_AI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI14 | C4S05,14 | 1756-IF16-14 |  |  | AI | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-612 | C4S05,15 | 1756-IF16-15 | X1 | C4S05-X1 | Spare_AI_0 |  | Packing Tower 2th Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C4S05 | C4S05AI15 | C4S05,15 | 1756-IF16-15 |  |  | AI | C4 | 5 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 | C4S06,00 | 1756-IF16-0 | X1 | C4S06-X1 | PT-60220_AI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | PT-60220 | Pressure Transmitter | 6th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas Pressure Transmitter for Chamber (CHAM-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-60220_AI_1 | AI | 3 | 1 | C4S06 | C4S06AI00 | C4S06,00 | 1756-IF16-0 |  |  | AI | C4 | 6 | 0 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | IS-JB-608 | C4S06,01 | 1756-IF16-1 | X1 | C4S06-X1 | TT-60220_AI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | TT-60220 | 0 | 6th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-60220_AI_1 | AI | 3 | 1 | C4S06 | C4S06AI01 | C4S06,01 | 1756-IF16-1 |  |  | AI | C4 | 6 | 1 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | IS-JB-608 | C4S06,02 | 1756-IF16-2 | X1 | C4S06-X1 | TT-60221_AI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | TT-60221 | 0 | 6th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-60221_AI_1 | AI | 3 | 1 | C4S06 | C4S06AI02 | C4S06,02 | 1756-IF16-2 |  |  | AI | C4 | 6 | 2 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | IS-JB-608 | C4S06,03 | 1756-IF16-3 | X1 | C4S06-X1 | TT-60222_AI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | TT-60222 | 0 | 5th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-60222_AI_1 | AI | 3 | 1 | C4S06 | C4S06AI03 | C4S06,03 | 1756-IF16-3 |  |  | AI | C4 | 6 | 3 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | IS-JB-608 | C4S06,04 | 1756-IF16-4 | X1 | C4S06-X1 | TT-60223_AI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | TT-60223 | 0 | 5th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | TT-60223_AI_1 | AI | 3 | 1 | C4S06 | C4S06AI04 | C4S06,04 | 1756-IF16-4 |  |  | AI | C4 | 6 | 4 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | IS-JB-608 | C4S06,05 | 1756-IF16-5 | X1 | C4S06-X1 | XT-60201_AI_1 |  | Spray Dryer 8th Floor | JB-608 | Spray Dryer | XT-60201 | 0 | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | LEL gas analyzer |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | XT-60201_AI_1 | AI | 3 | 1 | C4S06 | C4S06AI05 | C4S06,05 | 1756-IF16-5 |  |  | AI | C4 | 6 | 5 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | IS-JB-612 | C4S06,06 | 1756-IF16-6 | X1 | C4S06-X1 | DPT-61310_AI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | DPT-61310 | Differential Pressure Transmitte | 2nd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Vent filter pressure |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | DPT-61310_AI_1 | AI | 3 | 1 | C4S06 | C4S06AI06 | C4S06,06 | 1756-IF16-6 |  |  | AI | C4 | 6 | 6 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M4 | IS-JB-612 | C4S06,07 | 1756-IF16-7 | X1 | C4S06-X1 | DPT-61312_AI_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | DPT-61312 |  | 2nd | 325-01-613-PD-05 | 3-25-01-613-PD-05 |  |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | DPT-61312_AI_1 | AI | 3 | 1 | C4S06 | C4S06AI07 | C4S06,07 | 1756-IF16-7 |  |  | AI | C4 | 6 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S01,00 | 1756-IB32-0 | X1 | C5S01-X1 | FS-20201_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | FS-20201 |  | 1st | - | 3-25-01-202-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | FS-20201_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI00 | C5S01,00 | 1756-IB32-0 |  |  | DI | C5 | 1 | 0 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S01,01 | 1756-IB32-1 | X1 | C5S01-X1 | FT-913201_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | FT-913201 | 0 | 1st | 325-01-803-PD-02 | 3-25-01-913-PD-02 | Flow outlet LPG line |  | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0 |  | FT-913201_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI01 | C5S01,01 | 1756-IB32-1 |  |  | DI | C5 | 1 | 1 |  | 1 | 0 | 2 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M5 | RIO-200 | C5S01,02 | 1756-IB32-2 | X1 | C5S01-X1 | FT-936201_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Process Water | FT-936201 | 0 | 1st | 325-01-930-PD-01 | 3-25-01-930-PD-08 | Process Water |  | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0 |  | FT-936201_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI02 | C5S01,02 | 1756-IB32-2 |  |  | DI | C5 | 1 | 2 |  | 1 | 0 | 1 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M5 | RIO-200 | C5S01,03 | 1756-IB32-3 | X1 | C5S01-X1 | FT-936202_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Process Water | FT-936202 | 0 | 1st | 325-01-930-PD-02 | 3-25-01-930-PD-07 | Process Water |  | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0 |  | FT-936202_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI03 | C5S01,03 | 1756-IB32-3 |  |  | DI | C5 | 1 | 3 |  | 1 | 0 | 1 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M5 | RIO-200 | C5S01,04 | 1756-IB32-4 | X1 | C5S01-X1 | LSL-814201_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | CIP Water System | LSL-814201 | 0 | 1st | - | 3-25-01-814-PD-01 | Low Level alarm |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | LSL-814201_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI04 | C5S01,04 | 1756-IB32-4 |  |  | DI | C5 | 1 | 4 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,05 | 1756-IB32-5 | X1 | C5S01-X1 | PK-913201_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | PK-913201 |  | 1st | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PK-913201_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI05 | C5S01,05 | 1756-IB32-5 |  |  | DI | C5 | 1 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S01,06 | 1756-IB32-6 | X1 | C5S01-X1 | PK-913202_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | PK-913202 |  | 1st | - | - |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | PK-913202_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI06 | C5S01,06 | 1756-IB32-6 |  |  | DI | C5 | 1 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S01,07 | 1756-IB32-7 | X1 | C5S01-X1 | HV-20204_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | HV-20204 | Manual Valve With Position Switch | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Drain line |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HV-20204_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI07 | C5S01,07 | 1756-IB32-7 |  |  | DI | C5 | 1 | 7 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,08 | 1756-IB32-8 | X1 | C5S01-X1 | HV-20205_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | HV-20205 | Manual Valve With Position Switch | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Drain line |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HV-20205_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI08 | C5S01,08 | 1756-IB32-8 |  |  | DI | C5 | 1 | 8 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,09 | 1756-IB32-9 | X1 | C5S01-X1 | HV-20206_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | HV-20206 | Manual Valve With Position Switch | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Drain line |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HV-20206_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI09 | C5S01,09 | 1756-IB32-9 |  |  | DI | C5 | 1 | 9 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,10 | 1756-IB32-10 | X1 | C5S01-X1 | HV-20207_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | HV-20207 | Manual Valve With Position Switch | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Drain line |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HV-20207_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI10 | C5S01,10 | 1756-IB32-10 |  |  | DI | C5 | 1 | 10 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,11 | 1756-IB32-11 | X1 | C5S01-X1 | HV-20208_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | HV-20208 | Manual Valve With Position Switch | 1st | 325-01-200-PD-02 | 3-25-01-202-PD-02 | Slurry Drain line |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HV-20208_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI11 | C5S01,11 | 1756-IB32-11 |  |  | DI | C5 | 1 | 11 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,12 | 1756-IB32-12 | X1 | C5S01-X1 | HV-20209_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | HV-20209 | Manual Valve With Position Switch | 1st | 325-01-200-PD-02 | 3-25-01-202-PD-02 | Slurry Drain line |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HV-20209_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI12 | C5S01,12 | 1756-IB32-12 |  |  | DI | C5 | 1 | 12 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,13 | 1756-IB32-13 | X1 | C5S01-X1 | HV-20210_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | HV-20210 | Manual Valve With Position Switch | 1st | 325-01-200-PD-02 | 3-25-01-202-PD-02 | Slurry Drain line |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HV-20210_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI13 | C5S01,13 | 1756-IB32-13 |  |  | DI | C5 | 1 | 13 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,14 | 1756-IB32-14 | X1 | C5S01-X1 | XA-80305A_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XA-80305A | 0 | 1st | 325-01-803-PD-02 | - | Gas Vaporizer 5 control status |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-80305A_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI14 | C5S01,14 | 1756-IB32-14 |  |  | DI | C5 | 1 | 14 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,15 | 1756-IB32-15 | X1 | C5S01-X1 | XA-80305B_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XA-80305B | 0 | 1st | 325-01-803-PD-02 | - | Gas Vaporizer 5 control status |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-80305B_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI15 | C5S01,15 | 1756-IB32-15 |  |  | DI | C5 | 1 | 15 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,16 | 1756-IB32-16 | X2 | C5S01-X2 | XA-80305C_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XA-80305C | 0 | 1st | 325-01-803-PD-02 | - | Gas Vaporizer 5 control status |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-80305C_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI16 | C5S01,16 | 1756-IB32-16 |  |  | DI | C5 | 1 | 16 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,17 | 1756-IB32-17 | X2 | C5S01-X2 | XA-80305D_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XA-80305D | 0 | 1st | 325-01-803-PD-02 | - | Gas Vaporizer 5 control status |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-80305D_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI17 | C5S01,17 | 1756-IB32-17 |  |  | DI | C5 | 1 | 17 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,18 | 1756-IB32-18 | X2 | C5S01-X2 | XA-80305E_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XA-80305E | 0 | 1st | 325-01-803-PD-02 | - | Gas Vaporizer 5 control status |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-80305E_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI18 | C5S01,18 | 1756-IB32-18 |  |  | DI | C5 | 1 | 18 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,19 | 1756-IB32-19 | X2 | C5S01-X2 | XA-80305F_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XA-80305F | 0 | 1st | 325-01-803-PD-02 | - | Gas Vaporizer 5 control status |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-80305F_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI19 | C5S01,19 | 1756-IB32-19 |  |  | DI | C5 | 1 | 19 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,20 | 1756-IB32-20 | X2 | C5S01-X2 | XA-80306A_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XA-80306A | 0 | 1st | 325-01-803-PD-02 | - | Gas Vaporizer 6 control status |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-80306A_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI20 | C5S01,20 | 1756-IB32-20 |  |  | DI | C5 | 1 | 20 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,21 | 1756-IB32-21 | X2 | C5S01-X2 | XA-80306B_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XA-80306B | 0 | 1st | 325-01-803-PD-02 | - | Gas Vaporizer 6 control status |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-80306B_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI21 | C5S01,21 | 1756-IB32-21 |  |  | DI | C5 | 1 | 21 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,22 | 1756-IB32-22 | X2 | C5S01-X2 | XA-80306C_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XA-80306C | 0 | 1st | 325-01-803-PD-02 | - | Gas Vaporizer 6 control status |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-80306C_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI22 | C5S01,22 | 1756-IB32-22 |  |  | DI | C5 | 1 | 22 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,23 | 1756-IB32-23 | X2 | C5S01-X2 | XA-80306D_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XA-80306D | 0 | 1st | 325-01-803-PD-02 | - | Gas Vaporizer 6 control status |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-80306D_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI23 | C5S01,23 | 1756-IB32-23 |  |  | DI | C5 | 1 | 23 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,24 | 1756-IB32-24 | X2 | C5S01-X2 | XA-80306E_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XA-80306E | 0 | 1st | 325-01-803-PD-02 | - | Gas Vaporizer 6 control status |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-80306E_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI24 | C5S01,24 | 1756-IB32-24 |  |  | DI | C5 | 1 | 24 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,25 | 1756-IB32-25 | X2 | C5S01-X2 | XA-80306F_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XA-80306F | 0 | 1st | 325-01-803-PD-02 | - | Gas Vaporizer 6 control status |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | XA-80306F_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI25 | C5S01,25 | 1756-IB32-25 |  |  | DI | C5 | 1 | 25 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
=CA1+MCP-M5 | RIO-200 | C5S01,26 | 1756-IB32-26 | X2 | C5S01-X2 | XV-20201_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20201 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20201_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI26 | C5S01,26 | 1756-IB32-26 |  |  | DI | C5 | 1 | 26 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S01,27 | 1756-IB32-27 | X2 | C5S01-X2 | XV-20201_DI_2 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20201 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20201_DI_2 | DI | 1 | 2 | C5S01 | C5S01DI27 | C5S01,27 | 1756-IB32-27 |  |  | DI | C5 | 1 | 27 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S01,28 | 1756-IB32-28 | X2 | C5S01-X2 | XV-20202_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20202 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20202_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI28 | C5S01,28 | 1756-IB32-28 |  |  | DI | C5 | 1 | 28 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S01,29 | 1756-IB32-29 | X2 | C5S01-X2 | XV-20202_DI_2 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20202 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20202_DI_2 | DI | 1 | 2 | C5S01 | C5S01DI29 | C5S01,29 | 1756-IB32-29 |  |  | DI | C5 | 1 | 29 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S01,30 | 1756-IB32-30 | X2 | C5S01-X2 | XV-20203_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20203 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20203_DI_1 | DI | 1 | 1 | C5S01 | C5S01DI30 | C5S01,30 | 1756-IB32-30 |  |  | DI | C5 | 1 | 30 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S01,31 | 1756-IB32-31 | X2 | C5S01-X2 | XV-20203_DI_2 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20203 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20203_DI_2 | DI | 1 | 2 | C5S01 | C5S01DI31 | C5S01,31 | 1756-IB32-31 |  |  | DI | C5 | 1 | 31 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S02,00 | 1756-IB32-0 | X1 | C5S02-X1 | XV-20211_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20211 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20211_DI_1 | DI | 1 | 1 | C5S02 | C5S02DI00 | C5S02,00 | 1756-IB32-0 |  |  | DI | C5 | 2 | 0 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S02,01 | 1756-IB32-1 | X1 | C5S02-X1 | XV-20211_DI_2 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20211 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20211_DI_2 | DI | 1 | 2 | C5S02 | C5S02DI01 | C5S02,01 | 1756-IB32-1 |  |  | DI | C5 | 2 | 1 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S02,02 | 1756-IB32-2 | X1 | C5S02-X1 | XV-20212_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20212 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20212_DI_1 | DI | 1 | 1 | C5S02 | C5S02DI02 | C5S02,02 | 1756-IB32-2 |  |  | DI | C5 | 2 | 2 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S02,03 | 1756-IB32-3 | X1 | C5S02-X1 | XV-20212_DI_2 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20212 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20212_DI_2 | DI | 1 | 2 | C5S02 | C5S02DI03 | C5S02,03 | 1756-IB32-3 |  |  | DI | C5 | 2 | 3 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S02,04 | 1756-IB32-4 | X1 | C5S02-X1 | XV-20213_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20213 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20213_DI_1 | DI | 1 | 1 | C5S02 | C5S02DI04 | C5S02,04 | 1756-IB32-4 |  |  | DI | C5 | 2 | 4 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S02,05 | 1756-IB32-5 | X1 | C5S02-X1 | XV-20213_DI_2 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20213 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20213_DI_2 | DI | 1 | 2 | C5S02 | C5S02DI05 | C5S02,05 | 1756-IB32-5 |  |  | DI | C5 | 2 | 5 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S02,06 | 1756-IB32-6 | X1 | C5S02-X1 | XV-913201_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XV-913201 | 0 | 1st | - | 3-25-01-913-PD-02 | Outlet LPG line |  | Require I/O DI= 2,DO=1,AI=1,AO=0,Bus=0 |  | XV-913201_DI_1 | DI | 1 | 1 | C5S02 | C5S02DI06 | C5S02,06 | 1756-IB32-6 |  |  | DI | C5 | 2 | 6 |  | 2 | 1 | 1 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S02,07 | 1756-IB32-7 | X1 | C5S02-X1 | XV-913201_DI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XV-913201 | 0 | 1st | - | 3-25-01-913-PD-02 | Outlet LPG line |  | Require I/O DI= 2,DO=1,AI=1,AO=0,Bus=0 |  | XV-913201_DI_1 | DI | 1 | 1 | C5S02 | C5S02DI07 | C5S02,07 | 1756-IB32-7 |  |  | DI | C5 | 2 | 7 |  | 2 | 1 | 1 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S02,08 | 1756-IB32-8 | X1 | C5S02-X1 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI08 | C5S02,08 | 1756-IB32-8 |  |  | DI | C5 | 2 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,09 | 1756-IB32-9 | X1 | C5S02-X1 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI09 | C5S02,09 | 1756-IB32-9 |  |  | DI | C5 | 2 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,10 | 1756-IB32-10 | X1 | C5S02-X1 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI10 | C5S02,10 | 1756-IB32-10 |  |  | DI | C5 | 2 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,11 | 1756-IB32-11 | X1 | C5S02-X1 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI11 | C5S02,11 | 1756-IB32-11 |  |  | DI | C5 | 2 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,12 | 1756-IB32-12 | X1 | C5S02-X1 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI12 | C5S02,12 | 1756-IB32-12 |  |  | DI | C5 | 2 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,13 | 1756-IB32-13 | X1 | C5S02-X1 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI13 | C5S02,13 | 1756-IB32-13 |  |  | DI | C5 | 2 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,14 | 1756-IB32-14 | X1 | C5S02-X1 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI14 | C5S02,14 | 1756-IB32-14 |  |  | DI | C5 | 2 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,15 | 1756-IB32-15 | X1 | C5S02-X1 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI15 | C5S02,15 | 1756-IB32-15 |  |  | DI | C5 | 2 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,16 | 1756-IB32-16 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI16 | C5S02,16 | 1756-IB32-16 |  |  | DI | C5 | 2 | 16 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,17 | 1756-IB32-17 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI17 | C5S02,17 | 1756-IB32-17 |  |  | DI | C5 | 2 | 17 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,18 | 1756-IB32-18 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI18 | C5S02,18 | 1756-IB32-18 |  |  | DI | C5 | 2 | 18 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,19 | 1756-IB32-19 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI19 | C5S02,19 | 1756-IB32-19 |  |  | DI | C5 | 2 | 19 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,20 | 1756-IB32-20 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI20 | C5S02,20 | 1756-IB32-20 |  |  | DI | C5 | 2 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,21 | 1756-IB32-21 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI21 | C5S02,21 | 1756-IB32-21 |  |  | DI | C5 | 2 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,22 | 1756-IB32-22 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI22 | C5S02,22 | 1756-IB32-22 |  |  | DI | C5 | 2 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,23 | 1756-IB32-23 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI23 | C5S02,23 | 1756-IB32-23 |  |  | DI | C5 | 2 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,24 | 1756-IB32-24 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI24 | C5S02,24 | 1756-IB32-24 |  |  | DI | C5 | 2 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,25 | 1756-IB32-25 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI25 | C5S02,25 | 1756-IB32-25 |  |  | DI | C5 | 2 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,26 | 1756-IB32-26 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI26 | C5S02,26 | 1756-IB32-26 |  |  | DI | C5 | 2 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,27 | 1756-IB32-27 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI27 | C5S02,27 | 1756-IB32-27 |  |  | DI | C5 | 2 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,28 | 1756-IB32-28 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI28 | C5S02,28 | 1756-IB32-28 |  |  | DI | C5 | 2 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,29 | 1756-IB32-29 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI29 | C5S02,29 | 1756-IB32-29 |  |  | DI | C5 | 2 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,30 | 1756-IB32-30 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI30 | C5S02,30 | 1756-IB32-30 |  |  | DI | C5 | 2 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S02,31 | 1756-IB32-31 | X2 | C5S02-X2 | Spare_DI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C5S02 | C5S02DI31 | C5S02,31 | 1756-IB32-31 |  |  | DI | C5 | 2 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,00 | 1756-OB32-0 | X1 | C5S03-X1 | XA-92201_DO_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Boiler System | XA-92201 | 0 | 1st | 325-01-923-PD-03 | 3-25-01-922-PD-03 | LEL gas Buzzer Alarm |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XA-92201_DO_1 | DO | 2 | 1 | C5S03 | C5S03DO00 | C5S03,00 | 1756-OB32-0 |  |  | DO | C5 | 3 | 0 |  | 0 | 1 | 0 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M5 | RIO-200 | C5S03,01 | 1756-OB32-1 | X1 | C5S03-X1 | XV-20201_DO_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20201 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20201_DO_1 | DO | 2 | 1 | C5S03 | C5S03DO01 | C5S03,01 | 1756-OB32-1 |  |  | DO | C5 | 3 | 1 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S03,02 | 1756-OB32-2 | X1 | C5S03-X1 | XV-20202_DO_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20202 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20202_DO_1 | DO | 2 | 1 | C5S03 | C5S03DO02 | C5S03,02 | 1756-OB32-2 |  |  | DO | C5 | 3 | 2 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S03,03 | 1756-OB32-3 | X1 | C5S03-X1 | XV-20203_DO_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20203 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 1 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20203_DO_1 | DO | 2 | 1 | C5S03 | C5S03DO03 | C5S03,03 | 1756-OB32-3 |  |  | DO | C5 | 3 | 3 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S03,04 | 1756-OB32-4 | X1 | C5S03-X1 | XV-20211_DO_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20211 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20211_DO_1 | DO | 2 | 1 | C5S03 | C5S03DO04 | C5S03,04 | 1756-OB32-4 |  |  | DO | C5 | 3 | 4 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S03,05 | 1756-OB32-5 | X1 | C5S03-X1 | XV-20212_DO_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20212 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20212_DO_1 | DO | 2 | 1 | C5S03 | C5S03DO05 | C5S03,05 | 1756-OB32-5 |  |  | DO | C5 | 3 | 5 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S03,06 | 1756-OB32-6 | X1 | C5S03-X1 | XV-20213_DO_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Slurry - Out Building | XV-20213 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Slurry Preparation Tank 2 |  | Require I/O DI= 2,DO=1,AI=0,AO=0,Bus=0 | xx | XV-20213_DO_1 | DO | 2 | 1 | C5S03 | C5S03DO06 | C5S03,06 | 1756-OB32-6 |  |  | DO | C5 | 3 | 6 |  | 2 | 1 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S03,07 | 1756-OB32-7 | X1 | C5S03-X1 | XV-913201_DO_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XV-913201 | 0 | 1st | - | 3-25-01-913-PD-02 | Outlet LPG line |  | Require I/O DI= 2,DO=1,AI=1,AO=0,Bus=0 |  | XV-913201_DO_1 | DO | 2 | 1 | C5S03 | C5S03DO07 | C5S03,07 | 1756-OB32-7 |  |  | DO | C5 | 3 | 7 |  | 2 | 1 | 1 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S03,08 | 1756-OB32-8 | X1 | C5S03-X1 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO08 | C5S03,08 | 1756-OB32-8 |  |  | DO | C5 | 3 | 8 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,09 | 1756-OB32-9 | X1 | C5S03-X1 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO09 | C5S03,09 | 1756-OB32-9 |  |  | DO | C5 | 3 | 9 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,10 | 1756-OB32-10 | X1 | C5S03-X1 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO10 | C5S03,10 | 1756-OB32-10 |  |  | DO | C5 | 3 | 10 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,11 | 1756-OB32-11 | X1 | C5S03-X1 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO11 | C5S03,11 | 1756-OB32-11 |  |  | DO | C5 | 3 | 11 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,12 | 1756-OB32-12 | X1 | C5S03-X1 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO12 | C5S03,12 | 1756-OB32-12 |  |  | DO | C5 | 3 | 12 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,13 | 1756-OB32-13 | X1 | C5S03-X1 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO13 | C5S03,13 | 1756-OB32-13 |  |  | DO | C5 | 3 | 13 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,14 | 1756-OB32-14 | X1 | C5S03-X1 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO14 | C5S03,14 | 1756-OB32-14 |  |  | DO | C5 | 3 | 14 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,15 | 1756-OB32-15 | X1 | C5S03-X1 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO15 | C5S03,15 | 1756-OB32-15 |  |  | DO | C5 | 3 | 15 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,16 | 1756-OB32-16 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO16 | C5S03,16 | 1756-OB32-16 |  |  | DO | C5 | 3 | 16 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,17 | 1756-OB32-17 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO17 | C5S03,17 | 1756-OB32-17 |  |  | DO | C5 | 3 | 17 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,18 | 1756-OB32-18 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO18 | C5S03,18 | 1756-OB32-18 |  |  | DO | C5 | 3 | 18 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,19 | 1756-OB32-19 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO19 | C5S03,19 | 1756-OB32-19 |  |  | DO | C5 | 3 | 19 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,20 | 1756-OB32-20 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO20 | C5S03,20 | 1756-OB32-20 |  |  | DO | C5 | 3 | 20 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,21 | 1756-OB32-21 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO21 | C5S03,21 | 1756-OB32-21 |  |  | DO | C5 | 3 | 21 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,22 | 1756-OB32-22 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO22 | C5S03,22 | 1756-OB32-22 |  |  | DO | C5 | 3 | 22 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,23 | 1756-OB32-23 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO23 | C5S03,23 | 1756-OB32-23 |  |  | DO | C5 | 3 | 23 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,24 | 1756-OB32-24 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO24 | C5S03,24 | 1756-OB32-24 |  |  | DO | C5 | 3 | 24 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,25 | 1756-OB32-25 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO25 | C5S03,25 | 1756-OB32-25 |  |  | DO | C5 | 3 | 25 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,26 | 1756-OB32-26 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO26 | C5S03,26 | 1756-OB32-26 |  |  | DO | C5 | 3 | 26 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,27 | 1756-OB32-27 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO27 | C5S03,27 | 1756-OB32-27 |  |  | DO | C5 | 3 | 27 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,28 | 1756-OB32-28 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO28 | C5S03,28 | 1756-OB32-28 |  |  | DO | C5 | 3 | 28 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,29 | 1756-OB32-29 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO29 | C5S03,29 | 1756-OB32-29 |  |  | DO | C5 | 3 | 29 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,30 | 1756-OB32-30 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO30 | C5S03,30 | 1756-OB32-30 |  |  | DO | C5 | 3 | 30 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S03,31 | 1756-OB32-31 | X2 | C5S03-X2 | Spare_DO_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C5S03 | C5S03DO31 | C5S03,31 | 1756-OB32-31 |  |  | DO | C5 | 3 | 31 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S04,00 | 1756-IF16-0 | X1 | C5S04-X1 | EXT-BIILER_AI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Boiler System | EXT-BIILER |  | 1st |  | External Remote Setpoint |  |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | EXT-BIILER_AI_1 | AI | 3 | 1 | C5S04 | C5S04AI00 | C5S04,00 | 1756-IF16-0 |  |  | AI | C5 | 4 | 0 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S04,01 | 1756-IF16-1 | X1 | C5S04-X1 | FT-913201_AI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | FT-913201 | 0 | 1st | 325-01-803-PD-02 | 3-25-01-913-PD-02 | Flow outlet LPG line |  | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0 |  | FT-913201_AI_1 | AI | 3 | 1 | C5S04 | C5S04AI01 | C5S04,01 | 1756-IF16-1 |  |  | AI | C5 | 4 | 1 |  | 1 | 0 | 2 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M5 | RIO-200 | C5S04,02 | 1756-IF16-2 | X1 | C5S04-X1 | FT-913201_AI_2 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | FT-913201 | 0 | 1st | 325-01-803-PD-02 | 3-25-01-913-PD-02 | Flow outlet LPG line |  | Require I/O DI= 1,DO=0,AI=2,AO=0,Bus=0 |  | FT-913201_AI_2 | AI | 3 | 2 | C5S04 | C5S04AI02 | C5S04,02 | 1756-IF16-2 |  |  | AI | C5 | 4 | 2 |  | 1 | 0 | 2 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M5 | RIO-200 | C5S04,03 | 1756-IF16-3 | X1 | C5S04-X1 | FT-936201_AI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Process Water | FT-936201 | 0 | 1st | 325-01-930-PD-01 | 3-25-01-930-PD-08 | Process Water |  | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0 |  | FT-936201_AI_1 | AI | 3 | 1 | C5S04 | C5S04AI03 | C5S04,03 | 1756-IF16-3 |  |  | AI | C5 | 4 | 3 |  | 1 | 0 | 1 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M5 | RIO-200 | C5S04,04 | 1756-IF16-4 | X1 | C5S04-X1 | FT-936202_AI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Process Water | FT-936202 | 0 | 1st | 325-01-930-PD-02 | 3-25-01-930-PD-07 | Process Water |  | Require I/O DI= 1,DO=0,AI=1,AO=0,Bus=0 |  | FT-936202_AI_1 | AI | 3 | 1 | C5S04 | C5S04AI04 | C5S04,04 | 1756-IF16-4 |  |  | AI | C5 | 4 | 4 |  | 1 | 0 | 1 | 0 | 0 |  | 4 - 20 mA,Pulse
=CA1+MCP-M5 | RIO-200 | C5S04,05 | 1756-IF16-5 | X1 | C5S04-X1 | LT-913201_AI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | LT-913201 | Level Transmitter | 1st | 325-01-803-PD-01 | 3-25-01-913-PD-01 | Level LPG in storage |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | LT-913201_AI_1 | AI | 3 | 1 | C5S04 | C5S04AI05 | C5S04,05 | 1756-IF16-5 |  |  | AI | C5 | 4 | 5 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M5 | RIO-200 | C5S04,06 | 1756-IF16-6 | X1 | C5S04-X1 | PT-913201_AI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | PT-913201 | Pressure Transmitter | 1st | 325-01-803-PD-02 | 3-25-01-913-PD-02 | Pressure outlet LPG line |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | PT-913201_AI_1 | AI | 3 | 1 | C5S04 | C5S04AI06 | C5S04,06 | 1756-IF16-6 |  |  | AI | C5 | 4 | 6 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M5 | RIO-200 | C5S04,07 | 1756-IF16-7 | X1 | C5S04-X1 | XT-92201_AI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | Boiler System | XT-92201 | 0 | 1st | 325-01-923-PD-03 | 3-25-01-922-PD-03 | LEL gas analyzer |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | XT-92201_AI_1 | AI | 3 | 1 | C5S04 | C5S04AI07 | C5S04,07 | 1756-IF16-7 |  |  | AI | C5 | 4 | 7 |  | 0 | 0 | 1 | 0 | 0 |  | 4 - 20 mA
=CA1+MCP-M5 | RIO-200 | C5S04,08 | 1756-IF16-8 | X1 | C5S04-X1 | XV-913201_AI_1 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | XV-913201 | 0 | 1st | - | 3-25-01-913-PD-02 | Outlet LPG line |  | Require I/O DI= 0,DO=0,AI=0,AO=0,Bus=0 |  | XV-913201_AI_1 | AI | 3 | 1 | C5S04 | C5S04AI08 | C5S04,08 | 1756-IF16-8 |  |  | AI | C5 | 4 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 24 VDC energized
=CA1+MCP-M5 | RIO-200 | C5S04,09 | 1756-IF16-9 | X1 | C5S04-X1 | Spare_AI_0 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | Spare |  | 1st | - | 3-25-01-913-PD-02 |  |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C5S04 | C5S04AI09 | C5S04,09 | 1756-IF16-9 |  |  | AI | C5 | 4 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S04,10 | 1756-IF16-10 | X1 | C5S04-X1 | Spare_AI_0 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | Spare |  | 1st | - | 3-25-01-913-PD-02 |  |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C5S04 | C5S04AI10 | C5S04,10 | 1756-IF16-10 |  |  | AI | C5 | 4 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S04,11 | 1756-IF16-11 | X1 | C5S04-X1 | Spare_AI_0 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | Spare |  | 1st | - | 3-25-01-913-PD-02 |  |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C5S04 | C5S04AI11 | C5S04,11 | 1756-IF16-11 |  |  | AI | C5 | 4 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S04,12 | 1756-IF16-12 | X1 | C5S04-X1 | Spare_AI_0 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | Spare |  | 1st | - | 3-25-01-913-PD-02 |  |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C5S04 | C5S04AI12 | C5S04,12 | 1756-IF16-12 |  |  | AI | C5 | 4 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S04,13 | 1756-IF16-13 | X1 | C5S04-X1 | Spare_AI_0 |  | Slurry - Out Building 2nd Floor | RIO-200 | LPG System | Spare |  | 1st | - | 3-25-01-913-PD-02 |  |  | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C5S04 | C5S04AI13 | C5S04,13 | 1756-IF16-13 |  |  | AI | C5 | 4 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S04,14 | 1756-IF16-14 | X1 | C5S04-X1 | Spare_AI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C5S04 | C5S04AI14 | C5S04,14 | 1756-IF16-14 |  |  | AI | C5 | 4 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 | C5S04,15 | 1756-IF16-15 | X1 | C5S04-X1 | Spare_AI_0 |  | Slurry - Out Building 2nd Floor |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=0,AI=1,AO=0,Bus=0 |  | Spare_AI_0 | AI | 3 | 0 | C5S04 | C5S04AI15 | C5S04,15 | 1756-IF16-15 |  |  | AI | C5 | 4 | 15 |  | 0 | 0 | 1 | 0 | 0
MCC | MCC | C6S05,00 |  |  | C6S05- | PCM-2030_DO_1 |  | MCC Room | RIO-200 | Slurry - Out Building | PCM-2030 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 | xx | PCM-2030_DO_1 | DO | 2 | 1 | C6S05 | C6S05DO00 | C6S05,00 |  |  |  | DO | C6 | 5 | 0 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C6S05,01 |  |  | C6S05- | PCM-2030_DO_2 |  | MCC Room | RIO-200 | Slurry - Out Building | PCM-2030 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 | xx | PCM-2030_DO_2 | DO | 2 | 2 | C6S05 | C6S05DO01 | C6S05,01 |  |  |  | DO | C6 | 5 | 1 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C6S05,02 |  |  | C6S05- | PCM-2031_DO_1 |  | MCC Room | RIO-200 | Slurry - Out Building | PCM-2031 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Start / Stop Command for FVNR PC-2031 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 | xx | PCM-2031_DO_1 | DO | 2 | 1 | C6S05 | C6S05DO02 | C6S05,02 |  |  |  | DO | C6 | 5 | 2 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C6S05,03 |  |  | C6S05- | PCM-2031_DO_2 |  | MCC Room | RIO-200 | Slurry - Out Building | PCM-2031 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Start / Stop Command for FVNR PC-2031 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 | xx | PCM-2031_DO_2 | DO | 2 | 2 | C6S05 | C6S05DO03 | C6S05,03 |  |  |  | DO | C6 | 5 | 3 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C6S05,04 |  |  | C6S05- | PCY-814201_DO_1 |  | MCC Room | RIO-200 | CIP Water System | PCY-814201 | PUMP | 2nd | 3-25-01-810-PD-01 | - | Start / Stop Command to VSD PC-81001 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-814201_DO_1 | DO | 2 | 1 | C6S05 | C6S05DO04 | C6S05,04 |  |  |  | DO | C6 | 5 | 4 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C6S05,05 |  |  | C6S05- | PCY-814202_DO_1 |  | MCC Room | RIO-200 | CIP Water System | PCY-814202 | PUMP | 2nd | 3-25-01-810-PD-01 | - | Start / Stop Command to VSD PC-81002 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-814202_DO_1 | DO | 2 | 1 | C6S05 | C6S05DO05 | C6S05,05 |  |  |  | DO | C6 | 5 | 5 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C6S05,06 |  |  | C6S05- | XS-80305_DO_1 |  | MCC Room | RIO-200 | LPG System | XS-80305 | 0 | 1st | 325-01-803-PD-02 | - | Start / Stop Command for Gas Vaporizer 5 |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-80305_DO_1 | DO | 2 | 1 | C6S05 | C6S05DO06 | C6S05,06 |  |  |  | DO | C6 | 5 | 6 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C6S05,07 |  |  | C6S05- | XS-80306_DO_1 |  | MCC Room | RIO-200 | LPG System | XS-80306 | Pressure Transmitter | 1st | 325-01-803-PD-02 | - | Start / Stop Command for Gas Vaporizer 6 |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-80306_DO_1 | DO | 2 | 1 | C6S05 | C6S05DO07 | C6S05,07 |  |  |  | DO | C6 | 5 | 7 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C6S06,00 |  |  | C6S06- | PCM-2030_DI_1 |  | MCC Room | RIO-200 | Slurry - Out Building | PCM-2030 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 | xx | PCM-2030_DI_1 | DI | 1 | 1 | C6S06 | C6S06DI00 | C6S06,00 |  |  |  | DI | C6 | 6 | 0 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C6S06,01 |  |  | C6S06- | PCM-2030_DI_2 |  | MCC Room | RIO-200 | Slurry - Out Building | PCM-2030 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 | xx | PCM-2030_DI_2 | DI | 1 | 2 | C6S06 | C6S06DI01 | C6S06,01 |  |  |  | DI | C6 | 6 | 1 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C6S06,02 |  |  | C6S06- | PCM-2031_DI_1 |  | MCC Room | RIO-200 | Slurry - Out Building | PCM-2031 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Start / Stop Command for FVNR PC-2031 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 | xx | PCM-2031_DI_1 | DI | 1 | 1 | C6S06 | C6S06DI02 | C6S06,02 |  |  |  | DI | C6 | 6 | 2 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C6S06,03 |  |  | C6S06- | PCM-2031_DI_2 |  | MCC Room | RIO-200 | Slurry - Out Building | PCM-2031 | 0 | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | Start / Stop Command for FVNR PC-2031 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 | xx | PCM-2031_DI_2 | DI | 1 | 2 | C6S06 | C6S06DI03 | C6S06,03 |  |  |  | DI | C6 | 6 | 3 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C6S06,04 |  |  | C6S06- | PCY-814201_DI_1 |  | MCC Room | RIO-200 | CIP Water System | PCY-814201 | PUMP | 2nd | 3-25-01-810-PD-01 | - | Start / Stop Command to VSD PC-81001 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-814201_DI_1 | DI | 1 | 1 | C6S06 | C6S06DI04 | C6S06,04 |  |  |  | DI | C6 | 6 | 4 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C6S06,05 |  |  | C6S06- | PCY-814201_DI_2 |  | MCC Room | RIO-200 | CIP Water System | PCY-814201 | PUMP | 2nd | 3-25-01-810-PD-01 | - | Start / Stop Command to VSD PC-81001 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-814201_DI_2 | DI | 1 | 2 | C6S06 | C6S06DI05 | C6S06,05 |  |  |  | DI | C6 | 6 | 5 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C6S06,06 |  |  | C6S06- | PCY-814201_DI_3 |  | MCC Room | RIO-200 | CIP Water System | PCY-814201 | PUMP | 2nd | 3-25-01-810-PD-01 | - | Start / Stop Command to VSD PC-81001 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-814201_DI_3 | DI | 1 | 3 | C6S06 | C6S06DI06 | C6S06,06 |  |  |  | DI | C6 | 6 | 6 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C6S06,07 |  |  | C6S06- | PCY-814202_DI_1 |  | MCC Room | RIO-200 | CIP Water System | PCY-814202 | PUMP | 2nd | 3-25-01-810-PD-01 | - | Start / Stop Command to VSD PC-81002 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-814202_DI_1 | DI | 1 | 1 | C6S06 | C6S06DI07 | C6S06,07 |  |  |  | DI | C6 | 6 | 7 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C6S06,08 |  |  | C6S06- | PCY-814202_DI_2 |  | MCC Room | RIO-200 | CIP Water System | PCY-814202 | PUMP | 2nd | 3-25-01-810-PD-01 | - | Start / Stop Command to VSD PC-81002 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-814202_DI_2 | DI | 1 | 2 | C6S06 | C6S06DI08 | C6S06,08 |  |  |  | DI | C6 | 6 | 8 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C6S06,09 |  |  | C6S06- | PCY-814202_DI_3 |  | MCC Room | RIO-200 | CIP Water System | PCY-814202 | PUMP | 2nd | 3-25-01-810-PD-01 | - | Start / Stop Command to VSD PC-81002 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-814202_DI_3 | DI | 1 | 3 | C6S06 | C6S06DI09 | C6S06,09 |  |  |  | DI | C6 | 6 | 9 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S00,00 |  |  | C7S00- | ATY-40201_BUS_1 |  | MCC Room | JB-401 | PH Adjustment | ATY-40201 | Tank Agitator | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40201 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40201_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | ATY-40202_BUS_1 |  | MCC Room | JB-401 | PH Adjustment | ATY-40202 | Tank Agitator | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40202 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40202_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | ATY-40203_BUS_1 |  | MCC Room | JB-401 | Infeed Tank | ATY-40203 | Tank Agitator | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Start / Stop Command for VSD AT-40203 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40203_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | BFY-60206_BUS_1 |  | MCC Room | JB-601 | Spray Dryer | BFY-60206 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60206_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | BFY-60210_BUS_1 |  | MCC Room | JB-602 | Spray Dryer | BFY-60210 | 0 | 5th | 325-01-600-PD-03 | - | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60210_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | BFY-60211_BUS_1 |  | MCC Room | JB-602 | Spray Dryer | BFY-60211 | 0 | 5th | 325-01-600-PD-03 | - | Start / Stop Command for VSD FANC-21 (Combustion Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60211_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | BFY-60220_BUS_1 |  | MCC Room | JB-607 | Spray Dryer | BFY-60220 | 0 | 7th | 325-01-600-PD-04 | - | Start / Stop Command for VSD FANS-22 (Cooling Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60220_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | BFY-60240_BUS_1 |  | MCC Room | JB-602 | Spray Dryer | BFY-60240 | 0 | 5th | 325-01-600-PD-05 | - | Start / Stop Command for VSD FANE-21 (Exhaust Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60240_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | BFY-61301_BUS_1 |  | MCC Room | JB-618 | Packing Tower | BFY-61301 | 0 | 8th | 325-01-613-PD-01 | - | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-61301_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | BFY-61302_BUS_1 |  | MCC Room | JB-612 | Packing Tower | BFY-61302 | 0 | 2nd | 325-01-613-PD-05 | - | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-61302_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | BFY-61303_BUS_1 |  | MCC Room | JB-618 | Packing Tower | BFY-61303 | 0 | 9th | 325-01-613-PD-01 | - | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-61303_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | JB-607 | C7S00,00 |  |  | C7S00- | COM-FH-60210B_BUS_1 |  | Spray Dryer 7th Floor | JB-607 | Spray Dryer | COM-FH-60210B | 0 | 7th | 325-01-600-PD-06 | - | Communication Signal |  | Require I/O DI= 0,DO=0,AI=0,AO=0,Bus=1 |  | COM-FH-60210B_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 0 | 0 | 0 | 0 | 1 |  | BUS
MCC | JB-612 | C7S00,00 |  |  | C7S00- | Communication Signal_BUS_1 |  | Packing Tower 2th Floor | JB-612 | Packing Tower | Communication Signal |  | 1st | 325-01-613-PD-02 | - |  |  | Require I/O DI= 0,DO=0,AI=0,AO=0,Bus=1 |  | Communication Signal_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 0 | 0 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | PCY-40201_BUS_1 |  | MCC Room | JB-401 | PH Adjustment | PCY-40201 | PUMP | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40201 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40201_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | PCY-40202_BUS_1 |  | MCC Room | JB-401 | PH Adjustment | PCY-40202 | PUMP | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40202 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40202_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | PCY-40203_BUS_1 |  | MCC Room | JB-401 | Infeed Tank | PCY-40203 | PUMP | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40203_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | JB-601 | C7S00,00 |  |  | C7S00- | PCY-60205_BUS_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | PCY-60205 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-60205_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | PCY-60215_BUS_1 |  | MCC Room | JB-602 | Spray Dryer | PCY-60215 | PUMP | 5th | 325-01-600-PD-03 | - | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-60215_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | PCY-814201_BUS_1 |  | MCC Room | RIO-200 | CIP Water System | PCY-814201 | PUMP | 2nd | 3-25-01-810-PD-01 | - | Start / Stop Command to VSD PC-81001 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-814201_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S00,00 |  |  | C7S00- | PCY-814202_BUS_1 |  | MCC Room | RIO-200 | CIP Water System | PCY-814202 | PUMP | 2nd | 3-25-01-810-PD-01 | - | Start / Stop Command to VSD PC-81002 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-814202_BUS_1 | BUS | 0 | 1 | C7S00 | C7S00BUS00 | C7S00,00 |  |  |  | BUS | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | C7S01,00 |  |  | C7S01- | Spare_DI_0 |  | MCC Room | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S01 | C7S01DI00 | C7S01,00 |  |  |  | DI | C7 | 1 | 0 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S01,01 |  |  | C7S01- | Spare_DI_0 |  | MCC Room | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S01 | C7S01DI01 | C7S01,01 |  |  |  | DI | C7 | 1 | 1 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S01,02 |  |  | C7S01- | Spare_DI_0 |  | MCC Room | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S01 | C7S01DI02 | C7S01,02 |  |  |  | DI | C7 | 1 | 2 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S01,03 |  |  | C7S01- | Spare_DI_0 |  | MCC Room | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S01 | C7S01DI03 | C7S01,03 |  |  |  | DI | C7 | 1 | 3 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S01,04 |  |  | C7S01- | Spare_DI_0 |  | MCC Room | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S01 | C7S01DI04 | C7S01,04 |  |  |  | DI | C7 | 1 | 4 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S01,05 |  |  | C7S01- | Spare_DI_0 |  | MCC Room | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S01 | C7S01DI05 | C7S01,05 |  |  |  | DI | C7 | 1 | 5 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S01,06 |  |  | C7S01- | Spare_DI_0 |  | MCC Room | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S01 | C7S01DI06 | C7S01,06 |  |  |  | DI | C7 | 1 | 6 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S01,07 |  |  | C7S01- | Spare_DI_0 |  | MCC Room | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S01 | C7S01DI07 | C7S01,07 |  |  |  | DI | C7 | 1 | 7 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S01,08 |  |  | C7S01- | ATY-40201_DI_1 |  | MCC Room | JB-401 | PH Adjustment | ATY-40201 | Tank Agitator | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40201 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40201_DI_1 | DI | 1 | 1 | C7S01 | C7S01DI08 | C7S01,08 |  |  |  | DI | C7 | 1 | 8 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,09 |  |  | C7S01- | ATY-40201_DI_2 |  | MCC Room | JB-401 | PH Adjustment | ATY-40201 | Tank Agitator | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40201 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40201_DI_2 | DI | 1 | 2 | C7S01 | C7S01DI09 | C7S01,09 |  |  |  | DI | C7 | 1 | 9 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,10 |  |  | C7S01- | ATY-40201_DI_3 |  | MCC Room | JB-401 | PH Adjustment | ATY-40201 | Tank Agitator | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40201 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40201_DI_3 | DI | 1 | 3 | C7S01 | C7S01DI10 | C7S01,10 |  |  |  | DI | C7 | 1 | 10 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,11 |  |  | C7S01- | ATY-40202_DI_1 |  | MCC Room | JB-401 | PH Adjustment | ATY-40202 | Tank Agitator | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40202 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40202_DI_1 | DI | 1 | 1 | C7S01 | C7S01DI11 | C7S01,11 |  |  |  | DI | C7 | 1 | 11 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,12 |  |  | C7S01- | ATY-40202_DI_2 |  | MCC Room | JB-401 | PH Adjustment | ATY-40202 | Tank Agitator | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40202 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40202_DI_2 | DI | 1 | 2 | C7S01 | C7S01DI12 | C7S01,12 |  |  |  | DI | C7 | 1 | 12 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,13 |  |  | C7S01- | ATY-40202_DI_3 |  | MCC Room | JB-401 | PH Adjustment | ATY-40202 | Tank Agitator | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40202 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40202_DI_3 | DI | 1 | 3 | C7S01 | C7S01DI13 | C7S01,13 |  |  |  | DI | C7 | 1 | 13 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,14 |  |  | C7S01- | ATY-40203_DI_1 |  | MCC Room | JB-401 | Infeed Tank | ATY-40203 | Tank Agitator | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Start / Stop Command for VSD AT-40203 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40203_DI_1 | DI | 1 | 1 | C7S01 | C7S01DI14 | C7S01,14 |  |  |  | DI | C7 | 1 | 14 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,15 |  |  | C7S01- | ATY-40203_DI_2 |  | MCC Room | JB-401 | Infeed Tank | ATY-40203 | Tank Agitator | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Start / Stop Command for VSD AT-40203 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40203_DI_2 | DI | 1 | 2 | C7S01 | C7S01DI15 | C7S01,15 |  |  |  | DI | C7 | 1 | 15 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,16 |  |  | C7S01- | ATY-40203_DI_3 |  | MCC Room | JB-401 | Infeed Tank | ATY-40203 | Tank Agitator | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Start / Stop Command for VSD AT-40203 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40203_DI_3 | DI | 1 | 3 | C7S01 | C7S01DI16 | C7S01,16 |  |  |  | DI | C7 | 1 | 16 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,17 |  |  | C7S01- | PCY-40201_DI_1 |  | MCC Room | JB-401 | PH Adjustment | PCY-40201 | PUMP | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40201 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40201_DI_1 | DI | 1 | 1 | C7S01 | C7S01DI17 | C7S01,17 |  |  |  | DI | C7 | 1 | 17 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,18 |  |  | C7S01- | PCY-40201_DI_2 |  | MCC Room | JB-401 | PH Adjustment | PCY-40201 | PUMP | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40201 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40201_DI_2 | DI | 1 | 2 | C7S01 | C7S01DI18 | C7S01,18 |  |  |  | DI | C7 | 1 | 18 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,19 |  |  | C7S01- | PCY-40201_DI_3 |  | MCC Room | JB-401 | PH Adjustment | PCY-40201 | PUMP | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40201 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40201_DI_3 | DI | 1 | 3 | C7S01 | C7S01DI19 | C7S01,19 |  |  |  | DI | C7 | 1 | 19 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,20 |  |  | C7S01- | PCY-40202_DI_1 |  | MCC Room | JB-401 | PH Adjustment | PCY-40202 | PUMP | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40202 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40202_DI_1 | DI | 1 | 1 | C7S01 | C7S01DI20 | C7S01,20 |  |  |  | DI | C7 | 1 | 20 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,21 |  |  | C7S01- | PCY-40202_DI_2 |  | MCC Room | JB-401 | PH Adjustment | PCY-40202 | PUMP | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40202 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40202_DI_2 | DI | 1 | 2 | C7S01 | C7S01DI21 | C7S01,21 |  |  |  | DI | C7 | 1 | 21 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,22 |  |  | C7S01- | PCY-40202_DI_3 |  | MCC Room | JB-401 | PH Adjustment | PCY-40202 | PUMP | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40202 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40202_DI_3 | DI | 1 | 3 | C7S01 | C7S01DI22 | C7S01,22 |  |  |  | DI | C7 | 1 | 22 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,23 |  |  | C7S01- | PCY-40203_DI_1 |  | MCC Room | JB-401 | Infeed Tank | PCY-40203 | PUMP | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40203_DI_1 | DI | 1 | 1 | C7S01 | C7S01DI23 | C7S01,23 |  |  |  | DI | C7 | 1 | 23 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,24 |  |  | C7S01- | PCY-40203_DI_2 |  | MCC Room | JB-401 | Infeed Tank | PCY-40203 | PUMP | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40203_DI_2 | DI | 1 | 2 | C7S01 | C7S01DI24 | C7S01,24 |  |  |  | DI | C7 | 1 | 24 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,25 |  |  | C7S01- | PCY-40203_DI_3 |  | MCC Room | JB-401 | Infeed Tank | PCY-40203 | PUMP | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40203_DI_3 | DI | 1 | 3 | C7S01 | C7S01DI25 | C7S01,25 |  |  |  | DI | C7 | 1 | 25 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,26 |  |  | C7S01- | BFY-60206_DI_1 |  | MCC Room | JB-601 | Spray Dryer | BFY-60206 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60206_DI_1 | DI | 1 | 1 | C7S01 | C7S01DI26 | C7S01,26 |  |  |  | DI | C7 | 1 | 26 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S01,27 |  |  | C7S01- | PCM-60205-2_DI_1 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-2 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-2_DI_1 | DI | 1 | 1 | C7S01 | C7S01DI27 | C7S01,27 |  |  |  | DI | C7 | 1 | 27 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S01,28 |  |  | C7S01- | PCM-60205-2_DI_2 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-2 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-2_DI_2 | DI | 1 | 2 | C7S01 | C7S01DI28 | C7S01,28 |  |  |  | DI | C7 | 1 | 28 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S01,29 |  |  | C7S01- | PCM-60205-3_DI_1 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-3 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-3_DI_1 | DI | 1 | 1 | C7S01 | C7S01DI29 | C7S01,29 |  |  |  | DI | C7 | 1 | 29 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S01,30 |  |  | C7S01- | PCM-60205-3_DI_2 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-3 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-3_DI_2 | DI | 1 | 2 | C7S01 | C7S01DI30 | C7S01,30 |  |  |  | DI | C7 | 1 | 30 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S01,31 |  |  | C7S01- | PCM-60205-4_DI_1 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-4 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-4_DI_1 | DI | 1 | 1 | C7S01 | C7S01DI31 | C7S01,31 |  |  |  | DI | C7 | 1 | 31 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S02,00 |  |  | C7S02- | PCM-60205-4_DI_2 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-4 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-4_DI_2 | DI | 1 | 2 | C7S02 | C7S02DI00 | C7S02,00 |  |  |  | DI | C7 | 2 | 0 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S02,01 |  |  | C7S02- | PCM-60205-5_DI_1 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-5 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-5_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI01 | C7S02,01 |  |  |  | DI | C7 | 2 | 1 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S02,02 |  |  | C7S02- | PCM-60205-5_DI_2 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-5 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-5_DI_2 | DI | 1 | 2 | C7S02 | C7S02DI02 | C7S02,02 |  |  |  | DI | C7 | 2 | 2 |  | 2 | 2 | 0 | 0 | 0
MCC | JB-601 | C7S02,03 |  |  | C7S02- | PCY-60205_DI_1 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | PCY-60205 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-60205_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI03 | C7S02,03 |  |  |  | DI | C7 | 2 | 3 |  | 3 | 1 | 0 | 0 | 1
MCC | JB-601 | C7S02,04 |  |  | C7S02- | PCY-60205_DI_2 |  | Spray Dryer 1st Floor | JB-601 | Spray Dryer | PCY-60205 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-60205_DI_2 | DI | 1 | 2 | C7S02 | C7S02DI04 | C7S02,04 |  |  |  | DI | C7 | 2 | 4 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | C7S02,05 |  |  | C7S02- | RVM-60201_DI_1 |  | MCC Room | JB-601 | Spray Dryer | RVM-60201 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60201_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI05 | C7S02,05 |  |  |  | DI | C7 | 2 | 5 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S02,06 |  |  | C7S02- | RVM-60201_DI_2 |  | MCC Room | JB-601 | Spray Dryer | RVM-60201 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60201_DI_2 | DI | 1 | 2 | C7S02 | C7S02DI06 | C7S02,06 |  |  |  | DI | C7 | 2 | 6 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S02,07 |  |  | C7S02- | RVM-60202_DI_1 |  | MCC Room | JB-601 | Spray Dryer | RVM-60202 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60202_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI07 | C7S02,07 |  |  |  | DI | C7 | 2 | 7 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S02,08 |  |  | C7S02- | RVM-60202_DI_2 |  | MCC Room | JB-601 | Spray Dryer | RVM-60202 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60202_DI_2 | DI | 1 | 2 | C7S02 | C7S02DI08 | C7S02,08 |  |  |  | DI | C7 | 2 | 8 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S02,09 |  |  | C7S02- | RVM-60203_DI_1 |  | MCC Room | JB-601 | Spray Dryer | RVM-60203 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60203_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI09 | C7S02,09 |  |  |  | DI | C7 | 2 | 9 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S02,10 |  |  | C7S02- | RVM-60203_DI_2 |  | MCC Room | JB-601 | Spray Dryer | RVM-60203 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60203_DI_2 | DI | 1 | 2 | C7S02 | C7S02DI10 | C7S02,10 |  |  |  | DI | C7 | 2 | 10 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S02,11 |  |  | C7S02- | BFY-60210_DI_1 |  | MCC Room | JB-602 | Spray Dryer | BFY-60210 | 0 | 5th | 325-01-600-PD-03 | - | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60210_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI11 | C7S02,11 |  |  |  | DI | C7 | 2 | 11 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S02,12 |  |  | C7S02- | BFY-60211_DI_1 |  | MCC Room | JB-602 | Spray Dryer | BFY-60211 | 0 | 5th | 325-01-600-PD-03 | - | Start / Stop Command for VSD FANC-21 (Combustion Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60211_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI12 | C7S02,12 |  |  |  | DI | C7 | 2 | 12 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S02,13 |  |  | C7S02- | BFY-60240_DI_1 |  | MCC Room | JB-602 | Spray Dryer | BFY-60240 | 0 | 5th | 325-01-600-PD-05 | - | Start / Stop Command for VSD FANE-21 (Exhaust Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60240_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI13 | C7S02,13 |  |  |  | DI | C7 | 2 | 13 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S02,14 |  |  | C7S02- | PCY-60215_DI_1 |  | MCC Room | JB-602 | Spray Dryer | PCY-60215 | PUMP | 5th | 325-01-600-PD-03 | - | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-60215_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI14 | C7S02,14 |  |  |  | DI | C7 | 2 | 14 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S02,15 |  |  | C7S02- | PCY-60215_DI_2 |  | MCC Room | JB-602 | Spray Dryer | PCY-60215 | PUMP | 5th | 325-01-600-PD-03 | - | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-60215_DI_2 | DI | 1 | 2 | C7S02 | C7S02DI15 | C7S02,15 |  |  |  | DI | C7 | 2 | 15 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S02,16 |  |  | C7S02- | PCY-60215_DI_3 |  | MCC Room | JB-602 | Spray Dryer | PCY-60215 | PUMP | 5th | 325-01-600-PD-03 | - | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-60215_DI_3 | DI | 1 | 3 | C7S02 | C7S02DI16 | C7S02,16 |  |  |  | DI | C7 | 2 | 16 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S02,17 |  |  | C7S02- | BFY-60220_DI_1 |  | MCC Room | JB-607 | Spray Dryer | BFY-60220 | 0 | 7th | 325-01-600-PD-04 | - | Start / Stop Command for VSD FANS-22 (Cooling Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60220_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI17 | C7S02,17 |  |  |  | DI | C7 | 2 | 17 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S02,18 |  |  | C7S02- | BFY-61302_DI_1 |  | MCC Room | JB-612 | Packing Tower | BFY-61302 | 0 | 2nd | 325-01-613-PD-05 | - | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-61302_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI18 | C7S02,18 |  |  |  | DI | C7 | 2 | 18 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S02,19 |  |  | C7S02- | HS-61307F_DI_1 |  | MCC Room | JB-612 | Packing Tower | HS-61307F | 0 | 4th | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307F_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI19 | C7S02,19 |  |  |  | DI | C7 | 2 | 19 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S02,20 |  |  | C7S02- | HS-61307G_DI_1 |  | MCC Room | JB-612 | Packing Tower | HS-61307G | 0 | 3rd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307G_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI20 | C7S02,20 |  |  |  | DI | C7 | 2 | 20 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S02,21 |  |  | C7S02- | HS-61307H_DI_1 |  | MCC Room | JB-612 | Packing Tower | HS-61307H | 0 | 3rd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307H_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI21 | C7S02,21 |  |  |  | DI | C7 | 2 | 21 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S02,22 |  |  | C7S02- | HS-61307I_DI_1 |  | MCC Room | JB-612 | Packing Tower | HS-61307I | 0 | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307I_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI22 | C7S02,22 |  |  |  | DI | C7 | 2 | 22 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S02,23 |  |  | C7S02- | HS-61307J_DI_1 |  | MCC Room | JB-612 | Packing Tower | HS-61307J | 0 | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307J_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI23 | C7S02,23 |  |  |  | DI | C7 | 2 | 23 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S02,24 |  |  | C7S02- | HS-61307K_DI_1 |  | MCC Room | JB-612 | Packing Tower | HS-61307K | 0 | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307K_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI24 | C7S02,24 |  |  |  | DI | C7 | 2 | 24 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S02,25 |  |  | C7S02- | HS-61307L_DI_1 |  | MCC Room | JB-612 | Packing Tower | HS-61307L | 0 | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307L_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI25 | C7S02,25 |  |  |  | DI | C7 | 2 | 25 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S02,26 |  |  | C7S02- | HS-61307M_DI_1 |  | MCC Room | JB-612 | Packing Tower | HS-61307M | 0 | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307M_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI26 | C7S02,26 |  |  |  | DI | C7 | 2 | 26 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S02,27 |  |  | C7S02- | HS-61307N_DI_1 |  | MCC Room | JB-612 | Packing Tower | HS-61307N | 0 | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307N_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI27 | C7S02,27 |  |  |  | DI | C7 | 2 | 27 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S02,28 |  |  | C7S02- | HS-61307O_DI_1 |  | MCC Room | JB-612 | Packing Tower | HS-61307O | 0 | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307O_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI28 | C7S02,28 |  |  |  | DI | C7 | 2 | 28 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S02,29 |  |  | C7S02- | HS-61307P_DI_1 |  | MCC Room | JB-612 | Packing Tower | HS-61307P | 0 | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307P_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI29 | C7S02,29 |  |  |  | DI | C7 | 2 | 29 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S02,30 |  |  | C7S02- | HS-61307Q_DI_1 |  | MCC Room | JB-612 | Packing Tower | HS-61307Q | 0 | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307Q_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI30 | C7S02,30 |  |  |  | DI | C7 | 2 | 30 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S02,31 |  |  | C7S02- | HS-61307R_DI_1 |  | MCC Room | JB-612 | Packing Tower | HS-61307R | 0 | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307R_DI_1 | DI | 1 | 1 | C7S02 | C7S02DI31 | C7S02,31 |  |  |  | DI | C7 | 2 | 31 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S03,00 |  |  | C7S03- | RVM-61302_DI_1 |  | MCC Room | JB-612 | Packing Tower | RVM-61302 | 0 | 1st | 325-01-613-PD-03 | - | Start / Stop Command for FVNR RV-61302 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61302_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI00 | C7S03,00 |  |  |  | DI | C7 | 3 | 0 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,01 |  |  | C7S03- | RVM-61302_DI_2 |  | MCC Room | JB-612 | Packing Tower | RVM-61302 | 0 | 1st | 325-01-613-PD-03 | - | Start / Stop Command for FVNR RV-61302 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61302_DI_2 | DI | 1 | 2 | C7S03 | C7S03DI01 | C7S03,01 |  |  |  | DI | C7 | 3 | 1 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,02 |  |  | C7S03- | RVM-61303_DI_1 |  | MCC Room | JB-612 | Packing Tower | RVM-61303 | 0 | 1st | 325-01-613-PD-05 | - | Start / Stop Command for FVNR RV-61303 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61303_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI02 | C7S03,02 |  |  |  | DI | C7 | 3 | 2 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,03 |  |  | C7S03- | RVM-61303_DI_2 |  | MCC Room | JB-612 | Packing Tower | RVM-61303 | 0 | 1st | 325-01-613-PD-05 | - | Start / Stop Command for FVNR RV-61303 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61303_DI_2 | DI | 1 | 2 | C7S03 | C7S03DI03 | C7S03,03 |  |  |  | DI | C7 | 3 | 3 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,04 |  |  | C7S03- | SCM-61301_DI_1 |  | MCC Room | JB-612 | Packing Tower | SCM-61301 | 0 | 4th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR SC-61301 (Sifter ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | SCM-61301_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI04 | C7S03,04 |  |  |  | DI | C7 | 3 | 4 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,05 |  |  | C7S03- | SCM-61301_DI_2 |  | MCC Room | JB-612 | Packing Tower | SCM-61301 | 0 | 4th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR SC-61301 (Sifter ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | SCM-61301_DI_2 | DI | 1 | 2 | C7S03 | C7S03DI05 | C7S03,05 |  |  |  | DI | C7 | 3 | 5 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,06 |  |  | C7S03- | SCM-61302_DI_2 |  | MCC Room | JB-612 | Packing Tower | SCM-61302 | 0 | 4th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR SC-61302 (Sifter ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | SCM-61302_DI_2 | DI | 1 | 2 | C7S03 | C7S03DI06 | C7S03,06 |  |  |  | DI | C7 | 3 | 6 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,07 |  |  | C7S03- | SCM-61302_DI_1 |  | MCC Room | JB-612 | Packing Tower | SCM-61302 | 0 | 4th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR SC-61302 (Sifter ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | SCM-61302_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI07 | C7S03,07 |  |  |  | DI | C7 | 3 | 7 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,08 |  |  | C7S03- | BFY-61301_DI_1 |  | MCC Room | JB-618 | Packing Tower | BFY-61301 | 0 | 8th | 325-01-613-PD-01 | - | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-61301_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI08 | C7S03,08 |  |  |  | DI | C7 | 3 | 8 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S03,09 |  |  | C7S03- | BFY-61303_DI_1 |  | MCC Room | JB-618 | Packing Tower | BFY-61303 | 0 | 9th | 325-01-613-PD-01 | - | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-61303_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI09 | C7S03,09 |  |  |  | DI | C7 | 3 | 9 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S03,10 |  |  | C7S03- | BLM-61302_DI_1 |  | MCC Room | JB-618 | Packing Tower | BLM-61302 | 0 | 5th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | BLM-61302_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI10 | C7S03,10 |  |  |  | DI | C7 | 3 | 10 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,11 |  |  | C7S03- | BLM-61302_DI_2 |  | MCC Room | JB-618 | Packing Tower | BLM-61302 | 0 | 5th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | BLM-61302_DI_2 | DI | 1 | 2 | C7S03 | C7S03DI11 | C7S03,11 |  |  |  | DI | C7 | 3 | 11 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,12 |  |  | C7S03- | HS-61307A_DI_1 |  | MCC Room | JB-618 | Packing Tower | HS-61307A | 0 | 8th | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307A_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI12 | C7S03,12 |  |  |  | DI | C7 | 3 | 12 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S03,13 |  |  | C7S03- | HS-61307B_DI_1 |  | MCC Room | JB-618 | Packing Tower | HS-61307B | 0 | 8th | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307B_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI13 | C7S03,13 |  |  |  | DI | C7 | 3 | 13 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S03,14 |  |  | C7S03- | HS-61307C_DI_1 |  | MCC Room | JB-618 | Packing Tower | HS-61307C | 0 | 7th | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307C_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI14 | C7S03,14 |  |  |  | DI | C7 | 3 | 14 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S03,15 |  |  | C7S03- | HS-61307D_DI_1 |  | MCC Room | JB-618 | Packing Tower | HS-61307D | 0 | 5th | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307D_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI15 | C7S03,15 |  |  |  | DI | C7 | 3 | 15 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S03,16 |  |  | C7S03- | HS-61307E_DI_1 |  | MCC Room | JB-618 | Packing Tower | HS-61307E | 0 | 5th | 325-01-613-PD-03 | 3-25-01-613-PD-03 | Start/Stop |  | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | HS-61307E_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI16 | C7S03,16 |  |  |  | DI | C7 | 3 | 16 |  | 1 | 0 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S03,17 |  |  | C7S03- | RVM-60204_DI_1 |  | MCC Room | JB-618 | Packing Tower | RVM-60204 | 0 | 9th | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60204_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI17 | C7S03,17 |  |  |  | DI | C7 | 3 | 17 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,18 |  |  | C7S03- | RVM-60204_DI_2 |  | MCC Room | JB-618 | Packing Tower | RVM-60204 | 0 | 9th | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60204_DI_2 | DI | 1 | 2 | C7S03 | C7S03DI18 | C7S03,18 |  |  |  | DI | C7 | 3 | 18 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,19 |  |  | C7S03- | RVM-61301_DI_1 |  | MCC Room | JB-618 | Packing Tower | RVM-61301 | 0 | 6th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR RV-61301 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61301_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI19 | C7S03,19 |  |  |  | DI | C7 | 3 | 19 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,20 |  |  | C7S03- | RVM-61301_DI_2 |  | MCC Room | JB-618 | Packing Tower | RVM-61301 | 0 | 6th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR RV-61301 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61301_DI_2 | DI | 1 | 2 | C7S03 | C7S03DI20 | C7S03,20 |  |  |  | DI | C7 | 3 | 20 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,21 |  |  | C7S03- | RVM-61304_DI_1 |  | MCC Room | JB-618 | Packing Tower | RVM-61304 | 0 | 9th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR RV-61304 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61304_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI21 | C7S03,21 |  |  |  | DI | C7 | 3 | 21 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,22 |  |  | C7S03- | RVM-61304_DI_2 |  | MCC Room | JB-618 | Packing Tower | RVM-61304 | 0 | 9th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR RV-61304 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61304_DI_2 | DI | 1 | 2 | C7S03 | C7S03DI22 | C7S03,22 |  |  |  | DI | C7 | 3 | 22 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,23 |  |  | C7S03- | RVM-61305_DI_1 |  | MCC Room | JB-618 | Packing Tower | RVM-61305 | 0 | 9th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR RV-61305 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61305_DI_1 | DI | 1 | 1 | C7S03 | C7S03DI23 | C7S03,23 |  |  |  | DI | C7 | 3 | 23 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S03,24 |  |  | C7S03- | RVM-61305_DI_2 |  | MCC Room | JB-618 | Packing Tower | RVM-61305 | 0 | 9th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR RV-61305 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61305_DI_2 | DI | 1 | 2 | C7S03 | C7S03DI24 | C7S03,24 |  |  |  | DI | C7 | 3 | 24 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | JB-601 | C7S03,25 |  |  | C7S03- | PCY-60205_DI_3 |  | Spray Dryer 1st Floor | MCC | Spray Dryer | PCY-60205 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-60205_DI_3 | DI | 1 | 3 | C7S03 | C7S03DI25 | C7S03,25 |  |  |  | DI | C7 | 3 | 25 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | C7S04,04 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI04 | C7S04,04 |  |  |  | DI | C7 | 4 | 4 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,05 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI05 | C7S04,05 |  |  |  | DI | C7 | 4 | 5 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,06 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI06 | C7S04,06 |  |  |  | DI | C7 | 4 | 6 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,07 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI07 | C7S04,07 |  |  |  | DI | C7 | 4 | 7 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,08 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI08 | C7S04,08 |  |  |  | DI | C7 | 4 | 8 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,09 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI09 | C7S04,09 |  |  |  | DI | C7 | 4 | 9 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,10 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI10 | C7S04,10 |  |  |  | DI | C7 | 4 | 10 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,11 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI11 | C7S04,11 |  |  |  | DI | C7 | 4 | 11 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,12 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI12 | C7S04,12 |  |  |  | DI | C7 | 4 | 12 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,13 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI13 | C7S04,13 |  |  |  | DI | C7 | 4 | 13 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,14 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI14 | C7S04,14 |  |  |  | DI | C7 | 4 | 14 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,15 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI15 | C7S04,15 |  |  |  | DI | C7 | 4 | 15 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,16 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI16 | C7S04,16 |  |  |  | DI | C7 | 4 | 16 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,17 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI17 | C7S04,17 |  |  |  | DI | C7 | 4 | 17 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,18 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI18 | C7S04,18 |  |  |  | DI | C7 | 4 | 18 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,19 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI19 | C7S04,19 |  |  |  | DI | C7 | 4 | 19 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,20 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI20 | C7S04,20 |  |  |  | DI | C7 | 4 | 20 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,21 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI21 | C7S04,21 |  |  |  | DI | C7 | 4 | 21 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,22 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI22 | C7S04,22 |  |  |  | DI | C7 | 4 | 22 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,23 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI23 | C7S04,23 |  |  |  | DI | C7 | 4 | 23 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,24 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI24 | C7S04,24 |  |  |  | DI | C7 | 4 | 24 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,25 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI25 | C7S04,25 |  |  |  | DI | C7 | 4 | 25 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,26 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI26 | C7S04,26 |  |  |  | DI | C7 | 4 | 26 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,27 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI27 | C7S04,27 |  |  |  | DI | C7 | 4 | 27 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,28 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI28 | C7S04,28 |  |  |  | DI | C7 | 4 | 28 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,29 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI29 | C7S04,29 |  |  |  | DI | C7 | 4 | 29 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,30 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI30 | C7S04,30 |  |  |  | DI | C7 | 4 | 30 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S04,31 |  |  | C7S04- | Spare_DI_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 1,DO=0,AI=0,AO=0,Bus=0 |  | Spare_DI_0 | DI | 1 | 0 | C7S04 | C7S04DI31 | C7S04,31 |  |  |  | DI | C7 | 4 | 31 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | C7S05,00 |  |  | C7S05- | Spare_DO_0 |  | MCC Room | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S05 | C7S05DO00 | C7S05,00 |  |  |  | DO | C7 | 5 | 0 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S05,01 |  |  | C7S05- | Spare_DO_0 |  | MCC Room | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S05 | C7S05DO01 | C7S05,01 |  |  |  | DO | C7 | 5 | 1 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S05,02 |  |  | C7S05- | Spare_DO_0 |  | MCC Room | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S05 | C7S05DO02 | C7S05,02 |  |  |  | DO | C7 | 5 | 2 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S05,03 |  |  | C7S05- | Spare_DO_0 |  | MCC Room | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S05 | C7S05DO03 | C7S05,03 |  |  |  | DO | C7 | 5 | 3 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S05,04 |  |  | C7S05- | Spare_DO_0 |  | MCC Room | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S05 | C7S05DO04 | C7S05,04 |  |  |  | DO | C7 | 5 | 4 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S05,05 |  |  | C7S05- | Spare_DO_0 |  | MCC Room | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S05 | C7S05DO05 | C7S05,05 |  |  |  | DO | C7 | 5 | 5 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S05,06 |  |  | C7S05- | Spare_DO_0 |  | MCC Room | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S05 | C7S05DO06 | C7S05,06 |  |  |  | DO | C7 | 5 | 6 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S05,07 |  |  | C7S05- | Spare_DO_0 |  | MCC Room | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S05 | C7S05DO07 | C7S05,07 |  |  |  | DO | C7 | 5 | 7 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S05,08 |  |  | C7S05- | ATY-40201_DO_1 |  | MCC Room | JB-401 | PH Adjustment | ATY-40201 | Tank Agitator | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40201 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40201_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO08 | C7S05,08 |  |  |  | DO | C7 | 5 | 8 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S05,09 |  |  | C7S05- | ATY-40202_DO_1 |  | MCC Room | JB-401 | PH Adjustment | ATY-40202 | Tank Agitator | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD AT-40202 |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40202_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO09 | C7S05,09 |  |  |  | DO | C7 | 5 | 9 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S05,10 |  |  | C7S05- | ATY-40203_DO_1 |  | MCC Room | JB-401 | Infeed Tank | ATY-40203 | Tank Agitator | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Start / Stop Command for VSD AT-40203 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | ATY-40203_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO10 | C7S05,10 |  |  |  | DO | C7 | 5 | 10 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S05,11 |  |  | C7S05- | PCY-40201_DO_1 |  | MCC Room | JB-401 | PH Adjustment | PCY-40201 | PUMP | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40201 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40201_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO11 | C7S05,11 |  |  |  | DO | C7 | 5 | 11 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S05,12 |  |  | C7S05- | PCY-40202_DO_1 |  | MCC Room | JB-401 | PH Adjustment | PCY-40202 | PUMP | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | Start / Stop Command for VSD PC-40202 |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40202_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO12 | C7S05,12 |  |  |  | DO | C7 | 5 | 12 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S05,13 |  |  | C7S05- | PCY-40203_DO_1 |  | MCC Room | JB-401 | Infeed Tank | PCY-40203 | PUMP | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-40203_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO13 | C7S05,13 |  |  |  | DO | C7 | 5 | 13 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S05,14 |  |  | C7S05- | BFY-60206_DO_1 |  | MCC Room | JB-601 | Spray Dryer | BFY-60206 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60206_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO14 | C7S05,14 |  |  |  | DO | C7 | 5 | 14 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S05,15 |  |  | C7S05- | PCM-60205-2_DO_1 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-2 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-2_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO15 | C7S05,15 |  |  |  | DO | C7 | 5 | 15 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S05,16 |  |  | C7S05- | PCM-60205-2_DO_2 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-2 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-2_DO_2 | DO | 2 | 2 | C7S05 | C7S05DO16 | C7S05,16 |  |  |  | DO | C7 | 5 | 16 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S05,17 |  |  | C7S05- | PCM-60205-3_DO_1 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-3 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-3_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO17 | C7S05,17 |  |  |  | DO | C7 | 5 | 17 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S05,18 |  |  | C7S05- | PCM-60205-3_DO_2 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-3 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-3_DO_2 | DO | 2 | 2 | C7S05 | C7S05DO18 | C7S05,18 |  |  |  | DO | C7 | 5 | 18 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S05,19 |  |  | C7S05- | PCM-60205-4_DO_1 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-4 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-4_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO19 | C7S05,19 |  |  |  | DO | C7 | 5 | 19 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S05,20 |  |  | C7S05- | PCM-60205-4_DO_2 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-4 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-4_DO_2 | DO | 2 | 2 | C7S05 | C7S05DO20 | C7S05,20 |  |  |  | DO | C7 | 5 | 20 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S05,21 |  |  | C7S05- | PCM-60205-5_DO_1 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-5 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-5_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO21 | C7S05,21 |  |  |  | DO | C7 | 5 | 21 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S05,22 |  |  | C7S05- | PCM-60205-5_DO_2 |  | MCC Room | JB-601 | Spray Dryer | PCM-60205-5 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | PCM-60205-5_DO_2 | DO | 2 | 2 | C7S05 | C7S05DO22 | C7S05,22 |  |  |  | DO | C7 | 5 | 22 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | C7S05,23 |  |  | C7S05- | RVM-60201_DO_1 |  | MCC Room | JB-601 | Spray Dryer | RVM-60201 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60201_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO23 | C7S05,23 |  |  |  | DO | C7 | 5 | 23 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S05,24 |  |  | C7S05- | RVM-60201_DO_2 |  | MCC Room | JB-601 | Spray Dryer | RVM-60201 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60201_DO_2 | DO | 2 | 2 | C7S05 | C7S05DO24 | C7S05,24 |  |  |  | DO | C7 | 5 | 24 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S05,25 |  |  | C7S05- | RVM-60202_DO_1 |  | MCC Room | JB-601 | Spray Dryer | RVM-60202 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60202_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO25 | C7S05,25 |  |  |  | DO | C7 | 5 | 25 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S05,26 |  |  | C7S05- | RVM-60202_DO_2 |  | MCC Room | JB-601 | Spray Dryer | RVM-60202 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60202_DO_2 | DO | 2 | 2 | C7S05 | C7S05DO26 | C7S05,26 |  |  |  | DO | C7 | 5 | 26 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S05,27 |  |  | C7S05- | RVM-60203_DO_1 |  | MCC Room | JB-601 | Spray Dryer | RVM-60203 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60203_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO27 | C7S05,27 |  |  |  | DO | C7 | 5 | 27 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S05,28 |  |  | C7S05- | RVM-60203_DO_2 |  | MCC Room | JB-601 | Spray Dryer | RVM-60203 | 0 | 1st | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60203_DO_2 | DO | 2 | 2 | C7S05 | C7S05DO28 | C7S05,28 |  |  |  | DO | C7 | 5 | 28 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S05,29 |  |  | C7S05- | XS-60205_DO_1 |  | MCC Room | JB-601 | Spray Dryer | XS-60205 | 0 | 1st | 325-01-600-PD-01 | - | Start / Stop Command for PUPD-11 (Positive Displacement Pump ) |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-60205_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO29 | C7S05,29 |  |  |  | DO | C7 | 5 | 29 |  | 0 | 1 | 0 | 0 | 0 |  | 0
MCC | MCC | C7S05,30 |  |  | C7S05- | BFY-60210_DO_1 |  | MCC Room | JB-602 | Spray Dryer | BFY-60210 | 0 | 5th | 325-01-600-PD-03 | - | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60210_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO30 | C7S05,30 |  |  |  | DO | C7 | 5 | 30 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S05,31 |  |  | C7S05- | BFY-60211_DO_1 |  | MCC Room | JB-602 | Spray Dryer | BFY-60211 | 0 | 5th | 325-01-600-PD-03 | - | Start / Stop Command for VSD FANC-21 (Combustion Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60211_DO_1 | DO | 2 | 1 | C7S05 | C7S05DO31 | C7S05,31 |  |  |  | DO | C7 | 5 | 31 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S06,00 |  |  | C7S06- | BFY-60240_DO_1 |  | MCC Room | JB-602 | Spray Dryer | BFY-60240 | 0 | 5th | 325-01-600-PD-05 | - | Start / Stop Command for VSD FANE-21 (Exhaust Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60240_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO00 | C7S06,00 |  |  |  | DO | C7 | 6 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S06,01 |  |  | C7S06- | PCY-60215_DO_1 |  | MCC Room | JB-602 | Spray Dryer | PCY-60215 | PUMP | 5th | 325-01-600-PD-03 | - | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-60215_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO01 | C7S06,01 |  |  |  | DO | C7 | 6 | 1 |  | 3 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S06,02 |  |  | C7S06- | XS-60240A_DO_1 |  | MCC Room | JB-602 | Spray Dryer | XS-60240A | 0 | 4th | 325-01-600-PD-05 | - | Start / Stop Command for BGHS-21 (Bag House Air Pulsing) |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-60240A_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO02 | C7S06,02 |  |  |  | DO | C7 | 6 | 2 |  | 0 | 1 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S06,03 |  |  | C7S06- | XS-60241A_DO_1 |  | MCC Room | JB-602 | Spray Dryer | XS-60241A | 0 | 4th | 325-01-600-PD-05 | - | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-60241A_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO03 | C7S06,03 |  |  |  | DO | C7 | 6 | 3 |  | 0 | 1 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S06,04 |  |  | C7S06- | XS-60242A_DO_1 |  | MCC Room | JB-602 | Spray Dryer | XS-60242A | 0 | 3rd | 325-01-600-PD-05 | - | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-60242A_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO04 | C7S06,04 |  |  |  | DO | C7 | 6 | 4 |  | 0 | 1 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S06,04 |  |  | C7S06- | XS-60243A_DO_1 |  | MCC Room | JB-602 | Spray Dryer | XS-60243A | 0 | 4th | 325-01-600-PD-05 | - | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-60243A_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO04 | C7S06,04 |  |  |  | DO | C7 | 6 | 4 |  | 0 | 1 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S06,06 |  |  | C7S06- | XS-60260_DO_1 |  | MCC Room | JB-606 | Spray Dryer | XS-60260 | 0 | 6th | 325-01-600-PD-05 | - | Start / Stop Command for FWDP-21 (Fire Deluge) |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-60260_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO06 | C7S06,06 |  |  |  | DO | C7 | 6 | 6 |  | 0 | 1 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,07 |  |  | C7S06- | BFY-60220_DO_1 |  | MCC Room | JB-607 | Spray Dryer | BFY-60220 | 0 | 7th | 325-01-600-PD-04 | - | Start / Stop Command for VSD FANS-22 (Cooling Fan) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-60220_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO07 | C7S06,07 |  |  |  | DO | C7 | 6 | 7 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S06,08 |  |  | C7S06- | XS-FH-60210A_DO_1 |  | MCC Room | JB-607 | Spray Dryer | XS-FH-60210A | 0 | 7th | 325-01-600-PD-06 | - | Start / Stop Command Burner Remote Start for AHTR-21 |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-FH-60210A_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO08 | C7S06,08 |  |  |  | DO | C7 | 6 | 8 |  | 0 | 1 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S06,09 |  |  | C7S06- | XS-FH-60210B_DO_1 |  | MCC Room | JB-607 | Spray Dryer | XS-FH-60210B | 0 | 7th | 325-01-600-PD-06 | - | Start / Stop Command Dryer Interlocks for AHTR-21 |  | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | XS-FH-60210B_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO09 | C7S06,09 |  |  |  | DO | C7 | 6 | 9 |  | 0 | 1 | 0 | 0 | 0 |  | Dry Contact
MCC | MCC | C7S06,10 |  |  | C7S06- | BFY-61302_DO_1 |  | MCC Room | JB-612 | Packing Tower | BFY-61302 | 0 | 2nd | 325-01-613-PD-05 | - | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-61302_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO10 | C7S06,10 |  |  |  | DO | C7 | 6 | 10 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S06,11 |  |  | C7S06- | RVM-61302_DO_1 |  | MCC Room | JB-612 | Packing Tower | RVM-61302 | 0 | 1st | 325-01-613-PD-03 | - | Start / Stop Command for FVNR RV-61302 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61302_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO11 | C7S06,11 |  |  |  | DO | C7 | 6 | 11 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,12 |  |  | C7S06- | RVM-61302_DO_2 |  | MCC Room | JB-612 | Packing Tower | RVM-61302 | 0 | 1st | 325-01-613-PD-03 | - | Start / Stop Command for FVNR RV-61302 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61302_DO_2 | DO | 2 | 2 | C7S06 | C7S06DO12 | C7S06,12 |  |  |  | DO | C7 | 6 | 12 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,13 |  |  | C7S06- | RVM-61303_DO_1 |  | MCC Room | JB-612 | Packing Tower | RVM-61303 | 0 | 1st | 325-01-613-PD-05 | - | Start / Stop Command for FVNR RV-61303 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61303_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO13 | C7S06,13 |  |  |  | DO | C7 | 6 | 13 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,14 |  |  | C7S06- | RVM-61303_DO_2 |  | MCC Room | JB-612 | Packing Tower | RVM-61303 | 0 | 1st | 325-01-613-PD-05 | - | Start / Stop Command for FVNR RV-61303 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61303_DO_2 | DO | 2 | 2 | C7S06 | C7S06DO14 | C7S06,14 |  |  |  | DO | C7 | 6 | 14 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,15 |  |  | C7S06- | SCM-61301_DO_1 |  | MCC Room | JB-612 | Packing Tower | SCM-61301 | 0 | 4th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR SC-61301 (Sifter ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | SCM-61301_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO15 | C7S06,15 |  |  |  | DO | C7 | 6 | 15 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,16 |  |  | C7S06- | SCM-61301_DO_2 |  | MCC Room | JB-612 | Packing Tower | SCM-61301 | 0 | 4th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR SC-61301 (Sifter ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | SCM-61301_DO_2 | DO | 2 | 2 | C7S06 | C7S06DO16 | C7S06,16 |  |  |  | DO | C7 | 6 | 16 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,17 |  |  | C7S06- | SCM-61302_DO_1 |  | MCC Room | JB-612 | Packing Tower | SCM-61302 | 0 | 4th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR SC-61302 (Sifter ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | SCM-61302_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO17 | C7S06,17 |  |  |  | DO | C7 | 6 | 17 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,18 |  |  | C7S06- | SCM-61302_DO_2 |  | MCC Room | JB-612 | Packing Tower | SCM-61302 | 0 | 4th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR SC-61302 (Sifter ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | SCM-61302_DO_2 | DO | 2 | 2 | C7S06 | C7S06DO18 | C7S06,18 |  |  |  | DO | C7 | 6 | 18 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,19 |  |  | C7S06- | BFY-61301_DO_1 |  | MCC Room | JB-618 | Packing Tower | BFY-61301 | 0 | 8th | 325-01-613-PD-01 | - | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-61301_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO19 | C7S06,19 |  |  |  | DO | C7 | 6 | 19 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S06,20 |  |  | C7S06- | BFY-61303_DO_1 |  | MCC Room | JB-618 | Packing Tower | BFY-61303 | 0 | 9th | 325-01-613-PD-01 | - | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) |  | Require I/O DI= 1,DO=1,AI=0,AO=0,Bus=1 |  | BFY-61303_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO20 | C7S06,20 |  |  |  | DO | C7 | 6 | 20 |  | 1 | 1 | 0 | 0 | 1 |  | 24 VDC energized
MCC | MCC | C7S06,21 |  |  | C7S06- | BLM-61302_DO_1 |  | MCC Room | JB-618 | Packing Tower | BLM-61302 | 0 | 5th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | BLM-61302_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO21 | C7S06,21 |  |  |  | DO | C7 | 6 | 21 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,22 |  |  | C7S06- | BLM-61302_DO_2 |  | MCC Room | JB-618 | Packing Tower | BLM-61302 | 0 | 5th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | BLM-61302_DO_2 | DO | 2 | 2 | C7S06 | C7S06DO22 | C7S06,22 |  |  |  | DO | C7 | 6 | 22 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,23 |  |  | C7S06- | RVM-60204_DO_1 |  | MCC Room | JB-618 | Packing Tower | RVM-60204 | 0 | 9th | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60204_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO23 | C7S06,23 |  |  |  | DO | C7 | 6 | 23 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,24 |  |  | C7S06- | RVM-60204_DO_2 |  | MCC Room | JB-618 | Packing Tower | RVM-60204 | 0 | 9th | 325-01-600-PD-08 | - | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-60204_DO_2 | DO | 2 | 2 | C7S06 | C7S06DO24 | C7S06,24 |  |  |  | DO | C7 | 6 | 24 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,25 |  |  | C7S06- | RVM-61301_DO_1 |  | MCC Room | JB-618 | Packing Tower | RVM-61301 | 0 | 6th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR RV-61301 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61301_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO25 | C7S06,25 |  |  |  | DO | C7 | 6 | 25 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,26 |  |  | C7S06- | RVM-61301_DO_2 |  | MCC Room | JB-618 | Packing Tower | RVM-61301 | 0 | 6th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR RV-61301 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61301_DO_2 | DO | 2 | 2 | C7S06 | C7S06DO26 | C7S06,26 |  |  |  | DO | C7 | 6 | 26 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,27 |  |  | C7S06- | RVM-61304_DO_1 |  | MCC Room | JB-618 | Packing Tower | RVM-61304 | 0 | 9th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR RV-61304 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61304_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO27 | C7S06,27 |  |  |  | DO | C7 | 6 | 27 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,28 |  |  | C7S06- | RVM-61304_DO_2 |  | MCC Room | JB-618 | Packing Tower | RVM-61304 | 0 | 9th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR RV-61304 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61304_DO_2 | DO | 2 | 2 | C7S06 | C7S06DO28 | C7S06,28 |  |  |  | DO | C7 | 6 | 28 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,29 |  |  | C7S06- | RVM-61305_DO_1 |  | MCC Room | JB-618 | Packing Tower | RVM-61305 | 0 | 9th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR RV-61305 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61305_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO29 | C7S06,29 |  |  |  | DO | C7 | 6 | 29 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | MCC | C7S06,30 |  |  | C7S06- | RVM-61305_DO_2 |  | MCC Room | JB-618 | Packing Tower | RVM-61305 | 0 | 9th | 325-01-613-PD-01 | - | Start / Stop Command for FVNR RV-61305 |  | Require I/O DI= 2,DO=2,AI=0,AO=0,Bus=0 |  | RVM-61305_DO_2 | DO | 2 | 2 | C7S06 | C7S06DO30 | C7S06,30 |  |  |  | DO | C7 | 6 | 30 |  | 2 | 2 | 0 | 0 | 0 |  | 24 VDC energized
MCC | JB-601 | C7S06,31 |  |  | C7S06- | PCY-60205_DO_1 |  | Spray Dryer 1st Floor | MCC | Spray Dryer | PCY-60205 |  | 1st | 325-01-600-PD-01 | - |  |  | Require I/O DI= 3,DO=1,AI=0,AO=0,Bus=1 |  | PCY-60205_DO_1 | DO | 2 | 1 | C7S06 | C7S06DO31 | C7S06,31 |  |  |  | DO | C7 | 6 | 31 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | C7S07,08 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO08 | C7S07,08 |  |  |  | DO | C7 | 7 | 8 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,09 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO09 | C7S07,09 |  |  |  | DO | C7 | 7 | 9 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,10 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO10 | C7S07,10 |  |  |  | DO | C7 | 7 | 10 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,11 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO11 | C7S07,11 |  |  |  | DO | C7 | 7 | 11 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,12 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO12 | C7S07,12 |  |  |  | DO | C7 | 7 | 12 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,13 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO13 | C7S07,13 |  |  |  | DO | C7 | 7 | 13 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,14 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO14 | C7S07,14 |  |  |  | DO | C7 | 7 | 14 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,15 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO15 | C7S07,15 |  |  |  | DO | C7 | 7 | 15 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,16 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO16 | C7S07,16 |  |  |  | DO | C7 | 7 | 16 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,17 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO17 | C7S07,17 |  |  |  | DO | C7 | 7 | 17 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,18 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO18 | C7S07,18 |  |  |  | DO | C7 | 7 | 18 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,19 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO19 | C7S07,19 |  |  |  | DO | C7 | 7 | 19 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,20 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO20 | C7S07,20 |  |  |  | DO | C7 | 7 | 20 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,21 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO21 | C7S07,21 |  |  |  | DO | C7 | 7 | 21 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,22 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO22 | C7S07,22 |  |  |  | DO | C7 | 7 | 22 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,23 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO23 | C7S07,23 |  |  |  | DO | C7 | 7 | 23 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,24 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO24 | C7S07,24 |  |  |  | DO | C7 | 7 | 24 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,25 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO25 | C7S07,25 |  |  |  | DO | C7 | 7 | 25 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,26 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO26 | C7S07,26 |  |  |  | DO | C7 | 7 | 26 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,27 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO27 | C7S07,27 |  |  |  | DO | C7 | 7 | 27 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,28 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO28 | C7S07,28 |  |  |  | DO | C7 | 7 | 28 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,29 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO29 | C7S07,29 |  |  |  | DO | C7 | 7 | 29 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,30 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO30 | C7S07,30 |  |  |  | DO | C7 | 7 | 30 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | C7S07,31 |  |  | C7S07- | Spare_DO_0 |  | MCC Room |  |  | Spare | [6 empty] | Require I/O DI= 0,DO=1,AI=0,AO=0,Bus=0 |  | Spare_DO_0 | DO | 2 | 0 | C7S07 | C7S07DO31 | C7S07,31 |  |  |  | DO | C7 | 7 | 31 |  | 0 | 1 | 0 | 0 | 0

## Chassis_C1
CHASSIS C1 ¦ PANEL / ENCLOSURE: =CA1+MCP-M1 ¦ PROJECT JET COOKER
Item | Slot | Point | Channel Code | Terminal | Card Model | I/O Type | Signal | Instrument Tag | Instrument Description | PLC Tag | P&ID No. | Destination JB | Status
1 | 3 | 0 | C1S03,00 | C1S03-X1 | 1756-IB32-0 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
2 | 3 | 1 | C1S03,01 | C1S03-X1 | 1756-IB32-1 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
3 | 3 | 2 | C1S03,02 | C1S03-X1 | 1756-IB32-2 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
4 | 3 | 3 | C1S03,03 | C1S03-X1 | 1756-IB32-3 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
5 | 3 | 4 | C1S03,04 | C1S03-X1 | 1756-IB32-4 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
6 | 3 | 5 | C1S03,05 | C1S03-X1 | 1756-IB32-5 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
7 | 3 | 6 | C1S03,06 | C1S03-X1 | 1756-IB32-6 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
8 | 3 | 7 | C1S03,07 | C1S03-X1 | 1756-IB32-7 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
9 | 3 | 8 | C1S03,08 | C1S03-X1 | 1756-IB32-8 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
10 | 3 | 9 | C1S03,09 | C1S03-X1 | 1756-IB32-9 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
11 | 3 | 10 | C1S03,10 | C1S03-X1 | 1756-IB32-10 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
12 | 3 | 11 | C1S03,11 | C1S03-X1 | 1756-IB32-11 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
13 | 3 | 12 | C1S03,12 | C1S03-X1 | 1756-IB32-12 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
14 | 3 | 13 | C1S03,13 | C1S03-X1 | 1756-IB32-13 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
15 | 3 | 14 | C1S03,14 | C1S03-X1 | 1756-IB32-14 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
16 | 3 | 15 | C1S03,15 | C1S03-X1 | 1756-IB32-15 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | CA1 | SPARE
17 | 3 | 16 | C1S03,16 | C1S03-X2 | 1756-IB32-16 | DI | Dry Contact | FSL-40201 | Flow Switch | FSL-40201_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
18 | 3 | 17 | C1S03,17 | C1S03-X2 | 1756-IB32-17 | DI | Dry Contact | FSL-40202 | Flow Switch | FSL-40202_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
19 | 3 | 18 | C1S03,18 | C1S03-X2 | 1756-IB32-18 | DI | 4 - 20 mA,Pulse | FT-40201 | Coriolis Flow Transmitter | FT-40201_DI_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
20 | 3 | 19 | C1S03,19 | C1S03-X2 | 1756-IB32-19 | DI | 4 - 20 mA,Pulse | FT-40202 | Magnetic Flow Transmitter | FT-40202_DI_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
21 | 3 | 20 | C1S03,20 | C1S03-X2 | 1756-IB32-20 | DI | Dry Contact | HV-40201 | Manual Valve With Position Switch | HV-40201_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
22 | 3 | 21 | C1S03,21 | C1S03-X2 | 1756-IB32-21 | DI | Dry Contact | HV-40202 | Manual Valve With Position Switch | HV-40202_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
23 | 3 | 22 | C1S03,22 | C1S03-X2 | 1756-IB32-22 | DI | Dry Contact | HV-40203 | Manual Valve With Position Switch | HV-40203_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
24 | 3 | 23 | C1S03,23 | C1S03-X2 | 1756-IB32-23 | DI | Dry Contact | HV-40204 | Manual Valve With Position Switch | HV-40204_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
25 | 3 | 24 | C1S03,24 | C1S03-X2 | 1756-IB32-24 | DI | Dry Contact | HV-40205 | Manual Valve With Position Switch | HV-40205_DI_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
26 | 3 | 25 | C1S03,25 | C1S03-X2 | 1756-IB32-25 | DI | Dry Contact | HV-40206 | Manual Valve With Position Switch | HV-40206_DI_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
27 | 3 | 26 | C1S03,26 | C1S03-X2 | 1756-IB32-26 | DI | 24 VDC energized | XV-40201A | 0 | XV-40201A_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
28 | 3 | 27 | C1S03,27 | C1S03-X2 | 1756-IB32-27 | DI | 24 VDC energized | XV-40201A | 0 | XV-40201A_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
29 | 3 | 28 | C1S03,28 | C1S03-X2 | 1756-IB32-28 | DI | 24 VDC energized | XV-40201B | 0 | XV-40201B_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
30 | 3 | 29 | C1S03,29 | C1S03-X2 | 1756-IB32-29 | DI | 24 VDC energized | XV-40201B | 0 | XV-40201B_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
31 | 3 | 30 | C1S03,30 | C1S03-X2 | 1756-IB32-30 | DI | 24 VDC energized | XV-40201C | 0 | XV-40201C_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
32 | 3 | 31 | C1S03,31 | C1S03-X2 | 1756-IB32-31 | DI | 24 VDC energized | XV-40201C | 0 | XV-40201C_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
33 | 4 | 0 | C1S04,00 | C1S04-X1 | 1756-IB32-0 | DI | 24 VDC energized | XV-40201D | 0 | XV-40201D_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
34 | 4 | 1 | C1S04,01 | C1S04-X1 | 1756-IB32-1 | DI | 24 VDC energized | XV-40201D | 0 | XV-40201D_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
35 | 4 | 2 | C1S04,02 | C1S04-X1 | 1756-IB32-2 | DI | 24 VDC energized | XV-40201E | 0 | XV-40201E_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
36 | 4 | 3 | C1S04,03 | C1S04-X1 | 1756-IB32-3 | DI | 24 VDC energized | XV-40201E | 0 | XV-40201E_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
37 | 4 | 4 | C1S04,04 | C1S04-X1 | 1756-IB32-4 | DI | 24 VDC energized | XV-40201F | 0 | XV-40201F_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
38 | 4 | 5 | C1S04,05 | C1S04-X1 | 1756-IB32-5 | DI | 24 VDC energized | XV-40201F | 0 | XV-40201F_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
39 | 4 | 6 | C1S04,06 | C1S04-X1 | 1756-IB32-6 | DI | 24 VDC energized | XV-40201G | 0 | XV-40201G_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
40 | 4 | 7 | C1S04,07 | C1S04-X1 | 1756-IB32-7 | DI | 24 VDC energized | XV-40201G | 0 | XV-40201G_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
41 | 4 | 8 | C1S04,08 | C1S04-X1 | 1756-IB32-8 | DI | 24 VDC energized | XV-40201H | 0 | XV-40201H_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
42 | 4 | 9 | C1S04,09 | C1S04-X1 | 1756-IB32-9 | DI | 24 VDC energized | XV-40201H | 0 | XV-40201H_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
43 | 4 | 11 | C1S04,11 | C1S04-X1 | 1756-IB32-11 | DI | 24 VDC energized | XV-40202A | 0 | XV-40202A_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
44 | 4 | 12 | C1S04,12 | C1S04-X1 | 1756-IB32-12 | DI | 24 VDC energized | XV-40202B | 0 | XV-40202B_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
45 | 4 | 13 | C1S04,13 | C1S04-X1 | 1756-IB32-13 | DI | 24 VDC energized | XV-40202B | 0 | XV-40202B_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
46 | 4 | 14 | C1S04,14 | C1S04-X1 | 1756-IB32-14 | DI | 24 VDC energized | XV-40202C | 0 | XV-40202C_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
47 | 4 | 15 | C1S04,15 | C1S04-X1 | 1756-IB32-15 | DI | 24 VDC energized | XV-40202C | 0 | XV-40202C_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
48 | 4 | 16 | C1S04,16 | C1S04-X2 | 1756-IB32-16 | DI | 24 VDC energized | XV-40202D | 0 | XV-40202D_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
49 | 4 | 17 | C1S04,17 | C1S04-X2 | 1756-IB32-17 | DI | 24 VDC energized | XV-40202D | 0 | XV-40202D_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
50 | 4 | 18 | C1S04,18 | C1S04-X2 | 1756-IB32-18 | DI | 24 VDC energized | XV-40202E | 0 | XV-40202E_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
51 | 4 | 19 | C1S04,19 | C1S04-X2 | 1756-IB32-19 | DI | 24 VDC energized | XV-40202A | 0 | XV-40202A_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
52 | 4 | 19 | C1S04,19 | C1S04-X2 | 1756-IB32-19 | DI | 24 VDC energized | XV-40202E | 0 | XV-40202E_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
53 | 4 | 20 | C1S04,20 | C1S04-X2 | 1756-IB32-20 | DI | 24 VDC energized | XV-40202F | 0 | XV-40202F_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
54 | 4 | 21 | C1S04,21 | C1S04-X2 | 1756-IB32-21 | DI | 24 VDC energized | XV-40202F | 0 | XV-40202F_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
55 | 4 | 22 | C1S04,22 | C1S04-X2 | 1756-IB32-22 | DI | 24 VDC energized | XV-40202G | 0 | XV-40202G_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
56 | 4 | 23 | C1S04,23 | C1S04-X2 | 1756-IB32-23 | DI | 24 VDC energized | XV-40202G | 0 | XV-40202G_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
57 | 4 | 24 | C1S04,24 | C1S04-X2 | 1756-IB32-24 | DI | 24 VDC energized | XV-40202H | 0 | XV-40202H_DI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
58 | 4 | 25 | C1S04,25 | C1S04-X2 | 1756-IB32-25 | DI | 24 VDC energized | XV-40202H | 0 | XV-40202H_DI_2 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
59 | 4 | 26 | C1S04,26 | C1S04-X2 | 1756-IB32-26 | DI | 24 VDC energized | XV-40203B | 0 | XV-40203B_DI_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
60 | 4 | 27 | C1S04,27 | C1S04-X2 | 1756-IB32-27 | DI | 24 VDC energized | XV-40203B | 0 | XV-40203B_DI_2 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
61 | 4 | 28 | C1S04,28 | C1S04-X2 | 1756-IB32-28 | DI | 24 VDC energized | XV-40203C | 0 | XV-40203C_DI_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
62 | 4 | 29 | C1S04,29 | C1S04-X2 | 1756-IB32-29 | DI | 24 VDC energized | XV-40203C | 0 | XV-40203C_DI_2 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
63 | 4 | 30 | C1S04,30 | C1S04-X2 | 1756-IB32-30 | DI | 24 VDC energized | XV-40203D | 0 | XV-40203D_DI_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
64 | 4 | 31 | C1S04,31 | C1S04-X2 | 1756-IB32-31 | DI | 24 VDC energized | XV-40203D | 0 | XV-40203D_DI_2 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
65 | 5 | 0 | C1S05,00 | C1S05-X1 | 1756-IB32-0 | DI | 24 VDC energized | XV-40203E | 0 | XV-40203E_DI_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
66 | 5 | 1 | C1S05,01 | C1S05-X1 | 1756-IB32-1 | DI | 24 VDC energized | XV-40203E | 0 | XV-40203E_DI_2 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
67 | 5 | 2 | C1S05,02 | C1S05-X1 | 1756-IB32-2 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
68 | 5 | 3 | C1S05,03 | C1S05-X1 | 1756-IB32-3 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
69 | 5 | 4 | C1S05,04 | C1S05-X1 | 1756-IB32-4 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
70 | 5 | 5 | C1S05,05 | C1S05-X1 | 1756-IB32-5 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
71 | 5 | 6 | C1S05,06 | C1S05-X1 | 1756-IB32-6 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
72 | 5 | 7 | C1S05,07 | C1S05-X1 | 1756-IB32-7 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
73 | 5 | 8 | C1S05,08 | C1S05-X1 | 1756-IB32-8 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
74 | 5 | 9 | C1S05,09 | C1S05-X1 | 1756-IB32-9 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
75 | 5 | 10 | C1S05,10 | C1S05-X1 | 1756-IB32-10 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
76 | 5 | 11 | C1S05,11 | C1S05-X1 | 1756-IB32-11 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
77 | 5 | 12 | C1S05,12 | C1S05-X1 | 1756-IB32-12 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
78 | 5 | 13 | C1S05,13 | C1S05-X1 | 1756-IB32-13 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
79 | 5 | 14 | C1S05,14 | C1S05-X1 | 1756-IB32-14 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
80 | 5 | 15 | C1S05,15 | C1S05-X1 | 1756-IB32-15 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-401 | SPARE
81 | 5 | 16 | C1S05,16 | C1S05-X2 | 1756-IB32-16 | DI | 0 | ES-60202 | 0 | ES-60202_DI_1 | 325-01-600-PD-01 | JB-601 | ACTIVE
82 | 5 | 17 | C1S05,17 | C1S05-X2 | 1756-IB32-17 | DI | 0 | FS-60205 | Flow Switch | FS-60205_DI_1 | 3-25-01-602-PD-01 | JB-601 | ACTIVE
83 | 5 | 18 | C1S05,18 | C1S05-X2 | 1756-IB32-18 | DI | Dry Contact | LSL-60201 | 0 | LSL-60201_DI_1 | 3-25-01-602-PD-11 | JB-601 | ACTIVE
84 | 5 | 19 | C1S05,19 | C1S05-X2 | 1756-IB32-19 | DI | 24 VDC energized | SV-60201 | 0 | SV-60201_DI_1 | 3-25-01-602-PD-08 | JB-601 | ACTIVE
85 | 5 | 20 | C1S05,20 | C1S05-X2 | 1756-IB32-20 | DI | 24 VDC energized | SV-60201 | 0 | SV-60201_DI_2 | 3-25-01-602-PD-08 | JB-601 | ACTIVE
86 | 5 | 21 | C1S05,21 | C1S05-X2 | 1756-IB32-21 | DI | 24 VDC energized | SV-60202 | 0 | SV-60202_DI_1 | 3-25-01-602-PD-08 | JB-601 | ACTIVE
87 | 5 | 22 | C1S05,22 | C1S05-X2 | 1756-IB32-22 | DI | 24 VDC energized | SV-60202 | 0 | SV-60202_DI_2 | 3-25-01-602-PD-08 | JB-601 | ACTIVE
88 | 5 | 23 | C1S05,23 | C1S05-X2 | 1756-IB32-23 | DI | 24 VDC energized | SV-60203 | 0 | SV-60203_DI_1 | 3-25-01-602-PD-08 | JB-601 | ACTIVE
89 | 5 | 24 | C1S05,24 | C1S05-X2 | 1756-IB32-24 | DI | 24 VDC energized | SV-60203 | 0 | SV-60203_DI_2 | 3-25-01-602-PD-08 | JB-601 | ACTIVE
90 | 5 | 25 | C1S05,25 | C1S05-X2 | 1756-IB32-25 | DI | Dry Contact | VS-60205 | Vibration Switch | VS-60205_DI_1 | 3-25-01-602-PD-01 | JB-601 | ACTIVE
91 | 5 | 26 | C1S05,26 | C1S05-X2 | 1756-IB32-26 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
92 | 5 | 27 | C1S05,27 | C1S05-X2 | 1756-IB32-27 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
93 | 5 | 28 | C1S05,28 | C1S05-X2 | 1756-IB32-28 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
94 | 5 | 29 | C1S05,29 | C1S05-X2 | 1756-IB32-29 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
95 | 5 | 30 | C1S05,30 | C1S05-X2 | 1756-IB32-30 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
96 | 5 | 31 | C1S05,31 | C1S05-X2 | 1756-IB32-31 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
97 | 6 | 0 | C1S06,00 | C1S06-X1 | 1756-IB32-0 | DI | Dry Contact | XA-60202A | 0 | XA-60202A_DI_1 | 325-01-600-PD-08 | JB-601 | ACTIVE
98 | 6 | 1 | C1S06,01 | C1S06-X1 | 1756-IB32-1 | DI | Dry Contact | XA-60202B | 0 | XA-60202B_DI_1 | 325-01-600-PD-08 | JB-601 | ACTIVE
99 | 6 | 2 | C1S06,02 | C1S06-X1 | 1756-IB32-2 | DI | Dry Contact | XA-60202C | 0 | XA-60202C_DI_1 | 325-01-600-PD-08 | JB-601 | ACTIVE
100 | 6 | 3 | C1S06,03 | C1S06-X1 | 1756-IB32-3 | DI | Dry Contact | XA-60202D | 0 | XA-60202D_DI_1 | 325-01-600-PD-08 | JB-601 | ACTIVE
101 | 6 | 4 | C1S06,04 | C1S06-X1 | 1756-IB32-4 | DI | Dry Contact | XA-60202E | 0 | XA-60202E_DI_1 | 325-01-600-PD-08 | JB-601 | ACTIVE
102 | 6 | 5 | C1S06,05 | C1S06-X1 | 1756-IB32-5 | DI | Dry Contact | XA-60202F | 0 | XA-60202F_DI_1 | 325-01-600-PD-08 | JB-601 | ACTIVE
103 | 6 | 6 | C1S06,06 | C1S06-X1 | 1756-IB32-6 | DI | Dry Contact | XA-60202G | 0 | XA-60202G_DI_1 | 325-01-600-PD-08 | JB-601 | ACTIVE
104 | 6 | 7 | C1S06,07 | C1S06-X1 | 1756-IB32-7 | DI | Dry Contact | XA-60202H | 0 | XA-60202H_DI_1 | 325-01-600-PD-08 | JB-601 | ACTIVE
105 | 6 | 8 | C1S06,08 | C1S06-X1 | 1756-IB32-8 | DI | - | XA-60202I | - | XA-60202I_DI_1 | 325-01-600-PD-08 | JB-601 | ACTIVE
106 | 6 | 9 | C1S06,09 | C1S06-X1 | 1756-IB32-9 | DI | Dry Contact | XA-60202J | 0 | XA-60202J_DI_1 | 325-01-600-PD-08 | JB-601 | ACTIVE
107 | 6 | 10 | C1S06,10 | C1S06-X1 | 1756-IB32-10 | DI | Dry Contact | XA-60202K | 0 | XA-60202K_DI_1 | 325-01-600-PD-08 | JB-601 | ACTIVE
108 | 6 | 11 | C1S06,11 | C1S06-X1 | 1756-IB32-11 | DI | Dry Contact | XA-60202L | 0 | XA-60202L_DI_1 | 325-01-600-PD-08 | JB-601 | ACTIVE
109 | 6 | 12 | C1S06,12 | C1S06-X1 | 1756-IB32-12 | DI | Dry Contact | XA-60202M | 0 | XA-60202M_DI_1 | 325-01-600-PD-08 | JB-601 | ACTIVE
110 | 6 | 13 | C1S06,13 | C1S06-X1 | 1756-IB32-13 | DI | 24 VDC energized | XV-60202 | 0 | XV-60202_DI_1 | 3-25-01-602-PD-11 | JB-601 | ACTIVE
111 | 6 | 14 | C1S06,14 | C1S06-X1 | 1756-IB32-14 | DI | 24 VDC energized | XV-60202 | 0 | XV-60202_DI_2 | 3-25-01-602-PD-11 | JB-601 | ACTIVE
112 | 6 | 15 | C1S06,15 | C1S06-X1 | 1756-IB32-15 | DI | 24 VDC energized,Dry Contact | XV-60205A | 0 | XV-60205A_DI_1 | 3-25-01-602-PD-01 | JB-601 | ACTIVE
113 | 6 | 16 | C1S06,16 | C1S06-X2 | 1756-IB32-16 | DI | 24 VDC energized,Dry Contact | XV-60205A | 0 | XV-60205A_DI_2 | 3-25-01-602-PD-01 | JB-601 | ACTIVE
114 | 6 | 17 | C1S06,17 | C1S06-X2 | 1756-IB32-17 | DI | - | XV-60240D | - | XV-60240D_DI_1 | 325-01-600-PD-05 | JB-601 | ACTIVE
115 | 6 | 18 | C1S06,18 | C1S06-X2 | 1756-IB32-18 | DI | - | XV-60240D | - | XV-60240D_DI_2 | 3-25-01-602-PD-05 | JB-601 | ACTIVE
116 | 6 | 19 | C1S06,19 | C1S06-X2 | 1756-IB32-19 | DI | - | XV-60240D | - | XV-60240D_DI_1 | 325-01-600-PD-05 | JB-601 | ACTIVE
117 | 6 | 20 | C1S06,20 | C1S06-X2 | 1756-IB32-20 | DI | - | XV-60240D | - | XV-60240D_DI_2 | 3-25-01-602-PD-05 | JB-601 | ACTIVE
118 | 6 | 21 | C1S06,21 | C1S06-X2 | 1756-IB32-21 | DI | 0 | YA-60205 | 0 | YA-60205_DI_1 | 325-01-600-PD-01 | JB-601 | ACTIVE
119 | 6 | 22 | C1S06,22 | C1S06-X2 | 1756-IB32-22 | DI | 0 | YI-60205 | 0 | YI-60205_DI_1 | 325-01-600-PD-01 | JB-601 | ACTIVE
120 | 6 | 23 | C1S06,23 | C1S06-X2 | 1756-IB32-23 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
121 | 6 | 24 | C1S06,24 | C1S06-X2 | 1756-IB32-24 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
122 | 6 | 25 | C1S06,25 | C1S06-X2 | 1756-IB32-25 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
123 | 6 | 26 | C1S06,26 | C1S06-X2 | 1756-IB32-26 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
124 | 6 | 27 | C1S06,27 | C1S06-X2 | 1756-IB32-27 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
125 | 6 | 28 | C1S06,28 | C1S06-X2 | 1756-IB32-28 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
126 | 6 | 29 | C1S06,29 | C1S06-X2 | 1756-IB32-29 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
127 | 6 | 30 | C1S06,30 | C1S06-X2 | 1756-IB32-30 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
128 | 6 | 31 | C1S06,31 | C1S06-X2 | 1756-IB32-31 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-601 | SPARE
129 | 7 | 0 | C1S07,00 | C1S07-X1 | 1756-OB32-0 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
130 | 7 | 1 | C1S07,01 | C1S07-X1 | 1756-OB32-1 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
131 | 7 | 2 | C1S07,02 | C1S07-X1 | 1756-OB32-2 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
132 | 7 | 3 | C1S07,03 | C1S07-X1 | 1756-OB32-3 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
133 | 7 | 4 | C1S07,04 | C1S07-X1 | 1756-OB32-4 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
134 | 7 | 5 | C1S07,05 | C1S07-X1 | 1756-OB32-5 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
135 | 7 | 6 | C1S07,06 | C1S07-X1 | 1756-OB32-6 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
136 | 7 | 7 | C1S07,07 | C1S07-X1 | 1756-OB32-7 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
137 | 7 | 8 | C1S07,08 | C1S07-X1 | 1756-OB32-8 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
138 | 7 | 9 | C1S07,09 | C1S07-X1 | 1756-OB32-9 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
139 | 7 | 10 | C1S07,10 | C1S07-X1 | 1756-OB32-10 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
140 | 7 | 11 | C1S07,11 | C1S07-X1 | 1756-OB32-11 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
141 | 7 | 12 | C1S07,12 | C1S07-X1 | 1756-OB32-12 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
142 | 7 | 13 | C1S07,13 | C1S07-X1 | 1756-OB32-13 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
143 | 7 | 14 | C1S07,14 | C1S07-X1 | 1756-OB32-14 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
144 | 7 | 15 | C1S07,15 | C1S07-X1 | 1756-OB32-15 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | CA1 | SPARE
145 | 7 | 16 | C1S07,16 | C1S07-X2 | 1756-OB32-16 | DO | 24 VDC energized | XV-40202E | 0 | XV-40202E_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
146 | 7 | 17 | C1S07,17 | C1S07-X2 | 1756-OB32-17 | DO | 24 VDC energized | XV-40202F | 0 | XV-40202F_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
147 | 7 | 18 | C1S07,18 | C1S07-X2 | 1756-OB32-18 | DO | 24 VDC energized | XV-40202G | 0 | XV-40202G_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
148 | 7 | 19 | C1S07,19 | C1S07-X2 | 1756-OB32-19 | DO | 24 VDC energized | XV-40202H | 0 | XV-40202H_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
149 | 7 | 20 | C1S07,20 | C1S07-X2 | 1756-OB32-20 | DO | 24 VDC energized | XV-40203B | 0 | XV-40203B_DO_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
150 | 7 | 21 | C1S07,21 | C1S07-X2 | 1756-OB32-21 | DO | 24 VDC energized | XV-40203C | 0 | XV-40203C_DO_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
151 | 7 | 22 | C1S07,22 | C1S07-X2 | 1756-OB32-22 | DO | 24 VDC energized | XV-40203D | 0 | XV-40203D_DO_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
152 | 7 | 23 | C1S07,23 | C1S07-X2 | 1756-OB32-23 | DO | 24 VDC energized | XV-40203E | 0 | XV-40203E_DO_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
153 | 7 | 24 | C1S07,24 | C1S07-X2 | 1756-OB32-24 | DO | 24 VDC energized | SV-40201 | 0 | SV-40201_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
154 | 7 | 25 | C1S07,25 | C1S07-X2 | 1756-OB32-25 | DO | 24 VDC energized | SV-40202 | 0 | SV-40202_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
155 | 7 | 26 | C1S07,26 | C1S07-X2 | 1756-OB32-26 | DO | 24 VDC energized | SV-40203 | 0 | SV-40203_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
156 | 7 | 27 | C1S07,27 | C1S07-X2 | 1756-OB32-27 | DO | 24 VDC energized | SV-40204 | 0 | SV-40204_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
157 | 7 | 28 | C1S07,28 | C1S07-X2 | 1756-OB32-28 | DO | 24 VDC energized | XV-40201A | 0 | XV-40201A_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
158 | 7 | 29 | C1S07,29 | C1S07-X2 | 1756-OB32-29 | DO | 24 VDC energized | XV-40201B | 0 | XV-40201B_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
159 | 7 | 30 | C1S07,30 | C1S07-X2 | 1756-OB32-30 | DO | 24 VDC energized | XV-40201C | 0 | XV-40201C_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
160 | 7 | 31 | C1S07,31 | C1S07-X2 | 1756-OB32-31 | DO | 24 VDC energized | XV-40201D | 0 | XV-40201D_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
161 | 8 | 0 | C1S08,00 | C1S08-X1 | 1756-OB32-0 | DO | 24 VDC energized | XV-40201E | 0 | XV-40201E_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
162 | 8 | 1 | C1S08,01 | C1S08-X1 | 1756-OB32-1 | DO | 24 VDC energized | XV-40201F | 0 | XV-40201F_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
163 | 8 | 2 | C1S08,02 | C1S08-X1 | 1756-OB32-2 | DO | 24 VDC energized | XV-40201G | 0 | XV-40201G_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
164 | 8 | 3 | C1S08,03 | C1S08-X1 | 1756-OB32-3 | DO | 24 VDC energized | XV-40201H | 0 | XV-40201H_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
165 | 8 | 4 | C1S08,04 | C1S08-X1 | 1756-OB32-4 | DO | 24 VDC energized | XV-40202A | 0 | XV-40202A_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
166 | 8 | 5 | C1S08,05 | C1S08-X1 | 1756-OB32-5 | DO | 24 VDC energized | XV-40202B | 0 | XV-40202B_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
167 | 8 | 6 | C1S08,06 | C1S08-X1 | 1756-OB32-6 | DO | 24 VDC energized | XV-40202C | 0 | XV-40202C_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
168 | 8 | 7 | C1S08,07 | C1S08-X1 | 1756-OB32-7 | DO | 24 VDC energized | XV-40202D | 0 | XV-40202D_DO_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
169 | 8 | 8 | C1S08,08 | C1S08-X1 | 1756-OB32-8 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-401 | SPARE
170 | 8 | 9 | C1S08,09 | C1S08-X1 | 1756-OB32-9 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-401 | SPARE
171 | 8 | 10 | C1S08,10 | C1S08-X1 | 1756-OB32-10 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-401 | SPARE
172 | 8 | 11 | C1S08,11 | C1S08-X1 | 1756-OB32-11 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-401 | SPARE
173 | 8 | 12 | C1S08,12 | C1S08-X1 | 1756-OB32-12 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-401 | SPARE
174 | 8 | 13 | C1S08,13 | C1S08-X1 | 1756-OB32-13 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-401 | SPARE
175 | 8 | 14 | C1S08,14 | C1S08-X1 | 1756-OB32-14 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-401 | SPARE
176 | 8 | 15 | C1S08,15 | C1S08-X1 | 1756-OB32-15 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-401 | SPARE
177 | 8 | 16 | C1S08,16 | C1S08-X2 | 1756-OB32-16 | DO | 24 VDC energized | SV-60201 | 0 | SV-60201_DO_1 | 3-25-01-602-PD-08 | JB-601 | ACTIVE
178 | 8 | 17 | C1S08,17 | C1S08-X2 | 1756-OB32-17 | DO | 24 VDC energized | SV-60202 | 0 | SV-60202_DO_1 | 3-25-01-602-PD-08 | JB-601 | ACTIVE
179 | 8 | 18 | C1S08,18 | C1S08-X2 | 1756-OB32-18 | DO | 24 VDC energized | SV-60230 | 0 | SV-60230_DO_1 | 3-25-01-602-PD-04 | JB-601 | ACTIVE
180 | 8 | 19 | C1S08,19 | C1S08-X2 | 1756-OB32-19 | DO | 24 VDC energized | SV-60203 | 0 | SV-60203_DO_1 | 3-25-01-602-PD-08 | JB-601 | ACTIVE
181 | 8 | 20 | C1S08,20 | C1S08-X2 | 1756-OB32-20 | DO | 24 VDC energized | SV-60240A | 0 | SV-60240A_DO_1 | 3-25-01-602-PD-05 | JB-601 | ACTIVE
182 | 8 | 21 | C1S08,21 | C1S08-X2 | 1756-OB32-21 | DO | 24 VDC energized | SV-60231 | 0 | SV-60231_DO_1 | 3-25-01-602-PD-04 | JB-601 | ACTIVE
183 | 8 | 22 | C1S08,22 | C1S08-X2 | 1756-OB32-22 | DO | 24 VDC energized | SV-60240B | 0 | SV-60240B_DO_1 | 3-25-01-602-PD-05 | JB-601 | ACTIVE
184 | 8 | 23 | C1S08,23 | C1S08-X2 | 1756-OB32-23 | DO | 24 VDC energized | SV-60240C | 0 | SV-60240C_DO_1 | 3-25-01-602-PD-05 | JB-601 | ACTIVE
185 | 8 | 24 | C1S08,24 | C1S08-X2 | 1756-OB32-24 | DO | - | XV-60240D | - | XV-60240D_DO_1 | 325-01-600-PD-05 | JB-601 | ACTIVE
186 | 8 | 25 | C1S08,25 | C1S08-X2 | 1756-OB32-25 | DO | 24 VDC energized | XV-60251 | 0 | XV-60251_DO_1 | 3-25-01-602-PD-01 | JB-601 | ACTIVE
187 | 8 | 26 | C1S08,26 | C1S08-X2 | 1756-OB32-26 | DO | 24 VDC energized | XV-60202 | 0 | XV-60202_DO_1 | 3-25-01-602-PD-11 | JB-601 | ACTIVE
188 | 8 | 27 | C1S08,27 | C1S08-X2 | 1756-OB32-27 | DO | 24 VDC energized,Dry Contact | XV-60205A | 0 | XV-60205A_DO_1 | 3-25-01-602-PD-01 | JB-601 | ACTIVE
189 | 8 | 28 | C1S08,28 | C1S08-X2 | 1756-OB32-28 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-601 | SPARE
190 | 8 | 29 | C1S08,29 | C1S08-X2 | 1756-OB32-29 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-601 | SPARE
191 | 8 | 30 | C1S08,30 | C1S08-X2 | 1756-OB32-30 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-601 | SPARE
192 | 8 | 31 | C1S08,31 | C1S08-X2 | 1756-OB32-31 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-601 | SPARE
193 | 9 | 0 | C1S09,00 | C1S09-X1 | 1756-IF16-0 | AI | 4 - 20 mA,Pulse | FT-40201 | Coriolis Flow Transmitter | FT-40201_AI_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
194 | 9 | 1 | C1S09,01 | C1S09-X1 | 1756-IF16-1 | AI | 4 - 20 mA,Pulse | FT-40201 | Coriolis Flow Transmitter | FT-40201_AI_2 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
195 | 9 | 2 | C1S09,02 | C1S09-X1 | 1756-IF16-2 | AI | 4 - 20 mA,Pulse | FT-40202 | Magnetic Flow Transmitter | FT-40202_AI_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
196 | 9 | 3 | C1S09,03 | C1S09-X1 | 1756-IF16-3 | AI | 4 - 20 mA | LT-40203 | Level Transmitter | LT-40203_AI_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
197 | 9 | 4 | C1S09,04 | C1S09-X1 | 1756-IF16-4 | AI | 4 - 20 mA | LT-40201 | Level Transmitter | LT-40201_AI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
198 | 9 | 5 | C1S09,05 | C1S09-X1 | 1756-IF16-5 | AI | 4 - 20 mA | LT-40202 | Level Transmitter | LT-40202_AI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
199 | 9 | 6 | C1S09,06 | C1S09-X1 | 1756-IF16-6 | AI | 4 - 20 mA | pHT-40201 | PH Transmitter | pHT-40201_AI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
200 | 9 | 7 | C1S09,07 | C1S09-X1 | 1756-IF16-7 | AI | 4 - 20 mA | pHT-40202 | PH Transmitter | pHT-40202_AI_1 | 3-25-01-402-PD-01 | JB-401 | ACTIVE
201 | 9 | 8 | C1S09,08 | C1S09-X1 | 1756-IF16-8 | AI | 4 - 20 mA | PT-40201 | Pressure Transmitter | PT-40201_AI_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
202 | 9 | 9 | C1S09,09 | C1S09-X1 | 1756-IF16-9 | AI | 4 - 20 mA | PT-40202 | Pressure Transmitter | PT-40202_AI_1 | 3-25-01-402-PD-02 | JB-401 | ACTIVE
203 | 9 | 10 | C1S09,10 | C1S09-X1 | 1756-IF16-10 | AI | 4 - 20 mA | PT-60202 | Pressure Transmitter | PT-60202_AI_1 | 3-25-01-602-PD-01 | JB-401 | ACTIVE
204 | 9 | 11 | C1S09,11 | C1S09-X1 | 1756-IF16-11 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-401 | SPARE
205 | 9 | 12 | C1S09,12 | C1S09-X1 | 1756-IF16-12 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-401 | SPARE
206 | 9 | 13 | C1S09,13 | C1S09-X1 | 1756-IF16-13 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-401 | SPARE
207 | 9 | 14 | C1S09,14 | C1S09-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-401 | SPARE
208 | 9 | 15 | C1S09,15 | C1S09-X1 | 1756-IF16-15 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-401 | SPARE
209 | 10 | 0 | C1S10,00 | C1S10-X1 | 1756-IF16-0 | AI | 4 - 20 mA | DPI-60240 | 0 | DPI-60240_AI_1 | 325-01-600-PD-05 | JB-601 | ACTIVE
210 | 10 | 1 | C1S10,01 | C1S10-X1 | 1756-IF16-1 | AI | 4 - 20 mA | DPT-60202 | Differential Pressure Transmitte | DPT-60202_AI_1 | 3-25-01-602-PD-08 | JB-601 | ACTIVE
211 | 10 | 2 | C1S10,02 | C1S10-X1 | 1756-IF16-2 | AI | 4 - 20 mA | FT-60201 | 0 | FT-60201_AI_1 | 3-25-01-602-PD-08 | JB-601 | ACTIVE
212 | 10 | 3 | C1S10,03 | C1S10-X1 | 1756-IF16-3 | AI | 4 - 20 mA | FT-60204 | 0 | FT-60204_AI_1 | 3-25-01-602-PD-10 | JB-601 | ACTIVE
213 | 10 | 4 | C1S10,04 | C1S10-X1 | 1756-IF16-4 | AI | 4 - 20 mA | FT-61307 | 0 | FT-61307_AI_1 | 3-25-01-613-PD-04 | JB-601 | ACTIVE
214 | 10 | 5 | C1S10,05 | C1S10-X1 | 1756-IF16-5 | AI | 4 - 20 mA | PT-60203 | Pressure Transmitter | PT-60203_AI_1 | 3-25-01-602-PD-08 | JB-601 | ACTIVE
215 | 10 | 6 | C1S10,06 | C1S10-X1 | 1756-IF16-6 | AI | 4 - 20 mA | PT-60204 | Pressure Transmitter | PT-60204_AI_1 | 3-25-01-602-PD-10 | JB-601 | ACTIVE
216 | 10 | 7 | C1S10,07 | C1S10-X1 | 1756-IF16-7 | AI | 4 - 20 mA | PT-60205 | Pressure Transmitter | PT-60205_AI_1 | 3-25-01-602-PD-01 | JB-601 | ACTIVE
217 | 10 | 8 | C1S10,08 | C1S10-X1 | 1756-IF16-8 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-601 | SPARE
218 | 10 | 9 | C1S10,09 | C1S10-X1 | 1756-IF16-9 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-601 | SPARE
219 | 10 | 10 | C1S10,10 | C1S10-X1 | 1756-IF16-10 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-601 | SPARE
220 | 10 | 11 | C1S10,11 | C1S10-X1 | 1756-IF16-11 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-601 | SPARE
221 | 10 | 12 | C1S10,12 | C1S10-X1 | 1756-IF16-12 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-601 | SPARE
222 | 10 | 13 | C1S10,13 | C1S10-X1 | 1756-IF16-13 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-601 | SPARE
223 | 10 | 14 | C1S10,14 | C1S10-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-601 | SPARE
224 | 10 | 15 | C1S10,15 | C1S10-X1 | 1756-IF16-15 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-601 | SPARE

## Chassis_C2
CHASSIS C2 ¦ PANEL / ENCLOSURE: =CA1+MCP-M2 ¦ PROJECT JET COOKER
Item | Slot | Point | Channel Code | Terminal | Card Model | I/O Type | Signal | Instrument Tag | Instrument Description | PLC Tag | P&ID No. | Destination JB | Status
1 | 1 | 0 | C2S01,00 | C2S01-X1 | 1756-IB32-0 | DI | Dry Contact | FS-40204 | Flow Switch | FS-40204_DI_1 | 325-01-402-PD-01 | JB-402 | ACTIVE
2 | 1 | 1 | C2S01,01 | C2S01-X1 | 1756-IB32-1 | DI | Dry Contact | FS-40205 | Flow Switch | FS-40205_DI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
3 | 1 | 2 | C2S01,02 | C2S01-X1 | 1756-IB32-2 | DI | 4 - 20 mA,Pulse | FT-40221 | Coriolis Flow Transmitter | FT-40221_DI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
4 | 1 | 3 | C2S01,03 | C2S01-X1 | 1756-IB32-3 | DI | 4 - 20 mA,Pulse | FT-40222 | Coriolis Flow Transmitter | FT-40222_DI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
5 | 1 | 4 | C2S01,04 | C2S01-X1 | 1756-IB32-4 | DI | Dry Contact | HV-40207 | Manual Valve With Position Switch | HV-40207_DI_1 | 325-01-402-PD-01 | JB-402 | ACTIVE
6 | 1 | 5 | C2S01,05 | C2S01-X1 | 1756-IB32-5 | DI | Dry Contact | HV-40208 | Manual Valve With Position Switch | HV-40208_DI_1 | 325-01-402-PD-01 | JB-402 | ACTIVE
7 | 1 | 6 | C2S01,06 | C2S01-X1 | 1756-IB32-6 | DI | 24 VDC energized | XV-40203F | 0 | XV-40203F_DI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
8 | 1 | 7 | C2S01,07 | C2S01-X1 | 1756-IB32-7 | DI | 24 VDC energized | XV-40203F | 0 | XV-40203F_DI_2 | 325-01-402-PD-02 | JB-402 | ACTIVE
9 | 1 | 8 | C2S01,08 | C2S01-X1 | 1756-IB32-8 | DI | 24 VDC energized | XV-40204B | 0 | XV-40204B_DI_1 | 325-01-402-PD-01 | JB-402 | ACTIVE
10 | 1 | 9 | C2S01,09 | C2S01-X1 | 1756-IB32-9 | DI | 24 VDC energized | XV-40204B | 0 | XV-40204B_DI_2 | 325-01-402-PD-01 | JB-402 | ACTIVE
11 | 1 | 10 | C2S01,10 | C2S01-X1 | 1756-IB32-10 | DI | 24 VDC energized | XV-40204C | 0 | XV-40204C_DI_1 | 325-01-402-PD-01 | JB-402 | ACTIVE
12 | 1 | 11 | C2S01,11 | C2S01-X1 | 1756-IB32-11 | DI | 24 VDC energized | XV-40204C | 0 | XV-40204C_DI_2 | 325-01-402-PD-01 | JB-402 | ACTIVE
13 | 1 | 12 | C2S01,12 | C2S01-X1 | 1756-IB32-12 | DI | 24 VDC energized | XV-40205A | 0 | XV-40205A_DI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
14 | 1 | 13 | C2S01,13 | C2S01-X1 | 1756-IB32-13 | DI | 24 VDC energized | XV-40205A | 0 | XV-40205A_DI_2 | 325-01-402-PD-02 | JB-402 | ACTIVE
15 | 1 | 14 | C2S01,14 | C2S01-X1 | 1756-IB32-14 | DI | 24 VDC energized | XV-40205B | 0 | XV-40205B_DI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
16 | 1 | 15 | C2S01,15 | C2S01-X1 | 1756-IB32-15 | DI | 24 VDC energized | XV-40205B | 0 | XV-40205B_DI_2 | 325-01-402-PD-02 | JB-402 | ACTIVE
17 | 1 | 16 | C2S01,16 | C2S01-X2 | 1756-IB32-16 | DI | 24 VDC energized | XV-40205C | 0 | XV-40205C_DI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
18 | 1 | 17 | C2S01,17 | C2S01-X2 | 1756-IB32-17 | DI | 24 VDC energized | XV-40205C | 0 | XV-40205C_DI_2 | 325-01-402-PD-02 | JB-402 | ACTIVE
19 | 1 | 18 | C2S01,18 | C2S01-X2 | 1756-IB32-18 | DI | 24 VDC energized | XV-40205D | 0 | XV-40205D_DI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
20 | 1 | 19 | C2S01,19 | C2S01-X2 | 1756-IB32-19 | DI | 24 VDC energized | XV-40205D | 0 | XV-40205D_DI_2 | 325-01-402-PD-02 | JB-402 | ACTIVE
21 | 1 | 20 | C2S01,20 | C2S01-X2 | 1756-IB32-20 | DI | 24 VDC energized | XV-40205F | 0 | XV-40205F_DI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
22 | 1 | 21 | C2S01,21 | C2S01-X2 | 1756-IB32-21 | DI | 24 VDC energized | XV-40205F | 0 | XV-40205F_DI_2 | 325-01-402-PD-02 | JB-402 | ACTIVE
23 | 1 | 22 | C2S01,22 | C2S01-X2 | 1756-IB32-22 | DI | 24 VDC energized | XV-40222 | 0 | XV-40222_DI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
24 | 1 | 23 | C2S01,23 | C2S01-X2 | 1756-IB32-23 | DI | 24 VDC energized | XV-40222 | 0 | XV-40222_DI_2 | - | JB-402 | ACTIVE
25 | 1 | 24 | C2S01,24 | C2S01-X2 | 1756-IB32-24 | DI | - | Spare | Spare I/O Point | Spare_DI_2 | - | JB-402 | SPARE
26 | 1 | 25 | C2S01,25 | C2S01-X2 | 1756-IB32-25 | DI | - | Spare | Spare I/O Point | Spare_DI_2 | - | JB-402 | SPARE
27 | 1 | 26 | C2S01,26 | C2S01-X2 | 1756-IB32-26 | DI | - | Spare | Spare I/O Point | Spare_DI_2 | - | JB-402 | SPARE
28 | 1 | 27 | C2S01,27 | C2S01-X2 | 1756-IB32-27 | DI | - | Spare | Spare I/O Point | Spare_DI_2 | - | JB-402 | SPARE
29 | 1 | 28 | C2S01,28 | C2S01-X2 | 1756-IB32-28 | DI | - | Spare | Spare I/O Point | Spare_DI_2 | - | JB-402 | SPARE
30 | 1 | 29 | C2S01,29 | C2S01-X2 | 1756-IB32-29 | DI | - | Spare | Spare I/O Point | Spare_DI_2 | - | JB-402 | SPARE
31 | 1 | 30 | C2S01,30 | C2S01-X2 | 1756-IB32-30 | DI | - | Spare | Spare I/O Point | Spare_DI_2 | - | JB-402 | SPARE
32 | 1 | 31 | C2S01,31 | C2S01-X2 | 1756-IB32-31 | DI | - | Spare | Spare I/O Point | Spare_DI_2 | - | JB-402 | SPARE
33 | 2 | 0 | C2S02,00 | C2S02-X1 | 1756-IB32-0 | DI | 4 - 20 mA | FT-60202 | 0 | FT-60202_DI_1 | 3-25-01-602-PD-09 | JB-602 | ACTIVE
34 | 2 | 1 | C2S02,01 | C2S02-X1 | 1756-IB32-1 | DI | Dry Contact | LSH-60251 | 0 | LSH-60251_DI_1 | 3-25-01-602-PD-04 | JB-602 | ACTIVE
35 | 2 | 2 | C2S02,02 | C2S02-X1 | 1756-IB32-2 | DI | Dry Contact | PSL-60220 | 0 | PSL-60220_DI_1 | 3-25-01-602-PD-04 | JB-602 | ACTIVE
36 | 2 | 3 | C2S02,03 | C2S02-X1 | 1756-IB32-3 | DI | Dry Contact | TSH-60230 | 0 | TSH-60230_DI_1 | 3-25-01-602-PD-04 | JB-602 | ACTIVE
37 | 2 | 4 | C2S02,04 | C2S02-X1 | 1756-IB32-4 | DI | Dry Contact | TSH-60240 | 0 | TSH-60240_DI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
38 | 2 | 5 | C2S02,05 | C2S02-X1 | 1756-IB32-5 | DI | Dry Contact | TSH-60241A | 0 | TSH-60241A_DI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
39 | 2 | 6 | C2S02,06 | C2S02-X1 | 1756-IB32-6 | DI | Dry Contact | TSH-60242A | 0 | TSH-60242A_DI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
40 | 2 | 7 | C2S02,07 | C2S02-X1 | 1756-IB32-7 | DI | Dry Contact | TSH-60243A | 0 | TSH-60243A_DI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
41 | 2 | 8 | C2S02,08 | C2S02-X1 | 1756-IB32-8 | DI | Dry Contact | TSL-60241B | 0 | TSL-60241B_DI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
42 | 2 | 9 | C2S02,09 | C2S02-X1 | 1756-IB32-9 | DI | Dry Contact | TSL-60242B | 0 | TSL-60242B_DI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
43 | 2 | 10 | C2S02,10 | C2S02-X1 | 1756-IB32-10 | DI | Dry Contact | TSL-60243B | 0 | TSL-60243B_DI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
44 | 2 | 11 | C2S02,11 | C2S02-X1 | 1756-IB32-11 | DI | Dry Contact | XA-60240A | 0 | XA-60240A_DI_1 | 325-01-600-PD-05 | JB-602 | ACTIVE
45 | 2 | 12 | C2S02,12 | C2S02-X1 | 1756-IB32-12 | DI | Dry Contact | XA-60240B | 0 | XA-60240B_DI_1 | 325-01-600-PD-05 | JB-602 | ACTIVE
46 | 2 | 13 | C2S02,13 | C2S02-X1 | 1756-IB32-13 | DI | Dry Contact | XA-60241A | 0 | XA-60241A_DI_1 | 325-01-600-PD-05 | JB-602 | ACTIVE
47 | 2 | 14 | C2S02,14 | C2S02-X1 | 1756-IB32-14 | DI | Dry Contact | XA-60241B | 0 | XA-60241B_DI_1 | 325-01-600-PD-05 | JB-602 | ACTIVE
48 | 2 | 15 | C2S02,15 | C2S02-X1 | 1756-IB32-15 | DI | Dry Contact | XA-60242A | 0 | XA-60242A_DI_1 | 325-01-600-PD-05 | JB-602 | ACTIVE
49 | 2 | 16 | C2S02,16 | C2S02-X2 | 1756-IB32-16 | DI | Dry Contact | XA-60242B | 0 | XA-60242B_DI_1 | 325-01-600-PD-05 | JB-602 | ACTIVE
50 | 2 | 17 | C2S02,17 | C2S02-X2 | 1756-IB32-17 | DI | Dry Contact | XA-60243A | 0 | XA-60243A_DI_1 | 325-01-600-PD-05 | JB-602 | ACTIVE
51 | 2 | 18 | C2S02,18 | C2S02-X2 | 1756-IB32-18 | DI | Dry Contact | XA-60243B | 0 | XA-60243B_DI_1 | 325-01-600-PD-05 | JB-602 | ACTIVE
52 | 2 | 19 | C2S02,19 | C2S02-X2 | 1756-IB32-19 | DI | 24 VDC energized | XV-60214 | 0 | XV-60214_DI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
53 | 2 | 20 | C2S02,20 | C2S02-X2 | 1756-IB32-20 | DI | 24 VDC energized | XV-60214 | 0 | XV-60214_DI_2 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
54 | 2 | 21 | C2S02,21 | C2S02-X2 | 1756-IB32-21 | DI | 24 VDC energized,Dry Contact | XV-60241 | 0 | XV-60241_DI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
55 | 2 | 22 | C2S02,22 | C2S02-X2 | 1756-IB32-22 | DI | 24 VDC energized,Dry Contact | XV-60241 | 0 | XV-60241_DI_2 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
56 | 2 | 23 | C2S02,23 | C2S02-X2 | 1756-IB32-23 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-602 | SPARE
57 | 2 | 24 | C2S02,24 | C2S02-X2 | 1756-IB32-24 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-602 | SPARE
58 | 2 | 25 | C2S02,25 | C2S02-X2 | 1756-IB32-25 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-602 | SPARE
59 | 2 | 26 | C2S02,26 | C2S02-X2 | 1756-IB32-26 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-602 | SPARE
60 | 2 | 27 | C2S02,27 | C2S02-X2 | 1756-IB32-27 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-602 | SPARE
61 | 2 | 28 | C2S02,28 | C2S02-X2 | 1756-IB32-28 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-602 | SPARE
62 | 2 | 29 | C2S02,29 | C2S02-X2 | 1756-IB32-29 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-602 | SPARE
63 | 2 | 30 | C2S02,30 | C2S02-X2 | 1756-IB32-30 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-602 | SPARE
64 | 2 | 31 | C2S02,31 | C2S02-X2 | 1756-IB32-31 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-602 | SPARE
65 | 3 | 0 | C2S03,00 | C2S03-X1 | 1756-IB32-0 | DI | Dry Contact | XA-FH-60210A | 0 | XA-FH-60210A_DI_1 | 325-01-600-PD-06 | JB-607 | ACTIVE
66 | 3 | 1 | C2S03,01 | C2S03-X1 | 1756-IB32-1 | DI | Dry Contact | XA-FH-60210B | 0 | XA-FH-60210B_DI_1 | 325-01-600-PD-06 | JB-607 | ACTIVE
67 | 3 | 2 | C2S03,02 | C2S03-X1 | 1756-IB32-2 | DI | Dry Contact | XA-FH-60210C | 0 | XA-FH-60210C_DI_1 | 325-01-600-PD-06 | JB-607 | ACTIVE
68 | 3 | 3 | C2S03,03 | C2S03-X1 | 1756-IB32-3 | DI | Dry Contact | XA-FH-60210D | 0 | XA-FH-60210D_DI_1 | 325-01-600-PD-06 | JB-607 | ACTIVE
69 | 3 | 4 | C2S03,04 | C2S03-X1 | 1756-IB32-4 | DI | Dry Contact | XA-FH-60210E | 0 | XA-FH-60210E_DI_1 | 325-01-600-PD-06 | JB-607 | ACTIVE
70 | 3 | 8 | C2S03,08 | C2S03-X1 | 1756-IB32-8 | DI | 24 VDC energized | SV-60207 | 0 | SV-60207_DI_1 | 3-25-01-602-PD-07 | JB-607 | ACTIVE
71 | 3 | 9 | C2S03,09 | C2S03-X1 | 1756-IB32-9 | DI | 24 VDC energized | SV-60207 | 0 | SV-60207_DI_2 | 3-25-01-602-PD-07 | JB-607 | ACTIVE
72 | 3 | 10 | C2S03,10 | C2S03-X1 | 1756-IB32-10 | DI | - | XV-60264 | - | XV-60264_DI_1 | 325-01-600-PD-02 | JB-607 | ACTIVE
73 | 3 | 11 | C2S03,11 | C2S03-X1 | 1756-IB32-11 | DI | - | XV-60264 | - | XV-60264_DI_2 | 325-01-600-PD-02 | JB-607 | ACTIVE
74 | 3 | 12 | C2S03,12 | C2S03-X1 | 1756-IB32-12 | DI | 24 VDC energized,Dry Contact | XV-60264FN | 0 | XV-60264FN_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
75 | 3 | 13 | C2S03,13 | C2S03-X1 | 1756-IB32-13 | DI | 24 VDC energized,Dry Contact | XV-60264FN | 0 | XV-60264FN_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
76 | 3 | 14 | C2S03,14 | C2S03-X1 | 1756-IB32-14 | DI | 24 VDC energized,Dry Contact | XV-60264FP | 0 | XV-60264FP_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
77 | 3 | 15 | C2S03,15 | C2S03-X1 | 1756-IB32-15 | DI | 24 VDC energized,Dry Contact | XV-60264FP | 0 | XV-60264FP_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
78 | 3 | 16 | C2S03,16 | C2S03-X2 | 1756-IB32-16 | DI | 24 VDC energized | XV-60201 | 0 | XV-60201_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
79 | 3 | 17 | C2S03,17 | C2S03-X2 | 1756-IB32-17 | DI | 24 VDC energized | XV-60201 | 0 | XV-60201_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
80 | 3 | 18 | C2S03,18 | C2S03-X2 | 1756-IB32-18 | DI | 24 VDC energized,Dry Contact | XV-60264FQ | 0 | XV-60264FQ_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
81 | 3 | 19 | C2S03,19 | C2S03-X2 | 1756-IB32-19 | DI | 24 VDC energized,Dry Contact | XV-60264FQ | 0 | XV-60264FQ_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
82 | 3 | 20 | C2S03,20 | C2S03-X2 | 1756-IB32-20 | DI | - | XV-60261 | - | XV-60261_DI_1 | 325-01-600-PD-02 | JB-607 | ACTIVE
83 | 3 | 21 | C2S03,21 | C2S03-X2 | 1756-IB32-21 | DI | - | XV-60261 | - | XV-60261_DI_2 | 325-01-600-PD-02 | JB-607 | ACTIVE
84 | 3 | 22 | C2S03,22 | C2S03-X2 | 1756-IB32-22 | DI | 24 VDC energized,Dry Contact | XV-60264FR | 0 | XV-60264FR_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
85 | 3 | 23 | C2S03,23 | C2S03-X2 | 1756-IB32-23 | DI | 24 VDC energized,Dry Contact | XV-60264FR | 0 | XV-60264FR_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
86 | 3 | 24 | C2S03,24 | C2S03-X2 | 1756-IB32-24 | DI | 24 VDC energized,Dry Contact | XV-60261FA | 0 | XV-60261FA_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
87 | 3 | 25 | C2S03,25 | C2S03-X2 | 1756-IB32-25 | DI | 24 VDC energized,Dry Contact | XV-60261FA | 0 | XV-60261FA_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
88 | 3 | 26 | C2S03,26 | C2S03-X2 | 1756-IB32-26 | DI | 24 VDC energized,Dry Contact | XV-60264SN | 0 | XV-60264SN_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
89 | 3 | 27 | C2S03,27 | C2S03-X2 | 1756-IB32-27 | DI | 24 VDC energized,Dry Contact | XV-60264SN | 0 | XV-60264SN_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
90 | 3 | 28 | C2S03,28 | C2S03-X2 | 1756-IB32-28 | DI | 24 VDC energized,Dry Contact | XV-60261FB | 0 | XV-60261FB_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
91 | 3 | 29 | C2S03,29 | C2S03-X2 | 1756-IB32-29 | DI | 24 VDC energized,Dry Contact | XV-60261FB | 0 | XV-60261FB_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
92 | 3 | 30 | C2S03,30 | C2S03-X2 | 1756-IB32-30 | DI | 24 VDC energized,Dry Contact | XV-60264SP | 0 | XV-60264SP_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
93 | 3 | 31 | C2S03,31 | C2S03-X2 | 1756-IB32-31 | DI | 24 VDC energized,Dry Contact | XV-60264SP | 0 | XV-60264SP_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
94 | 4 | 0 | C2S04,00 | C2S04-X1 | 1756-IB32-0 | DI | 24 VDC energized,Dry Contact | XV-60261FC | 0 | XV-60261FC_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
95 | 4 | 1 | C2S04,01 | C2S04-X1 | 1756-IB32-1 | DI | 24 VDC energized,Dry Contact | XV-60261FC | 0 | XV-60261FC_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
96 | 4 | 2 | C2S04,02 | C2S04-X1 | 1756-IB32-2 | DI | 24 VDC energized,Dry Contact | XV-60264SQ | 0 | XV-60264SQ_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
97 | 4 | 3 | C2S04,03 | C2S04-X1 | 1756-IB32-3 | DI | 24 VDC energized,Dry Contact | XV-60264SQ | 0 | XV-60264SQ_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
98 | 4 | 4 | C2S04,04 | C2S04-X1 | 1756-IB32-4 | DI | 24 VDC energized,Dry Contact | XV-60261FD | 0 | XV-60261FD_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
99 | 4 | 5 | C2S04,05 | C2S04-X1 | 1756-IB32-5 | DI | 24 VDC energized,Dry Contact | XV-60261FD | 0 | XV-60261FD_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
100 | 4 | 6 | C2S04,06 | C2S04-X1 | 1756-IB32-6 | DI | 24 VDC energized,Dry Contact | XV-60264SR | 0 | XV-60264SR_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
101 | 4 | 7 | C2S04,07 | C2S04-X1 | 1756-IB32-7 | DI | 24 VDC energized,Dry Contact | XV-60264SR | 0 | XV-60264SR_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
102 | 4 | 8 | C2S04,08 | C2S04-X1 | 1756-IB32-8 | DI | 24 VDC energized,Dry Contact | XV-60261SA | 0 | XV-60261SA_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
103 | 4 | 9 | C2S04,09 | C2S04-X1 | 1756-IB32-9 | DI | 24 VDC energized,Dry Contact | XV-60261SA | 0 | XV-60261SA_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
104 | 4 | 10 | C2S04,10 | C2S04-X1 | 1756-IB32-10 | DI | 24 VDC energized,Dry Contact | XV-60261SB | 0 | XV-60261SB_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
105 | 4 | 11 | C2S04,11 | C2S04-X1 | 1756-IB32-11 | DI | 24 VDC energized,Dry Contact | XV-60261SB | 0 | XV-60261SB_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
106 | 4 | 12 | C2S04,12 | C2S04-X1 | 1756-IB32-12 | DI | 24 VDC energized,Dry Contact | XV-60261SC | 0 | XV-60261SC_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
107 | 4 | 13 | C2S04,13 | C2S04-X1 | 1756-IB32-13 | DI | 24 VDC energized,Dry Contact | XV-60261SC | 0 | XV-60261SC_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
108 | 4 | 14 | C2S04,14 | C2S04-X1 | 1756-IB32-14 | DI | 24 VDC energized,Dry Contact | XV-60261SD | 0 | XV-60261SD_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
109 | 4 | 15 | C2S04,15 | C2S04-X1 | 1756-IB32-15 | DI | 24 VDC energized,Dry Contact | XV-60261SD | 0 | XV-60261SD_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
110 | 4 | 16 | C2S04,16 | C2S04-X2 | 1756-IB32-16 | DI | - | XV-60262 | - | XV-60262_DI_1 | 325-01-600-PD-02 | JB-607 | ACTIVE
111 | 4 | 17 | C2S04,17 | C2S04-X2 | 1756-IB32-17 | DI | - | XV-60262 | - | XV-60262_DI_2 | 325-01-600-PD-02 | JB-607 | ACTIVE
112 | 4 | 18 | C2S04,18 | C2S04-X2 | 1756-IB32-18 | DI | 24 VDC energized,Dry Contact | XV-60262FE | 0 | XV-60262FE_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
113 | 4 | 19 | C2S04,19 | C2S04-X2 | 1756-IB32-19 | DI | 24 VDC energized,Dry Contact | XV-60262FE | 0 | XV-60262FE_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
114 | 4 | 20 | C2S04,20 | C2S04-X2 | 1756-IB32-20 | DI | 24 VDC energized,Dry Contact | XV-60262FF | 0 | XV-60262FF_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
115 | 4 | 21 | C2S04,21 | C2S04-X2 | 1756-IB32-21 | DI | 24 VDC energized,Dry Contact | XV-60262FF | 0 | XV-60262FF_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
116 | 4 | 22 | C2S04,22 | C2S04-X2 | 1756-IB32-22 | DI | 24 VDC energized,Dry Contact | XV-60262FG | 0 | XV-60262FG_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
117 | 4 | 23 | C2S04,23 | C2S04-X2 | 1756-IB32-23 | DI | 24 VDC energized,Dry Contact | XV-60262FG | 0 | XV-60262FG_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
118 | 4 | 24 | C2S04,24 | C2S04-X2 | 1756-IB32-24 | DI | 24 VDC energized,Dry Contact | XV-60262FH | 0 | XV-60262FH_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
119 | 4 | 25 | C2S04,25 | C2S04-X2 | 1756-IB32-25 | DI | 24 VDC energized,Dry Contact | XV-60262FH | 0 | XV-60262FH_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
120 | 4 | 26 | C2S04,26 | C2S04-X2 | 1756-IB32-26 | DI | 24 VDC energized,Dry Contact | XV-60262SE | 0 | XV-60262SE_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
121 | 4 | 27 | C2S04,27 | C2S04-X2 | 1756-IB32-27 | DI | 24 VDC energized,Dry Contact | XV-60262SE | 0 | XV-60262SE_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
122 | 4 | 28 | C2S04,28 | C2S04-X2 | 1756-IB32-28 | DI | 24 VDC energized,Dry Contact | XV-60262SF | 0 | XV-60262SF_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
123 | 4 | 29 | C2S04,29 | C2S04-X2 | 1756-IB32-29 | DI | 24 VDC energized,Dry Contact | XV-60262SF | 0 | XV-60262SF_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
124 | 4 | 30 | C2S04,30 | C2S04-X2 | 1756-IB32-30 | DI | 24 VDC energized,Dry Contact | XV-60262SG | 0 | XV-60262SG_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
125 | 4 | 31 | C2S04,31 | C2S04-X2 | 1756-IB32-31 | DI | 24 VDC energized,Dry Contact | XV-60262SG | 0 | XV-60262SG_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
126 | 5 | 0 | C2S05,00 | C2S05-X1 | 1756-IB32-0 | DI | 24 VDC energized,Dry Contact | XV-60262SH | 0 | XV-60262SH_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
127 | 5 | 1 | C2S05,01 | C2S05-X1 | 1756-IB32-1 | DI | 24 VDC energized,Dry Contact | XV-60262SH | 0 | XV-60262SH_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
128 | 5 | 2 | C2S05,02 | C2S05-X1 | 1756-IB32-2 | DI | - | XV-60263 | - | XV-60263_DI_1 | 325-01-600-PD-02 | JB-607 | ACTIVE
129 | 5 | 3 | C2S05,03 | C2S05-X1 | 1756-IB32-3 | DI | - | XV-60263 | - | XV-60263_DI_2 | 325-01-600-PD-02 | JB-607 | ACTIVE
130 | 5 | 4 | C2S05,04 | C2S05-X1 | 1756-IB32-4 | DI | 24 VDC energized,Dry Contact | XV-60263FJ | 0 | XV-60263FJ_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
131 | 5 | 5 | C2S05,05 | C2S05-X1 | 1756-IB32-5 | DI | 24 VDC energized,Dry Contact | XV-60263FJ | 0 | XV-60263FJ_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
132 | 5 | 6 | C2S05,06 | C2S05-X1 | 1756-IB32-6 | DI | 24 VDC energized,Dry Contact | XV-60263FK | 0 | XV-60263FK_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
133 | 5 | 7 | C2S05,07 | C2S05-X1 | 1756-IB32-7 | DI | 24 VDC energized,Dry Contact | XV-60263FK | 0 | XV-60263FK_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
134 | 5 | 8 | C2S05,08 | C2S05-X1 | 1756-IB32-8 | DI | 24 VDC energized,Dry Contact | XV-60263FL | 0 | XV-60263FL_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
135 | 5 | 9 | C2S05,09 | C2S05-X1 | 1756-IB32-9 | DI | 24 VDC energized,Dry Contact | XV-60263FL | 0 | XV-60263FL_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
136 | 5 | 10 | C2S05,10 | C2S05-X1 | 1756-IB32-10 | DI | 24 VDC energized,Dry Contact | XV-60263FM | 0 | XV-60263FM_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
137 | 5 | 11 | C2S05,11 | C2S05-X1 | 1756-IB32-11 | DI | 24 VDC energized,Dry Contact | XV-60263FM | 0 | XV-60263FM_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
138 | 5 | 12 | C2S05,12 | C2S05-X1 | 1756-IB32-12 | DI | 24 VDC energized,Dry Contact | XV-60263SJ | 0 | XV-60263SJ_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
139 | 5 | 13 | C2S05,13 | C2S05-X1 | 1756-IB32-13 | DI | 24 VDC energized,Dry Contact | XV-60263SJ | 0 | XV-60263SJ_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
140 | 5 | 14 | C2S05,14 | C2S05-X1 | 1756-IB32-14 | DI | 24 VDC energized,Dry Contact | XV-60263SK | 0 | XV-60263SK_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
141 | 5 | 15 | C2S05,15 | C2S05-X1 | 1756-IB32-15 | DI | 24 VDC energized,Dry Contact | XV-60263SK | 0 | XV-60263SK_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
142 | 5 | 16 | C2S05,16 | C2S05-X2 | 1756-IB32-16 | DI | 24 VDC energized,Dry Contact | XV-60263SL | 0 | XV-60263SL_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
143 | 5 | 17 | C2S05,17 | C2S05-X2 | 1756-IB32-17 | DI | 24 VDC energized,Dry Contact | XV-60263SL | 0 | XV-60263SL_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
144 | 5 | 18 | C2S05,18 | C2S05-X2 | 1756-IB32-18 | DI | 24 VDC energized,Dry Contact | XV-60263SM | 0 | XV-60263SM_DI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
145 | 5 | 19 | C2S05,19 | C2S05-X2 | 1756-IB32-19 | DI | 24 VDC energized,Dry Contact | XV-60263SM | 0 | XV-60263SM_DI_2 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
146 | 5 | 20 | C2S05,20 | C2S05-X2 | 1756-IB32-20 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-607 | SPARE
147 | 5 | 21 | C2S05,21 | C2S05-X2 | 1756-IB32-21 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-607 | SPARE
148 | 5 | 22 | C2S05,22 | C2S05-X2 | 1756-IB32-22 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-607 | SPARE
149 | 5 | 23 | C2S05,23 | C2S05-X2 | 1756-IB32-23 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-607 | SPARE
150 | 5 | 24 | C2S05,24 | C2S05-X2 | 1756-IB32-24 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-607 | SPARE
151 | 5 | 25 | C2S05,25 | C2S05-X2 | 1756-IB32-25 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-607 | SPARE
152 | 5 | 26 | C2S05,26 | C2S05-X2 | 1756-IB32-26 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-607 | SPARE
153 | 5 | 27 | C2S05,27 | C2S05-X2 | 1756-IB32-27 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-607 | SPARE
154 | 5 | 28 | C2S05,28 | C2S05-X2 | 1756-IB32-28 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-607 | SPARE
155 | 5 | 29 | C2S05,29 | C2S05-X2 | 1756-IB32-29 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-607 | SPARE
156 | 5 | 30 | C2S05,30 | C2S05-X2 | 1756-IB32-30 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-607 | SPARE
157 | 5 | 31 | C2S05,31 | C2S05-X2 | 1756-IB32-31 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-607 | SPARE
158 | 6 | 0 | C2S06,00 | C2S06-X1 | 1756-OB32-0 | DO | 24 VDC energized | XV-40203F | 0 | XV-40203F_DO_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
159 | 6 | 1 | C2S06,01 | C2S06-X1 | 1756-OB32-1 | DO | 24 VDC energized | XV-40204B | 0 | XV-40204B_DO_1 | 325-01-402-PD-01 | JB-402 | ACTIVE
160 | 6 | 2 | C2S06,02 | C2S06-X1 | 1756-OB32-2 | DO | 24 VDC energized | XV-40204C | 0 | XV-40204C_DO_1 | 325-01-402-PD-01 | JB-402 | ACTIVE
161 | 6 | 3 | C2S06,03 | C2S06-X1 | 1756-OB32-3 | DO | 24 VDC energized | XV-40205A | 0 | XV-40205A_DO_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
162 | 6 | 4 | C2S06,04 | C2S06-X1 | 1756-OB32-4 | DO | 24 VDC energized | XV-40205B | 0 | XV-40205B_DO_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
163 | 6 | 5 | C2S06,05 | C2S06-X1 | 1756-OB32-5 | DO | 24 VDC energized | XV-40205C | 0 | XV-40205C_DO_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
164 | 6 | 6 | C2S06,06 | C2S06-X1 | 1756-OB32-6 | DO | 24 VDC energized | XV-40205D | 0 | XV-40205D_DO_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
165 | 6 | 7 | C2S06,07 | C2S06-X1 | 1756-OB32-7 | DO | 24 VDC energized | XV-40205F | 0 | XV-40205F_DO_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
166 | 6 | 8 | C2S06,08 | C2S06-X1 | 1756-OB32-8 | DO | 24 VDC energized | XV-40222 | 0 | XV-40222_DO_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
167 | 6 | 9 | C2S06,09 | C2S06-X1 | 1756-OB32-9 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-402 | SPARE
168 | 6 | 10 | C2S06,10 | C2S06-X1 | 1756-OB32-10 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-402 | SPARE
169 | 6 | 11 | C2S06,11 | C2S06-X1 | 1756-OB32-11 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-402 | SPARE
170 | 6 | 12 | C2S06,12 | C2S06-X1 | 1756-OB32-12 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-402 | SPARE
171 | 6 | 13 | C2S06,13 | C2S06-X1 | 1756-OB32-13 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-402 | SPARE
172 | 6 | 14 | C2S06,14 | C2S06-X1 | 1756-OB32-14 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-402 | SPARE
173 | 6 | 15 | C2S06,15 | C2S06-X1 | 1756-OB32-15 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-402 | SPARE
174 | 6 | 16 | C2S06,16 | C2S06-X2 | 1756-OB32-16 | DO | Dry Contact | XS-60240B | 0 | XS-60240B_DO_1 | 325-01-600-PD-05 | JB-602 | ACTIVE
175 | 6 | 17 | C2S06,17 | C2S06-X2 | 1756-OB32-17 | DO | 24 VDC energized | XV-60214 | 0 | XV-60214_DO_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
176 | 6 | 18 | C2S06,18 | C2S06-X2 | 1756-OB32-18 | DO | 24 VDC energized,Dry Contact | XV-60241 | 0 | XV-60241_DO_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
177 | 6 | 19 | C2S06,19 | C2S06-X2 | 1756-OB32-19 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-602 | SPARE
178 | 6 | 20 | C2S06,20 | C2S06-X2 | 1756-OB32-20 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-602 | SPARE
179 | 6 | 21 | C2S06,21 | C2S06-X2 | 1756-OB32-21 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-602 | SPARE
180 | 6 | 22 | C2S06,22 | C2S06-X2 | 1756-OB32-22 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-602 | SPARE
181 | 6 | 23 | C2S06,23 | C2S06-X2 | 1756-OB32-23 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-602 | SPARE
182 | 6 | 24 | C2S06,24 | C2S06-X2 | 1756-OB32-24 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-602 | SPARE
183 | 6 | 25 | C2S06,25 | C2S06-X2 | 1756-OB32-25 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-602 | SPARE
184 | 6 | 26 | C2S06,26 | C2S06-X2 | 1756-OB32-26 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-602 | SPARE
185 | 6 | 27 | C2S06,27 | C2S06-X2 | 1756-OB32-27 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-602 | SPARE
186 | 6 | 28 | C2S06,28 | C2S06-X2 | 1756-OB32-28 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-602 | SPARE
187 | 6 | 29 | C2S06,29 | C2S06-X2 | 1756-OB32-29 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-602 | SPARE
188 | 6 | 30 | C2S06,30 | C2S06-X2 | 1756-OB32-30 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-602 | SPARE
189 | 6 | 31 | C2S06,31 | C2S06-X2 | 1756-OB32-31 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-602 | SPARE
190 | 7 | 0 | C2S07,00 | C2S07-X1 | 1756-OB32-0 | DO | 24 VDC energized | SV-60207 | 0 | SV-60207_DO_1 | 3-25-01-602-PD-07 | JB-607 | ACTIVE
191 | 7 | 1 | C2S07,01 | C2S07-X1 | 1756-OB32-1 | DO | Dry Contact | XS-FH-60210C | 0 | XS-FH-60210C_DO_1 | 325-01-600-PD-06 | JB-607 | ACTIVE
192 | 7 | 2 | C2S07,02 | C2S07-X1 | 1756-OB32-2 | DO | Dry Contact | XS-FH-60210D | 0 | XS-FH-60210D_DO_1 | 325-01-600-PD-06 | JB-607 | ACTIVE
193 | 7 | 3 | C2S07,03 | C2S07-X1 | 1756-OB32-3 | DO | 24 VDC energized | XV-60201 | 0 | XV-60201_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
194 | 7 | 4 | C2S07,04 | C2S07-X1 | 1756-OB32-4 | DO | - | XV-60261 | - | XV-60261_DO_1 | 325-01-600-PD-02 | JB-607 | ACTIVE
195 | 7 | 5 | C2S07,05 | C2S07-X1 | 1756-OB32-5 | DO | 24 VDC energized,Dry Contact | XV-60261FA | 0 | XV-60261FA_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
196 | 7 | 6 | C2S07,06 | C2S07-X1 | 1756-OB32-6 | DO | 24 VDC energized,Dry Contact | XV-60261FB | 0 | XV-60261FB_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
197 | 7 | 7 | C2S07,07 | C2S07-X1 | 1756-OB32-7 | DO | 24 VDC energized,Dry Contact | XV-60261FC | 0 | XV-60261FC_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
198 | 7 | 8 | C2S07,08 | C2S07-X1 | 1756-OB32-8 | DO | 24 VDC energized,Dry Contact | XV-60261FD | 0 | XV-60261FD_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
199 | 7 | 9 | C2S07,09 | C2S07-X1 | 1756-OB32-9 | DO | 24 VDC energized,Dry Contact | XV-60261SA | 0 | XV-60261SA_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
200 | 7 | 10 | C2S07,10 | C2S07-X1 | 1756-OB32-10 | DO | 24 VDC energized,Dry Contact | XV-60261SB | 0 | XV-60261SB_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
201 | 7 | 11 | C2S07,11 | C2S07-X1 | 1756-OB32-11 | DO | 24 VDC energized,Dry Contact | XV-60261SC | 0 | XV-60261SC_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
202 | 7 | 12 | C2S07,12 | C2S07-X1 | 1756-OB32-12 | DO | 24 VDC energized,Dry Contact | XV-60261SD | 0 | XV-60261SD_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
203 | 7 | 13 | C2S07,13 | C2S07-X1 | 1756-OB32-13 | DO | - | XV-60262 | - | XV-60262_DO_1 | 325-01-600-PD-02 | JB-607 | ACTIVE
204 | 7 | 14 | C2S07,14 | C2S07-X1 | 1756-OB32-14 | DO | 24 VDC energized,Dry Contact | XV-60262FE | 0 | XV-60262FE_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
205 | 7 | 15 | C2S07,15 | C2S07-X1 | 1756-OB32-15 | DO | 24 VDC energized,Dry Contact | XV-60262FF | 0 | XV-60262FF_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
206 | 7 | 16 | C2S07,16 | C2S07-X2 | 1756-OB32-16 | DO | 24 VDC energized,Dry Contact | XV-60262FG | 0 | XV-60262FG_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
207 | 7 | 17 | C2S07,17 | C2S07-X2 | 1756-OB32-17 | DO | 24 VDC energized,Dry Contact | XV-60262FH | 0 | XV-60262FH_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
208 | 7 | 18 | C2S07,18 | C2S07-X2 | 1756-OB32-18 | DO | 24 VDC energized,Dry Contact | XV-60262SE | 0 | XV-60262SE_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
209 | 7 | 19 | C2S07,19 | C2S07-X2 | 1756-OB32-19 | DO | 24 VDC energized,Dry Contact | XV-60262SF | 0 | XV-60262SF_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
210 | 7 | 20 | C2S07,20 | C2S07-X2 | 1756-OB32-20 | DO | 24 VDC energized,Dry Contact | XV-60262SG | 0 | XV-60262SG_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
211 | 7 | 21 | C2S07,21 | C2S07-X2 | 1756-OB32-21 | DO | 24 VDC energized,Dry Contact | XV-60262SH | 0 | XV-60262SH_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
212 | 7 | 22 | C2S07,22 | C2S07-X2 | 1756-OB32-22 | DO | - | XV-60263 | - | XV-60263_DO_1 | 325-01-600-PD-02 | JB-607 | ACTIVE
213 | 7 | 23 | C2S07,23 | C2S07-X2 | 1756-OB32-23 | DO | 24 VDC energized,Dry Contact | XV-60263FJ | 0 | XV-60263FJ_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
214 | 7 | 24 | C2S07,24 | C2S07-X2 | 1756-OB32-24 | DO | 24 VDC energized,Dry Contact | XV-60263FK | 0 | XV-60263FK_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
215 | 7 | 25 | C2S07,25 | C2S07-X2 | 1756-OB32-25 | DO | 24 VDC energized,Dry Contact | XV-60263FL | 0 | XV-60263FL_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
216 | 7 | 26 | C2S07,26 | C2S07-X2 | 1756-OB32-26 | DO | 24 VDC energized,Dry Contact | XV-60263FM | 0 | XV-60263FM_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
217 | 7 | 27 | C2S07,27 | C2S07-X2 | 1756-OB32-27 | DO | 24 VDC energized,Dry Contact | XV-60263SJ | 0 | XV-60263SJ_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
218 | 7 | 28 | C2S07,28 | C2S07-X2 | 1756-OB32-28 | DO | 24 VDC energized,Dry Contact | XV-60263SK | 0 | XV-60263SK_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
219 | 7 | 29 | C2S07,29 | C2S07-X2 | 1756-OB32-29 | DO | 24 VDC energized,Dry Contact | XV-60263SL | 0 | XV-60263SL_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
220 | 7 | 30 | C2S07,30 | C2S07-X2 | 1756-OB32-30 | DO | 24 VDC energized,Dry Contact | XV-60263SM | 0 | XV-60263SM_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
221 | 7 | 31 | C2S07,31 | C2S07-X2 | 1756-OB32-31 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
222 | 8 | 0 | C2S08,00 | C2S08-X1 | 1756-OB32-0 | DO | - | XV-60264 | - | XV-60264_DO_1 | 325-01-600-PD-02 | JB-607 | ACTIVE
223 | 8 | 1 | C2S08,01 | C2S08-X1 | 1756-OB32-1 | DO | 24 VDC energized,Dry Contact | XV-60264FN | 0 | XV-60264FN_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
224 | 8 | 2 | C2S08,02 | C2S08-X1 | 1756-OB32-2 | DO | 24 VDC energized,Dry Contact | XV-60264FP | 0 | XV-60264FP_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
225 | 8 | 3 | C2S08,03 | C2S08-X1 | 1756-OB32-3 | DO | 24 VDC energized,Dry Contact | XV-60264FQ | 0 | XV-60264FQ_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
226 | 8 | 4 | C2S08,04 | C2S08-X1 | 1756-OB32-4 | DO | 24 VDC energized,Dry Contact | XV-60264FR | 0 | XV-60264FR_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
227 | 8 | 5 | C2S08,05 | C2S08-X1 | 1756-OB32-5 | DO | 24 VDC energized,Dry Contact | XV-60264SN | 0 | XV-60264SN_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
228 | 8 | 6 | C2S08,06 | C2S08-X1 | 1756-OB32-6 | DO | 24 VDC energized,Dry Contact | XV-60264SP | 0 | XV-60264SP_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
229 | 8 | 7 | C2S08,07 | C2S08-X1 | 1756-OB32-7 | DO | 24 VDC energized,Dry Contact | XV-60264SQ | 0 | XV-60264SQ_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
230 | 8 | 8 | C2S08,08 | C2S08-X1 | 1756-OB32-8 | DO | 24 VDC energized,Dry Contact | XV-60264SR | 0 | XV-60264SR_DO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
231 | 8 | 9 | C2S08,09 | C2S08-X1 | 1756-OB32-9 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
232 | 8 | 10 | C2S08,10 | C2S08-X1 | 1756-OB32-10 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
233 | 8 | 11 | C2S08,11 | C2S08-X1 | 1756-OB32-11 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
234 | 8 | 12 | C2S08,12 | C2S08-X1 | 1756-OB32-12 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
235 | 8 | 13 | C2S08,13 | C2S08-X1 | 1756-OB32-13 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
236 | 8 | 14 | C2S08,14 | C2S08-X1 | 1756-OB32-14 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
237 | 8 | 15 | C2S08,15 | C2S08-X1 | 1756-OB32-15 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
238 | 8 | 16 | C2S08,16 | C2S08-X2 | 1756-OB32-16 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
239 | 8 | 17 | C2S08,17 | C2S08-X2 | 1756-OB32-17 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
240 | 8 | 18 | C2S08,18 | C2S08-X2 | 1756-OB32-18 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
241 | 8 | 19 | C2S08,19 | C2S08-X2 | 1756-OB32-19 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
242 | 8 | 20 | C2S08,20 | C2S08-X2 | 1756-OB32-20 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
243 | 8 | 21 | C2S08,21 | C2S08-X2 | 1756-OB32-21 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
244 | 8 | 22 | C2S08,22 | C2S08-X2 | 1756-OB32-22 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
245 | 8 | 23 | C2S08,23 | C2S08-X2 | 1756-OB32-23 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
246 | 8 | 24 | C2S08,24 | C2S08-X2 | 1756-OB32-24 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
247 | 8 | 25 | C2S08,25 | C2S08-X2 | 1756-OB32-25 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
248 | 8 | 26 | C2S08,26 | C2S08-X2 | 1756-OB32-26 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
249 | 8 | 27 | C2S08,27 | C2S08-X2 | 1756-OB32-27 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
250 | 8 | 28 | C2S08,28 | C2S08-X2 | 1756-OB32-28 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
251 | 8 | 29 | C2S08,29 | C2S08-X2 | 1756-OB32-29 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
252 | 8 | 30 | C2S08,30 | C2S08-X2 | 1756-OB32-30 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
253 | 8 | 31 | C2S08,31 | C2S08-X2 | 1756-OB32-31 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-607 | SPARE
254 | 9 | 0 | C2S09,00 | C2S09-X1 | 1756-IF16-0 | AI | 4 - 20 mA,Pulse | FT-40221 | Coriolis Flow Transmitter | FT-40221_AI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
255 | 9 | 1 | C2S09,01 | C2S09-X1 | 1756-IF16-1 | AI | 4 - 20 mA,Pulse | FT-40221 | Coriolis Flow Transmitter | FT-40221_AI_2 | 325-01-402-PD-02 | JB-402 | ACTIVE
256 | 9 | 2 | C2S09,02 | C2S09-X1 | 1756-IF16-2 | AI | 4 - 20 mA,Pulse | FT-40222 | Coriolis Flow Transmitter | FT-40222_AI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
257 | 9 | 3 | C2S09,03 | C2S09-X1 | 1756-IF16-3 | AI | 4 - 20 mA,Pulse | FT-40222 | Coriolis Flow Transmitter | FT-40222_AI_2 | 325-01-402-PD-02 | JB-402 | ACTIVE
258 | 9 | 4 | C2S09,04 | C2S09-X1 | 1756-IF16-4 | AI | 4 - 20 mA | PT-40222 | Pressure Transmitter | PT-40222_AI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
259 | 9 | 5 | C2S09,05 | C2S09-X1 | 1756-IF16-5 | AI | 4 - 20 mA | TT-40221 | 0 | TT-40221_AI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
260 | 9 | 6 | C2S09,06 | C2S09-X1 | 1756-IF16-6 | AI | 4 - 20 mA | TT-40222 | 0 | TT-40222_AI_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
261 | 9 | 7 | C2S09,07 | C2S09-X1 | 1756-IF16-7 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-402 | SPARE
262 | 9 | 8 | C2S09,08 | C2S09-X1 | 1756-IF16-8 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-402 | SPARE
263 | 9 | 9 | C2S09,09 | C2S09-X1 | 1756-IF16-9 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-402 | SPARE
264 | 9 | 10 | C2S09,10 | C2S09-X1 | 1756-IF16-10 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-402 | SPARE
265 | 9 | 11 | C2S09,11 | C2S09-X1 | 1756-IF16-11 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-402 | SPARE
266 | 9 | 12 | C2S09,12 | C2S09-X1 | 1756-IF16-12 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-402 | SPARE
267 | 9 | 13 | C2S09,13 | C2S09-X1 | 1756-IF16-13 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-402 | SPARE
268 | 9 | 14 | C2S09,14 | C2S09-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-402 | SPARE
269 | 9 | 15 | C2S09,15 | C2S09-X1 | 1756-IF16-15 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-402 | SPARE
270 | 10 | 0 | C2S10,00 | C2S10-X1 | 1756-IF16-0 | AI | 4 - 20 mA | AT-60241 | Dust Analyzer Transmitter | AT-60241_AI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
271 | 10 | 1 | C2S10,01 | C2S10-X1 | 1756-IF16-1 | AI | 4 - 20 mA | DPT-60203 | Differential Pressure Transmitte | DPT-60203_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
272 | 10 | 2 | C2S10,02 | C2S10-X1 | 1756-IF16-2 | AI | 4 - 20 mA | FT-60202 | 0 | FT-60202_AI_1 | 3-25-01-602-PD-09 | JB-602 | ACTIVE
273 | 10 | 3 | C2S10,03 | C2S10-X1 | 1756-IF16-3 | AI | 4 - 20 mA | PT-60210 | Pressure Transmitter | PT-60210_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
274 | 10 | 4 | C2S10,04 | C2S10-X1 | 1756-IF16-4 | AI | 4 - 20 mA | PT-60215 | Pressure Transmitter | PT-60215_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
275 | 10 | 5 | C2S10,05 | C2S10-X1 | 1756-IF16-5 | AI | 4 - 20 mA | PT-60216 | Pressure Transmitter | PT-60216_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
276 | 10 | 6 | C2S10,06 | C2S10-X1 | 1756-IF16-6 | AI | 4 - 20 mA | PT-60240 | Pressure Transmitter | PT-60240_AI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
277 | 10 | 7 | C2S10,07 | C2S10-X1 | 1756-IF16-7 | AI | 4 - 20 mA | PT-60241 | Pressure Transmitter | PT-60241_AI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
278 | 10 | 8 | C2S10,08 | C2S10-X1 | 1756-IF16-8 | AI | 4 - 20 mA | TT-60210 | 0 | TT-60210_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
279 | 10 | 9 | C2S10,09 | C2S10-X1 | 1756-IF16-9 | AI | - | TT-60210A | - | TT-60210A_AI_1 | 325-01-600-PD-03 | JB-602 | ACTIVE
280 | 10 | 10 | C2S10,10 | C2S10-X1 | 1756-IF16-10 | AI | - | TT-60210B | - | TT-60210B_AI_1 | 325-01-600-PD-03 | JB-602 | ACTIVE
281 | 10 | 11 | C2S10,11 | C2S10-X1 | 1756-IF16-11 | AI | 4 - 20 mA | TT-60211 | 0 | TT-60211_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
282 | 10 | 12 | C2S10,12 | C2S10-X1 | 1756-IF16-12 | AI | 4 - 20 mA | TT-60212A | 0 | TT-60212A_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
283 | 10 | 13 | C2S10,13 | C2S10-X1 | 1756-IF16-13 | AI | 4 - 20 mA | TT-60212B | 0 | TT-60212B_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
284 | 10 | 14 | C2S10,14 | C2S10-X1 | 1756-IF16-14 | AI | 4 - 20 mA | TT-60214 | 0 | TT-60214_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
285 | 10 | 15 | C2S10,15 | C2S10-X1 | 1756-IF16-15 | AI | 4 - 20 mA | TT-60215A | 0 | TT-60215A_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
286 | 11 | 0 | C2S11,00 | C2S11-X1 | 1756-IF16-0 | AI | 4 - 20 mA | TT-60215B | 0 | TT-60215B_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
287 | 11 | 1 | C2S11,01 | C2S11-X1 | 1756-IF16-1 | AI | 4 - 20 mA | TT-60216 | 0 | TT-60216_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
288 | 11 | 2 | C2S11,02 | C2S11-X1 | 1756-IF16-2 | AI | 4 - 20 mA | TT-60240 | 0 | TT-60240_AI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
289 | 11 | 3 | C2S11,03 | C2S11-X1 | 1756-IF16-3 | AI | 4 - 20 mA | TT-60241A | 0 | TT-60241A_AI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
290 | 11 | 4 | C2S11,04 | C2S11-X1 | 1756-IF16-4 | AI | 4 - 20 mA | TT-60241B | 0 | TT-60241B_AI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
291 | 11 | 5 | C2S11,05 | C2S11-X1 | 1756-IF16-5 | AI | 4 - 20 mA | VT-60210A | 0 | VT-60210A_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
292 | 11 | 6 | C2S11,06 | C2S11-X1 | 1756-IF16-6 | AI | 4 - 20 mA | VT-60210B | 0 | VT-60210B_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
293 | 11 | 7 | C2S11,07 | C2S11-X1 | 1756-IF16-7 | AI | 4 - 20 mA | VT-60241A | 0 | VT-60241A_AI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
294 | 11 | 8 | C2S11,08 | C2S11-X1 | 1756-IF16-8 | AI | 4 - 20 mA | VT-60241B | 0 | VT-60241B_AI_1 | 3-25-01-602-PD-05 | JB-602 | ACTIVE
295 | 11 | 9 | C2S11,09 | C2S11-X1 | 1756-IF16-9 | AI | 4 - 20 mA | FT-60210 | 0 | FT-60210_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
296 | 11 | 10 | C2S11,10 | C2S11-X1 | 1756-IF16-10 | AI | 4 - 20 mA | FT-60211 | 0 | FT-60211_AI_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
297 | 11 | 11 | C2S11,11 | C2S11-X1 | 1756-IF16-11 | AI | 4 - 20 mA | FT-60210 | 0 | FT-60210_AI_2 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
298 | 11 | 12 | C2S11,12 | C2S11-X1 | 1756-IF16-12 | AI | 4 - 20 mA | FT-60211 | 0 | FT-60211_AI_2 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
299 | 11 | 13 | C2S11,13 | C2S11-X1 | 1756-IF16-13 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-602 | SPARE
300 | 11 | 14 | C2S11,14 | C2S11-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-602 | SPARE
301 | 11 | 15 | C2S11,15 | C2S11-X1 | 1756-IF16-15 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-602 | SPARE
302 | 12 | 0 | C2S12,00 | C2S12-X1 | 1756-IF16-0 | AI | 4 - 20 mA | FT-60207 | 0 | FT-60207_AI_1 | 3-25-01-602-PD-07 | JB-607 | ACTIVE
303 | 12 | 1 | C2S12,01 | C2S12-X1 | 1756-IF16-1 | AI | 4 - 20 mA | FT-60221 | 0 | FT-60221_AI_1 | 3-25-01-602-PD-04 | JB-607 | ACTIVE
304 | 12 | 2 | C2S12,02 | C2S12-X1 | 1756-IF16-2 | AI | 4 - 20 mA | FT-60261FA | 0 | FT-60261FA_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
305 | 12 | 3 | C2S12,03 | C2S12-X1 | 1756-IF16-3 | AI | 4 - 20 mA | FT-60261FB | 0 | FT-60261FB_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
306 | 12 | 4 | C2S12,04 | C2S12-X1 | 1756-IF16-4 | AI | 4 - 20 mA | FT-60261FC | 0 | FT-60261FC_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
307 | 12 | 5 | C2S12,05 | C2S12-X1 | 1756-IF16-5 | AI | 4 - 20 mA | FT-60261FD | 0 | FT-60261FD_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
308 | 12 | 6 | C2S12,06 | C2S12-X1 | 1756-IF16-6 | AI | 4 - 20 mA | FT-60262FE | 0 | FT-60262FE_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
309 | 12 | 7 | C2S12,07 | C2S12-X1 | 1756-IF16-7 | AI | 4 - 20 mA | FT-60262FF | 0 | FT-60262FF_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
310 | 12 | 8 | C2S12,08 | C2S12-X1 | 1756-IF16-8 | AI | 4 - 20 mA | FT-60262FG | 0 | FT-60262FG_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
311 | 12 | 9 | C2S12,09 | C2S12-X1 | 1756-IF16-9 | AI | 4 - 20 mA | FT-60262FH | 0 | FT-60262FH_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
312 | 12 | 10 | C2S12,10 | C2S12-X1 | 1756-IF16-10 | AI | 4 - 20 mA | FT-60263FJ | 0 | FT-60263FJ_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
313 | 12 | 11 | C2S12,11 | C2S12-X1 | 1756-IF16-11 | AI | 4 - 20 mA | FT-60263FK | 0 | FT-60263FK_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
314 | 12 | 12 | C2S12,12 | C2S12-X1 | 1756-IF16-12 | AI | 4 - 20 mA | FT-60263FL | 0 | FT-60263FL_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
315 | 12 | 13 | C2S12,13 | C2S12-X1 | 1756-IF16-13 | AI | 4 - 20 mA | FT-60263FM | 0 | FT-60263FM_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
316 | 12 | 14 | C2S12,14 | C2S12-X1 | 1756-IF16-14 | AI | 4 - 20 mA | FT-60264FN | 0 | FT-60264FN_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
317 | 12 | 15 | C2S12,15 | C2S12-X1 | 1756-IF16-15 | AI | 4 - 20 mA | FT-60264FP | 0 | FT-60264FP_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
318 | 13 | 0 | C2S13,00 | C2S13-X1 | 1756-IF16-0 | AI | 4 - 20 mA | FT-60264FQ | 0 | FT-60264FQ_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
319 | 13 | 1 | C2S13,01 | C2S13-X1 | 1756-IF16-1 | AI | 4 - 20 mA | FT-60264FR | 0 | FT-60264FR_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
320 | 13 | 2 | C2S13,02 | C2S13-X1 | 1756-IF16-2 | AI | 4 - 20 mA | PT-60201 | Pressure Transmitter | PT-60201_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
321 | 13 | 3 | C2S13,03 | C2S13-X1 | 1756-IF16-3 | AI | 4 - 20 mA | PT-60207 | Pressure Transmitter | PT-60207_AI_1 | 3-25-01-602-PD-07 | JB-607 | ACTIVE
322 | 13 | 4 | C2S13,04 | C2S13-X1 | 1756-IF16-4 | AI | 4 - 20 mA | PT-60221 | Pressure Transmitter | PT-60221_AI_1 | 3-25-01-602-PD-04 | JB-607 | ACTIVE
323 | 13 | 5 | C2S13,05 | C2S13-X1 | 1756-IF16-5 | AI | 4 - 20 mA | PT-60221 | Pressure Transmitter | PT-60221_AI_1 | 3-25-01-602-PD-04 | JB-607 | ACTIVE
324 | 13 | 6 | C2S13,06 | C2S13-X1 | 1756-IF16-6 | AI | 4 - 20 mA | TI-FH-60210 | 0 | TI-FH-60210_AI_1 | 325-01-600-PD-06 | JB-607 | ACTIVE
325 | 13 | 7 | C2S13,07 | C2S13-X1 | 1756-IF16-7 | AI | 4 - 20 mA | TT-60201 | 0 | TT-60201_AI_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
326 | 13 | 8 | C2S13,08 | C2S13-X1 | 1756-IF16-8 | AI | 4 - 20 mA | TT-60202 | 0 | TT-60202_AI_1 | 3-25-01-602-PD-07 | JB-607 | ACTIVE
327 | 13 | 9 | C2S13,09 | C2S13-X1 | 1756-IF16-9 | AI | 4 - 20 mA | TT-60207 | 0 | TT-60207_AI_1 | 3-25-01-602-PD-07 | JB-607 | ACTIVE
328 | 13 | 10 | C2S13,10 | C2S13-X1 | 1756-IF16-10 | AI | 4 - 20 mA | UY-FH-60210A | 0 | UY-FH-60210A_AI_1 | 325-01-600-PD-06 | JB-607 | ACTIVE
329 | 13 | 11 | C2S13,11 | C2S13-X1 | 1756-IF16-11 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-607 | SPARE
330 | 13 | 12 | C2S13,12 | C2S13-X1 | 1756-IF16-12 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-607 | SPARE
331 | 13 | 13 | C2S13,13 | C2S13-X1 | 1756-IF16-13 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-607 | SPARE
332 | 13 | 14 | C2S13,14 | C2S13-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-607 | SPARE
333 | 13 | 15 | C2S13,15 | C2S13-X1 | 1756-IF16-15 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-607 | SPARE

## Chassis_C3
CHASSIS C3 ¦ PANEL / ENCLOSURE: =CA1+MCP-M3 ¦ PROJECT JET COOKER
Item | Slot | Point | Channel Code | Terminal | Card Model | I/O Type | Signal | Instrument Tag | Instrument Description | PLC Tag | P&ID No. | Destination JB | Status
1 | 1 | 0 | C3S01,00 | C3S01-X1 | 1756-IB32-0 | DI | - | AT-40201 | - | AT-40201_DI_1 | - | IS-JB-603 | ACTIVE
2 | 1 | 1 | C3S01,01 | C3S01-X1 | 1756-IB32-1 | DI | - | AT-40202 | - | AT-40202_DI_1 | - | IS-JB-603 | ACTIVE
3 | 1 | 2 | C3S01,02 | C3S01-X1 | 1756-IB32-2 | DI | - | AT-40203 | - | AT-40203_DI_1 | - | IS-JB-603 | ACTIVE
4 | 1 | 3 | C3S01,03 | C3S01-X1 | 1756-IB32-3 | DI | Dry Contact | LSH-60230 | 0 | LSH-60230_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
5 | 1 | 4 | C3S01,04 | C3S01-X1 | 1756-IB32-4 | DI | Dry Contact | LSH-60231 | 0 | LSH-60231_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
6 | 1 | 5 | C3S01,05 | C3S01-X1 | 1756-IB32-5 | DI | Dry Contact | LSH-60240 | 0 | LSH-60240_DI_1 | 3-25-01-602-PD-05 | IS-JB-603 | ACTIVE
7 | 1 | 6 | C3S01,06 | C3S01-X1 | 1756-IB32-6 | DI | - | PD-60202 | - | PD-60202_DI_1 | - | IS-JB-603 | ACTIVE
8 | 1 | 7 | C3S01,07 | C3S01-X1 | 1756-IB32-7 | DI | - | RV-60204 | - | RV-60204_DI_1 | - | IS-JB-603 | ACTIVE
9 | 1 | 8 | C3S01,08 | C3S01-X1 | 1756-IB32-8 | DI | Dry Contact | ZS-60201C | 0 | ZS-60201C_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
10 | 1 | 9 | C3S01,09 | C3S01-X1 | 1756-IB32-9 | DI | Dry Contact | ZS-60201D | 0 | ZS-60201D_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
11 | 1 | 10 | C3S01,10 | C3S01-X1 | 1756-IB32-10 | DI | Dry Contact | ZS-60201E | 0 | ZS-60201E_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
12 | 1 | 11 | C3S01,11 | C3S01-X1 | 1756-IB32-11 | DI | Dry Contact | ZS-60229 | 0 | ZS-60229_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
13 | 1 | 12 | C3S01,12 | C3S01-X1 | 1756-IB32-12 | DI | Dry Contact | ZS-60230 | 0 | ZS-60230_DI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
14 | 1 | 13 | C3S01,13 | C3S01-X1 | 1756-IB32-13 | DI | Dry Contact | ZS-60231A | 0 | ZS-60231A_DI_1 | 3-25-01-602-PD-05 | IS-JB-603 | ACTIVE
15 | 1 | 14 | C3S01,14 | C3S01-X1 | 1756-IB32-14 | DI | Dry Contact | ZS-60231B | 0 | ZS-60231B_DI_1 | 3-25-01-602-PD-05 | IS-JB-603 | ACTIVE
16 | 1 | 15 | C3S01,15 | C3S01-X1 | 1756-IB32-15 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-603 | SPARE
17 | 1 | 16 | C3S01,16 | C3S01-X2 | 1756-IB32-16 | DI | 24 VDC energized | DV-61301 | 0 | DV-61301_DI_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
18 | 1 | 17 | C3S01,17 | C3S01-X2 | 1756-IB32-17 | DI | 24 VDC energized | DV-61301 | 0 | DV-61301_DI_2 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
19 | 1 | 18 | C3S01,18 | C3S01-X2 | 1756-IB32-18 | DI | 24 VDC energized | DV-61302 | 0 | DV-61302_DI_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
20 | 1 | 19 | C3S01,19 | C3S01-X2 | 1756-IB32-19 | DI | 24 VDC energized | DV-61302 | 0 | DV-61302_DI_2 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
21 | 1 | 20 | C3S01,20 | C3S01-X2 | 1756-IB32-20 | DI | Dry Contact | LS-61303 | 0 | LS-61303_DI_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
22 | 1 | 21 | C3S01,21 | C3S01-X2 | 1756-IB32-21 | DI | Dry Contact | PSL-61301 | 0 | PSL-61301_DI_1 | 325-01-613-PD-01 | JB-618 | ACTIVE
23 | 1 | 22 | C3S01,22 | C3S01-X2 | 1756-IB32-22 | DI | Dry Contact | PSL-61302 | 0 | PSL-61302_DI_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
24 | 1 | 28 | C3S01,28 | C3S01-X2 | 1756-IB32-28 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-618 | SPARE
25 | 1 | 29 | C3S01,29 | C3S01-X2 | 1756-IB32-29 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-618 | SPARE
26 | 1 | 30 | C3S01,30 | C3S01-X2 | 1756-IB32-30 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-618 | SPARE
27 | 1 | 31 | C3S01,31 | C3S01-X2 | 1756-IB32-31 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-618 | SPARE
28 | 2 | 0 | C3S02,00 | C3S02-X1 | 1756-IB32-0 | DI | - | ISV-61301 | - | ISV-61301_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
29 | 2 | 1 | C3S02,01 | C3S02-X1 | 1756-IB32-1 | DI | Dry Contact | LSH-61301 | 0 | LSH-61301_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
30 | 2 | 2 | C3S02,02 | C3S02-X1 | 1756-IB32-2 | DI | - | LSH-61303 | - | LSH-61303_DI_1 | 325-01-613-PD-01 | IS-JB-618 | ACTIVE
31 | 2 | 3 | C3S02,03 | C3S02-X1 | 1756-IB32-3 | DI | Dry Contact | LSH-61306 | 0 | LSH-61306_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
32 | 2 | 4 | C3S02,04 | C3S02-X1 | 1756-IB32-4 | DI | Dry Contact | LSH-61308 | 0 | LSH-61308_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
33 | 2 | 5 | C3S02,05 | C3S02-X1 | 1756-IB32-5 | DI | Dry Contact | LSL-61302 | 0 | LSL-61302_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
34 | 2 | 6 | C3S02,06 | C3S02-X1 | 1756-IB32-6 | DI | Dry Contact | PSE-61300 | 0 | PSE-61300_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
35 | 2 | 7 | C3S02,07 | C3S02-X1 | 1756-IB32-7 | DI | Dry Contact | PSE-61301 | 0 | PSE-61301_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
36 | 2 | 8 | C3S02,08 | C3S02-X1 | 1756-IB32-8 | DI | Dry Contact | PSE-61304 | 0 | PSE-61304_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
37 | 2 | 9 | C3S02,09 | C3S02-X1 | 1756-IB32-9 | DI | - | PSV-61301A | - | PSV-61301A_DI_1 | 325-01-613-PD-01 | IS-JB-618 | ACTIVE
38 | 2 | 10 | C3S02,10 | C3S02-X1 | 1756-IB32-10 | DI | - | PSV-61301B | - | PSV-61301B_DI_1 | 325-01-613-PD-01 | IS-JB-618 | ACTIVE
39 | 2 | 11 | C3S02,11 | C3S02-X1 | 1756-IB32-11 | DI | Dry Contact | ZS-61310 | 0 | ZS-61310_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
40 | 2 | 12 | C3S02,12 | C3S02-X1 | 1756-IB32-12 | DI | Dry Contact | ZS-61311 | 0 | ZS-61311_DI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
41 | 2 | 13 | C3S02,13 | C3S02-X1 | 1756-IB32-13 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
42 | 2 | 14 | C3S02,14 | C3S02-X1 | 1756-IB32-14 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
43 | 2 | 15 | C3S02,15 | C3S02-X1 | 1756-IB32-15 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
44 | 2 | 16 | C3S02,16 | C3S02-X2 | 1756-IB32-16 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
45 | 2 | 17 | C3S02,17 | C3S02-X2 | 1756-IB32-17 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
46 | 2 | 18 | C3S02,18 | C3S02-X2 | 1756-IB32-18 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
47 | 2 | 19 | C3S02,19 | C3S02-X2 | 1756-IB32-19 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
48 | 2 | 20 | C3S02,20 | C3S02-X2 | 1756-IB32-20 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
49 | 2 | 21 | C3S02,21 | C3S02-X2 | 1756-IB32-21 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
50 | 2 | 22 | C3S02,22 | C3S02-X2 | 1756-IB32-22 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
51 | 2 | 23 | C3S02,23 | C3S02-X2 | 1756-IB32-23 | DI | Dry Contact | PSL-61311 | 0 | PSL-61311_DI_1 | 3-25-01-613-PD-04 | JB-618 | ACTIVE
52 | 2 | 23 | C3S02,23 | C3S02-X2 | 1756-IB32-23 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
53 | 2 | 24 | C3S02,24 | C3S02-X2 | 1756-IB32-24 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
54 | 2 | 24 | C3S02,24 | C3S02-X2 | 1756-IB32-24 | DI | 24 VDC energized | SV-61304 | 0 | SV-61304_DI_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
55 | 2 | 25 | C3S02,25 | C3S02-X2 | 1756-IB32-25 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
56 | 2 | 25 | C3S02,25 | C3S02-X2 | 1756-IB32-25 | DI | 24 VDC energized | SV-61304 | 0 | SV-61304_DI_2 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
57 | 2 | 26 | C3S02,26 | C3S02-X2 | 1756-IB32-26 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
58 | 2 | 26 | C3S02,26 | C3S02-X2 | 1756-IB32-26 | DI | 24 VDC energized | XV-61301 | 0 | XV-61301_DI_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
59 | 2 | 27 | C3S02,27 | C3S02-X2 | 1756-IB32-27 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
60 | 2 | 27 | C3S02,27 | C3S02-X2 | 1756-IB32-27 | DI | 24 VDC energized | XV-61301 | 0 | XV-61301_DI_2 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
61 | 2 | 28 | C3S02,28 | C3S02-X2 | 1756-IB32-28 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
62 | 2 | 29 | C3S02,29 | C3S02-X2 | 1756-IB32-29 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
63 | 2 | 30 | C3S02,30 | C3S02-X2 | 1756-IB32-30 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
64 | 2 | 31 | C3S02,31 | C3S02-X2 | 1756-IB32-31 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-613-PD-01 | IS-JB-618 | SPARE
65 | 3 | 0 | C3S03,00 | C3S03-X1 | 1756-OB32-0 | DO | 24 VDC energized | DV-61301 | 0 | DV-61301_DO_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
66 | 3 | 1 | C3S03,01 | C3S03-X1 | 1756-OB32-1 | DO | 24 VDC energized | DV-61302 | 0 | DV-61302_DO_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
67 | 3 | 2 | C3S03,02 | C3S03-X1 | 1756-OB32-2 | DO | 24 VDC energized | SV-61301 | 0 | SV-61301_DO_1 | 325-01-613-PD-01 | JB-618 | ACTIVE
68 | 3 | 3 | C3S03,03 | C3S03-X1 | 1756-OB32-3 | DO | 24 VDC energized | SV-61302 | 0 | SV-61302_DO_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
69 | 3 | 4 | C3S03,04 | C3S03-X1 | 1756-OB32-4 | DO | 24 VDC energized | SV-61303 | 0 | SV-61303_DO_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
70 | 3 | 5 | C3S03,05 | C3S03-X1 | 1756-OB32-5 | DO | 24 VDC energized | SV-61304 | 0 | SV-61304_DO_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
71 | 3 | 6 | C3S03,06 | C3S03-X1 | 1756-OB32-6 | DO | 24 VDC energized | SV-61305 | 0 | SV-61305_DO_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
72 | 3 | 7 | C3S03,07 | C3S03-X1 | 1756-OB32-7 | DO | - | SV-61306 | - | SV-61306_DO_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
73 | 3 | 8 | C3S03,08 | C3S03-X1 | 1756-OB32-8 | DO | 24 VDC energized | XV-61301 | 0 | XV-61301_DO_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
74 | 3 | 9 | C3S03,09 | C3S03-X1 | 1756-OB32-9 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
75 | 3 | 10 | C3S03,10 | C3S03-X1 | 1756-OB32-10 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
76 | 3 | 11 | C3S03,11 | C3S03-X1 | 1756-OB32-11 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
77 | 3 | 12 | C3S03,12 | C3S03-X1 | 1756-OB32-12 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
78 | 3 | 13 | C3S03,13 | C3S03-X1 | 1756-OB32-13 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
79 | 3 | 14 | C3S03,14 | C3S03-X1 | 1756-OB32-14 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
80 | 3 | 15 | C3S03,15 | C3S03-X1 | 1756-OB32-15 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
81 | 3 | 16 | C3S03,16 | C3S03-X2 | 1756-OB32-16 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
82 | 3 | 17 | C3S03,17 | C3S03-X2 | 1756-OB32-17 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
83 | 3 | 18 | C3S03,18 | C3S03-X2 | 1756-OB32-18 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
84 | 3 | 19 | C3S03,19 | C3S03-X2 | 1756-OB32-19 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
85 | 3 | 20 | C3S03,20 | C3S03-X2 | 1756-OB32-20 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
86 | 3 | 21 | C3S03,21 | C3S03-X2 | 1756-OB32-21 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
87 | 3 | 22 | C3S03,22 | C3S03-X2 | 1756-OB32-22 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
88 | 3 | 23 | C3S03,23 | C3S03-X2 | 1756-OB32-23 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
89 | 3 | 24 | C3S03,24 | C3S03-X2 | 1756-OB32-24 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
90 | 3 | 25 | C3S03,25 | C3S03-X2 | 1756-OB32-25 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
91 | 3 | 26 | C3S03,26 | C3S03-X2 | 1756-OB32-26 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
92 | 3 | 27 | C3S03,27 | C3S03-X2 | 1756-OB32-27 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
93 | 3 | 28 | C3S03,28 | C3S03-X2 | 1756-OB32-28 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
94 | 3 | 29 | C3S03,29 | C3S03-X2 | 1756-OB32-29 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
95 | 3 | 30 | C3S03,30 | C3S03-X2 | 1756-OB32-30 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
96 | 3 | 31 | C3S03,31 | C3S03-X2 | 1756-OB32-31 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-618 | SPARE
97 | 4 | 0 | C3S04,00 | C3S04-X1 | 1756-IF16-0 | AI | 4 - 20 mA | PT-60230 | Pressure Transmitter | PT-60230_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
98 | 4 | 1 | C3S04,01 | C3S04-X1 | 1756-IF16-1 | AI | 4 - 20 mA | PT-60231 | Pressure Transmitter | PT-60231_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
99 | 4 | 2 | C3S04,02 | C3S04-X1 | 1756-IF16-2 | AI | 4 - 20 mA | TT-60224 | 0 | TT-60224_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
100 | 4 | 3 | C3S04,03 | C3S04-X1 | 1756-IF16-3 | AI | 4 - 20 mA | TT-60225 | 0 | TT-60225_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
101 | 4 | 4 | C3S04,04 | C3S04-X1 | 1756-IF16-4 | AI | 4 - 20 mA | TT-60226 | 0 | TT-60226_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
102 | 4 | 5 | C3S04,05 | C3S04-X1 | 1756-IF16-5 | AI | 4 - 20 mA | TT-60227 | 0 | TT-60227_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
103 | 4 | 6 | C3S04,06 | C3S04-X1 | 1756-IF16-6 | AI | 4 - 20 mA | TT-60230 | 0 | TT-60230_AI_1 | 3-25-01-602-PD-04 | IS-JB-603 | ACTIVE
104 | 4 | 7 | C3S04,07 | C3S04-X1 | 1756-IF16-7 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-603 | SPARE
105 | 4 | 8 | C3S04,08 | C3S04-X1 | 1756-IF16-8 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-603 | SPARE
106 | 4 | 9 | C3S04,09 | C3S04-X1 | 1756-IF16-9 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-603 | SPARE
107 | 4 | 10 | C3S04,10 | C3S04-X1 | 1756-IF16-10 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-603 | SPARE
108 | 4 | 11 | C3S04,11 | C3S04-X1 | 1756-IF16-11 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-603 | SPARE
109 | 4 | 12 | C3S04,12 | C3S04-X1 | 1756-IF16-12 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-603 | SPARE
110 | 4 | 13 | C3S04,13 | C3S04-X1 | 1756-IF16-13 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-603 | SPARE
111 | 4 | 14 | C3S04,14 | C3S04-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-603 | SPARE
112 | 4 | 15 | C3S04,15 | C3S04-X1 | 1756-IF16-15 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-603 | SPARE
113 | 5 | 0 | C3S05,00 | C3S05-X1 | 1756-IF16-0 | AI | 4 - 20 mA | PT-61303 | Pressure Transmitter | PT-61303_AI_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
114 | 5 | 1 | C3S05,01 | C3S05-X1 | 1756-IF16-1 | AI | - | PT-61306 | - | PT-61306_AI_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
115 | 5 | 2 | C3S05,02 | C3S05-X1 | 1756-IF16-2 | AI | - | TT-61303 | - | TT-61303_AI_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
116 | 5 | 3 | C3S05,03 | C3S05-X1 | 1756-IF16-3 | AI | - | TT-61304 | - | TT-61304_AI_1 | 3-25-01-613-PD-01 | JB-618 | ACTIVE
117 | 5 | 4 | C3S05,04 | C3S05-X1 | 1756-IF16-4 | AI | 4 - 20 mA | DPT-61301 | Differential Pressure Transmitte | DPT-61301_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
118 | 5 | 5 | C3S05,05 | C3S05-X1 | 1756-IF16-5 | AI | 4 - 20 mA | DPT-61302 | Differential Pressure Transmitte | DPT-61302_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
119 | 5 | 6 | C3S05,06 | C3S05-X1 | 1756-IF16-6 | AI | 4 - 20 mA | LT-61301 | Level Transmitter | LT-61301_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
120 | 5 | 7 | C3S05,07 | C3S05-X1 | 1756-IF16-7 | AI | 4 - 20 mA | PT-61301 | Pressure Transmitter | PT-61301_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
121 | 5 | 8 | C3S05,08 | C3S05-X1 | 1756-IF16-8 | AI | 4 - 20 mA | PT-61303 | Pressure Transmitter | PT-61303_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
122 | 5 | 9 | C3S05,09 | C3S05-X1 | 1756-IF16-9 | AI | 4 - 20 mA | PT-61304 | Pressure Transmitter | PT-61304_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
123 | 5 | 10 | C3S05,10 | C3S05-X1 | 1756-IF16-10 | AI | 4 - 20 mA | PT-61305 | Pressure Transmitter | PT-61305_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
124 | 5 | 11 | C3S05,11 | C3S05-X1 | 1756-IF16-11 | AI | 4 - 20 mA | TT-61301 | 0 | TT-61301_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
125 | 5 | 12 | C3S05,12 | C3S05-X1 | 1756-IF16-12 | AI | 4 - 20 mA | TT-61302 | 0 | TT-61302_AI_1 | 3-25-01-613-PD-01 | IS-JB-618 | ACTIVE
126 | 5 | 13 | C3S05,13 | C3S05-X1 | 1756-IF16-13 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-618 | SPARE
127 | 5 | 14 | C3S05,14 | C3S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-618 | SPARE
128 | 5 | 15 | C3S05,15 | C3S05-X1 | 1756-IF16-15 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-618 | SPARE
129 | 13 | 0 | C3S13,00 | C3S13-X1 | 1756-OF8-0 | AO | 4 - 20 mA | TCV-40222 | 0 | TCV-40222_AO_1 | 325-01-402-PD-02 | JB-402 | ACTIVE
130 | 13 | 1 | C3S13,01 | C3S13-X1 | 1756-OF8-1 | AO | - | TV-60202 | - | TV-60202_AO_1 | 3-25-01-602-PD-07 | JB-602 | ACTIVE
131 | 13 | 2 | C3S13,02 | C3S13-X1 | 1756-OF8-2 | AO | - | TV-60214 | - | TV-60214_AO_1 | 3-25-01-602-PD-03 | JB-602 | ACTIVE
132 | 13 | 3 | C3S13,03 | C3S13-X1 | 1756-OF8-3 | AO | - | PV-60201 | - | PV-60201_AO_1 | 3-25-01-602-PD-02 | JB-607 | ACTIVE
133 | 13 | 4 | C3S13,04 | C3S13-X1 | 1756-OF8-4 | AO | 4 - 20 mA | UY-FH-60210B | 0 | UY-FH-60210B_AO_1 | 325-01-600-PD-06 | JB-607 | ACTIVE
134 | 13 | 5 | C3S13,05 | C3S13-X1 | 1756-OF8-5 | AO | - | Spare | Spare I/O Point | Spare_AO_0 | - | JB-607 | SPARE
135 | 13 | 6 | C3S13,06 | C3S13-X1 | 1756-OF8-6 | AO | - | Spare | Spare I/O Point | Spare_AO_0 | - | JB-607 | SPARE
136 | 13 | 7 | C3S13,07 | C3S13-X1 | 1756-OF8-7 | AO | - | Spare | Spare I/O Point | Spare_AO_0 | - | JB-607 | SPARE

## Chassis_C4
CHASSIS C4 ¦ PANEL / ENCLOSURE: =CA1+MCP-M4 ¦ PROJECT JET COOKER
Item | Slot | Point | Channel Code | Terminal | Card Model | I/O Type | Signal | Instrument Tag | Instrument Description | PLC Tag | P&ID No. | Destination JB | Status
1 | 1 | 0 | C4S01,00 | C4S01-X1 | 1756-IB32-0 | DI | 4 - 20 mA | FT-60203 | 0 | FT-60203_DI_1 | 3-25-01-602-PD-09 | JB-606 | ACTIVE
2 | 1 | 1 | C4S01,01 | C4S01-X1 | 1756-IB32-1 | DI | Dry Contact | LSH-60250 | 0 | LSH-60250_DI_1 | 3-25-01-602-PD-05 | JB-606 | ACTIVE
3 | 1 | 2 | C4S01,02 | C4S01-X1 | 1756-IB32-2 | DI | Dry Contact | XA-60261 | 0 | XA-60261_DI_1 | 325-01-600-PD-05 | JB-606 | ACTIVE
4 | 1 | 3 | C4S01,03 | C4S01-X1 | 1756-IB32-3 | DI | Dry Contact | XA-60262 | 0 | XA-60262_DI_1 | 325-01-600-PD-05 | JB-606 | ACTIVE
5 | 1 | 4 | C4S01,04 | C4S01-X1 | 1756-IB32-4 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-606 | SPARE
6 | 1 | 5 | C4S01,05 | C4S01-X1 | 1756-IB32-5 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-606 | SPARE
7 | 1 | 6 | C4S01,06 | C4S01-X1 | 1756-IB32-6 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-606 | SPARE
8 | 1 | 7 | C4S01,07 | C4S01-X1 | 1756-IB32-7 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-606 | SPARE
9 | 1 | 8 | C4S01,08 | C4S01-X1 | 1756-IB32-8 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-606 | SPARE
10 | 1 | 9 | C4S01,09 | C4S01-X1 | 1756-IB32-9 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-606 | SPARE
11 | 1 | 10 | C4S01,10 | C4S01-X1 | 1756-IB32-10 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-606 | SPARE
12 | 1 | 11 | C4S01,11 | C4S01-X1 | 1756-IB32-11 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-606 | SPARE
13 | 1 | 12 | C4S01,12 | C4S01-X1 | 1756-IB32-12 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-606 | SPARE
14 | 1 | 13 | C4S01,13 | C4S01-X1 | 1756-IB32-13 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-606 | SPARE
15 | 1 | 14 | C4S01,14 | C4S01-X1 | 1756-IB32-14 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-606 | SPARE
16 | 1 | 15 | C4S01,15 | C4S01-X1 | 1756-IB32-15 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-606 | SPARE
17 | 1 | 16 | C4S01,16 | C4S01-X2 | 1756-IB32-16 | DI | Dry Contact | ZS-60201A | 0 | ZS-60201A_DI_1 | 3-25-01-602-PD-04 | IS-JB-608 | ACTIVE
18 | 1 | 17 | C4S01,17 | C4S01-X2 | 1756-IB32-17 | DI | Dry Contact | ZS-60201B | 0 | ZS-60201B_DI_1 | 3-25-01-602-PD-04 | IS-JB-608 | ACTIVE
19 | 1 | 18 | C4S01,18 | C4S01-X2 | 1756-IB32-18 | DI | Dry Contact | ZS-60231C | 0 | ZS-60231C_DI_1 | 3-25-01-602-PD-04 | IS-JB-608 | ACTIVE
20 | 1 | 19 | C4S01,19 | C4S01-X2 | 1756-IB32-19 | DI | Dry Contact | ZS-60231D | 0 | ZS-60231D_DI_1 | 3-25-01-602-PD-04 | IS-JB-608 | ACTIVE
21 | 1 | 20 | C4S01,20 | C4S01-X2 | 1756-IB32-20 | DI | Dry Contact | ZS-60231E | 0 | ZS-60231E_DI_1 | 3-25-01-602-PD-05 | IS-JB-608 | ACTIVE
22 | 1 | 21 | C4S01,21 | C4S01-X2 | 1756-IB32-21 | DI | Dry Contact | ZS-60231F | 0 | ZS-60231F_DI_1 | 3-25-01-602-PD-05 | IS-JB-608 | ACTIVE
23 | 1 | 22 | C4S01,22 | C4S01-X2 | 1756-IB32-22 | DI | Dry Contact | ZS-60240 | 0 | ZS-60240_DI_1 | 3-25-01-602-PD-05 | IS-JB-608 | ACTIVE
24 | 1 | 23 | C4S01,23 | C4S01-X2 | 1756-IB32-23 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-608 | SPARE
25 | 1 | 24 | C4S01,24 | C4S01-X2 | 1756-IB32-24 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-608 | SPARE
26 | 1 | 25 | C4S01,25 | C4S01-X2 | 1756-IB32-25 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-608 | SPARE
27 | 1 | 26 | C4S01,26 | C4S01-X2 | 1756-IB32-26 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-608 | SPARE
28 | 1 | 27 | C4S01,27 | C4S01-X2 | 1756-IB32-27 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-608 | SPARE
29 | 1 | 28 | C4S01,28 | C4S01-X2 | 1756-IB32-28 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-608 | SPARE
30 | 1 | 29 | C4S01,29 | C4S01-X2 | 1756-IB32-29 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-608 | SPARE
31 | 1 | 30 | C4S01,30 | C4S01-X2 | 1756-IB32-30 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-608 | SPARE
32 | 1 | 31 | C4S01,31 | C4S01-X2 | 1756-IB32-31 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-608 | SPARE
33 | 2 | 0 | C4S02,00 | C4S02-X1 | 1756-IB32-0 | DI | Dry Contact | PSL-61305 | 0 | PSL-61305_DI_1 | 3-25-01-613-PD-03 | JB-612 | ACTIVE
34 | 2 | 1 | C4S02,01 | C4S02-X1 | 1756-IB32-1 | DI | Dry Contact | PSL-61306 | 0 | PSL-61306_DI_1 | 3-25-01-613-PD-05 | JB-612 | ACTIVE
35 | 2 | 2 | C4S02,02 | C4S02-X1 | 1756-IB32-2 | DI | - | PVM-61301 | - | PVM-61301_DI_1 | 325-01-613-PD-03 | JB-612 | ACTIVE
36 | 2 | 3 | C4S02,03 | C4S02-X1 | 1756-IB32-3 | DI | - | PVM-61301 | - | PVM-61301_DI_2 | 325-01-613-PD-03 | JB-612 | ACTIVE
37 | 2 | 4 | C4S02,04 | C4S02-X1 | 1756-IB32-4 | DI | Dry Contact | XA-61301A | 0 | XA-61301A_DI_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
38 | 2 | 5 | C4S02,05 | C4S02-X1 | 1756-IB32-5 | DI | Dry Contact | XA-61301B | 0 | XA-61301B_DI_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
39 | 2 | 6 | C4S02,06 | C4S02-X1 | 1756-IB32-6 | DI | Dry Contact | XA-61301C | 0 | XA-61301C_DI_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
40 | 2 | 7 | C4S02,07 | C4S02-X1 | 1756-IB32-7 | DI | Dry Contact | XA-61301D | 0 | XA-61301D_DI_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
41 | 2 | 8 | C4S02,08 | C4S02-X1 | 1756-IB32-8 | DI | Dry Contact | XA-61301E | 0 | XA-61301E_DI_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
42 | 2 | 9 | C4S02,09 | C4S02-X1 | 1756-IB32-9 | DI | Dry Contact | XA-61301F | 0 | XA-61301F_DI_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
43 | 2 | 10 | C4S02,10 | C4S02-X1 | 1756-IB32-10 | DI | Dry Contact | XA-61301G | 0 | XA-61301G_DI_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
44 | 2 | 11 | C4S02,11 | C4S02-X1 | 1756-IB32-11 | DI | Dry Contact | XA-61301H | 0 | XA-61301H_DI_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
45 | 2 | 12 | C4S02,12 | C4S02-X1 | 1756-IB32-12 | DI | Dry Contact | XA-61301J | 0 | XA-61301J_DI_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
46 | 2 | 13 | C4S02,13 | C4S02-X1 | 1756-IB32-13 | DI | 24 VDC energized | XV-61302 | 0 | XV-61302_DI_1 | 3-25-01-613-PD-02 | JB-612 | ACTIVE
47 | 2 | 14 | C4S02,14 | C4S02-X1 | 1756-IB32-14 | DI | 24 VDC energized | XV-61302 | 0 | XV-61302_DI_2 | 3-25-01-613-PD-02 | JB-612 | ACTIVE
48 | 2 | 15 | C4S02,15 | C4S02-X1 | 1756-IB32-15 | DI | 24 VDC energized | XV-61303 | 0 | XV-61303_DI_1 | 3-25-01-613-PD-02 | JB-612 | ACTIVE
49 | 2 | 16 | C4S02,16 | C4S02-X2 | 1756-IB32-16 | DI | 24 VDC energized | XV-61303 | 0 | XV-61303_DI_2 | 3-25-01-613-PD-02 | JB-612 | ACTIVE
50 | 2 | 17 | C4S02,17 | C4S02-X2 | 1756-IB32-17 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
51 | 2 | 18 | C4S02,18 | C4S02-X2 | 1756-IB32-18 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
52 | 2 | 19 | C4S02,19 | C4S02-X2 | 1756-IB32-19 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
53 | 2 | 20 | C4S02,20 | C4S02-X2 | 1756-IB32-20 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
54 | 2 | 21 | C4S02,21 | C4S02-X2 | 1756-IB32-21 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
55 | 2 | 22 | C4S02,22 | C4S02-X2 | 1756-IB32-22 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
56 | 2 | 23 | C4S02,23 | C4S02-X2 | 1756-IB32-23 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
57 | 2 | 24 | C4S02,24 | C4S02-X2 | 1756-IB32-24 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
58 | 2 | 25 | C4S02,25 | C4S02-X2 | 1756-IB32-25 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
59 | 2 | 26 | C4S02,26 | C4S02-X2 | 1756-IB32-26 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
60 | 2 | 27 | C4S02,27 | C4S02-X2 | 1756-IB32-27 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
61 | 2 | 28 | C4S02,28 | C4S02-X2 | 1756-IB32-28 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
62 | 2 | 29 | C4S02,29 | C4S02-X2 | 1756-IB32-29 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
63 | 2 | 30 | C4S02,30 | C4S02-X2 | 1756-IB32-30 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
64 | 2 | 31 | C4S02,31 | C4S02-X2 | 1756-IB32-31 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | JB-612 | SPARE
65 | 3 | 0 | C4S03,00 | C4S03-X1 | 1756-IB32-0 | DI | Dry Contact | ISV-61303 | 0 | ISV-61303_DI_1 | 3-25-01-613-PD-03 | IS-JB-612 | ACTIVE
66 | 3 | 1 | C4S03,01 | C4S03-X1 | 1756-IB32-1 | DI | Dry Contact | ISV-61304 | 0 | ISV-61304_DI_1 | 3-25-01-613-PD-05 | IS-JB-612 | ACTIVE
67 | 3 | 2 | C4S03,02 | C4S03-X1 | 1756-IB32-2 | DI | Dry Contact | LSH-61304 | 0 | LSH-61304_DI_1 | 3-25-01-613-PD-03 | IS-JB-612 | ACTIVE
68 | 3 | 3 | C4S03,03 | C4S03-X1 | 1756-IB32-3 | DI | Dry Contact | LSH-61305 | 0 | LSH-61305_DI_1 | 3-25-01-613-PD-05 | IS-JB-612 | ACTIVE
69 | 3 | 4 | C4S03,04 | C4S03-X1 | 1756-IB32-4 | DI | Dry Contact | LSH-61307 | 0 | LSH-61307_DI_1 | 3-25-01-613-PD-01 | IS-JB-612 | ACTIVE
70 | 3 | 5 | C4S03,05 | C4S03-X1 | 1756-IB32-5 | DI | Dry Contact | LSH-61312 | 0 | LSH-61312_DI_1 | 3-25-01-613-PD-05 | IS-JB-612 | ACTIVE
71 | 3 | 6 | C4S03,06 | C4S03-X1 | 1756-IB32-6 | DI | Dry Contact | PSE-61302 | 0 | PSE-61302_DI_1 | 3-25-01-613-PD-03 | IS-JB-612 | ACTIVE
72 | 3 | 7 | C4S03,07 | C4S03-X1 | 1756-IB32-7 | DI | Dry Contact | PSE-61303 | 0 | PSE-61303_DI_1 | 3-25-01-613-PD-05 | IS-JB-612 | ACTIVE
73 | 3 | 9 | C4S03,09 | C4S03-X1 | 1756-IB32-9 | DI | - | RV-61301 | - | RV-61301_DI_1 | - | IS-JB-612 | ACTIVE
74 | 3 | 10 | C4S03,10 | C4S03-X1 | 1756-IB32-10 | DI | - | RV-61304 | - | RV-61304_DI_1 | - | IS-JB-612 | ACTIVE
75 | 3 | 11 | C4S03,11 | C4S03-X1 | 1756-IB32-11 | DI | - | RV-61305 | - | RV-61305_DI_1 | - | IS-JB-612 | ACTIVE
76 | 3 | 12 | C4S03,12 | C4S03-X1 | 1756-IB32-12 | DI | - | SC-61301 | - | SC-61301_DI_1 | - | IS-JB-612 | ACTIVE
77 | 3 | 13 | C4S03,13 | C4S03-X1 | 1756-IB32-13 | DI | - | SC-61302 | - | SC-61302_DI_1 | - | IS-JB-612 | ACTIVE
78 | 3 | 14 | C4S03,14 | C4S03-X1 | 1756-IB32-14 | DI | Dry Contact | ZS-61312 | 0 | ZS-61312_DI_1 | 3-25-01-613-PD-01 | IS-JB-612 | ACTIVE
79 | 3 | 15 | C4S03,15 | C4S03-X1 | 1756-IB32-15 | DI | Dry Contact | ZS-61313 | 0 | ZS-61313_DI_1 | 3-25-01-613-PD-01 | IS-JB-612 | ACTIVE
80 | 3 | 16 | C4S03,16 | C4S03-X2 | 1756-IB32-16 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
81 | 3 | 17 | C4S03,17 | C4S03-X2 | 1756-IB32-17 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
82 | 3 | 18 | C4S03,18 | C4S03-X2 | 1756-IB32-18 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
83 | 3 | 19 | C4S03,19 | C4S03-X2 | 1756-IB32-19 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
84 | 3 | 20 | C4S03,20 | C4S03-X2 | 1756-IB32-20 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
85 | 3 | 21 | C4S03,21 | C4S03-X2 | 1756-IB32-21 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
86 | 3 | 22 | C4S03,22 | C4S03-X2 | 1756-IB32-22 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
87 | 3 | 23 | C4S03,23 | C4S03-X2 | 1756-IB32-23 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
88 | 3 | 24 | C4S03,24 | C4S03-X2 | 1756-IB32-24 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
89 | 3 | 25 | C4S03,25 | C4S03-X2 | 1756-IB32-25 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
90 | 3 | 26 | C4S03,26 | C4S03-X2 | 1756-IB32-26 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
91 | 3 | 27 | C4S03,27 | C4S03-X2 | 1756-IB32-27 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
92 | 3 | 28 | C4S03,28 | C4S03-X2 | 1756-IB32-28 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
93 | 3 | 29 | C4S03,29 | C4S03-X2 | 1756-IB32-29 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
94 | 3 | 30 | C4S03,30 | C4S03-X2 | 1756-IB32-30 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
95 | 3 | 31 | C4S03,31 | C4S03-X2 | 1756-IB32-31 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | IS-JB-612 | SPARE
96 | 4 | 0 | C4S04,00 | C4S04-X1 | 1756-OB32-0 | DO | 24 VDC energized | SV-60220 | 0 | SV-60220_DO_1 | 3-25-01-602-PD-04 | JB-606 | ACTIVE
97 | 4 | 1 | C4S04,01 | C4S04-X1 | 1756-OB32-1 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-606 | SPARE
98 | 4 | 2 | C4S04,02 | C4S04-X1 | 1756-OB32-2 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-606 | SPARE
99 | 4 | 3 | C4S04,03 | C4S04-X1 | 1756-OB32-3 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-606 | SPARE
100 | 4 | 4 | C4S04,04 | C4S04-X1 | 1756-OB32-4 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-606 | SPARE
101 | 4 | 5 | C4S04,05 | C4S04-X1 | 1756-OB32-5 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-606 | SPARE
102 | 4 | 6 | C4S04,06 | C4S04-X1 | 1756-OB32-6 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-606 | SPARE
103 | 4 | 7 | C4S04,07 | C4S04-X1 | 1756-OB32-7 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-606 | SPARE
104 | 4 | 8 | C4S04,08 | C4S04-X1 | 1756-OB32-8 | DO | 4 - 20 mA | XA-60201 | 0 | XA-60201_DO_1 | 3-25-01-602-PD-03 | IS-JB-608 | ACTIVE
105 | 4 | 9 | C4S04,09 | C4S04-X1 | 1756-OB32-9 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | IS-JB-608 | SPARE
106 | 4 | 10 | C4S04,10 | C4S04-X1 | 1756-OB32-10 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | IS-JB-608 | SPARE
107 | 4 | 11 | C4S04,11 | C4S04-X1 | 1756-OB32-11 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | IS-JB-608 | SPARE
108 | 4 | 12 | C4S04,12 | C4S04-X1 | 1756-OB32-12 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | IS-JB-608 | SPARE
109 | 4 | 13 | C4S04,13 | C4S04-X1 | 1756-OB32-13 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | IS-JB-608 | SPARE
110 | 4 | 14 | C4S04,14 | C4S04-X1 | 1756-OB32-14 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | IS-JB-608 | SPARE
111 | 4 | 15 | C4S04,15 | C4S04-X1 | 1756-OB32-15 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | IS-JB-608 | SPARE
112 | 4 | 16 | C4S04,16 | C4S04-X2 | 1756-OB32-16 | DO | - | PVM-61301 | - | PVM-61301_DO_1 | 325-01-613-PD-03 | JB-612 | ACTIVE
113 | 4 | 17 | C4S04,17 | C4S04-X2 | 1756-OB32-17 | DO | - | PVM-61301 | - | PVM-61301_DO_2 | 325-01-613-PD-03 | JB-612 | ACTIVE
114 | 4 | 18 | C4S04,18 | C4S04-X2 | 1756-OB32-18 | DO | - | SV-61307 | - | SV-61307_DO_1 | 3-25-01-613-PD-01 | JB-612 | ACTIVE
115 | 4 | 19 | C4S04,19 | C4S04-X2 | 1756-OB32-19 | DO | 24 VDC energized | SV-61308 | 0 | SV-61308_DO_1 | 325-01-613-PD-03 | JB-612 | ACTIVE
116 | 4 | 20 | C4S04,20 | C4S04-X2 | 1756-OB32-20 | DO | 24 VDC energized | SV-61309 | 0 | SV-61309_DO_1 | 3-25-01-613-PD-03 | JB-612 | ACTIVE
117 | 4 | 21 | C4S04,21 | C4S04-X2 | 1756-OB32-21 | DO | 24 VDC energized | SV-61310 | 0 | SV-61310_DO_1 | 325-01-613-PD-05 | JB-612 | ACTIVE
118 | 4 | 22 | C4S04,22 | C4S04-X2 | 1756-OB32-22 | DO | 24 VDC energized | SV-61311 | 0 | SV-61311_DO_1 | 3-25-01-613-PD-05 | JB-612 | ACTIVE
119 | 4 | 23 | C4S04,23 | C4S04-X2 | 1756-OB32-23 | DO | 24 VDC energized | XS-61301A | 0 | XS-61301A_DO_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
120 | 4 | 24 | C4S04,24 | C4S04-X2 | 1756-OB32-24 | DO | 24 VDC energized | XS-61301B | 0 | XS-61301B_DO_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
121 | 4 | 25 | C4S04,25 | C4S04-X2 | 1756-OB32-25 | DO | 24 VDC energized | XS-61301C | 0 | XS-61301C_DO_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
122 | 4 | 26 | C4S04,26 | C4S04-X2 | 1756-OB32-26 | DO | 24 VDC energized | XS-61301D | 0 | XS-61301D_DO_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
123 | 4 | 27 | C4S04,27 | C4S04-X2 | 1756-OB32-27 | DO | 24 VDC energized | XS-61301E | 0 | XS-61301E_DO_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
124 | 4 | 28 | C4S04,28 | C4S04-X2 | 1756-OB32-28 | DO | 24 VDC energized | XS-61301F | 0 | XS-61301F_DO_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
125 | 4 | 29 | C4S04,29 | C4S04-X2 | 1756-OB32-29 | DO | 24 VDC energized | XV-61302 | 0 | XV-61302_DO_1 | 3-25-01-613-PD-02 | JB-612 | ACTIVE
126 | 4 | 30 | C4S04,30 | C4S04-X2 | 1756-OB32-30 | DO | 24 VDC energized | XV-61303 | 0 | XV-61303_DO_1 | 3-25-01-613-PD-02 | JB-612 | ACTIVE
127 | 4 | 31 | C4S04,31 | C4S04-X2 | 1756-OB32-31 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | JB-612 | SPARE
128 | 5 | 0 | C4S05,00 | C4S05-X1 | 1756-IF16-0 | AI | 4 - 20 mA | DPT-60201 | Differential Pressure Transmitte | DPT-60201_AI_1 | 3-25-01-602-PD-09 | JB-606 | ACTIVE
129 | 5 | 1 | C4S05,01 | C4S05-X1 | 1756-IF16-1 | AI | 4 - 20 mA | FT-60203 | 0 | FT-60203_AI_1 | 3-25-01-602-PD-09 | JB-606 | ACTIVE
130 | 5 | 2 | C4S05,02 | C4S05-X1 | 1756-IF16-2 | AI | 4 - 20 mA | TT-60245 | 0 | TT-60245_AI_1 | 3-25-01-602-PD-05 | JB-608 | ACTIVE
131 | 5 | 3 | C4S05,03 | C4S05-X1 | 1756-IF16-3 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-608 | SPARE
132 | 5 | 4 | C4S05,04 | C4S05-X1 | 1756-IF16-4 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-608 | SPARE
133 | 5 | 5 | C4S05,05 | C4S05-X1 | 1756-IF16-5 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-608 | SPARE
134 | 5 | 6 | C4S05,06 | C4S05-X1 | 1756-IF16-6 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-608 | SPARE
135 | 5 | 6 | C4S05,06 | C4S05-X1 | 1756-IF16-6 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-608 | SPARE
136 | 5 | 7 | C4S05,07 | C4S05-X1 | 1756-IF16-7 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-608 | SPARE
137 | 5 | 7 | C4S05,07 | C4S05-X1 | 1756-IF16-7 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-608 | SPARE
138 | 5 | 8 | C4S05,08 | C4S05-X1 | 1756-IF16-8 | AI | 4 - 20 mA | PT-61302 | Pressure Transmitter | PT-61302_AI_1 | 3-25-01-613-PD-03 | JB-612 | ACTIVE
139 | 5 | 9 | C4S05,09 | C4S05-X1 | 1756-IF16-9 | AI | 4 - 20 mA | PT-61309 | Pressure Transmitter | PT-61309_AI_1 | 3-25-01-613-PD-04 | JB-612 | ACTIVE
140 | 5 | 10 | C4S05,10 | C4S05-X1 | 1756-IF16-10 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-612 | SPARE
141 | 5 | 11 | C4S05,11 | C4S05-X1 | 1756-IF16-11 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-612 | SPARE
142 | 5 | 12 | C4S05,12 | C4S05-X1 | 1756-IF16-12 | AI | 4 - 20 mA | PT-61302 | Pressure Transmitter | PT-61302_AI_1 | 3-25-01-613-PD-03 | JB-612 | ACTIVE
143 | 5 | 13 | C4S05,13 | C4S05-X1 | 1756-IF16-13 | AI | 4 - 20 mA | PT-61309 | Pressure Transmitter | PT-61309_AI_1 | 3-25-01-613-PD-04 | JB-612 | ACTIVE
144 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-612 | SPARE
145 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-612 | SPARE
146 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-612 | SPARE
147 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-612 | SPARE
148 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-612 | SPARE
149 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-612 | SPARE
150 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-612 | SPARE
151 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-612 | SPARE
152 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | IS-JB-612 | SPARE
153 | 5 | 15 | C4S05,15 | C4S05-X1 | 1756-IF16-15 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | JB-612 | SPARE
154 | 6 | 0 | C4S06,00 | C4S06-X1 | 1756-IF16-0 | AI | 4 - 20 mA | PT-60220 | Pressure Transmitter | PT-60220_AI_1 | 3-25-01-602-PD-04 | IS-JB-608 | ACTIVE
155 | 6 | 1 | C4S06,01 | C4S06-X1 | 1756-IF16-1 | AI | 4 - 20 mA | TT-60220 | 0 | TT-60220_AI_1 | 3-25-01-602-PD-04 | IS-JB-608 | ACTIVE
156 | 6 | 2 | C4S06,02 | C4S06-X1 | 1756-IF16-2 | AI | 4 - 20 mA | TT-60221 | 0 | TT-60221_AI_1 | 3-25-01-602-PD-04 | IS-JB-608 | ACTIVE
157 | 6 | 3 | C4S06,03 | C4S06-X1 | 1756-IF16-3 | AI | 4 - 20 mA | TT-60222 | 0 | TT-60222_AI_1 | 3-25-01-602-PD-04 | IS-JB-608 | ACTIVE
158 | 6 | 4 | C4S06,04 | C4S06-X1 | 1756-IF16-4 | AI | 4 - 20 mA | TT-60223 | 0 | TT-60223_AI_1 | 3-25-01-602-PD-04 | IS-JB-608 | ACTIVE
159 | 6 | 5 | C4S06,05 | C4S06-X1 | 1756-IF16-5 | AI | 4 - 20 mA | XT-60201 | 0 | XT-60201_AI_1 | 3-25-01-602-PD-03 | IS-JB-608 | ACTIVE
160 | 6 | 6 | C4S06,06 | C4S06-X1 | 1756-IF16-6 | AI | 4 - 20 mA | DPT-61310 | Differential Pressure Transmitte | DPT-61310_AI_1 | 3-25-01-613-PD-03 | IS-JB-612 | ACTIVE
161 | 6 | 7 | C4S06,07 | C4S06-X1 | 1756-IF16-7 | AI | - | DPT-61312 | - | DPT-61312_AI_1 | 3-25-01-613-PD-05 | IS-JB-612 | ACTIVE

## Chassis_C5
CHASSIS C5 ¦ PANEL / ENCLOSURE: =CA1+MCP-M5 ¦ PROJECT JET COOKER
Item | Slot | Point | Channel Code | Terminal | Card Model | I/O Type | Signal | Instrument Tag | Instrument Description | PLC Tag | P&ID No. | Destination JB | Status
1 | 1 | 0 | C5S01,00 | C5S01-X1 | 1756-IB32-0 | DI | - | FS-20201 | - | FS-20201_DI_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
2 | 1 | 1 | C5S01,01 | C5S01-X1 | 1756-IB32-1 | DI | 4 - 20 mA,Pulse | FT-913201 | 0 | FT-913201_DI_1 | 3-25-01-913-PD-02 | RIO-200 | ACTIVE
3 | 1 | 2 | C5S01,02 | C5S01-X1 | 1756-IB32-2 | DI | 4 - 20 mA,Pulse | FT-936201 | 0 | FT-936201_DI_1 | 3-25-01-930-PD-08 | RIO-200 | ACTIVE
4 | 1 | 3 | C5S01,03 | C5S01-X1 | 1756-IB32-3 | DI | 4 - 20 mA,Pulse | FT-936202 | 0 | FT-936202_DI_1 | 3-25-01-930-PD-07 | RIO-200 | ACTIVE
5 | 1 | 4 | C5S01,04 | C5S01-X1 | 1756-IB32-4 | DI | Dry Contact | LSL-814201 | 0 | LSL-814201_DI_1 | 3-25-01-814-PD-01 | RIO-200 | ACTIVE
6 | 1 | 5 | C5S01,05 | C5S01-X1 | 1756-IB32-5 | DI | - | PK-913201 | - | PK-913201_DI_1 | - | RIO-200 | ACTIVE
7 | 1 | 6 | C5S01,06 | C5S01-X1 | 1756-IB32-6 | DI | - | PK-913202 | - | PK-913202_DI_1 | - | RIO-200 | ACTIVE
8 | 1 | 7 | C5S01,07 | C5S01-X1 | 1756-IB32-7 | DI | Dry Contact | HV-20204 | Manual Valve With Position Switch | HV-20204_DI_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
9 | 1 | 8 | C5S01,08 | C5S01-X1 | 1756-IB32-8 | DI | Dry Contact | HV-20205 | Manual Valve With Position Switch | HV-20205_DI_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
10 | 1 | 9 | C5S01,09 | C5S01-X1 | 1756-IB32-9 | DI | Dry Contact | HV-20206 | Manual Valve With Position Switch | HV-20206_DI_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
11 | 1 | 10 | C5S01,10 | C5S01-X1 | 1756-IB32-10 | DI | Dry Contact | HV-20207 | Manual Valve With Position Switch | HV-20207_DI_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
12 | 1 | 11 | C5S01,11 | C5S01-X1 | 1756-IB32-11 | DI | Dry Contact | HV-20208 | Manual Valve With Position Switch | HV-20208_DI_1 | 3-25-01-202-PD-02 | RIO-200 | ACTIVE
13 | 1 | 12 | C5S01,12 | C5S01-X1 | 1756-IB32-12 | DI | Dry Contact | HV-20209 | Manual Valve With Position Switch | HV-20209_DI_1 | 3-25-01-202-PD-02 | RIO-200 | ACTIVE
14 | 1 | 13 | C5S01,13 | C5S01-X1 | 1756-IB32-13 | DI | Dry Contact | HV-20210 | Manual Valve With Position Switch | HV-20210_DI_1 | 3-25-01-202-PD-02 | RIO-200 | ACTIVE
15 | 1 | 14 | C5S01,14 | C5S01-X1 | 1756-IB32-14 | DI | Dry Contact | XA-80305A | 0 | XA-80305A_DI_1 | 325-01-803-PD-02 | RIO-200 | ACTIVE
16 | 1 | 15 | C5S01,15 | C5S01-X1 | 1756-IB32-15 | DI | Dry Contact | XA-80305B | 0 | XA-80305B_DI_1 | 325-01-803-PD-02 | RIO-200 | ACTIVE
17 | 1 | 16 | C5S01,16 | C5S01-X2 | 1756-IB32-16 | DI | Dry Contact | XA-80305C | 0 | XA-80305C_DI_1 | 325-01-803-PD-02 | RIO-200 | ACTIVE
18 | 1 | 17 | C5S01,17 | C5S01-X2 | 1756-IB32-17 | DI | Dry Contact | XA-80305D | 0 | XA-80305D_DI_1 | 325-01-803-PD-02 | RIO-200 | ACTIVE
19 | 1 | 18 | C5S01,18 | C5S01-X2 | 1756-IB32-18 | DI | Dry Contact | XA-80305E | 0 | XA-80305E_DI_1 | 325-01-803-PD-02 | RIO-200 | ACTIVE
20 | 1 | 19 | C5S01,19 | C5S01-X2 | 1756-IB32-19 | DI | Dry Contact | XA-80305F | 0 | XA-80305F_DI_1 | 325-01-803-PD-02 | RIO-200 | ACTIVE
21 | 1 | 20 | C5S01,20 | C5S01-X2 | 1756-IB32-20 | DI | Dry Contact | XA-80306A | 0 | XA-80306A_DI_1 | 325-01-803-PD-02 | RIO-200 | ACTIVE
22 | 1 | 21 | C5S01,21 | C5S01-X2 | 1756-IB32-21 | DI | Dry Contact | XA-80306B | 0 | XA-80306B_DI_1 | 325-01-803-PD-02 | RIO-200 | ACTIVE
23 | 1 | 22 | C5S01,22 | C5S01-X2 | 1756-IB32-22 | DI | Dry Contact | XA-80306C | 0 | XA-80306C_DI_1 | 325-01-803-PD-02 | RIO-200 | ACTIVE
24 | 1 | 23 | C5S01,23 | C5S01-X2 | 1756-IB32-23 | DI | Dry Contact | XA-80306D | 0 | XA-80306D_DI_1 | 325-01-803-PD-02 | RIO-200 | ACTIVE
25 | 1 | 24 | C5S01,24 | C5S01-X2 | 1756-IB32-24 | DI | Dry Contact | XA-80306E | 0 | XA-80306E_DI_1 | 325-01-803-PD-02 | RIO-200 | ACTIVE
26 | 1 | 25 | C5S01,25 | C5S01-X2 | 1756-IB32-25 | DI | Dry Contact | XA-80306F | 0 | XA-80306F_DI_1 | 325-01-803-PD-02 | RIO-200 | ACTIVE
27 | 1 | 26 | C5S01,26 | C5S01-X2 | 1756-IB32-26 | DI | 24 VDC energized | XV-20201 | 0 | XV-20201_DI_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
28 | 1 | 27 | C5S01,27 | C5S01-X2 | 1756-IB32-27 | DI | 24 VDC energized | XV-20201 | 0 | XV-20201_DI_2 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
29 | 1 | 28 | C5S01,28 | C5S01-X2 | 1756-IB32-28 | DI | 24 VDC energized | XV-20202 | 0 | XV-20202_DI_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
30 | 1 | 29 | C5S01,29 | C5S01-X2 | 1756-IB32-29 | DI | 24 VDC energized | XV-20202 | 0 | XV-20202_DI_2 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
31 | 1 | 30 | C5S01,30 | C5S01-X2 | 1756-IB32-30 | DI | 24 VDC energized | XV-20203 | 0 | XV-20203_DI_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
32 | 1 | 31 | C5S01,31 | C5S01-X2 | 1756-IB32-31 | DI | 24 VDC energized | XV-20203 | 0 | XV-20203_DI_2 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
33 | 2 | 0 | C5S02,00 | C5S02-X1 | 1756-IB32-0 | DI | 24 VDC energized | XV-20211 | 0 | XV-20211_DI_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
34 | 2 | 1 | C5S02,01 | C5S02-X1 | 1756-IB32-1 | DI | 24 VDC energized | XV-20211 | 0 | XV-20211_DI_2 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
35 | 2 | 2 | C5S02,02 | C5S02-X1 | 1756-IB32-2 | DI | 24 VDC energized | XV-20212 | 0 | XV-20212_DI_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
36 | 2 | 3 | C5S02,03 | C5S02-X1 | 1756-IB32-3 | DI | 24 VDC energized | XV-20212 | 0 | XV-20212_DI_2 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
37 | 2 | 4 | C5S02,04 | C5S02-X1 | 1756-IB32-4 | DI | 24 VDC energized | XV-20213 | 0 | XV-20213_DI_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
38 | 2 | 5 | C5S02,05 | C5S02-X1 | 1756-IB32-5 | DI | 24 VDC energized | XV-20213 | 0 | XV-20213_DI_2 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
39 | 2 | 6 | C5S02,06 | C5S02-X1 | 1756-IB32-6 | DI | 24 VDC energized | XV-913201 | 0 | XV-913201_DI_1 | 3-25-01-913-PD-02 | RIO-200 | ACTIVE
40 | 2 | 7 | C5S02,07 | C5S02-X1 | 1756-IB32-7 | DI | 24 VDC energized | XV-913201 | 0 | XV-913201_DI_1 | 3-25-01-913-PD-02 | RIO-200 | ACTIVE
41 | 2 | 8 | C5S02,08 | C5S02-X1 | 1756-IB32-8 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
42 | 2 | 9 | C5S02,09 | C5S02-X1 | 1756-IB32-9 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
43 | 2 | 10 | C5S02,10 | C5S02-X1 | 1756-IB32-10 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
44 | 2 | 11 | C5S02,11 | C5S02-X1 | 1756-IB32-11 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
45 | 2 | 12 | C5S02,12 | C5S02-X1 | 1756-IB32-12 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
46 | 2 | 13 | C5S02,13 | C5S02-X1 | 1756-IB32-13 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
47 | 2 | 14 | C5S02,14 | C5S02-X1 | 1756-IB32-14 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
48 | 2 | 15 | C5S02,15 | C5S02-X1 | 1756-IB32-15 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
49 | 2 | 16 | C5S02,16 | C5S02-X2 | 1756-IB32-16 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
50 | 2 | 17 | C5S02,17 | C5S02-X2 | 1756-IB32-17 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
51 | 2 | 18 | C5S02,18 | C5S02-X2 | 1756-IB32-18 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
52 | 2 | 19 | C5S02,19 | C5S02-X2 | 1756-IB32-19 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
53 | 2 | 20 | C5S02,20 | C5S02-X2 | 1756-IB32-20 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
54 | 2 | 21 | C5S02,21 | C5S02-X2 | 1756-IB32-21 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
55 | 2 | 22 | C5S02,22 | C5S02-X2 | 1756-IB32-22 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
56 | 2 | 23 | C5S02,23 | C5S02-X2 | 1756-IB32-23 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
57 | 2 | 24 | C5S02,24 | C5S02-X2 | 1756-IB32-24 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
58 | 2 | 25 | C5S02,25 | C5S02-X2 | 1756-IB32-25 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
59 | 2 | 26 | C5S02,26 | C5S02-X2 | 1756-IB32-26 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
60 | 2 | 27 | C5S02,27 | C5S02-X2 | 1756-IB32-27 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
61 | 2 | 28 | C5S02,28 | C5S02-X2 | 1756-IB32-28 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
62 | 2 | 29 | C5S02,29 | C5S02-X2 | 1756-IB32-29 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
63 | 2 | 30 | C5S02,30 | C5S02-X2 | 1756-IB32-30 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
64 | 2 | 31 | C5S02,31 | C5S02-X2 | 1756-IB32-31 | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | RIO-200 | SPARE
65 | 3 | 0 | C5S03,00 | C5S03-X1 | 1756-OB32-0 | DO | 4 - 20 mA | XA-92201 | 0 | XA-92201_DO_1 | 3-25-01-922-PD-03 | RIO-200 | ACTIVE
66 | 3 | 1 | C5S03,01 | C5S03-X1 | 1756-OB32-1 | DO | 24 VDC energized | XV-20201 | 0 | XV-20201_DO_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
67 | 3 | 2 | C5S03,02 | C5S03-X1 | 1756-OB32-2 | DO | 24 VDC energized | XV-20202 | 0 | XV-20202_DO_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
68 | 3 | 3 | C5S03,03 | C5S03-X1 | 1756-OB32-3 | DO | 24 VDC energized | XV-20203 | 0 | XV-20203_DO_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
69 | 3 | 4 | C5S03,04 | C5S03-X1 | 1756-OB32-4 | DO | 24 VDC energized | XV-20211 | 0 | XV-20211_DO_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
70 | 3 | 5 | C5S03,05 | C5S03-X1 | 1756-OB32-5 | DO | 24 VDC energized | XV-20212 | 0 | XV-20212_DO_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
71 | 3 | 6 | C5S03,06 | C5S03-X1 | 1756-OB32-6 | DO | 24 VDC energized | XV-20213 | 0 | XV-20213_DO_1 | 3-25-01-202-PD-01 | RIO-200 | ACTIVE
72 | 3 | 7 | C5S03,07 | C5S03-X1 | 1756-OB32-7 | DO | 24 VDC energized | XV-913201 | 0 | XV-913201_DO_1 | 3-25-01-913-PD-02 | RIO-200 | ACTIVE
73 | 3 | 8 | C5S03,08 | C5S03-X1 | 1756-OB32-8 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
74 | 3 | 9 | C5S03,09 | C5S03-X1 | 1756-OB32-9 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
75 | 3 | 10 | C5S03,10 | C5S03-X1 | 1756-OB32-10 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
76 | 3 | 11 | C5S03,11 | C5S03-X1 | 1756-OB32-11 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
77 | 3 | 12 | C5S03,12 | C5S03-X1 | 1756-OB32-12 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
78 | 3 | 13 | C5S03,13 | C5S03-X1 | 1756-OB32-13 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
79 | 3 | 14 | C5S03,14 | C5S03-X1 | 1756-OB32-14 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
80 | 3 | 15 | C5S03,15 | C5S03-X1 | 1756-OB32-15 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
81 | 3 | 16 | C5S03,16 | C5S03-X2 | 1756-OB32-16 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
82 | 3 | 17 | C5S03,17 | C5S03-X2 | 1756-OB32-17 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
83 | 3 | 18 | C5S03,18 | C5S03-X2 | 1756-OB32-18 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
84 | 3 | 19 | C5S03,19 | C5S03-X2 | 1756-OB32-19 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
85 | 3 | 20 | C5S03,20 | C5S03-X2 | 1756-OB32-20 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
86 | 3 | 21 | C5S03,21 | C5S03-X2 | 1756-OB32-21 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
87 | 3 | 22 | C5S03,22 | C5S03-X2 | 1756-OB32-22 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
88 | 3 | 23 | C5S03,23 | C5S03-X2 | 1756-OB32-23 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
89 | 3 | 24 | C5S03,24 | C5S03-X2 | 1756-OB32-24 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
90 | 3 | 25 | C5S03,25 | C5S03-X2 | 1756-OB32-25 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
91 | 3 | 26 | C5S03,26 | C5S03-X2 | 1756-OB32-26 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
92 | 3 | 27 | C5S03,27 | C5S03-X2 | 1756-OB32-27 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
93 | 3 | 28 | C5S03,28 | C5S03-X2 | 1756-OB32-28 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
94 | 3 | 29 | C5S03,29 | C5S03-X2 | 1756-OB32-29 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
95 | 3 | 30 | C5S03,30 | C5S03-X2 | 1756-OB32-30 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
96 | 3 | 31 | C5S03,31 | C5S03-X2 | 1756-OB32-31 | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | RIO-200 | SPARE
97 | 4 | 0 | C5S04,00 | C5S04-X1 | 1756-IF16-0 | AI | - | EXT-BIILER | - | EXT-BIILER_AI_1 | External Remote Setpoint | RIO-200 | ACTIVE
98 | 4 | 1 | C5S04,01 | C5S04-X1 | 1756-IF16-1 | AI | 4 - 20 mA,Pulse | FT-913201 | 0 | FT-913201_AI_1 | 3-25-01-913-PD-02 | RIO-200 | ACTIVE
99 | 4 | 2 | C5S04,02 | C5S04-X1 | 1756-IF16-2 | AI | 4 - 20 mA,Pulse | FT-913201 | 0 | FT-913201_AI_2 | 3-25-01-913-PD-02 | RIO-200 | ACTIVE
100 | 4 | 3 | C5S04,03 | C5S04-X1 | 1756-IF16-3 | AI | 4 - 20 mA,Pulse | FT-936201 | 0 | FT-936201_AI_1 | 3-25-01-930-PD-08 | RIO-200 | ACTIVE
101 | 4 | 4 | C5S04,04 | C5S04-X1 | 1756-IF16-4 | AI | 4 - 20 mA,Pulse | FT-936202 | 0 | FT-936202_AI_1 | 3-25-01-930-PD-07 | RIO-200 | ACTIVE
102 | 4 | 5 | C5S04,05 | C5S04-X1 | 1756-IF16-5 | AI | 4 - 20 mA | LT-913201 | Level Transmitter | LT-913201_AI_1 | 3-25-01-913-PD-01 | RIO-200 | ACTIVE
103 | 4 | 6 | C5S04,06 | C5S04-X1 | 1756-IF16-6 | AI | 4 - 20 mA | PT-913201 | Pressure Transmitter | PT-913201_AI_1 | 3-25-01-913-PD-02 | RIO-200 | ACTIVE
104 | 4 | 7 | C5S04,07 | C5S04-X1 | 1756-IF16-7 | AI | 4 - 20 mA | XT-92201 | 0 | XT-92201_AI_1 | 3-25-01-922-PD-03 | RIO-200 | ACTIVE
105 | 4 | 8 | C5S04,08 | C5S04-X1 | 1756-IF16-8 | AI | 24 VDC energized | XV-913201 | 0 | XV-913201_AI_1 | 3-25-01-913-PD-02 | RIO-200 | ACTIVE
106 | 4 | 9 | C5S04,09 | C5S04-X1 | 1756-IF16-9 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | 3-25-01-913-PD-02 | RIO-200 | SPARE
107 | 4 | 10 | C5S04,10 | C5S04-X1 | 1756-IF16-10 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | 3-25-01-913-PD-02 | RIO-200 | SPARE
108 | 4 | 11 | C5S04,11 | C5S04-X1 | 1756-IF16-11 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | 3-25-01-913-PD-02 | RIO-200 | SPARE
109 | 4 | 12 | C5S04,12 | C5S04-X1 | 1756-IF16-12 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | 3-25-01-913-PD-02 | RIO-200 | SPARE
110 | 4 | 13 | C5S04,13 | C5S04-X1 | 1756-IF16-13 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | 3-25-01-913-PD-02 | RIO-200 | SPARE
111 | 4 | 14 | C5S04,14 | C5S04-X1 | 1756-IF16-14 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | RIO-200 | SPARE
112 | 4 | 15 | C5S04,15 | C5S04-X1 | 1756-IF16-15 | AI | - | Spare | Spare I/O Point | Spare_AI_0 | - | RIO-200 | SPARE

## Chassis_C6
CHASSIS C6 ¦ PANEL / ENCLOSURE: MCC ¦ PROJECT JET COOKER
Item | Slot | Point | Channel Code | Terminal | Card Model | I/O Type | Signal | Instrument Tag | Instrument Description | PLC Tag | P&ID No. | Destination JB | Status
1 | 5 | 0 | C6S05,00 | C6S05- | - | DO | - | PCM-2030 | - | PCM-2030_DO_1 | 3-25-01-202-PD-01 | MCC | ACTIVE
2 | 5 | 1 | C6S05,01 | C6S05- | - | DO | - | PCM-2030 | - | PCM-2030_DO_2 | 3-25-01-202-PD-01 | MCC | ACTIVE
3 | 5 | 2 | C6S05,02 | C6S05- | - | DO | 24 VDC energized | PCM-2031 | 0 | PCM-2031_DO_1 | 3-25-01-202-PD-01 | MCC | ACTIVE
4 | 5 | 3 | C6S05,03 | C6S05- | - | DO | 24 VDC energized | PCM-2031 | 0 | PCM-2031_DO_2 | 3-25-01-202-PD-01 | MCC | ACTIVE
5 | 5 | 4 | C6S05,04 | C6S05- | - | DO | 24 VDC energized | PCY-814201 | PUMP | PCY-814201_DO_1 | 3-25-01-810-PD-01 | MCC | ACTIVE
6 | 5 | 5 | C6S05,05 | C6S05- | - | DO | 24 VDC energized | PCY-814202 | PUMP | PCY-814202_DO_1 | 3-25-01-810-PD-01 | MCC | ACTIVE
7 | 5 | 6 | C6S05,06 | C6S05- | - | DO | 24 VDC energized | XS-80305 | 0 | XS-80305_DO_1 | 325-01-803-PD-02 | MCC | ACTIVE
8 | 5 | 7 | C6S05,07 | C6S05- | - | DO | 24 VDC energized | XS-80306 | Pressure Transmitter | XS-80306_DO_1 | 325-01-803-PD-02 | MCC | ACTIVE
9 | 6 | 0 | C6S06,00 | C6S06- | - | DI | - | PCM-2030 | - | PCM-2030_DI_1 | 3-25-01-202-PD-01 | MCC | ACTIVE
10 | 6 | 1 | C6S06,01 | C6S06- | - | DI | - | PCM-2030 | - | PCM-2030_DI_2 | 3-25-01-202-PD-01 | MCC | ACTIVE
11 | 6 | 2 | C6S06,02 | C6S06- | - | DI | 24 VDC energized | PCM-2031 | 0 | PCM-2031_DI_1 | 3-25-01-202-PD-01 | MCC | ACTIVE
12 | 6 | 3 | C6S06,03 | C6S06- | - | DI | 24 VDC energized | PCM-2031 | 0 | PCM-2031_DI_2 | 3-25-01-202-PD-01 | MCC | ACTIVE
13 | 6 | 4 | C6S06,04 | C6S06- | - | DI | 24 VDC energized | PCY-814201 | PUMP | PCY-814201_DI_1 | 3-25-01-810-PD-01 | MCC | ACTIVE
14 | 6 | 5 | C6S06,05 | C6S06- | - | DI | 24 VDC energized | PCY-814201 | PUMP | PCY-814201_DI_2 | 3-25-01-810-PD-01 | MCC | ACTIVE
15 | 6 | 6 | C6S06,06 | C6S06- | - | DI | 24 VDC energized | PCY-814201 | PUMP | PCY-814201_DI_3 | 3-25-01-810-PD-01 | MCC | ACTIVE
16 | 6 | 7 | C6S06,07 | C6S06- | - | DI | 24 VDC energized | PCY-814202 | PUMP | PCY-814202_DI_1 | 3-25-01-810-PD-01 | MCC | ACTIVE
17 | 6 | 8 | C6S06,08 | C6S06- | - | DI | 24 VDC energized | PCY-814202 | PUMP | PCY-814202_DI_2 | 3-25-01-810-PD-01 | MCC | ACTIVE
18 | 6 | 9 | C6S06,09 | C6S06- | - | DI | 24 VDC energized | PCY-814202 | PUMP | PCY-814202_DI_3 | 3-25-01-810-PD-01 | MCC | ACTIVE

## Chassis_C7
CHASSIS C7 ¦ PANEL / ENCLOSURE: MCC ¦ PROJECT JET COOKER
Item | Slot | Point | Channel Code | Terminal | Card Model | I/O Type | Signal | Instrument Tag | Instrument Description | PLC Tag | P&ID No. | Destination JB | Status
1 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | ATY-40201 | Tank Agitator | ATY-40201_BUS_1 | 3-25-01-402-PD-01 | MCC | ACTIVE
2 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | ATY-40202 | Tank Agitator | ATY-40202_BUS_1 | 3-25-01-402-PD-01 | MCC | ACTIVE
3 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | ATY-40203 | Tank Agitator | ATY-40203_BUS_1 | 3-25-01-402-PD-02 | MCC | ACTIVE
4 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60206 | 0 | BFY-60206_BUS_1 | 325-01-600-PD-08 | MCC | ACTIVE
5 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60210 | 0 | BFY-60210_BUS_1 | 325-01-600-PD-03 | MCC | ACTIVE
6 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60211 | 0 | BFY-60211_BUS_1 | 325-01-600-PD-03 | MCC | ACTIVE
7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60220 | 0 | BFY-60220_BUS_1 | 325-01-600-PD-04 | MCC | ACTIVE
8 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60240 | 0 | BFY-60240_BUS_1 | 325-01-600-PD-05 | MCC | ACTIVE
9 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-61301 | 0 | BFY-61301_BUS_1 | 325-01-613-PD-01 | MCC | ACTIVE
10 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-61302 | 0 | BFY-61302_BUS_1 | 325-01-613-PD-05 | MCC | ACTIVE
11 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-61303 | 0 | BFY-61303_BUS_1 | 325-01-613-PD-01 | MCC | ACTIVE
12 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | COM-FH-60210B | 0 | COM-FH-60210B_BUS_1 | 325-01-600-PD-06 | JB-607 | ACTIVE
13 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | Communication Signal | - | Communication Signal_BUS_1 | 325-01-613-PD-02 | JB-612 | ACTIVE
14 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-40201 | PUMP | PCY-40201_BUS_1 | 3-25-01-402-PD-01 | MCC | ACTIVE
15 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-40202 | PUMP | PCY-40202_BUS_1 | 3-25-01-402-PD-01 | MCC | ACTIVE
16 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-40203 | PUMP | PCY-40203_BUS_1 | 3-25-01-402-PD-02 | MCC | ACTIVE
17 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-60205 | - | PCY-60205_BUS_1 | 325-01-600-PD-01 | JB-601 | ACTIVE
18 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-60215 | PUMP | PCY-60215_BUS_1 | 325-01-600-PD-03 | MCC | ACTIVE
19 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-814201 | PUMP | PCY-814201_BUS_1 | 3-25-01-810-PD-01 | MCC | ACTIVE
20 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-814202 | PUMP | PCY-814202_BUS_1 | 3-25-01-810-PD-01 | MCC | ACTIVE
21 | 1 | 0 | C7S01,00 | C7S01- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | SPARE
22 | 1 | 1 | C7S01,01 | C7S01- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | SPARE
23 | 1 | 2 | C7S01,02 | C7S01- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | SPARE
24 | 1 | 3 | C7S01,03 | C7S01- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | SPARE
25 | 1 | 4 | C7S01,04 | C7S01- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | SPARE
26 | 1 | 5 | C7S01,05 | C7S01- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | SPARE
27 | 1 | 6 | C7S01,06 | C7S01- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | SPARE
28 | 1 | 7 | C7S01,07 | C7S01- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | 3-25-01-402-PD-01 | MCC | SPARE
29 | 1 | 8 | C7S01,08 | C7S01- | - | DI | 24 VDC energized | ATY-40201 | Tank Agitator | ATY-40201_DI_1 | 3-25-01-402-PD-01 | MCC | ACTIVE
30 | 1 | 9 | C7S01,09 | C7S01- | - | DI | 24 VDC energized | ATY-40201 | Tank Agitator | ATY-40201_DI_2 | 3-25-01-402-PD-01 | MCC | ACTIVE
31 | 1 | 10 | C7S01,10 | C7S01- | - | DI | 24 VDC energized | ATY-40201 | Tank Agitator | ATY-40201_DI_3 | 3-25-01-402-PD-01 | MCC | ACTIVE
32 | 1 | 11 | C7S01,11 | C7S01- | - | DI | 24 VDC energized | ATY-40202 | Tank Agitator | ATY-40202_DI_1 | 3-25-01-402-PD-01 | MCC | ACTIVE
33 | 1 | 12 | C7S01,12 | C7S01- | - | DI | 24 VDC energized | ATY-40202 | Tank Agitator | ATY-40202_DI_2 | 3-25-01-402-PD-01 | MCC | ACTIVE
34 | 1 | 13 | C7S01,13 | C7S01- | - | DI | 24 VDC energized | ATY-40202 | Tank Agitator | ATY-40202_DI_3 | 3-25-01-402-PD-01 | MCC | ACTIVE
35 | 1 | 14 | C7S01,14 | C7S01- | - | DI | 24 VDC energized | ATY-40203 | Tank Agitator | ATY-40203_DI_1 | 3-25-01-402-PD-02 | MCC | ACTIVE
36 | 1 | 15 | C7S01,15 | C7S01- | - | DI | 24 VDC energized | ATY-40203 | Tank Agitator | ATY-40203_DI_2 | 3-25-01-402-PD-02 | MCC | ACTIVE
37 | 1 | 16 | C7S01,16 | C7S01- | - | DI | 24 VDC energized | ATY-40203 | Tank Agitator | ATY-40203_DI_3 | 3-25-01-402-PD-02 | MCC | ACTIVE
38 | 1 | 17 | C7S01,17 | C7S01- | - | DI | 24 VDC energized | PCY-40201 | PUMP | PCY-40201_DI_1 | 3-25-01-402-PD-01 | MCC | ACTIVE
39 | 1 | 18 | C7S01,18 | C7S01- | - | DI | 24 VDC energized | PCY-40201 | PUMP | PCY-40201_DI_2 | 3-25-01-402-PD-01 | MCC | ACTIVE
40 | 1 | 19 | C7S01,19 | C7S01- | - | DI | 24 VDC energized | PCY-40201 | PUMP | PCY-40201_DI_3 | 3-25-01-402-PD-01 | MCC | ACTIVE
41 | 1 | 20 | C7S01,20 | C7S01- | - | DI | 24 VDC energized | PCY-40202 | PUMP | PCY-40202_DI_1 | 3-25-01-402-PD-01 | MCC | ACTIVE
42 | 1 | 21 | C7S01,21 | C7S01- | - | DI | 24 VDC energized | PCY-40202 | PUMP | PCY-40202_DI_2 | 3-25-01-402-PD-01 | MCC | ACTIVE
43 | 1 | 22 | C7S01,22 | C7S01- | - | DI | 24 VDC energized | PCY-40202 | PUMP | PCY-40202_DI_3 | 3-25-01-402-PD-01 | MCC | ACTIVE
44 | 1 | 23 | C7S01,23 | C7S01- | - | DI | 24 VDC energized | PCY-40203 | PUMP | PCY-40203_DI_1 | 3-25-01-402-PD-02 | MCC | ACTIVE
45 | 1 | 24 | C7S01,24 | C7S01- | - | DI | 24 VDC energized | PCY-40203 | PUMP | PCY-40203_DI_2 | 3-25-01-402-PD-02 | MCC | ACTIVE
46 | 1 | 25 | C7S01,25 | C7S01- | - | DI | 24 VDC energized | PCY-40203 | PUMP | PCY-40203_DI_3 | 3-25-01-402-PD-02 | MCC | ACTIVE
47 | 1 | 26 | C7S01,26 | C7S01- | - | DI | 24 VDC energized | BFY-60206 | 0 | BFY-60206_DI_1 | 325-01-600-PD-08 | MCC | ACTIVE
48 | 1 | 27 | C7S01,27 | C7S01- | - | DI | - | PCM-60205-2 | - | PCM-60205-2_DI_1 | 325-01-600-PD-01 | MCC | ACTIVE
49 | 1 | 28 | C7S01,28 | C7S01- | - | DI | - | PCM-60205-2 | - | PCM-60205-2_DI_2 | 325-01-600-PD-01 | MCC | ACTIVE
50 | 1 | 29 | C7S01,29 | C7S01- | - | DI | - | PCM-60205-3 | - | PCM-60205-3_DI_1 | 325-01-600-PD-01 | MCC | ACTIVE
51 | 1 | 30 | C7S01,30 | C7S01- | - | DI | - | PCM-60205-3 | - | PCM-60205-3_DI_2 | 325-01-600-PD-01 | MCC | ACTIVE
52 | 1 | 31 | C7S01,31 | C7S01- | - | DI | - | PCM-60205-4 | - | PCM-60205-4_DI_1 | 325-01-600-PD-01 | MCC | ACTIVE
53 | 2 | 0 | C7S02,00 | C7S02- | - | DI | - | PCM-60205-4 | - | PCM-60205-4_DI_2 | 325-01-600-PD-01 | MCC | ACTIVE
54 | 2 | 1 | C7S02,01 | C7S02- | - | DI | - | PCM-60205-5 | - | PCM-60205-5_DI_1 | 325-01-600-PD-01 | MCC | ACTIVE
55 | 2 | 2 | C7S02,02 | C7S02- | - | DI | - | PCM-60205-5 | - | PCM-60205-5_DI_2 | 325-01-600-PD-01 | MCC | ACTIVE
56 | 2 | 3 | C7S02,03 | C7S02- | - | DI | - | PCY-60205 | - | PCY-60205_DI_1 | 325-01-600-PD-01 | JB-601 | ACTIVE
57 | 2 | 4 | C7S02,04 | C7S02- | - | DI | - | PCY-60205 | - | PCY-60205_DI_2 | 325-01-600-PD-01 | JB-601 | ACTIVE
58 | 2 | 5 | C7S02,05 | C7S02- | - | DI | 24 VDC energized | RVM-60201 | 0 | RVM-60201_DI_1 | 325-01-600-PD-08 | MCC | ACTIVE
59 | 2 | 6 | C7S02,06 | C7S02- | - | DI | 24 VDC energized | RVM-60201 | 0 | RVM-60201_DI_2 | 325-01-600-PD-08 | MCC | ACTIVE
60 | 2 | 7 | C7S02,07 | C7S02- | - | DI | 24 VDC energized | RVM-60202 | 0 | RVM-60202_DI_1 | 325-01-600-PD-08 | MCC | ACTIVE
61 | 2 | 8 | C7S02,08 | C7S02- | - | DI | 24 VDC energized | RVM-60202 | 0 | RVM-60202_DI_2 | 325-01-600-PD-08 | MCC | ACTIVE
62 | 2 | 9 | C7S02,09 | C7S02- | - | DI | 24 VDC energized | RVM-60203 | 0 | RVM-60203_DI_1 | 325-01-600-PD-08 | MCC | ACTIVE
63 | 2 | 10 | C7S02,10 | C7S02- | - | DI | 24 VDC energized | RVM-60203 | 0 | RVM-60203_DI_2 | 325-01-600-PD-08 | MCC | ACTIVE
64 | 2 | 11 | C7S02,11 | C7S02- | - | DI | 24 VDC energized | BFY-60210 | 0 | BFY-60210_DI_1 | 325-01-600-PD-03 | MCC | ACTIVE
65 | 2 | 12 | C7S02,12 | C7S02- | - | DI | 24 VDC energized | BFY-60211 | 0 | BFY-60211_DI_1 | 325-01-600-PD-03 | MCC | ACTIVE
66 | 2 | 13 | C7S02,13 | C7S02- | - | DI | 24 VDC energized | BFY-60240 | 0 | BFY-60240_DI_1 | 325-01-600-PD-05 | MCC | ACTIVE
67 | 2 | 14 | C7S02,14 | C7S02- | - | DI | 24 VDC energized | PCY-60215 | PUMP | PCY-60215_DI_1 | 325-01-600-PD-03 | MCC | ACTIVE
68 | 2 | 15 | C7S02,15 | C7S02- | - | DI | 24 VDC energized | PCY-60215 | PUMP | PCY-60215_DI_2 | 325-01-600-PD-03 | MCC | ACTIVE
69 | 2 | 16 | C7S02,16 | C7S02- | - | DI | 24 VDC energized | PCY-60215 | PUMP | PCY-60215_DI_3 | 325-01-600-PD-03 | MCC | ACTIVE
70 | 2 | 17 | C7S02,17 | C7S02- | - | DI | 24 VDC energized | BFY-60220 | 0 | BFY-60220_DI_1 | 325-01-600-PD-04 | MCC | ACTIVE
71 | 2 | 18 | C7S02,18 | C7S02- | - | DI | 24 VDC energized | BFY-61302 | 0 | BFY-61302_DI_1 | 325-01-613-PD-05 | MCC | ACTIVE
72 | 2 | 19 | C7S02,19 | C7S02- | - | DI | Dry Contact | HS-61307F | 0 | HS-61307F_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
73 | 2 | 20 | C7S02,20 | C7S02- | - | DI | Dry Contact | HS-61307G | 0 | HS-61307G_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
74 | 2 | 21 | C7S02,21 | C7S02- | - | DI | Dry Contact | HS-61307H | 0 | HS-61307H_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
75 | 2 | 22 | C7S02,22 | C7S02- | - | DI | Dry Contact | HS-61307I | 0 | HS-61307I_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
76 | 2 | 23 | C7S02,23 | C7S02- | - | DI | Dry Contact | HS-61307J | 0 | HS-61307J_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
77 | 2 | 24 | C7S02,24 | C7S02- | - | DI | Dry Contact | HS-61307K | 0 | HS-61307K_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
78 | 2 | 25 | C7S02,25 | C7S02- | - | DI | Dry Contact | HS-61307L | 0 | HS-61307L_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
79 | 2 | 26 | C7S02,26 | C7S02- | - | DI | Dry Contact | HS-61307M | 0 | HS-61307M_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
80 | 2 | 27 | C7S02,27 | C7S02- | - | DI | Dry Contact | HS-61307N | 0 | HS-61307N_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
81 | 2 | 28 | C7S02,28 | C7S02- | - | DI | Dry Contact | HS-61307O | 0 | HS-61307O_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
82 | 2 | 29 | C7S02,29 | C7S02- | - | DI | Dry Contact | HS-61307P | 0 | HS-61307P_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
83 | 2 | 30 | C7S02,30 | C7S02- | - | DI | Dry Contact | HS-61307Q | 0 | HS-61307Q_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
84 | 2 | 31 | C7S02,31 | C7S02- | - | DI | Dry Contact | HS-61307R | 0 | HS-61307R_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
85 | 3 | 0 | C7S03,00 | C7S03- | - | DI | 24 VDC energized | RVM-61302 | 0 | RVM-61302_DI_1 | 325-01-613-PD-03 | MCC | ACTIVE
86 | 3 | 1 | C7S03,01 | C7S03- | - | DI | 24 VDC energized | RVM-61302 | 0 | RVM-61302_DI_2 | 325-01-613-PD-03 | MCC | ACTIVE
87 | 3 | 2 | C7S03,02 | C7S03- | - | DI | 24 VDC energized | RVM-61303 | 0 | RVM-61303_DI_1 | 325-01-613-PD-05 | MCC | ACTIVE
88 | 3 | 3 | C7S03,03 | C7S03- | - | DI | 24 VDC energized | RVM-61303 | 0 | RVM-61303_DI_2 | 325-01-613-PD-05 | MCC | ACTIVE
89 | 3 | 4 | C7S03,04 | C7S03- | - | DI | 24 VDC energized | SCM-61301 | 0 | SCM-61301_DI_1 | 325-01-613-PD-01 | MCC | ACTIVE
90 | 3 | 5 | C7S03,05 | C7S03- | - | DI | 24 VDC energized | SCM-61301 | 0 | SCM-61301_DI_2 | 325-01-613-PD-01 | MCC | ACTIVE
91 | 3 | 6 | C7S03,06 | C7S03- | - | DI | 24 VDC energized | SCM-61302 | 0 | SCM-61302_DI_2 | 325-01-613-PD-01 | MCC | ACTIVE
92 | 3 | 7 | C7S03,07 | C7S03- | - | DI | 24 VDC energized | SCM-61302 | 0 | SCM-61302_DI_1 | 325-01-613-PD-01 | MCC | ACTIVE
93 | 3 | 8 | C7S03,08 | C7S03- | - | DI | 24 VDC energized | BFY-61301 | 0 | BFY-61301_DI_1 | 325-01-613-PD-01 | MCC | ACTIVE
94 | 3 | 9 | C7S03,09 | C7S03- | - | DI | 24 VDC energized | BFY-61303 | 0 | BFY-61303_DI_1 | 325-01-613-PD-01 | MCC | ACTIVE
95 | 3 | 10 | C7S03,10 | C7S03- | - | DI | 24 VDC energized | BLM-61302 | 0 | BLM-61302_DI_1 | 325-01-613-PD-01 | MCC | ACTIVE
96 | 3 | 11 | C7S03,11 | C7S03- | - | DI | 24 VDC energized | BLM-61302 | 0 | BLM-61302_DI_2 | 325-01-613-PD-01 | MCC | ACTIVE
97 | 3 | 12 | C7S03,12 | C7S03- | - | DI | Dry Contact | HS-61307A | 0 | HS-61307A_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
98 | 3 | 13 | C7S03,13 | C7S03- | - | DI | Dry Contact | HS-61307B | 0 | HS-61307B_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
99 | 3 | 14 | C7S03,14 | C7S03- | - | DI | Dry Contact | HS-61307C | 0 | HS-61307C_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
100 | 3 | 15 | C7S03,15 | C7S03- | - | DI | Dry Contact | HS-61307D | 0 | HS-61307D_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
101 | 3 | 16 | C7S03,16 | C7S03- | - | DI | Dry Contact | HS-61307E | 0 | HS-61307E_DI_1 | 3-25-01-613-PD-03 | MCC | ACTIVE
102 | 3 | 17 | C7S03,17 | C7S03- | - | DI | 24 VDC energized | RVM-60204 | 0 | RVM-60204_DI_1 | 325-01-600-PD-08 | MCC | ACTIVE
103 | 3 | 18 | C7S03,18 | C7S03- | - | DI | 24 VDC energized | RVM-60204 | 0 | RVM-60204_DI_2 | 325-01-600-PD-08 | MCC | ACTIVE
104 | 3 | 19 | C7S03,19 | C7S03- | - | DI | 24 VDC energized | RVM-61301 | 0 | RVM-61301_DI_1 | 325-01-613-PD-01 | MCC | ACTIVE
105 | 3 | 20 | C7S03,20 | C7S03- | - | DI | 24 VDC energized | RVM-61301 | 0 | RVM-61301_DI_2 | 325-01-613-PD-01 | MCC | ACTIVE
106 | 3 | 21 | C7S03,21 | C7S03- | - | DI | 24 VDC energized | RVM-61304 | 0 | RVM-61304_DI_1 | 325-01-613-PD-01 | MCC | ACTIVE
107 | 3 | 22 | C7S03,22 | C7S03- | - | DI | 24 VDC energized | RVM-61304 | 0 | RVM-61304_DI_2 | 325-01-613-PD-01 | MCC | ACTIVE
108 | 3 | 23 | C7S03,23 | C7S03- | - | DI | 24 VDC energized | RVM-61305 | 0 | RVM-61305_DI_1 | 325-01-613-PD-01 | MCC | ACTIVE
109 | 3 | 24 | C7S03,24 | C7S03- | - | DI | 24 VDC energized | RVM-61305 | 0 | RVM-61305_DI_2 | 325-01-613-PD-01 | MCC | ACTIVE
110 | 3 | 25 | C7S03,25 | C7S03- | - | DI | - | PCY-60205 | - | PCY-60205_DI_3 | 325-01-600-PD-01 | JB-601 | ACTIVE
111 | 4 | 4 | C7S04,04 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
112 | 4 | 5 | C7S04,05 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
113 | 4 | 6 | C7S04,06 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
114 | 4 | 7 | C7S04,07 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
115 | 4 | 8 | C7S04,08 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
116 | 4 | 9 | C7S04,09 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
117 | 4 | 10 | C7S04,10 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
118 | 4 | 11 | C7S04,11 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
119 | 4 | 12 | C7S04,12 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
120 | 4 | 13 | C7S04,13 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
121 | 4 | 14 | C7S04,14 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
122 | 4 | 15 | C7S04,15 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
123 | 4 | 16 | C7S04,16 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
124 | 4 | 17 | C7S04,17 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
125 | 4 | 18 | C7S04,18 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
126 | 4 | 19 | C7S04,19 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
127 | 4 | 20 | C7S04,20 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
128 | 4 | 21 | C7S04,21 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
129 | 4 | 22 | C7S04,22 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
130 | 4 | 23 | C7S04,23 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
131 | 4 | 24 | C7S04,24 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
132 | 4 | 25 | C7S04,25 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
133 | 4 | 26 | C7S04,26 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
134 | 4 | 27 | C7S04,27 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
135 | 4 | 28 | C7S04,28 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
136 | 4 | 29 | C7S04,29 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
137 | 4 | 30 | C7S04,30 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
138 | 4 | 31 | C7S04,31 | C7S04- | - | DI | - | Spare | Spare I/O Point | Spare_DI_0 | - | MCC | SPARE
139 | 5 | 0 | C7S05,00 | C7S05- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | SPARE
140 | 5 | 1 | C7S05,01 | C7S05- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | SPARE
141 | 5 | 2 | C7S05,02 | C7S05- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | SPARE
142 | 5 | 3 | C7S05,03 | C7S05- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | SPARE
143 | 5 | 4 | C7S05,04 | C7S05- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | SPARE
144 | 5 | 5 | C7S05,05 | C7S05- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | SPARE
145 | 5 | 6 | C7S05,06 | C7S05- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | SPARE
146 | 5 | 7 | C7S05,07 | C7S05- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | 3-25-01-402-PD-01 | MCC | SPARE
147 | 5 | 8 | C7S05,08 | C7S05- | - | DO | 24 VDC energized | ATY-40201 | Tank Agitator | ATY-40201_DO_1 | 3-25-01-402-PD-01 | MCC | ACTIVE
148 | 5 | 9 | C7S05,09 | C7S05- | - | DO | 24 VDC energized | ATY-40202 | Tank Agitator | ATY-40202_DO_1 | 3-25-01-402-PD-01 | MCC | ACTIVE
149 | 5 | 10 | C7S05,10 | C7S05- | - | DO | 24 VDC energized | ATY-40203 | Tank Agitator | ATY-40203_DO_1 | 3-25-01-402-PD-02 | MCC | ACTIVE
150 | 5 | 11 | C7S05,11 | C7S05- | - | DO | 24 VDC energized | PCY-40201 | PUMP | PCY-40201_DO_1 | 3-25-01-402-PD-01 | MCC | ACTIVE
151 | 5 | 12 | C7S05,12 | C7S05- | - | DO | 24 VDC energized | PCY-40202 | PUMP | PCY-40202_DO_1 | 3-25-01-402-PD-01 | MCC | ACTIVE
152 | 5 | 13 | C7S05,13 | C7S05- | - | DO | 24 VDC energized | PCY-40203 | PUMP | PCY-40203_DO_1 | 3-25-01-402-PD-02 | MCC | ACTIVE
153 | 5 | 14 | C7S05,14 | C7S05- | - | DO | 24 VDC energized | BFY-60206 | 0 | BFY-60206_DO_1 | 325-01-600-PD-08 | MCC | ACTIVE
154 | 5 | 15 | C7S05,15 | C7S05- | - | DO | - | PCM-60205-2 | - | PCM-60205-2_DO_1 | 325-01-600-PD-01 | MCC | ACTIVE
155 | 5 | 16 | C7S05,16 | C7S05- | - | DO | - | PCM-60205-2 | - | PCM-60205-2_DO_2 | 325-01-600-PD-01 | MCC | ACTIVE
156 | 5 | 17 | C7S05,17 | C7S05- | - | DO | - | PCM-60205-3 | - | PCM-60205-3_DO_1 | 325-01-600-PD-01 | MCC | ACTIVE
157 | 5 | 18 | C7S05,18 | C7S05- | - | DO | - | PCM-60205-3 | - | PCM-60205-3_DO_2 | 325-01-600-PD-01 | MCC | ACTIVE
158 | 5 | 19 | C7S05,19 | C7S05- | - | DO | - | PCM-60205-4 | - | PCM-60205-4_DO_1 | 325-01-600-PD-01 | MCC | ACTIVE
159 | 5 | 20 | C7S05,20 | C7S05- | - | DO | - | PCM-60205-4 | - | PCM-60205-4_DO_2 | 325-01-600-PD-01 | MCC | ACTIVE
160 | 5 | 21 | C7S05,21 | C7S05- | - | DO | - | PCM-60205-5 | - | PCM-60205-5_DO_1 | 325-01-600-PD-01 | MCC | ACTIVE
161 | 5 | 22 | C7S05,22 | C7S05- | - | DO | - | PCM-60205-5 | - | PCM-60205-5_DO_2 | 325-01-600-PD-01 | MCC | ACTIVE
162 | 5 | 23 | C7S05,23 | C7S05- | - | DO | 24 VDC energized | RVM-60201 | 0 | RVM-60201_DO_1 | 325-01-600-PD-08 | MCC | ACTIVE
163 | 5 | 24 | C7S05,24 | C7S05- | - | DO | 24 VDC energized | RVM-60201 | 0 | RVM-60201_DO_2 | 325-01-600-PD-08 | MCC | ACTIVE
164 | 5 | 25 | C7S05,25 | C7S05- | - | DO | 24 VDC energized | RVM-60202 | 0 | RVM-60202_DO_1 | 325-01-600-PD-08 | MCC | ACTIVE
165 | 5 | 26 | C7S05,26 | C7S05- | - | DO | 24 VDC energized | RVM-60202 | 0 | RVM-60202_DO_2 | 325-01-600-PD-08 | MCC | ACTIVE
166 | 5 | 27 | C7S05,27 | C7S05- | - | DO | 24 VDC energized | RVM-60203 | 0 | RVM-60203_DO_1 | 325-01-600-PD-08 | MCC | ACTIVE
167 | 5 | 28 | C7S05,28 | C7S05- | - | DO | 24 VDC energized | RVM-60203 | 0 | RVM-60203_DO_2 | 325-01-600-PD-08 | MCC | ACTIVE
168 | 5 | 29 | C7S05,29 | C7S05- | - | DO | 0 | XS-60205 | 0 | XS-60205_DO_1 | 325-01-600-PD-01 | MCC | ACTIVE
169 | 5 | 30 | C7S05,30 | C7S05- | - | DO | 24 VDC energized | BFY-60210 | 0 | BFY-60210_DO_1 | 325-01-600-PD-03 | MCC | ACTIVE
170 | 5 | 31 | C7S05,31 | C7S05- | - | DO | 24 VDC energized | BFY-60211 | 0 | BFY-60211_DO_1 | 325-01-600-PD-03 | MCC | ACTIVE
171 | 6 | 0 | C7S06,00 | C7S06- | - | DO | 24 VDC energized | BFY-60240 | 0 | BFY-60240_DO_1 | 325-01-600-PD-05 | MCC | ACTIVE
172 | 6 | 1 | C7S06,01 | C7S06- | - | DO | 24 VDC energized | PCY-60215 | PUMP | PCY-60215_DO_1 | 325-01-600-PD-03 | MCC | ACTIVE
173 | 6 | 2 | C7S06,02 | C7S06- | - | DO | Dry Contact | XS-60240A | 0 | XS-60240A_DO_1 | 325-01-600-PD-05 | MCC | ACTIVE
174 | 6 | 3 | C7S06,03 | C7S06- | - | DO | Dry Contact | XS-60241A | 0 | XS-60241A_DO_1 | 325-01-600-PD-05 | MCC | ACTIVE
175 | 6 | 4 | C7S06,04 | C7S06- | - | DO | Dry Contact | XS-60242A | 0 | XS-60242A_DO_1 | 325-01-600-PD-05 | MCC | ACTIVE
176 | 6 | 4 | C7S06,04 | C7S06- | - | DO | Dry Contact | XS-60243A | 0 | XS-60243A_DO_1 | 325-01-600-PD-05 | MCC | ACTIVE
177 | 6 | 6 | C7S06,06 | C7S06- | - | DO | 24 VDC energized | XS-60260 | 0 | XS-60260_DO_1 | 325-01-600-PD-05 | MCC | ACTIVE
178 | 6 | 7 | C7S06,07 | C7S06- | - | DO | 24 VDC energized | BFY-60220 | 0 | BFY-60220_DO_1 | 325-01-600-PD-04 | MCC | ACTIVE
179 | 6 | 8 | C7S06,08 | C7S06- | - | DO | Dry Contact | XS-FH-60210A | 0 | XS-FH-60210A_DO_1 | 325-01-600-PD-06 | MCC | ACTIVE
180 | 6 | 9 | C7S06,09 | C7S06- | - | DO | Dry Contact | XS-FH-60210B | 0 | XS-FH-60210B_DO_1 | 325-01-600-PD-06 | MCC | ACTIVE
181 | 6 | 10 | C7S06,10 | C7S06- | - | DO | 24 VDC energized | BFY-61302 | 0 | BFY-61302_DO_1 | 325-01-613-PD-05 | MCC | ACTIVE
182 | 6 | 11 | C7S06,11 | C7S06- | - | DO | 24 VDC energized | RVM-61302 | 0 | RVM-61302_DO_1 | 325-01-613-PD-03 | MCC | ACTIVE
183 | 6 | 12 | C7S06,12 | C7S06- | - | DO | 24 VDC energized | RVM-61302 | 0 | RVM-61302_DO_2 | 325-01-613-PD-03 | MCC | ACTIVE
184 | 6 | 13 | C7S06,13 | C7S06- | - | DO | 24 VDC energized | RVM-61303 | 0 | RVM-61303_DO_1 | 325-01-613-PD-05 | MCC | ACTIVE
185 | 6 | 14 | C7S06,14 | C7S06- | - | DO | 24 VDC energized | RVM-61303 | 0 | RVM-61303_DO_2 | 325-01-613-PD-05 | MCC | ACTIVE
186 | 6 | 15 | C7S06,15 | C7S06- | - | DO | 24 VDC energized | SCM-61301 | 0 | SCM-61301_DO_1 | 325-01-613-PD-01 | MCC | ACTIVE
187 | 6 | 16 | C7S06,16 | C7S06- | - | DO | 24 VDC energized | SCM-61301 | 0 | SCM-61301_DO_2 | 325-01-613-PD-01 | MCC | ACTIVE
188 | 6 | 17 | C7S06,17 | C7S06- | - | DO | 24 VDC energized | SCM-61302 | 0 | SCM-61302_DO_1 | 325-01-613-PD-01 | MCC | ACTIVE
189 | 6 | 18 | C7S06,18 | C7S06- | - | DO | 24 VDC energized | SCM-61302 | 0 | SCM-61302_DO_2 | 325-01-613-PD-01 | MCC | ACTIVE
190 | 6 | 19 | C7S06,19 | C7S06- | - | DO | 24 VDC energized | BFY-61301 | 0 | BFY-61301_DO_1 | 325-01-613-PD-01 | MCC | ACTIVE
191 | 6 | 20 | C7S06,20 | C7S06- | - | DO | 24 VDC energized | BFY-61303 | 0 | BFY-61303_DO_1 | 325-01-613-PD-01 | MCC | ACTIVE
192 | 6 | 21 | C7S06,21 | C7S06- | - | DO | 24 VDC energized | BLM-61302 | 0 | BLM-61302_DO_1 | 325-01-613-PD-01 | MCC | ACTIVE
193 | 6 | 22 | C7S06,22 | C7S06- | - | DO | 24 VDC energized | BLM-61302 | 0 | BLM-61302_DO_2 | 325-01-613-PD-01 | MCC | ACTIVE
194 | 6 | 23 | C7S06,23 | C7S06- | - | DO | 24 VDC energized | RVM-60204 | 0 | RVM-60204_DO_1 | 325-01-600-PD-08 | MCC | ACTIVE
195 | 6 | 24 | C7S06,24 | C7S06- | - | DO | 24 VDC energized | RVM-60204 | 0 | RVM-60204_DO_2 | 325-01-600-PD-08 | MCC | ACTIVE
196 | 6 | 25 | C7S06,25 | C7S06- | - | DO | 24 VDC energized | RVM-61301 | 0 | RVM-61301_DO_1 | 325-01-613-PD-01 | MCC | ACTIVE
197 | 6 | 26 | C7S06,26 | C7S06- | - | DO | 24 VDC energized | RVM-61301 | 0 | RVM-61301_DO_2 | 325-01-613-PD-01 | MCC | ACTIVE
198 | 6 | 27 | C7S06,27 | C7S06- | - | DO | 24 VDC energized | RVM-61304 | 0 | RVM-61304_DO_1 | 325-01-613-PD-01 | MCC | ACTIVE
199 | 6 | 28 | C7S06,28 | C7S06- | - | DO | 24 VDC energized | RVM-61304 | 0 | RVM-61304_DO_2 | 325-01-613-PD-01 | MCC | ACTIVE
200 | 6 | 29 | C7S06,29 | C7S06- | - | DO | 24 VDC energized | RVM-61305 | 0 | RVM-61305_DO_1 | 325-01-613-PD-01 | MCC | ACTIVE
201 | 6 | 30 | C7S06,30 | C7S06- | - | DO | 24 VDC energized | RVM-61305 | 0 | RVM-61305_DO_2 | 325-01-613-PD-01 | MCC | ACTIVE
202 | 6 | 31 | C7S06,31 | C7S06- | - | DO | - | PCY-60205 | - | PCY-60205_DO_1 | 325-01-600-PD-01 | JB-601 | ACTIVE
203 | 7 | 8 | C7S07,08 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
204 | 7 | 9 | C7S07,09 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
205 | 7 | 10 | C7S07,10 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
206 | 7 | 11 | C7S07,11 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
207 | 7 | 12 | C7S07,12 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
208 | 7 | 13 | C7S07,13 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
209 | 7 | 14 | C7S07,14 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
210 | 7 | 15 | C7S07,15 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
211 | 7 | 16 | C7S07,16 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
212 | 7 | 17 | C7S07,17 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
213 | 7 | 18 | C7S07,18 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
214 | 7 | 19 | C7S07,19 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
215 | 7 | 20 | C7S07,20 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
216 | 7 | 21 | C7S07,21 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
217 | 7 | 22 | C7S07,22 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
218 | 7 | 23 | C7S07,23 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
219 | 7 | 24 | C7S07,24 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
220 | 7 | 25 | C7S07,25 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
221 | 7 | 26 | C7S07,26 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
222 | 7 | 27 | C7S07,27 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
223 | 7 | 28 | C7S07,28 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
224 | 7 | 29 | C7S07,29 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
225 | 7 | 30 | C7S07,30 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE
226 | 7 | 31 | C7S07,31 | C7S07- | - | DO | - | Spare | Spare I/O Point | Spare_DO_0 | - | MCC | SPARE