## Executive_Summary
INGREDION (THAILAND) CO., LTD. ¦ PROJECT JET COOKER
INSTRUMENT MODEL SPECIFICATION, PLC I/O MAP & CABLE SCHEDULE
Reconciliation between Rev 3.6 Master & Dev-Tag35-6 Hardware Architecture ¦ AEC Industrial Engineering
TOTAL INSTRUMENTS |  | WIRED TO PLC / MCC |  | PLC I/O CHANNELS |  | CONTROLLOGIX RACKS | VENDORS MAPPED
502 |  | 416 |  | 1,210 |  | 7 Racks | 10+ Brands
Rev 3.6 Engineering Master |  | 82.9% electrical loops |  | 763 Active / 447 Spare |  | Chassis C1 to C7 (47 Slots) | E+H, Samson, Mettler, etc.
1. Major Instrument Equipment Packages & Manufacturer Model Mapping
Package / Equipment Category | Tag Prefix | Primary Manufacturer | Standard Model Series | Process Connection | Standard Signal | Recommended Cable Spec
Coriolis Mass Flowmeter | FT | Endress+Hauser | Promass E 300 (8E3B50) | DN50 Cl.150 RF Flange | 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded Twisted Pair)
Electromagnetic Flowmeter | FT | Endress+Hauser | Promag P 300 (5P3B50/80/1H) | DN50/DN80/DN100 Cl.150 Flange | 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded Twisted Pair)
Vortex Steam Flowmeter | FT | Endress+Hauser | Prowirl F 200 (7F2C80/1H) | DN80/DN100 Cl.300 RF Flange | 4-20mA HART + Pulse | LiY-CY TP 1Px1.0 (Shielded Twisted Pair)
Thermal Mass Gas Flowmeter | FT | Endress+Hauser | t-mass F 300 / I 300 (6F3B/6I3B) | DN100 Flange / 1" NPT Insertion | 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded Twisted Pair)
Ultrasonic Flowmeter (Clamp-on) | FT | Keyence | FD-H Series (FD-H20/H32) | Non-invasive External Clamp-on | 4-20mA + Pulse / 24VDC | LiY-CY TP 2Px1.0 (Individually Shielded)
Differential Pressure Transmitter | DPT / DPIT | Endress+Hauser | Deltabar PMD55B Series | 1/4" NPT w/ 5-Valve Manifold DA63M | 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded Twisted Pair)
Gauge / Absolute Pressure Transmitter | PT | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | 1/2" NPT / Hygienic Clamp | 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded Twisted Pair)
Radar Level Transmitter | LT | Endress+Hauser | Micropilot FMR67B (80 GHz Radar) | DN80 3" Cl.150 Flange | 4-20mA HART / 24VDC | LiY-CY(EB) 1Px1.0 (Blue IS Sheath)
Hydrostatic Level Transmitter | LT | Endress+Hauser | Cerabar PMP43 (Flush Diaphragm) | Hygienic Universal Clamp | 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded Twisted Pair)
Vibrating Level Switch (Liquids) | LSH / LSL | Endress+Hauser | Liquiphant FTL51B | 3/4" NPT Threaded / Clamp | 24VDC / Relay Contact | CVV 3Cx1.5 (Control Cable)
Vibrating Level Switch (Solids) | LSH | Endress+Hauser | Soliphant FTM51 | 1-1/2" NPT Threaded / Flange | 24VDC / Relay Contact | CVV 3Cx1.5 (Control Cable)
Temperature Transmitter | TT | Endress+Hauser | iTEMP TMT71 + TM411 (Pt100 RTD) | 1/2" NPT w/ Threaded Thermowell | 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded Twisted Pair)
pH Analytical Transmitter | pHT / AT | Mettler Toledo | M300G2 4-Wire + InPro3250i + InTrac 777P | DN25 Weld-in Socket | 4-20mA HART / 24VDC | LiY-CY TP 2Px1.0 + CVV 3Cx1.5 (Pwr)
Dust Analyzer Transmitter | AT | ENVEA / PCME | PCME QAL 991 (Particulate Monitor) | DN100 Flange w/ Purge Air Unit | 4-20mA + Relays / 24VDC | LiY-CY TP 2Px1.0 + CVV 3Cx1.5 (Pwr)
Combustible / LEL Gas Detector | AT | Sensidyne / SmartGas | 925FGD Explosionproof Detector | 3/4" NPT Conduit Entry | 4-20mA + Relays / 24VDC | LiY-CY TP 2Px1.0 (Ex d Explosionproof)
Globe Control Valve (Modulating) | TCV / PCV | Samson | Type 3241 + Trovis 3730-1 Positioner | Flange ASME B16.5 Cl.150/300 RF | 4-20mA Setpoint + Feedback | LiY-CY TP 2Px1.0 (Dual Shielded Pairs)
Pneumatic On-Off Valve (Automated) | XV / SV | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Series + ESV Sol. | Flange Cl.150 RF, SS316 | 24VDC DO + 2x DI Limit Sw. | CVV 3Cx1.5 (Sol) + CVV 4Cx1.0 (Limit)
Manual Hand Valve w/ Position Sw. | HV | TeroFox / APL-HKC | TF-20DFS Valve + APL-210N/510N Box | Flange Cl.150 RF, SS316 | 2x DI Dry Contact Feedback | CVV 4Cx1.0 (Control Cable)
Pneumatic Turbine Vibrator | VIB | Netter Vibration | NCT 5 Pneumatic Turbine Vibrator | G 1/8" BSP Pneumatic Port | 24VDC Solenoid DO | CVV 3Cx1.5 (Solenoid Control)
2. Standard Instrumentation & Control Cable Selection Guide
Cable Type / Code | Conductor Spec | Screen / Shielding Construction | Voltage / Temp Rating | Jacket Color | Standard Project Application
LiY-CY TP 1Px1.0 | 1 Twisted Pair x 1.0 mm² Stranded Cu | Al-mylar tape screen + Tinned copper braid | 300/500 V, -30°C to +80°C | Gray (RAL 7001) / Black | Standard 2-wire 4-20mA HART transmitters (AI/AO)
LiY-CY(EB) 1Px1.0 | 1 Twisted Pair x 1.0 mm² Stranded Cu | Al-mylar tape screen + Tinned copper braid | 300/500 V, -30°C to +80°C | Blue (RAL 5015) for Ex i | Intrinsically Safe Ex i loops connected to IS-JB-603/608/612/618
LiY-CY TP 2Px1.0 | 2 Twisted Pairs x 1.0 mm² Stranded Cu | Individual pair screen + Overall copper braid | 300/500 V, -30°C to +80°C | Gray / Black | Control valves (AO setpoint + AI feedback), Analyzers (Signal + Alarm)
CVV 3Cx1.5 | 3 Cores x 1.5 mm² Annealed Solid Cu | Heavy-duty PVC jacket, unshielded | 600 V, 70°C | Black UV-Resistant | 24VDC Solenoid valves (DO), Level switches, 24VDC instrument power
CVV 4Cx1.0 | 4 Cores x 1.0 mm² Annealed Solid Cu | Heavy-duty PVC jacket, unshielded | 600 V, 70°C | Black UV-Resistant | Valve position limit switches (ZSO/ZSC Open & Close dry contact DI)
CVV 5Cx1.5 | 5 Cores x 1.5 mm² Annealed Solid Cu | Heavy-duty PVC jacket, unshielded | 600 V, 70°C | Black UV-Resistant | Combined on-off valve feed (Solenoid 24VDC + Limit switch common/signals)
CAT 6 S/FTP | 4 Pairs 24 AWG Solid Cu | Braided copper shield + Foil per pair (S/FTP) | Industrial High-Flex, 80°C | Teal / Green | EtherNet/IP digital communications, MCC gateway, remote field interfaces
LiY-CY(IS/OS) 16Px0.75 | 16 Twisted Pairs x 0.75 mm² Cu | Individual Foil + Overall Copper Braid Trunk | 300/500 V, 80°C | Black / Blue Trunk | Main analog trunk cable from field junction boxes to PLC Cabinet CA1
CVV 30Cx1.5 | 30 Cores x 1.5 mm² Multi-Core Cu | Overall PVC heavy-duty armored trunk | 600 V, 70°C | Black Industrial | Main discrete digital trunk cable from field junction boxes to CA1

## Instrument_Master_IO_Map
INGREDION (THAILAND) CO., LTD. ¦ PROJECT JET COOKER ¦ MASTER INSTRUMENT SPECIFICATION & I/O MAP
Loop-by-Loop Instrument Model, Electrical Parameter, PLC I/O Allocation, and Cable Schedule ¦ Rev 3.6 Master
Item | Tag No. (Rev 3.6) | Legacy Tag (3.3) | P&ID No. | Description | Instrument Name | Signal Type | Calibrated Range | Protection Class | Manufacturer | Model Series | Specific Order Code | Process Connection | Electrical / Power Rating | DO | DI | AO | AI | Bus | PLC Chassis | PLC Slot(s) | Channel Address(es) | PLC Tag Name(s) | Module Model(s) | Panel Enclosure | Destination JB | Status | Suggested Field Cable | Conductor Cores & Size | Shielding Construction | Cable Gland Spec | Trunk Cable Route
1 | AT-60241 | - | 325-01-602-PD-05 | Dust Analyzer Transmitter for Exhaust Duct (DTEX-22) | Dust Analyzer Transmitter | 4 - 20 mA | 5000 mg | - | ENVEA / PCME | PCME QAL 991 (Dust Analyzer) | 6626013-33-201-001 | Flange DN100 w/ Purge Air | 4-20mA Output + Alarm Relay / 24VDC | - | - | - | 1 | - | C2 | S10 | C2S10,00 (AI) | AT-60241_AI_1 | 1756-IF16-0 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 2Px1.0 (Signal + Alarm) + CVV 3Cx1.5 (24VDC Power) (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 2 Pairs x 1.0 mm² + 3 Cores x 1.5 mm² | Overall Tinned Copper Braid + Al-Mylar Screen | M20x1.5 Ex d/e Double Compression Gland | LiY-CY 16Px0.75 (Signals) + CVV Power Trunk to CA1
2 | DPT-60201 | DPT-60901 | 325-01-602-PD-09 | Steam filter pressure | Differential Pressure Transmitter | 4 - 20 mA | 0-1 barg | - | Endress+Hauser | Deltabar PMD55B (Diff. Pressure Transmitter) | PMD55B Series w/ 5-Valve Manifold | 1/4" NPT Female w/ 5-Valve Manifold DA63M | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C4 | S05 | C4S05,00 (AI) | DPT-60201_AI_1 | 1756-IF16-0 | =CA1+MCP-M4 | JB-606 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
3 | DPT-61301 | - | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | 4 - 20 mA | - | Ex t/d | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | PMD55B-2NTN7/0 | NPT 1/4" w/ 5-Valve Manifold DA63M | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S05 | C3S05,04 (AI) | DPT-61301_AI_1 | 1756-IF16-4 | =CA1+MCP-M3 | IS-JB-618 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
4 | DPT-61302 | - | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | 4 - 20 mA | - | Ex t/d | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | PMD55B-2NTN7/0 | NPT 1/4" w/ 5-Valve Manifold DA63M | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S05 | C3S05,05 (AI) | DPT-61302_AI_1 | 1756-IF16-5 | =CA1+MCP-M3 | IS-JB-618 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
5 | DPT-61310 | - | 325-01-613-PD-03 | Vent filter pressure | Differential Pressure Transmitter | 4 - 20 mA | - | Ex t/d | Endress+Hauser | Deltabar PMD55B (Diff. Pressure Transmitter) | PMD55B Series w/ 5-Valve Manifold | 1/4" NPT Female w/ 5-Valve Manifold DA63M | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C4 | S06 | C4S06,06 (AI) | DPT-61310_AI_1 | 1756-IF16-6 | =CA1+MCP-M4 | IS-JB-612 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
6 | DPT-61312 | - | 325-01-613-PD-05 | Vent filter pressure | Differential Pressure Transmitter | 4 - 20 mA | - | Ex t/d | Endress+Hauser | Deltabar PMD55B (Diff. Pressure Transmitter) | PMD55B Series w/ 5-Valve Manifold | 1/4" NPT Female w/ 5-Valve Manifold DA63M | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C4 | S06 | C4S06,07 (AI) | DPT-61312_AI_1 | 1756-IF16-7 | =CA1+MCP-M4 | IS-JB-612 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
7 | DPT-60202 | - | 325-01-602-PD-08 | Gas Pressure Differential Transmitter for Air Filter (FICA-31) | Differential Pressure Transmitter | 4 - 20 mA | -100 to 500 mBar | - | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | PMD55B-2Q8M4/0 | NPT 1/4" w/ 5-Valve Manifold DA63M | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C1 | S10 | C1S10,01 (AI) | DPT-60202_AI_1 | 1756-IF16-1 | =CA1+MCP-M1 | JB-601 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
8 | DPT-60203 | - | 325-01-602-PD-03 | Gas Pressure Differential Transmitter for Air Filter (FICA-21) | Differential Pressure Transmitter | 4 - 20 mA | -100 to 500 mBar | - | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | PMD55B-2Q8M4/0 | NPT 1/4" w/ 5-Valve Manifold DA63M | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S10 | C2S10,01 (AI) | DPT-60203_AI_1 | 1756-IF16-1 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
9 | FSL-20201 | - | 325-01-202-PD-01 | Slurry low flow | Flow Switch | Dry Contact | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
10 | FSL-40201 | - | 325-01-402-PD-01 | Slurry low flow | Flow Switch | Dry Contact | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S03 | C1S03,16 (DI) | FSL-40201_DI_1 | 1756-IB32-16 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
11 | FSL-40202 | - | 325-01-402-PD-01 | Slurry low flow | Flow Switch | Dry Contact | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S03 | C1S03,17 (DI) | FSL-40202_DI_1 | 1756-IB32-17 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
12 | FS-40204 | - | 325-01-402-PD-01 | Jet Cooker | Flow Switch | Dry Contact | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S01 | C2S01,00 (DI) | FS-40204_DI_1 | 1756-IB32-0 | =CA1+MCP-M2 | JB-402 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
13 | FS-40205 | - | 325-01-402-PD-02 | Jet Cooker | Flow Switch | Dry Contact | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S01 | C2S01,01 (DI) | FS-40205_DI_1 | 1756-IB32-1 | =CA1+MCP-M2 | JB-402 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
14 | FT-40201 | - | 325-01-402-PD-02 | Slurry flowrate & density check transfer line | Coriolis Flow Transmitter | 4 - 20 mA,Pulse | 0-15 m³/hr | - | Endress+Hauser | Promass E 300 (Coriolis Mass Flow) | 8E3B50-14000/0 | DN50 2" Cl.150 RF Flange | 4-20mA HART / 24VDC | - | 1 | - | 2 | - | C1 | S03, S09 | C1S03,18 (DI); C1S09,00 (AI); C1S09,01 (AI) | FT-40201_DI_1; FT-40201_AI_1; FT-40201_AI_2 | 1756-IB32-18, 1756-IF16-0, 1756-IF16-1 | =CA1+MCP-M1 | JB-401 | WIRED | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 3 Pairs x 1.0 mm² + 3 Cores x 1.5 mm² | Individually & Overall Shielded Twisted Pairs | M20x1.5 Brass Nickel-Plated Ex d/e Gland | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
15 | FT-40202 | - | 325-01-402-PD-02 | Feed Slurry Flow Transmitter for Pipe (PIPE) | Magnetic Flow Transmitter | 4 - 20 mA,Pulse | 0 to 8,000 m³/hr | - | Endress+Hauser | Promag P 300 (Electromagnetic Flow) | 5P3B50-355V8/0 | DN50 2" Cl.150 RF Flange, PTFE Liner | 4-20mA HART / 24VDC | - | 1 | - | 1 | - | C1 | S03, S09 | C1S03,19 (DI); C1S09,02 (AI) | FT-40202_DI_1; FT-40202_AI_1 | 1756-IB32-19, 1756-IF16-2 | =CA1+MCP-M1 | JB-401 | WIRED | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 3 Pairs x 1.0 mm² + 3 Cores x 1.5 mm² | Individually & Overall Shielded Twisted Pairs | M20x1.5 Brass Nickel-Plated Ex d/e Gland | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
16 | FT-40221 | - | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter | 4 - 20 mA,Pulse | 0-6 m³/hr | - | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | 8E3B50 Series | Flange ASME B16.5 Cl.150 RF, 316L | 4-20mA HART / 24VDC Loop/Aux | - | 1 | - | 2 | - | C2 | S01, S09 | C2S01,02 (DI); C2S09,00 (AI); C2S09,01 (AI) | FT-40221_DI_1; FT-40221_AI_1; FT-40221_AI_2 | 1756-IB32-2, 1756-IF16-0, 1756-IF16-1 | =CA1+MCP-M2 | JB-402 | WIRED | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 3 Pairs x 1.0 mm² + 3 Cores x 1.5 mm² | Individually & Overall Shielded Twisted Pairs | M20x1.5 Brass Nickel-Plated Ex d/e Gland | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
17 | FT-40222 | - | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter | 4 - 20 mA,Pulse | 0-850 kg/hr | - | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | 8E3B50 Series | Flange ASME B16.5 Cl.150 RF, 316L | 4-20mA HART / 24VDC Loop/Aux | - | 1 | - | 2 | - | C2 | S01, S09 | C2S01,03 (DI); C2S09,02 (AI); C2S09,03 (AI) | FT-40222_DI_1; FT-40222_AI_1; FT-40222_AI_2 | 1756-IB32-3, 1756-IF16-2, 1756-IF16-3 | =CA1+MCP-M2 | JB-402 | WIRED | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 3 Pairs x 1.0 mm² + 3 Cores x 1.5 mm² | Individually & Overall Shielded Twisted Pairs | M20x1.5 Brass Nickel-Plated Ex d/e Gland | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
18 | FT-60221 | - | 325-01-602-PD-04 | Cool air Flow | Thermal Mass Flow Transmitter | 4 - 20 mA | 2500 m3/h | - | Endress+Hauser | t-mass I 300 (Thermal Mass Flow) | 6I3BL3-83L4/0 | 1" NPT Insertion Sensor | 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,01 (AI) | FT-60221_AI_1 | 1756-IF16-1 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
19 | FT-60201 | - | 325-01-602-PD-08 | Gas Flow Transmitter for Cooling Conveying Cold Air Duct (DTCA-32) | Thermal Mass Flow Transmitter | 4 - 20 mA | 70000 m3/h | - | Endress+Hauser | t-mass I 300 (Thermal Mass Flow) | 6I3BL3-83L4/0 | 1" NPT Insertion Sensor | 4-20mA HART / 24VDC | - | - | - | 1 | - | C1 | S10 | C1S10,02 (AI) | FT-60201_AI_1 | 1756-IF16-2 | =CA1+MCP-M1 | JB-601 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
20 | FT-60210 | - | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) | Thermal Mass Flow Transmitter | 4 - 20 mA | 126000 m3/h | - | Endress+Hauser | t-mass F 300 (Thermal Mass Flow) | 6F3B1H-3ND2/0 | DN100 4" Cl.150 RF Flange | 4-20mA HART / 24VDC | - | - | - | 2 | - | C2 | S11 | C2S11,09 (AI); C2S11,11 (AI) | FT-60210_AI_1; FT-60210_AI_2 | 1756-IF16-11, 1756-IF16-9 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
21 | FT-60211 | - | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) | Thermal Mass Flow Transmitter | 4 - 20 mA | 126000 m3/h | - | Endress+Hauser | t-mass F 300 (Thermal Mass Flow) | 6F3B1H-3ND2/0 | DN100 4" Cl.150 RF Flange | 4-20mA HART / 24VDC | - | - | - | 2 | - | C2 | S11 | C2S11,10 (AI); C2S11,12 (AI) | FT-60211_AI_1; FT-60211_AI_2 | 1756-IF16-10, 1756-IF16-12 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
22 | FT-60261FA | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #1 (AMTV-11A) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,02 (AI) | FT-60261FA_AI_1 | 1756-IF16-2 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
23 | FT-60261FB | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #2 (AMTV-11A) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,03 (AI) | FT-60261FB_AI_1 | 1756-IF16-3 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
24 | FT-60261FC | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #3 (AMTV-11A) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,04 (AI) | FT-60261FC_AI_1 | 1756-IF16-4 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
25 | FT-60261FD | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #4 (AMTV-11A) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,05 (AI) | FT-60261FD_AI_1 | 1756-IF16-5 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
26 | FT-60262FE | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #5 (AMTV-11B) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,06 (AI) | FT-60262FE_AI_1 | 1756-IF16-6 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
27 | FT-60262FF | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #6 (AMTV-11B) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,07 (AI) | FT-60262FF_AI_1 | 1756-IF16-7 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
28 | FT-60262FG | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #7 (AMTV-11B) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,08 (AI) | FT-60262FG_AI_1 | 1756-IF16-8 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
29 | FT-60262FH | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #8 (AMTV-11B) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,09 (AI) | FT-60262FH_AI_1 | 1756-IF16-9 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
30 | FT-60263FJ | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #9 (AMTV-11C) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,10 (AI) | FT-60263FJ_AI_1 | 1756-IF16-10 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
31 | FT-60263FK | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #10 (AMTV-11C) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,11 (AI) | FT-60263FK_AI_1 | 1756-IF16-11 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
32 | FT-60263FL | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #11 (AMTV-11C) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,12 (AI) | FT-60263FL_AI_1 | 1756-IF16-12 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
33 | FT-60263FM | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #12 (AMTV-11C) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,13 (AI) | FT-60263FM_AI_1 | 1756-IF16-13 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
34 | FT-60264FN | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #13 (AMTV-11D) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,14 (AI) | FT-60264FN_AI_1 | 1756-IF16-14 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
35 | FT-60264FP | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #14 (AMTV-11D) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,15 (AI) | FT-60264FP_AI_1 | 1756-IF16-15 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
36 | FT-60264FQ | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #15 (AMTV-11D) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S13 | C2S13,00 (AI) | FT-60264FQ_AI_1 | 1756-IF16-0 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
37 | FT-60264FR | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #16 (AMTV-11D) | Ultrasonic Flow Transmitter | 4 - 20 mA | 0 to 100 l/h | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | - | - | - | 1 | - | C2 | S13 | C2S13,01 (AI) | FT-60264FR_AI_1 | 1756-IF16-1 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
38 | FT-61307 | FT-61307 | 325-01-613-PD-04 | Compressed air Flow | Thermal Mass Flow Transmitter | 4 - 20 mA | 0 - 1000 m3/hr | - | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | 8E3B50 Series | Flange ASME B16.5 Cl.150 RF, 316L | 4-20mA HART / 24VDC Loop/Aux | - | - | - | 1 | - | C1 | S10 | C1S10,04 (AI) | FT-61307_AI_1 | 1756-IF16-4 | =CA1+MCP-M1 | JB-601 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
39 | FT-60203 | FT-60901 | 325-01-602-PD-09 | Culinary steam feed to Spray dryer | Vortex Flow Transmitter | 4 - 20 mA | 0 - 7000 kg/hr | - | Endress+Hauser | Prowirl F 200 (Vortex Flowmeter) | 7F2C Series | Flange ASME B16.5 Cl.300 RF, 316L | 4-20mA HART + Pulse / 24VDC | - | 1 | - | 1 | - | C4 | S01, S05 | C4S01,00 (DI); C4S05,01 (AI) | FT-60203_DI_1; FT-60203_AI_1 | 1756-IB32-0, 1756-IF16-1 | =CA1+MCP-M4 | JB-606 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
40 | FT-60202 | FT-60902 | 325-01-602-PD-09 | Steam feed to Spray dryer | Vortex Flow Transmitter | 4 - 20 mA | 0 - 2000 kg/hr | - | Endress+Hauser | Prowirl F 200 (Vortex Flowmeter) | 7F2C Series | Flange ASME B16.5 Cl.300 RF, 316L | 4-20mA HART + Pulse / 24VDC | - | 1 | - | 1 | - | C2 | S02, S10 | C2S02,00 (DI); C2S10,02 (AI) | FT-60202_DI_1; FT-60202_AI_1 | 1756-IB32-0, 1756-IF16-2 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
41 | FT-60204 | FT-61101 | 325-01-602-PD-10 | Compressed air Flow | Thermal Mass Flow Transmitter | 4 - 20 mA | 0 - 1000 m3/hr | - | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | 8E3B50 Series | Flange ASME B16.5 Cl.150 RF, 316L | 4-20mA HART / 24VDC Loop/Aux | - | - | - | 1 | - | C1 | S10 | C1S10,03 (AI) | FT-60204_AI_1 | 1756-IF16-3 | =CA1+MCP-M1 | JB-601 | WIRED | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 3 Pairs x 1.0 mm² + 3 Cores x 1.5 mm² | Individually & Overall Shielded Twisted Pairs | M20x1.5 Brass Nickel-Plated Ex d/e Gland | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
42 | FT-936201 | FT-90301 | 325-01-930-PD-01 | Process Water | Magnetic Flow Transmitter | 4 - 20 mA,Pulse | 0-1000kg/m³ | - | Endress+Hauser | Promag P 300 (Electromagnetic Flowmeter) | 5P3B Series | Flange ASME B16.5 Cl.150 RF, PTFE Liner | 4-20mA HART / 24VDC | - | 1 | - | 1 | - | C5 | S01, S04 | C5S01,02 (DI); C5S04,03 (AI) | FT-936201_DI_1; FT-936201_AI_1 | 1756-IB32-2, 1756-IF16-3 | =CA1+MCP-M5 | RIO-200 | WIRED | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 3 Pairs x 1.0 mm² + 3 Cores x 1.5 mm² | Individually & Overall Shielded Twisted Pairs | M20x1.5 Brass Nickel-Plated Ex d/e Gland | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
43 | FT-936202 | FT-93001 | 325-01-930-PD-02 | Process Water | Magnetic Flow Transmitter | 4 - 20 mA,Pulse | 0 - 20 m3/ hr | - | Endress+Hauser | Promag P 300 (Electromagnetic Flowmeter) | 5P3B Series | Flange ASME B16.5 Cl.150 RF, PTFE Liner | 4-20mA HART / 24VDC | - | 1 | - | 1 | - | C5 | S01, S04 | C5S01,03 (DI); C5S04,04 (AI) | FT-936202_DI_1; FT-936202_AI_1 | 1756-IB32-3, 1756-IF16-4 | =CA1+MCP-M5 | RIO-200 | WIRED | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 3 Pairs x 1.0 mm² + 3 Cores x 1.5 mm² | Individually & Overall Shielded Twisted Pairs | M20x1.5 Brass Nickel-Plated Ex d/e Gland | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
44 | HS-61307A | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 2 | - | - | - | C7 | S03 | C7S03,12 (DI) | HS-61307A_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
45 | HS-61307B | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S03 | C7S03,13 (DI) | HS-61307B_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
46 | HS-61307C | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S03 | C7S03,14 (DI) | HS-61307C_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
47 | HS-61307D | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S03 | C7S03,15 (DI) | HS-61307D_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
48 | HS-61307E | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S03 | C7S03,16 (DI) | HS-61307E_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
49 | HS-61307F | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S02 | C7S02,19 (DI) | HS-61307F_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
50 | HS-61307G | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S02 | C7S02,20 (DI) | HS-61307G_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
51 | HS-61307H | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S02 | C7S02,21 (DI) | HS-61307H_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
52 | HS-61307I | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S02 | C7S02,22 (DI) | HS-61307I_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
53 | HS-61307J | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S02 | C7S02,23 (DI) | HS-61307J_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
54 | HS-61307K | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S02 | C7S02,24 (DI) | HS-61307K_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
55 | HS-61307L | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S02 | C7S02,25 (DI) | HS-61307L_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
56 | HS-61307M | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S02 | C7S02,26 (DI) | HS-61307M_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
57 | HS-61307N | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S02 | C7S02,27 (DI) | HS-61307N_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
58 | HS-61307O | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S02 | C7S02,28 (DI) | HS-61307O_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
59 | HS-61307P | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S02 | C7S02,29 (DI) | HS-61307P_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
60 | HS-61307Q | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S02 | C7S02,30 (DI) | HS-61307Q_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
61 | HS-61307R | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | - | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C7 | S02 | C7S02,31 (DI) | HS-61307R_DI_1 |  | MCC | MCC | MCC | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
62 | HV-40203 | HV-4106 | 325-01-402-PD-01 | Slurry Drain tank TS-40201 | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C1 | S03 | C1S03,22 (DI) | HV-40203_DI_1 | 1756-IB32-22 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
63 | HV-40201 | HV-4108 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C1 | S03 | C1S03,20 (DI) | HV-40201_DI_1 | 1756-IB32-20 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
64 | HV-40204 | HV-4126 | 325-01-402-PD-01 | Slurry Drain tank TS-40202 | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C1 | S03 | C1S03,23 (DI) | HV-40204_DI_1 | 1756-IB32-23 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
65 | HV-40202 | HV-4128 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C1 | S03 | C1S03,21 (DI) | HV-40202_DI_1 | 1756-IB32-21 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
66 | HV-40206 | HV-4208 | 325-01-402-PD-01 | Slurry Drain tank TS-40203 | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C1 | S03 | C1S03,25 (DI) | HV-40206_DI_1 | 1756-IB32-25 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
67 | HV-40205 | HV-4210 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C1 | S03 | C1S03,24 (DI) | HV-40205_DI_1 | 1756-IB32-24 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
68 | HV-40207 | - | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C2 | S01 | C2S01,04 (DI) | HV-40207_DI_1 | 1756-IB32-4 | =CA1+MCP-M2 | JB-402 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
69 | HV-40208 | - | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C2 | S01 | C2S01,05 (DI) | HV-40208_DI_1 | 1756-IB32-5 | =CA1+MCP-M2 | JB-402 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
70 | LSH-60230 | - | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-21) | Level switch | Dry Contact | - | Ex t/d | Endress+Hauser | Soliphant FTM51 (Vibrating Fork for Solids) | FTM51 Series | Thread 1-1/2" NPT / Flange | 24VDC / Relay Contact Output | - | 1 | - | - | - | C3 | S01 | C3S01,03 (DI) | LSH-60230_DI_1 | 1756-IB32-3 | =CA1+MCP-M3 | IS-JB-603 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
71 | LSH-60231 | - | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-22) | Level switch | Dry Contact | - | Ex t/d | Endress+Hauser | Soliphant FTM51 (Vibrating Fork for Solids) | FTM51 Series | Thread 1-1/2" NPT / Flange | 24VDC / Relay Contact Output | - | 1 | - | - | - | C3 | S01 | C3S01,04 (DI) | LSH-60231_DI_1 | 1756-IB32-4 | =CA1+MCP-M3 | IS-JB-603 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
72 | LSH-60240 | - | 325-01-602-PD-05 | Powder Level Switch High for Bag House (BGHS-21) | Level switch | Dry Contact | - | Ex t/d | Endress+Hauser | Soliphant FTM51 (Vibrating Fork for Solids) | FTM51 Series | Thread 1-1/2" NPT / Flange | 24VDC / Relay Contact Output | - | 1 | - | - | - | C3 | S01 | C3S01,05 (DI) | LSH-60240_DI_1 | 1756-IB32-5 | =CA1+MCP-M3 | IS-JB-603 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
73 | LSH-60250 | - | 325-01-602-PD-05 | Water Level Switch High for Fire Deluge Pipe (FWDP-21) | Level switch | Dry Contact | - | - | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | FTL51B Series | Thread 3/4" NPT / Tri-Clamp | 24VDC / Relay Contact Output | - | 1 | - | - | - | C4 | S01 | C4S01,01 (DI) | LSH-60250_DI_1 | 1756-IB32-1 | =CA1+MCP-M4 | JB-606 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
74 | LSH-60251 | - | 325-01-602-PD-04 | Water Level Switch High for Fire Deluge Pipe (FWDP-22) | Level switch | Dry Contact | - | - | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | FTL51B Series | Thread 3/4" NPT / Tri-Clamp | 24VDC / Relay Contact Output | - | 1 | - | - | - | C2 | S02 | C2S02,01 (DI) | LSH-60251_DI_1 | 1756-IB32-1 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
75 | LSL-60201 | LSL-61101 | 325-01-602-PD-11 | Level low switch | Level switch | Dry Contact | - | - | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | FTL51B Series | Thread 3/4" NPT / Tri-Clamp | 24VDC / Relay Contact Output | - | 1 | - | - | - | C1 | S05 | C1S05,18 (DI) | LSL-60201_DI_1 | 1756-IB32-18 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
76 | LSH-61301 | - | 325-01-613-PD-01 | Level alarm high | Level switch | Dry Contact | - | Ex t/d | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | FTL51B Series | Thread 3/4" NPT / Tri-Clamp | 24VDC / Relay Contact Output | - | 1 | - | - | - | C3 | S02 | C3S02,01 (DI) | LSH-61301_DI_1 | 1756-IB32-1 | =CA1+MCP-M3 | IS-JB-618 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
77 | LSL-61302 | - | 325-01-613-PD-01 | Level alarm low | Level switch | Dry Contact | - | Ex t/d | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | FTL51B Series | Thread 3/4" NPT / Tri-Clamp | 24VDC / Relay Contact Output | - | 1 | - | - | - | C3 | S02 | C3S02,05 (DI) | LSL-61302_DI_1 | 1756-IB32-5 | =CA1+MCP-M3 | IS-JB-618 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
78 | LS-61303 | - | 325-01-613-PD-01 | Level switch | Level switch | Dry Contact | - | Ex t/d | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | FTL51B Series | Thread 3/4" NPT / Tri-Clamp | 24VDC / Relay Contact Output | - | 1 | - | - | - | C3 | S01 | C3S01,20 (DI) | LS-61303_DI_1 | 1756-IB32-20 | =CA1+MCP-M3 | JB-618 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
79 | LSH-61304 | - | 325-01-613-PD-03 | Big bag level alarm high | Level switch | Dry Contact | - | Ex t/d | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | FTL51B Series | Thread 3/4" NPT / Tri-Clamp | 24VDC / Relay Contact Output | - | 1 | - | - | - | C4 | S03 | C4S03,02 (DI) | LSH-61304_DI_1 | 1756-IB32-2 | =CA1+MCP-M4 | IS-JB-612 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
80 | LSH-61305 | - | 325-01-613-PD-05 | Big bag level alarm high | Level switch | Dry Contact | - | Ex t/d | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | FTL51B Series | Thread 3/4" NPT / Tri-Clamp | 24VDC / Relay Contact Output | - | 1 | - | - | - | C4 | S03 | C4S03,03 (DI) | LSH-61305_DI_1 | 1756-IB32-3 | =CA1+MCP-M4 | IS-JB-612 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
81 | LSH-61306 | - | 325-01-613-PD-01 | Level alarm high | Level switch | Dry Contact | - | Ex t/d | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | FTL51B Series | Thread 3/4" NPT / Tri-Clamp | 24VDC / Relay Contact Output | - | 1 | - | - | - | C3 | S02 | C3S02,03 (DI) | LSH-61306_DI_1 | 1756-IB32-3 | =CA1+MCP-M3 | IS-JB-618 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
82 | LSH-61307 | - | 325-01-613-PD-01 | High Level alarm reject screen | Level switch | Dry Contact | - | Ex t/d | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | FTL51B Series | Thread 3/4" NPT / Tri-Clamp | 24VDC / Relay Contact Output | - | 1 | - | - | - | C4 | S03 | C4S03,04 (DI) | LSH-61307_DI_1 | 1756-IB32-4 | =CA1+MCP-M4 | IS-JB-612 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
83 | LSH-61308 | - | 325-01-613-PD-01 | High Level alarm Cooling cyclone | Level switch | Dry Contact | - | Ex t/d | Endress+Hauser | Soliphant FTM51 (Vibrating Fork for Solids) | FTM51 Series | Thread 1-1/2" NPT / Flange | 24VDC / Relay Contact Output | - | 1 | - | - | - | C3 | S02 | C3S02,04 (DI) | LSH-61308_DI_1 | 1756-IB32-4 | =CA1+MCP-M3 | IS-JB-618 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
84 | LSH-61312 | - | 325-01-613-PD-05 | Level alarm high | Level switch | Dry Contact | - | Ex t/d | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | FTL51B Series | Thread 3/4" NPT / Tri-Clamp | 24VDC / Relay Contact Output | - | 1 | - | - | - | C4 | S03 | C4S03,05 (DI) | LSH-61312_DI_1 | 1756-IB32-5 | =CA1+MCP-M4 | IS-JB-612 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
85 | LSL-814201 | LSL-81001 | 325-01-814-PD-01 | Low Level alarm | - | Dry Contact | - | Ex t/d | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | FTL51B Series | Thread 3/4" NPT / Tri-Clamp | 24VDC / Relay Contact Output | - | 1 | - | - | - | C5 | S01 | C5S01,04 (DI) | LSL-814201_DI_1 | 1756-IB32-4 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
86 | LT-40201 | LT-40101 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 1 | Level transmitter | 4 - 20 mA | 0 - 10 m. | - | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic Level) | PMP43 Flush Diaphragm | Universal Clamp / Flush Mount | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C1 | S09 | C1S09,04 (AI) | LT-40201_AI_1 | 1756-IF16-4 | =CA1+MCP-M1 | JB-401 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
87 | LT-40202 | LT-40102 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 2 | Level transmitter | 4 - 20 mA | 0 - 10 m. | - | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic Level) | PMP43 Flush Diaphragm | Universal Clamp / Flush Mount | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C1 | S09 | C1S09,05 (AI) | LT-40202_AI_1 | 1756-IF16-5 | =CA1+MCP-M1 | JB-401 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
88 | LT-40203 | LT-40201 | 325-01-402-PD-02 | Level transmitter in Spray dryer infeed tank | Level transmitter | 4 - 20 mA | 0 - 10 m. | - | Endress+Hauser | Micropilot FMR67B (80GHz Radar Level) | FMR67B Series | Flange DN80 3" / Cl.150 | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C1 | S09 | C1S09,03 (AI) | LT-40203_AI_1 | 1756-IF16-3 | =CA1+MCP-M1 | JB-401 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
89 | LT-61301 | - | 325-01-613-PD-01 | Level powder in silo | Level transmitter | 4 - 20 mA | - | Ex ia | Endress+Hauser | Micropilot FMR67B (80GHz Radar Level) | FMR67B Series | Flange DN80 3" / Cl.150 | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S05 | C3S05,06 (AI) | LT-61301_AI_1 | 1756-IF16-6 | =CA1+MCP-M3 | IS-JB-618 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
90 | pHT-40201 | pHT-40101 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 1 | pH Analyzer | 4 - 20 mA | 0-14 | - | Mettler Toledo | M300G2 + InPro3250i (pH System) | M300G2 4-Wire + InTrac 777P | DN25 Weld-in Socket w/ InTrac 777P | 4-20mA HART + Relay / 24VDC | - | 1 | - | 1 | - | C1 | S09 | C1S09,06 (AI) | pHT-40201_AI_1 | 1756-IF16-6 | =CA1+MCP-M1 | JB-401 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
91 | pHT-40202 | pHT-40102 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 2 | pH Analyzer | 4 - 20 mA | 0-14 | - | Mettler Toledo | M300G2 + InPro3250i (pH System) | M300G2 4-Wire + InTrac 777P | DN25 Weld-in Socket w/ InTrac 777P | 4-20mA HART + Relay / 24VDC | - | 1 | - | 1 | - | C1 | S09 | C1S09,07 (AI) | pHT-40202_AI_1 | 1756-IF16-7 | =CA1+MCP-M1 | JB-401 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
92 | PSL-60220 | - | 325-01-602-PD-04 | Gas Pressure Switch Low for Spray Chamber (CHAM-21) | Pressure switch | Dry Contact | -0.01 mbar | - | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | PTC31B Series | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C2 | S02 | C2S02,02 (DI) | PSL-60220_DI_1 | 1756-IB32-2 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
93 | PSL-61301 | - | 325-01-613-PD-01 | Pressure alarm low | Pressure switch | Dry Contact | 0.3-0.7barg | - | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | PTC31B Series | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C3 | S01 | C3S01,21 (DI) | PSL-61301_DI_1 | 1756-IB32-21 | =CA1+MCP-M3 | JB-618 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
94 | PSL-61302 | - | 325-01-613-PD-01 | Pressure alarm low | Pressure switch | Dry Contact | 40 mbarg | - | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | PTC31B Series | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C3 | S01 | C3S01,22 (DI) | PSL-61302_DI_1 | 1756-IB32-22 | =CA1+MCP-M3 | JB-618 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
95 | PSL-61305 | - | 325-01-613-PD-03 | Pressure alarm low | Pressure switch | Dry Contact | - | - | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | PTC31B Series | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C4 | S02 | C4S02,00 (DI) | PSL-61305_DI_1 | 1756-IB32-0 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
96 | PSL-61306 | - | 325-01-613-PD-05 | Pressure alarm low | Pressure switch | Dry Contact | - | - | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | PTC31B Series | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C4 | S02 | C4S02,01 (DI) | PSL-61306_DI_1 | 1756-IB32-1 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
97 | PSL-61311 | - | 325-01-613-PD-04 | Pressure alarm low | Pressure switch | Dry Contact | - | - | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | PTC31B Series | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C3 | S02 | C3S02,23 (DI) | PSL-61311_DI_1 | 1756-IB32-23 | =CA1+MCP-M3 | JB-618 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
98 | PT-40201 | - | 325-01-402-PD-02 | Pressure Transmitter for Inlet Filter Strainer (FSTR-11) | Pressure Transmitter | 4 - 20 mA | -100 to 500 mBar | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C1 | S09 | C1S09,08 (AI) | PT-40201_AI_1 | 1756-IF16-8 | =CA1+MCP-M1 | JB-401 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
99 | PT-40202 | - | 325-01-402-PD-02 | Feed Slurry Pressure Transmitter for Pipe (PIPE) | Pressure Transmitter | 4 - 20 mA | 0 - 10'barg | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C1 | S09 | C1S09,09 (AI) | PT-40202_AI_1 | 1756-IF16-9 | =CA1+MCP-M1 | JB-401 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
100 | PT-40222 | - | 325-01-402-PD-02 | Jet Cooker | Pressure Transmitter | 4 - 20 mA | 0 - 12'barg | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S09 | C2S09,04 (AI) | PT-40222_AI_1 | 1756-IF16-4 | =CA1+MCP-M2 | JB-402 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
101 | PT-60201 | - | 325-01-602-PD-02 | Steam feed to Spray dryer | Pressure Transmitter | 4 - 20 mA | 0 - 20 bar | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S13 | C2S13,02 (AI) | PT-60201_AI_1 | 1756-IF16-2 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
102 | PT-60202 | - | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter | 4 - 20 mA | 0 to 500 bar | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C1 | S09 | C1S09,10 (AI) | PT-60202_AI_1 | 1756-IF16-10 | =CA1+MCP-M1 | JB-401 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
103 | PT-60203 | - | 325-01-602-PD-08 | Gas Pressure Transmitter for Cool Air Duct (DTCA-32) | Pressure Transmitter | 4 - 20 mA | 0 - 0.1 mbar | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C1 | S10 | C1S10,05 (AI) | PT-60203_AI_1 | 1756-IF16-5 | =CA1+MCP-M1 | JB-601 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
104 | PT-60210 | - | 325-01-602-PD-03 | Gas Pressure Transmitter for Hot Air Duct (DTHA-21) | Pressure Transmitter | 4 - 20 mA | 0 - 0.1 mbar | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S10 | C2S10,03 (AI) | PT-60210_AI_1 | 1756-IF16-3 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
105 | PT-60215 | - | 325-01-602-PD-03 | 15% Polypropylene Glycol Pressure Indicator Transmitter for Heat Recovery Pumping Skid (PUCF-21) | Pressure Transmitter | 4 - 20 mA | 0 - 6 bar | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S10 | C2S10,04 (AI) | PT-60215_AI_1 | 1756-IF16-4 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
106 | PT-60216 | - | 325-01-602-PD-03 | Gas Pressure Transmitter for Combustion Air Burner Duct (DTCB-21) | Pressure Transmitter | 4 - 20 mA | 0 - 100 mbar | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S10 | C2S10,05 (AI) | PT-60216_AI_1 | 1756-IF16-5 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
107 | PT-60220 | - | 325-01-602-PD-04 | Gas Pressure Transmitter for Chamber (CHAM-21) | Pressure Transmitter | 4 - 20 mA | -100 - 100 mbar | Ex ic | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C4 | S06 | C4S06,00 (AI) | PT-60220_AI_1 | 1756-IF16-0 | =CA1+MCP-M4 | IS-JB-608 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
108 | PT-60221 | - | 325-01-602-PD-04 | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25) | Pressure Transmitter | 4 - 20 mA | 0 - 0.1 mbar | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S13 | C2S13,04 (AI); C2S13,05 (AI) | PT-60221_AI_1; PT-60221_AI_1 | 1756-IF16-4, 1756-IF16-5 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
109 | PT-60230 | - | 325-01-602-PD-04 | Gas Pressure Transmitter for Conveying Duct (DTCO-21) | Pressure Transmitter | 4 - 20 mA | 0 - 0.1 mbar | Ex ic | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S04 | C3S04,00 (AI) | PT-60230_AI_1 | 1756-IF16-0 | =CA1+MCP-M3 | IS-JB-603 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
110 | PT-60231 | - | 325-01-602-PD-04 | Gas Pressure Transmitter for Cyclone Exhaust Duct (DTCE-21) | Pressure Transmitter | 4 - 20 mA | -100 to 200 mbar | Ex ic | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S04 | C3S04,01 (AI) | PT-60231_AI_1 | 1756-IF16-1 | =CA1+MCP-M3 | IS-JB-603 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
111 | PT-60240 | - | 325-01-602-PD-05 | Gas Pressure Transmitter for Bag House Exhaust Duct (DTEX-22) | Pressure Transmitter | 4 - 20 mA | -100 to 200 mbar | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S10 | C2S10,06 (AI) | PT-60240_AI_1 | 1756-IF16-6 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
112 | PT-60241 | - | 325-01-602-PD-05 | Gas Pressure Transmitter for Exhaust Fan (FANE-21) | Pressure Transmitter | 4 - 20 mA | 0 - 0.1 mbar | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S10 | C2S10,07 (AI) | PT-60241_AI_1 | 1756-IF16-7 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
113 | PT-60204 | PT-61101 | 325-01-602-PD-10 | Pressure transmitter | Pressure Transmitter | 4 - 20 mA | 0 - 10 barg | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C1 | S10 | C1S10,06 (AI) | PT-60204_AI_1 | 1756-IF16-6 | =CA1+MCP-M1 | JB-601 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
114 | PT-61301 | - | 325-01-613-PD-01 | Pressure in silo | Pressure Transmitter | 4 - 20 mA | 0 - 1 barg | Ex ic | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S05 | C3S05,07 (AI) | PT-61301_AI_1 | 1756-IF16-7 | =CA1+MCP-M3 | IS-JB-618 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
115 | PT-61302 | - | 325-01-613-PD-03 | Pressure in vacuum line | Pressure Transmitter | 4 - 20 mA | -100 - 100 mbarg | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C4 | S05 | C4S05,08 (AI); C4S05,12 (AI) | PT-61302_AI_1; PT-61302_AI_1 | 1756-IF16-12, 1756-IF16-8 | =CA1+MCP-M4 | JB-612 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
116 | PT-61303 | - | 325-01-613-PD-01 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) | Pressure Transmitter | 4 - 20 mA | -100 to 200 mbar | Ex ic | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S05 | C3S05,00 (AI); C3S05,08 (AI) | PT-61303_AI_1; PT-61303_AI_1 | 1756-IF16-0, 1756-IF16-8 | =CA1+MCP-M3 | IS-JB-618, JB-618 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
117 | PT-61304 | - | 325-01-613-PD-01 | Gas Pressure Transmitter for Storage Bin Cyclone Inlet Duct (CYCL-31) | Pressure Transmitter | 4 - 20 mA | -100 to 200 mbar | Ex ic | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S05 | C3S05,09 (AI) | PT-61304_AI_1 | 1756-IF16-9 | =CA1+MCP-M3 | IS-JB-618 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
118 | PT-61305 | - | 325-01-613-PD-01 | Gas Pressure Transmitter for Exhaust Duct (DTEX-31) | Pressure Transmitter | 4 - 20 mA | -100 to 200 mbar | Ex ic | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S05 | C3S05,10 (AI) | PT-61305_AI_1 | 1756-IF16-10 | =CA1+MCP-M3 | IS-JB-618 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
119 | PT-61309 | - | 325-01-613-PD-04 | Pressure transmitter | Pressure Transmitter | 4 - 20 mA | 0 - 10 barg | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C4 | S05 | C4S05,09 (AI); C4S05,13 (AI) | PT-61309_AI_1; PT-61309_AI_1 | 1756-IF16-13, 1756-IF16-9 | =CA1+MCP-M4 | JB-612 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
120 | PCV-60201 | PV-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic Control valve | 4 - 20 mA | 0 - 100% | - | Samson | Type 3241 Globe Valve + Trovis 3730-1 Positioner | 3241-ANSI + 3730-1 Positioner | Flange ASME B16.5 Cl.150/300 RF | 4-20mA Setpoint + 4-20mA Feedback | - | - | 1 | - | - | C3 | S13 | C3S13,03 (AO) | PV-60201_AO_1 | 1756-OF8-3 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 2Px1.0 (Setpoint AO + Position Feedback AI) (Ref: LiY-CY TP 2P x1.0) | 2 Pairs x 1.0 mm² (Individually & Overall Shielded) | Individual Foil Screen per Pair + Overall Tinned Copper Braid | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
121 | SV-40201 | SV-40101 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 1 | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C1 | S07 | C1S07,24 (DO) | SV-40201_DO_1 | 1756-OB32-24 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
122 | SV-40202 | SV-40102 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 2 | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C1 | S07 | C1S07,25 (DO) | SV-40202_DO_1 | 1756-OB32-25 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
123 | SV-40203 | SV-40103 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 1 | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C1 | S07 | C1S07,26 (DO) | SV-40203_DO_1 | 1756-OB32-26 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
124 | SV-40204 | SV-40104 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 2 | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C1 | S07 | C1S07,27 (DO) | SV-40204_DO_1 | 1756-OB32-27 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
125 | SV-60220 | - | 325-01-602-PD-04 | PA On/Off Valve for Chamber PSE purge air (CHAM-21) | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C4 | S04 | C4S04,00 (DO) | SV-60220_DO_1 | 1756-OB32-0 | =CA1+MCP-M4 | JB-606 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
126 | SV-60230 | - | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 27 (CYCL-21) | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C1 | S08 | C1S08,18 (DO) | SV-60230_DO_1 | 1756-OB32-18 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
127 | SV-60231 | - | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 28 (CYCL-22) | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C1 | S08 | C1S08,21 (DO) | SV-60231_DO_1 | 1756-OB32-21 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
128 | SV-60240A | - | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29A (BGHS-21) | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C1 | S08 | C1S08,20 (DO) | SV-60240A_DO_1 | 1756-OB32-20 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
129 | SV-60240B | - | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29B (BGHS-21) | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C1 | S08 | C1S08,22 (DO) | SV-60240B_DO_1 | 1756-OB32-22 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
130 | SV-60240C | - | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29C (BGHS-21) | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C1 | S08 | C1S08,23 (DO) | SV-60240C_DO_1 | 1756-OB32-23 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
131 | SV-61301 | - | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C3 | S03 | C3S03,02 (DO) | SV-61301_DO_1 | 1756-OB32-2 | =CA1+MCP-M3 | JB-618 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
132 | SV-61302 | - | 325-01-613-PD-01 | Air service | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C3 | S03 | C3S03,03 (DO) | SV-61302_DO_1 | 1756-OB32-3 | =CA1+MCP-M3 | JB-618 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
133 | SV-61303 | - | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C3 | S03 | C3S03,04 (DO) | SV-61303_DO_1 | 1756-OB32-4 | =CA1+MCP-M3 | JB-618 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
134 | SV-61305 | - | 325-01-613-PD-01 | Air service | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C3 | S03 | C3S03,06 (DO) | SV-61305_DO_1 | 1756-OB32-6 | =CA1+MCP-M3 | JB-618 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
135 | SV-61308 | - | 325-01-613-PD-03 | Timer compress air pluse solenoid valve | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C4 | S04 | C4S04,19 (DO) | SV-61308_DO_1 | 1756-OB32-19 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
136 | SV-61309 | - | 325-01-613-PD-03 | Air service | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C4 | S04 | C4S04,20 (DO) | SV-61309_DO_1 | 1756-OB32-20 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
137 | SV-61310 | - | 325-01-613-PD-05 | Timer compress air pluse solenoid valve | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C4 | S04 | C4S04,21 (DO) | SV-61310_DO_1 | 1756-OB32-21 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
138 | SV-61311 | - | 325-01-613-PD-05 | Air service | Solenoid valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | - | - | - | - | C4 | S04 | C4S04,22 (DO) | SV-61311_DO_1 | 1756-OB32-22 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
139 | TSH-60230 | - | 325-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | Temperature Switch | Dry Contact | 0 - 140 C | Ex d | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | TTR35 Series | 1/2" NPT w/ Hygienic Adapter | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C2 | S02 | C2S02,03 (DI) | TSH-60230_DI_1 | 1756-IB32-3 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
140 | TSH-60240 | - | 325-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | Temperature Switch | Dry Contact | 0 - 140 C | Ex d | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | TTR35 Series | 1/2" NPT w/ Hygienic Adapter | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C2 | S02 | C2S02,04 (DI) | TSH-60240_DI_1 | 1756-IB32-4 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
141 | TT-40221 | - | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter | 4 - 20 mA | 0 - 120 C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S09 | C2S09,05 (AI) | TT-40221_AI_1 | 1756-IF16-5 | =CA1+MCP-M2 | JB-402 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
142 | TT-40222 | - | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter | 4 - 20 mA | 0 - 200 C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S09 | C2S09,06 (AI) | TT-40222_AI_1 | 1756-IF16-6 | =CA1+MCP-M2 | JB-402 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
143 | TT-60201 | - | 325-01-602-PD-02 | Steam feed to Spray dryer | Temperature Transmitter | 4 - 20 mA | 0 - 300 C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S13 | C2S13,07 (AI) | TT-60201_AI_1 | 1756-IF16-7 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
144 | TT-60210 | - | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S10 | C2S10,08 (AI) | TT-60210_AI_1 | 1756-IF16-8 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
145 | TT-60212A | - | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter | 4 - 20 mA | 0 - 100 C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S10 | C2S10,12 (AI) | TT-60212A_AI_1 | 1756-IF16-12 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
146 | TT-60212B | - | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter | 4 - 20 mA | 0 - 100 C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S10 | C2S10,13 (AI) | TT-60212B_AI_1 | 1756-IF16-13 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
147 | TT-60211 | - | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S10 | C2S10,11 (AI) | TT-60211_AI_1 | 1756-IF16-11 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
148 | TT-60214 | - | 325-01-602-PD-03 | Steam Temperature Transmitter for Cold Air Duct (DTCA-23) | Temperature Transmitter | 4 - 20 mA | -10 to 250°C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S10 | C2S10,14 (AI) | TT-60214_AI_1 | 1756-IF16-14 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
149 | TT-60215A | - | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter | 4 - 20 mA | -10 to 150°C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S10 | C2S10,15 (AI) | TT-60215A_AI_1 | 1756-IF16-15 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
150 | TT-60215B | - | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter | 4 - 20 mA | -10 to 150°C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S11 | C2S11,00 (AI) | TT-60215B_AI_1 | 1756-IF16-0 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
151 | TT-60216 | - | 325-01-602-PD-03 | Gas Temperature Transmitter for Combustion Air Burner Duct (DTCB-21) | Temperature Transmitter | 4 - 20 mA | 0 - 200'°C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S11 | C2S11,01 (AI) | TT-60216_AI_1 | 1756-IF16-1 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
152 | TT-60220 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | Ex ic | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C4 | S06 | C4S06,01 (AI) | TT-60220_AI_1 | 1756-IF16-1 | =CA1+MCP-M4 | IS-JB-608 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
153 | TT-60221 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | Ex ic | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C4 | S06 | C4S06,02 (AI) | TT-60221_AI_1 | 1756-IF16-2 | =CA1+MCP-M4 | IS-JB-608 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
154 | TT-60222 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | Ex ic | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C4 | S06 | C4S06,03 (AI) | TT-60222_AI_1 | 1756-IF16-3 | =CA1+MCP-M4 | IS-JB-608 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
155 | TT-60223 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | Ex ic | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C4 | S06 | C4S06,04 (AI) | TT-60223_AI_1 | 1756-IF16-4 | =CA1+MCP-M4 | IS-JB-608 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
156 | TT-60224 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | Ex ic | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S04 | C3S04,02 (AI) | TT-60224_AI_1 | 1756-IF16-2 | =CA1+MCP-M3 | IS-JB-603 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
157 | TT-60225 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | Ex ic | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S04 | C3S04,03 (AI) | TT-60225_AI_1 | 1756-IF16-3 | =CA1+MCP-M3 | IS-JB-603 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
158 | TT-60226 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | Ex ic | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S04 | C3S04,04 (AI) | TT-60226_AI_1 | 1756-IF16-4 | =CA1+MCP-M3 | IS-JB-603 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
159 | TT-60227 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | Ex ic | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S04 | C3S04,05 (AI) | TT-60227_AI_1 | 1756-IF16-5 | =CA1+MCP-M3 | IS-JB-603 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
160 | TT-60230 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Conveying Duct (DTCO-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | Ex ic | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S04 | C3S04,06 (AI) | TT-60230_AI_1 | 1756-IF16-6 | =CA1+MCP-M3 | IS-JB-603 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
161 | TT-60240 | - | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Fan (FANE-21) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S11 | C2S11,02 (AI) | TT-60240_AI_1 | 1756-IF16-2 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
162 | TT-60241A | - | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter | 4 - 20 mA | 0 - 100 C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S11 | C2S11,03 (AI) | TT-60241A_AI_1 | 1756-IF16-3 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
163 | TT-60241B | - | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter | 4 - 20 mA | 0 - 100 C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S11 | C2S11,04 (AI) | TT-60241B_AI_1 | 1756-IF16-4 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
164 | TT-60245 | - | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Stack (DTXS-21) | Temperature Transmitter | 4 - 20 mA | -10 to 150°C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C4 | S05 | C4S05,02 (AI) | TT-60245_AI_1 | 1756-IF16-2 | =CA1+MCP-M4 | JB-608 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
165 | TT-60202 | TT-60702 | 325-01-602-PD-07 | Compress air temp to camera | Temperature Transmitter | 4 - 20 mA | 0 - 40 C | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S13 | C2S13,08 (AI) | TT-60202_AI_1 | 1756-IF16-8 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
166 | TT-61301 | - | 325-01-613-PD-01 | Gas Temperature Transmitter for Cold Air Duct (DTCA-32) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | Ex ic | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S05 | C3S05,11 (AI) | TT-61301_AI_1 | 1756-IF16-11 | =CA1+MCP-M3 | IS-JB-618 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
167 | TT-61302 | - | 325-01-613-PD-01 | Gas and Powder Temperature Transmitter for Cooling Cyclone (CYCL-31) | Temperature Transmitter | 4 - 20 mA | 0 - 400'°C | Ex ic | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C3 | S05 | C3S05,12 (AI) | TT-61302_AI_1 | 1756-IF16-12 | =CA1+MCP-M3 | IS-JB-618 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
168 | TCV-40222 | - | 325-01-402-PD-02 | Jet Cooker | Automatic Control valve | 4 - 20 mA | 0 - 100% | - | Samson | Type 3241 Globe Valve + Trovis 3730-1 Positioner | 3241-ANSI + 3730-1 Positioner | Flange ASME B16.5 Cl.150/300 RF | 4-20mA Setpoint + 4-20mA Feedback | - | - | 1 | - | - | C3 | S13 | C3S13,00 (AO) | TCV-40222_AO_1 | 1756-OF8-0 | =CA1+MCP-M2 | JB-402 | WIRED | LiY-CY TP 2Px1.0 (Setpoint AO + Position Feedback AI) (Ref: LiY-CY TP 1P x1.0) | 2 Pairs x 1.0 mm² (Individually & Overall Shielded) | Individual Foil Screen per Pair + Overall Tinned Copper Braid | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
169 | TCV-60214 | TV-60214 | 325-01-602-PD-03 | Steam Temperature Valve for Pre-Heat Steam Heat Exchanger (HXCH-21) | Automatic Control valve | 4 - 20 mA | 0 - 100% | - | Samson | Type 3241 Globe Valve + Trovis 3730-1 Positioner | 3241-ANSI + 3730-1 Positioner | Flange ASME B16.5 Cl.150/300 RF | 4-20mA Setpoint + 4-20mA Feedback | - | - | 1 | - | - | C3 | S13 | C3S13,02 (AO) | TV-60214_AO_1 | 1756-OF8-2 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 2Px1.0 (Setpoint AO + Position Feedback AI) (Ref: LiY-CY TP 1P x1.0) | 2 Pairs x 1.0 mm² (Individually & Overall Shielded) | Individual Foil Screen per Pair + Overall Tinned Copper Braid | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
170 | TCV-60202 | TV-60702 | 325-01-602-PD-07 | Chiller water control valve | 3-way Control valve | 4 - 20 mA | 0 - 100% | - | Samson | Type 3241 Globe Valve + Trovis 3730-1 Positioner | 3241-ANSI + 3730-1 Positioner | Flange ASME B16.5 Cl.150/300 RF | 4-20mA Setpoint + 4-20mA Feedback | - | - | 1 | - | - | - | - | - | - | - | - | - | UNMAPPED | LiY-CY TP 2Px1.0 (Setpoint AO + Position Feedback AI) | 2 Pairs x 1.0 mm² (Individually & Overall Shielded) | Individual Foil Screen per Pair + Overall Tinned Copper Braid | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
171 | VT-60210A | - | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter | 4 - 20 mA | mm/sec | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | 1 | - | C2 | S11 | C2S11,05 (AI) | VT-60210A_AI_1 | 1756-IF16-5 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
172 | VT-60210B | - | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter | 4 - 20 mA | mm/sec | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | 1 | - | C2 | S11 | C2S11,06 (AI) | VT-60210B_AI_1 | 1756-IF16-6 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
173 | VT-60241A | - | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter | 4 - 20 mA | mm/sec | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | 1 | - | C2 | S11 | C2S11,07 (AI) | VT-60241A_AI_1 | 1756-IF16-7 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
174 | VT-60241B | - | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter | 4 - 20 mA | mm/sec | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | 1 | - | C2 | S11 | C2S11,08 (AI) | VT-60241B_AI_1 | 1756-IF16-8 | =CA1+MCP-M2 | JB-602 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
175 | XT-60201 | XT-60301 | 325-01-402-PD-03 | LEL gas analyzer | Gas detector | 4 - 20 mA | 0-10%LEL | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | 1 | - | C4 | S06 | C4S06,05 (AI) | XT-60201_AI_1 | 1756-IF16-5 | =CA1+MCP-M4 | IS-JB-608 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
176 | XA-60201 | XA-60301 | 325-01-402-PD-03 | LEL gas Buzzer Alarm | Gas detector | 4 - 20 mA | 0-10%LEL | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C4 | S04 | C4S04,08 (DO) | XA-60201_DO_1 | 1756-OB32-8 | =CA1+MCP-M4 | IS-JB-608 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
177 | XT-92201 | - | 325-01-923-PD-03 | LEL gas analyzer | Gas detector | 4 - 20 mA | 0-10%LEL | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | 1 | - | C5 | S04 | C5S04,07 (AI) | XT-92201_AI_1 | 1756-IF16-7 | =CA1+MCP-M5 | RIO-200 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
178 | XA-92201 | - | 325-01-923-PD-03 | LEL gas Buzzer Alarm | Gas detector | 4 - 20 mA | 0-10%LEL | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C5 | S03 | C5S03,00 (DO) | XA-92201_DO_1 | 1756-OB32-0 | =CA1+MCP-M5 | RIO-200 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
179 | XV-40201A | XV-40101A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S03, S07 | C1S03,26 (DI); C1S03,27 (DI); C1S07,28 (DO) | XV-40201A_DI_1; XV-40201A_DI_2; XV-40201A_DO_1 | 1756-IB32-26, 1756-IB32-27, 1756-OB32-28 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
180 | XV-40201B | XV-40101B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S03, S07 | C1S03,28 (DI); C1S03,29 (DI); C1S07,29 (DO) | XV-40201B_DI_1; XV-40201B_DI_2; XV-40201B_DO_1 | 1756-IB32-28, 1756-IB32-29, 1756-OB32-29 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
181 | XV-40201C | XV-40101C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S03, S07 | C1S03,30 (DI); C1S03,31 (DI); C1S07,30 (DO) | XV-40201C_DI_1; XV-40201C_DI_2; XV-40201C_DO_1 | 1756-IB32-30, 1756-IB32-31, 1756-OB32-30 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
182 | XV-40201D | XV-40101D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S07 | C1S04,00 (DI); C1S04,01 (DI); C1S07,31 (DO) | XV-40201D_DI_1; XV-40201D_DI_2; XV-40201D_DO_1 | 1756-IB32-0, 1756-IB32-1, 1756-OB32-31 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
183 | XV-40201E | XV-40101E | 325-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S08 | C1S04,02 (DI); C1S04,03 (DI); C1S08,00 (DO) | XV-40201E_DI_1; XV-40201E_DI_2; XV-40201E_DO_1 | 1756-IB32-2, 1756-IB32-3, 1756-OB32-0 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
184 | XV-40201F | XV-40101F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S08 | C1S04,04 (DI); C1S04,05 (DI); C1S08,01 (DO) | XV-40201F_DI_1; XV-40201F_DI_2; XV-40201F_DO_1 | 1756-IB32-4, 1756-IB32-5, 1756-OB32-1 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
185 | XV-40201G | XV-40101G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S08 | C1S04,06 (DI); C1S04,07 (DI); C1S08,02 (DO) | XV-40201G_DI_1; XV-40201G_DI_2; XV-40201G_DO_1 | 1756-IB32-6, 1756-IB32-7, 1756-OB32-2 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
186 | XV-40201H | XV-40101H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S08 | C1S04,08 (DI); C1S04,09 (DI); C1S08,03 (DO) | XV-40201H_DI_1; XV-40201H_DI_2; XV-40201H_DO_1 | 1756-IB32-8, 1756-IB32-9, 1756-OB32-3 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
187 | XV-40202A | XV-40102A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S08 | C1S04,11 (DI); C1S04,19 (DI); C1S08,04 (DO) | XV-40202A_DI_2; XV-40202A_DI_1; XV-40202A_DO_1 | 1756-IB32-11, 1756-IB32-19, 1756-OB32-4 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
188 | XV-40202B | XV-40102B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S08 | C1S04,12 (DI); C1S04,13 (DI); C1S08,05 (DO) | XV-40202B_DI_1; XV-40202B_DI_2; XV-40202B_DO_1 | 1756-IB32-12, 1756-IB32-13, 1756-OB32-5 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
189 | XV-40202C | XV-40102C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S08 | C1S04,14 (DI); C1S04,15 (DI); C1S08,06 (DO) | XV-40202C_DI_1; XV-40202C_DI_2; XV-40202C_DO_1 | 1756-IB32-14, 1756-IB32-15, 1756-OB32-6 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
190 | XV-40202D | XV-40102D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S08 | C1S04,16 (DI); C1S04,17 (DI); C1S08,07 (DO) | XV-40202D_DI_1; XV-40202D_DI_2; XV-40202D_DO_1 | 1756-IB32-16, 1756-IB32-17, 1756-OB32-7 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
191 | XV-40202E | XV-40102E | 325-01-402-PD-01 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S07 | C1S04,18 (DI); C1S04,19 (DI); C1S07,16 (DO) | XV-40202E_DI_1; XV-40202E_DI_2; XV-40202E_DO_1 | 1756-IB32-18, 1756-IB32-19, 1756-OB32-16 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
192 | XV-40202F | XV-40102F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S07 | C1S04,20 (DI); C1S04,21 (DI); C1S07,17 (DO) | XV-40202F_DI_1; XV-40202F_DI_2; XV-40202F_DO_1 | 1756-IB32-20, 1756-IB32-21, 1756-OB32-17 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
193 | XV-40202G | XV-40102G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S07 | C1S04,22 (DI); C1S04,23 (DI); C1S07,18 (DO) | XV-40202G_DI_1; XV-40202G_DI_2; XV-40202G_DO_1 | 1756-IB32-22, 1756-IB32-23, 1756-OB32-18 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
194 | XV-40202H | XV-40102H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S07 | C1S04,24 (DI); C1S04,25 (DI); C1S07,19 (DO) | XV-40202H_DI_1; XV-40202H_DI_2; XV-40202H_DO_1 | 1756-IB32-24, 1756-IB32-25, 1756-OB32-19 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
195 | XV-40203B | XV-40201B | 325-01-402-PD-02 | Slurry feed-out Spray dryer infeed tank | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S07 | C1S04,26 (DI); C1S04,27 (DI); C1S07,20 (DO) | XV-40203B_DI_1; XV-40203B_DI_2; XV-40203B_DO_1 | 1756-IB32-26, 1756-IB32-27, 1756-OB32-20 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
196 | XV-40203C | XV-40201C | 325-01-402-PD-02 | Water washing line outlet Spray dryer infeed tank | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S07 | C1S04,28 (DI); C1S04,29 (DI); C1S07,21 (DO) | XV-40203C_DI_1; XV-40203C_DI_2; XV-40203C_DO_1 | 1756-IB32-28, 1756-IB32-29, 1756-OB32-21 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
197 | XV-40203D | XV-40201D | 325-01-402-PD-02 | CIP water washing Spray dryer infeed tank | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S04, S07 | C1S04,30 (DI); C1S04,31 (DI); C1S07,22 (DO) | XV-40203D_DI_1; XV-40203D_DI_2; XV-40203D_DO_1 | 1756-IB32-30, 1756-IB32-31, 1756-OB32-22 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
198 | XV-40203E | XV-40201E | 325-01-402-PD-02 | CIP hight pressure water washing Spray dryer infeed tank | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S05, S07 | C1S05,00 (DI); C1S05,01 (DI); C1S07,23 (DO) | XV-40203E_DI_1; XV-40203E_DI_2; XV-40203E_DO_1 | 1756-IB32-0, 1756-IB32-1, 1756-OB32-23 | =CA1+MCP-M1 | JB-401 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
199 | XV-40203F | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S01, S06 | C2S01,06 (DI); C2S01,07 (DI); C2S06,00 (DO) | XV-40203F_DI_1; XV-40203F_DI_2; XV-40203F_DO_1 | 1756-IB32-6, 1756-IB32-7, 1756-OB32-0 | =CA1+MCP-M2 | JB-402 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
200 | XV-40204B | - | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S01, S06 | C2S01,08 (DI); C2S01,09 (DI); C2S06,01 (DO) | XV-40204B_DI_1; XV-40204B_DI_2; XV-40204B_DO_1 | 1756-IB32-8, 1756-IB32-9, 1756-OB32-1 | =CA1+MCP-M2 | JB-402 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
201 | XV-40204C | - | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S01, S06 | C2S01,10 (DI); C2S01,11 (DI); C2S06,02 (DO) | XV-40204C_DI_1; XV-40204C_DI_2; XV-40204C_DO_1 | 1756-IB32-10, 1756-IB32-11, 1756-OB32-2 | =CA1+MCP-M2 | JB-402 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
202 | XV-40205A | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S01, S06 | C2S01,12 (DI); C2S01,13 (DI); C2S06,03 (DO) | XV-40205A_DI_1; XV-40205A_DI_2; XV-40205A_DO_1 | 1756-IB32-12, 1756-IB32-13, 1756-OB32-3 | =CA1+MCP-M2 | JB-402 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
203 | XV-40205B | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S01, S06 | C2S01,14 (DI); C2S01,15 (DI); C2S06,04 (DO) | XV-40205B_DI_1; XV-40205B_DI_2; XV-40205B_DO_1 | 1756-IB32-14, 1756-IB32-15, 1756-OB32-4 | =CA1+MCP-M2 | JB-402 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
204 | XV-40205C | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S01, S06 | C2S01,16 (DI); C2S01,17 (DI); C2S06,05 (DO) | XV-40205C_DI_1; XV-40205C_DI_2; XV-40205C_DO_1 | 1756-IB32-16, 1756-IB32-17, 1756-OB32-5 | =CA1+MCP-M2 | JB-402 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
205 | XV-40205D | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S01, S06 | C2S01,18 (DI); C2S01,19 (DI); C2S06,06 (DO) | XV-40205D_DI_1; XV-40205D_DI_2; XV-40205D_DO_1 | 1756-IB32-18, 1756-IB32-19, 1756-OB32-6 | =CA1+MCP-M2 | JB-402 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
206 | XV-40205F | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S01, S06 | C2S01,20 (DI); C2S01,21 (DI); C2S06,07 (DO) | XV-40205F_DI_1; XV-40205F_DI_2; XV-40205F_DO_1 | 1756-IB32-20, 1756-IB32-21, 1756-OB32-7 | =CA1+MCP-M2 | JB-402 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
207 | XV-40222 | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S01, S06 | C2S01,22 (DI); C2S01,23 (DI); C2S06,08 (DO) | XV-40222_DI_1; XV-40222_DI_2; XV-40222_DO_1 | 1756-IB32-22, 1756-IB32-23, 1756-OB32-8 | =CA1+MCP-M2 | JB-402 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
208 | XV-60201 | - | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S03, S07 | C2S03,16 (DI); C2S03,17 (DI); C2S07,03 (DO) | XV-60201_DI_1; XV-60201_DI_2; XV-60201_DO_1 | 1756-IB32-16, 1756-IB32-17, 1756-OB32-3 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
209 | XV-60251 | - | 325-01-602-PD-01 | Liquid On/Off Valve for Drain Pipe (PIPE) | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S08 | C1S08,25 (DO) | XV-60251_DO_1 | 1756-OB32-25 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
210 | XV-60214 | XV-60301 | 325-01-602-PD-03 | Steam feed to Spray dryer | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S02, S06 | C2S02,19 (DI); C2S02,20 (DI); C2S06,17 (DO) | XV-60214_DI_1; XV-60214_DI_2; XV-60214_DO_1 | 1756-IB32-19, 1756-IB32-20, 1756-OB32-17 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
211 | XV-60202 | XV-61101 | 325-01-602-PD-11 | High Pressure Water On/Off Valve for Drain Pipe | Automatic on/off valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S06, S08 | C1S06,13 (DI); C1S06,14 (DI); C1S08,26 (DO) | XV-60202_DI_1; XV-60202_DI_2; XV-60202_DO_1 | 1756-IB32-13, 1756-IB32-14, 1756-OB32-26 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
212 | XV-61301 | HV-61301 | 325-01-613-PD-01 | Product feed-out Packing silo | Automatic on/off valve | 24 VDC energized | On-Off | Ex d | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | - | 2 | - | - | - | C3 | S02, S03 | C3S02,26 (DI); C3S02,27 (DI); C3S03,08 (DO) | XV-61301_DI_1; XV-61301_DI_2; XV-61301_DO_1 | 1756-IB32-26, 1756-IB32-27, 1756-OB32-8 | =CA1+MCP-M3 | JB-618 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
213 | XV-61302 | - | 325-01-613-PD-02 | Dust collector feed vent | Automatic on/off valve | 24 VDC energized | On-Off | Ex d | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C4 | S02, S04 | C4S02,13 (DI); C4S02,14 (DI); C4S04,29 (DO) | XV-61302_DI_1; XV-61302_DI_2; XV-61302_DO_1 | 1756-IB32-13, 1756-IB32-14, 1756-OB32-29 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
214 | XV-61303 | - | 325-01-613-PD-02 | Dust collector feed from packer | Automatic on/off valve | 24 VDC energized | On-Off | Ex d | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C4 | S02, S04 | C4S02,15 (DI); C4S02,16 (DI); C4S04,30 (DO) | XV-61303_DI_1; XV-61303_DI_2; XV-61303_DO_1 | 1756-IB32-15, 1756-IB32-16, 1756-OB32-30 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
215 | DV-61301 | - | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61301 | Automatic on/off valve | 24 VDC energized | On-Off | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | 2 | - | - | - | C3 | S01, S03 | C3S01,16 (DI); C3S01,17 (DI); C3S03,00 (DO) | DV-61301_DI_1; DV-61301_DI_2; DV-61301_DO_1 | 1756-IB32-16, 1756-IB32-17, 1756-OB32-0 | =CA1+MCP-M3 | JB-618 | WIRED | CVV 3Cx1 / CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
216 | DV-61302 | - | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61302 | Automatic on/off valve | 24 VDC energized | On-Off | Ex d | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | 2 | - | - | - | C3 | S01, S03 | C3S01,18 (DI); C3S01,19 (DI); C3S03,01 (DO) | DV-61302_DI_1; DV-61302_DI_2; DV-61302_DO_1 | 1756-IB32-18, 1756-IB32-19, 1756-OB32-1 | =CA1+MCP-M3 | JB-618 | WIRED | CVV 3Cx1 / CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
217 | ZS-60201A | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C4 | S01 | C4S01,16 (DI) | ZS-60201A_DI_1 | 1756-IB32-16 | =CA1+MCP-M4 | IS-JB-608 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
218 | ZS-60201B | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C4 | S01 | C4S01,17 (DI) | ZS-60201B_DI_1 | 1756-IB32-17 | =CA1+MCP-M4 | IS-JB-608 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
219 | ZS-60201C | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C3 | S01 | C3S01,08 (DI) | ZS-60201C_DI_1 | 1756-IB32-8 | =CA1+MCP-M3 | IS-JB-603 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
220 | ZS-60201D | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C3 | S01 | C3S01,09 (DI) | ZS-60201D_DI_1 | 1756-IB32-9 | =CA1+MCP-M3 | IS-JB-603 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
221 | ZS-60201E | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C3 | S01 | C3S01,10 (DI) | ZS-60201E_DI_1 | 1756-IB32-10 | =CA1+MCP-M3 | IS-JB-603 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
222 | ZS-60229 | - | 325-01-602-PD-04 | Limit Switch for CY-60230 (Door Service) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C3 | S01 | C3S01,11 (DI) | ZS-60229_DI_1 | 1756-IB32-11 | =CA1+MCP-M3 | IS-JB-603 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
223 | ZS-60230 | - | 325-01-602-PD-04 | Limit Switch for CY-60231 (Door Service) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C3 | S01 | C3S01,12 (DI) | ZS-60230_DI_1 | 1756-IB32-12 | =CA1+MCP-M3 | IS-JB-603 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
224 | ZS-60231A | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Spectacle Inserted) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C3 | S01 | C3S01,13 (DI) | ZS-60231A_DI_1 | 1756-IB32-13 | =CA1+MCP-M3 | IS-JB-603 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
225 | ZS-60231B | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Blind Inserted) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C3 | S01 | C3S01,14 (DI) | ZS-60231B_DI_1 | 1756-IB32-14 | =CA1+MCP-M3 | IS-JB-603 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
226 | ZS-60231C | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Spool Inserted) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C4 | S01 | C4S01,18 (DI) | ZS-60231C_DI_1 | 1756-IB32-18 | =CA1+MCP-M4 | IS-JB-608 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
227 | ZS-60231D | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Blind Inserted) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C4 | S01 | C4S01,19 (DI) | ZS-60231D_DI_1 | 1756-IB32-19 | =CA1+MCP-M4 | IS-JB-608 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
228 | ZS-60231E | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Spool Inserted) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C4 | S01 | C4S01,20 (DI) | ZS-60231E_DI_1 | 1756-IB32-20 | =CA1+MCP-M4 | IS-JB-608 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
229 | ZS-60231F | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Blind Inserted) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C4 | S01 | C4S01,21 (DI) | ZS-60231F_DI_1 | 1756-IB32-21 | =CA1+MCP-M4 | IS-JB-608 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
230 | ZS-60240 | - | 325-01-602-PD-05 | Limit Switch for FA-60240 (Door Service) | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C4 | S01 | C4S01,22 (DI) | ZS-60240_DI_1 | 1756-IB32-22 | =CA1+MCP-M4 | IS-JB-608 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
231 | ZS-61310 | - | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C3 | S02 | C3S02,11 (DI) | ZS-61310_DI_1 | 1756-IB32-11 | =CA1+MCP-M3 | IS-JB-618 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
232 | ZS-61311 | - | 325-01-613-PD-01 | Position Magnet Door | Position switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C3 | S02 | C3S02,12 (DI) | ZS-61311_DI_1 | 1756-IB32-12 | =CA1+MCP-M3 | IS-JB-618 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
233 | ZS-61312 | - | 325-01-613-PD-01 | Position Magnet Door | Position switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C4 | S03 | C4S03,14 (DI) | ZS-61312_DI_1 | 1756-IB32-14 | =CA1+MCP-M4 | IS-JB-612 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
234 | ZS-61313 | - | 325-01-613-PD-01 | Position Magnet Door | Position switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C4 | S03 | C4S03,15 (DI) | ZS-61313_DI_1 | 1756-IB32-15 | =CA1+MCP-M4 | IS-JB-612 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
235 | - | - | - | Lototo-01 | Position switch | Dry Contact | On-Off | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
236 | - | - | - | Lototo-02 | Position switch | Dry Contact | On-Off | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
237 | - | - | - | Lototo-03 | Position switch | Dry Contact | On-Off | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
238 | - | - | - | Lototo-04 | Position switch | Dry Contact | On-Off | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
239 | - | - | - | Lototo-05 | Position switch | Dry Contact | On-Off | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
240 | - | - | - | Lototo-06 | Position switch | Dry Contact | On-Off | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
241 | - | - | - | Lototo-07 | Position switch | Dry Contact | On-Off | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
242 | - | - | - | Lototo-08 | Position switch | Dry Contact | On-Off | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
243 | - | - | - | Lototo-09 | Position switch | Dry Contact | On-Off | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
244 | - | - | - | Lototo-10 | Position switch | Dry Contact | On-Off | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
245 | - | - | - | Lototo-11 | Position switch | Dry Contact | On-Off | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
246 | - | - | - | Lototo-12 | Position switch | Dry Contact | On-Off | Ex ic | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
247 | Machine Equipment Supply | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
248 | PSE-61300 | - | 325-01-613-PD-01 | Explosion Vent PSE-61300 | Position switch | Dry Contact | On-Off | Ex ic | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | Burst Disk Sensor | Cl.150 Flange Holder | Dry Contact NC Loop (DI) | - | 1 | - | - | - | C3 | S02 | C3S02,06 (DI) | PSE-61300_DI_1 | 1756-IB32-6 | =CA1+MCP-M3 | IS-JB-618 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
249 | PSE-61301 | - | 325-01-613-PD-01 | Explosion Vent PSE-61301 | Position switch | Dry Contact | On-Off | Ex ic | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | Burst Disk Sensor | Cl.150 Flange Holder | Dry Contact NC Loop (DI) | - | 1 | - | - | - | C3 | S02 | C3S02,07 (DI) | PSE-61301_DI_1 | 1756-IB32-7 | =CA1+MCP-M3 | IS-JB-618 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
250 | ISV-61302 | - | 325-01-613-PD-01 | Explosion isolation flap valve ISV-61302 | Position switch | Dry Contact | On-Off | Ex ic | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
251 | PSE-61302 | - | 325-01-613-PD-03 | Explosion Vent PSE-61302 | Position switch | Dry Contact | On-Off | Ex ic | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | Burst Disk Sensor | Cl.150 Flange Holder | Dry Contact NC Loop (DI) | - | 1 | - | - | - | C4 | S03 | C4S03,06 (DI) | PSE-61302_DI_1 | 1756-IB32-6 | =CA1+MCP-M4 | IS-JB-612 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
252 | PSE-61303 | - | 325-01-613-PD-05 | Explosion Vent PSE-61303 | Position switch | Dry Contact | On-Off | Ex ic | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | Burst Disk Sensor | Cl.150 Flange Holder | Dry Contact NC Loop (DI) | - | 1 | - | - | - | C4 | S03 | C4S03,07 (DI) | PSE-61303_DI_1 | 1756-IB32-7 | =CA1+MCP-M4 | IS-JB-612 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
253 | PSE-61304 | - | 325-01-613-PD-01 | Explosion Vent PSE-61304 | Position switch | Dry Contact | On-Off | Ex ic | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | Burst Disk Sensor | Cl.150 Flange Holder | Dry Contact NC Loop (DI) | - | 1 | - | - | - | C3 | S02 | C3S02,08 (DI) | PSE-61304_DI_1 | 1756-IB32-8 | =CA1+MCP-M3 | IS-JB-618 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
254 | ZS-61306 | PSV-61301A | 325-01-613-PD-01 | Position Brether Valve High Pressure PSV-61301 | Position switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C3 | S02 | C3S02,09 (DI) | PSV-61301A_DI_1 | 1756-IB32-9 | =CA1+MCP-M3 | IS-JB-618 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
255 | ZS-61307 | PSV-61301B | 325-01-613-PD-01 | Position Brether Valve Vacuum Pressure PSV-61301 | Position switch | Dry Contact | On-Off | Ex ic | APL-HKC | APL-210N / APL-510N Valve Position Monitor | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact Micro-switches (2x SPDT) | - | 1 | - | - | - | C3 | S02 | C3S02,10 (DI) | PSV-61301B_DI_1 | 1756-IB32-10 | =CA1+MCP-M3 | IS-JB-618 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
256 | ISV-61303 | - | 325-01-613-PD-03 | Explosion isolation flap valve ISV-61303 | Position switch | Dry Contact | On-Off | Ex ic | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | - | 1 | - | - | - | C4 | S03 | C4S03,00 (DI) | ISV-61303_DI_1 | 1756-IB32-0 | =CA1+MCP-M4 | IS-JB-612 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
257 | ISV-61304 | - | 325-01-613-PD-05 | Explosion isolation flap valve ISV-61304 | Position switch | Dry Contact | On-Off | Ex ic | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | - | 1 | - | - | - | C4 | S03 | C4S03,01 (DI) | ISV-61304_DI_1 | 1756-IB32-1 | =CA1+MCP-M4 | IS-JB-612 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
258 | MCC ROOM | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
259 | ATY-40201 | ATY-40101 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40201 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S01, S05 | C7S00,00 (BUS); C7S01,08 (DI); C7S01,09 (DI); C7S01,10 (DI)... | ATY-40201_BUS_1; ATY-40201_DI_1; ATY-40201_DI_2... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC PANEL) | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
260 | ATY-40202 | ATY-40102 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40202 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S01, S05 | C7S00,00 (BUS); C7S01,11 (DI); C7S01,12 (DI); C7S01,13 (DI)... | ATY-40202_BUS_1; ATY-40202_DI_1; ATY-40202_DI_2... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
261 | ATY-40203 | ATY-40201 | 325-01-402-PD-02 | Start / Stop Command for VSD AT-40203 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S01, S05 | C7S00,00 (BUS); C7S01,14 (DI); C7S01,15 (DI); C7S01,16 (DI)... | ATY-40203_BUS_1; ATY-40203_DI_1; ATY-40203_DI_2... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
262 | BFY-60210 | - | 325-01-602-PD-03 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S02, S05 | C7S00,00 (BUS); C7S02,11 (DI); C7S05,30 (DO) | BFY-60210_BUS_1; BFY-60210_DI_1; BFY-60210_DO_1 |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
263 | BFY-60211 | - | 325-01-602-PD-03 | Start / Stop Command for VSD FANC-21 (Combustion Fan) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S02, S05 | C7S00,00 (BUS); C7S02,12 (DI); C7S05,31 (DO) | BFY-60211_BUS_1; BFY-60211_DI_1; BFY-60211_DO_1 |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
264 | BFY-60240 | - | 325-01-602-PD-05 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S02, S06 | C7S00,00 (BUS); C7S02,13 (DI); C7S06,00 (DO) | BFY-60240_BUS_1; BFY-60240_DI_1; BFY-60240_DO_1 |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
265 | BFY-60220 | - | 325-01-602-PD-04 | Start / Stop Command for VSD FANS-22 (Cooling Fan) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S02, S06 | C7S00,00 (BUS); C7S02,17 (DI); C7S06,07 (DO) | BFY-60220_BUS_1; BFY-60220_DI_1; BFY-60220_DO_1 |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
266 | BFY-60206 | - | 325-01-602-PD-08 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S01, S05 | C7S00,00 (BUS); C7S01,26 (DI); C7S05,14 (DO) | BFY-60206_BUS_1; BFY-60206_DI_1; BFY-60206_DO_1 |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
267 | BFY-61301 | - | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S03, S06 | C7S00,00 (BUS); C7S03,08 (DI); C7S06,19 (DO) | BFY-61301_BUS_1; BFY-61301_DI_1; BFY-61301_DO_1 |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
268 | BFY-61302 | - | 325-01-613-PD-05 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S02, S06 | C7S00,00 (BUS); C7S02,18 (DI); C7S06,10 (DO) | BFY-61302_BUS_1; BFY-61302_DI_1; BFY-61302_DO_1 |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
269 | BFY-61303 | - | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S03, S06 | C7S00,00 (BUS); C7S03,09 (DI); C7S06,20 (DO) | BFY-61303_BUS_1; BFY-61303_DI_1; BFY-61303_DO_1 |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
270 | BLM-61302 | - | 325-01-613-PD-01 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 2 | 2 | - | - | - | C7 | S03, S06 | C7S03,10 (DI); C7S03,11 (DI); C7S06,21 (DO); C7S06,22 (DO) | BLM-61302_DI_1; BLM-61302_DI_2; BLM-61302_DO_1... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
271 | PDM-60202B | PCM-60205-B | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Oil Pump ) | - | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | 3 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
272 | PDM-60202C | PCM-60205-C | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 1 ) | - | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | 3 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
273 | PDM-60202D | PCM-60205-D | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 2 ) | - | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | 3 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
274 | PDM-60202E | PCM-60205-E | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Main motor Fan ) | - | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | 3 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
275 | PCY-40203 | PCY-40201 | 325-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S01, S05 | C7S00,00 (BUS); C7S01,23 (DI); C7S01,24 (DI); C7S01,25 (DI)... | PCY-40203_BUS_1; PCY-40203_DI_1; PCY-40203_DI_2... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
276 | PCY-40201 | PCY-40101 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40201 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S01, S05 | C7S00,00 (BUS); C7S01,17 (DI); C7S01,18 (DI); C7S01,19 (DI)... | PCY-40201_BUS_1; PCY-40201_DI_1; PCY-40201_DI_2... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
277 | PCY-40202 | PCY-40102 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40202 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S01, S05 | C7S00,00 (BUS); C7S01,20 (DI); C7S01,21 (DI); C7S01,22 (DI)... | PCY-40202_BUS_1; PCY-40202_DI_1; PCY-40202_DI_2... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
278 | PDY-40204 | - | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40204 | - | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | 3 | - | - | 1 | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
279 | PDY-40205 | - | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40205 | - | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | 3 | - | - | 1 | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
280 | PDY-60202A | PCY-60205-A | 325-01-602-PD-01 | Start / Stop Command for VSD PUPD-11 (Positive Displacement Pump ) | - | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | 3 | - | - | 1 | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
281 | PCY-60215 | - | 325-01-602-PD-03 | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C7 | S00, S02, S06 | C7S00,00 (BUS); C7S02,14 (DI); C7S02,15 (DI); C7S02,16 (DI)... | PCY-60215_BUS_1; PCY-60215_DI_1; PCY-60215_DI_2... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
282 | BLM-61301 | PVM-61301 | 325-01-613-PD-03 | Start / Stop Command for FVNR PV-61301 (Vacuum Cleaning Fan) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | - | C4 | S02, S04 | C4S02,02 (DI); C4S02,03 (DI); C4S04,16 (DO); C4S04,17 (DO) | PVM-61301_DI_1; PVM-61301_DI_2; PVM-61301_DO_1... | 1756-IB32-2, 1756-IB32-3, 1756-OB32-16, 1756-OB32-17 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
283 | RVM-60201 | - | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | - | C7 | S02, S05 | C7S02,05 (DI); C7S02,06 (DI); C7S05,23 (DO); C7S05,24 (DO) | RVM-60201_DI_1; RVM-60201_DI_2; RVM-60201_DO_1... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
284 | RVM-60202 | - | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | - | C7 | S02, S05 | C7S02,07 (DI); C7S02,08 (DI); C7S05,25 (DO); C7S05,26 (DO) | RVM-60202_DI_1; RVM-60202_DI_2; RVM-60202_DO_1... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
285 | RVM-60203 | - | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | - | C7 | S02, S05 | C7S02,09 (DI); C7S02,10 (DI); C7S05,27 (DO); C7S05,28 (DO) | RVM-60203_DI_1; RVM-60203_DI_2; RVM-60203_DO_1... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
286 | RVM-60204 | - | 325-01-602-PD-08 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | - | C7 | S03, S06 | C7S03,17 (DI); C7S03,18 (DI); C7S06,23 (DO); C7S06,24 (DO) | RVM-60204_DI_1; RVM-60204_DI_2; RVM-60204_DO_1... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
287 | RVM-61301 | - | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61301 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | - | C7 | S03, S06 | C7S03,19 (DI); C7S03,20 (DI); C7S06,25 (DO); C7S06,26 (DO) | RVM-61301_DI_1; RVM-61301_DI_2; RVM-61301_DO_1... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
288 | RVM-61302 | - | 325-01-613-PD-03 | Start / Stop Command for FVNR RV-61302 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | - | C7 | S03, S06 | C7S03,00 (DI); C7S03,01 (DI); C7S06,11 (DO); C7S06,12 (DO) | RVM-61302_DI_1; RVM-61302_DI_2; RVM-61302_DO_1... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
289 | RVM-61303 | - | 325-01-613-PD-05 | Start / Stop Command for FVNR RV-61303 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | - | C7 | S03, S06 | C7S03,02 (DI); C7S03,03 (DI); C7S06,13 (DO); C7S06,14 (DO) | RVM-61303_DI_1; RVM-61303_DI_2; RVM-61303_DO_1... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
290 | RVM-61304 | - | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61304 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | - | C7 | S03, S06 | C7S03,21 (DI); C7S03,22 (DI); C7S06,27 (DO); C7S06,28 (DO) | RVM-61304_DI_1; RVM-61304_DI_2; RVM-61304_DO_1... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
291 | RVM-61305 | - | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61305 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | - | C7 | S03, S06 | C7S03,23 (DI); C7S03,24 (DI); C7S06,29 (DO); C7S06,30 (DO) | RVM-61305_DI_1; RVM-61305_DI_2; RVM-61305_DO_1... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
292 | SCM-61301 | - | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61301 (Sifter ) | - | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | 3 | - | - | - | C7 | S03, S06 | C7S03,04 (DI); C7S03,05 (DI); C7S06,15 (DO); C7S06,16 (DO) | SCM-61301_DI_1; SCM-61301_DI_2; SCM-61301_DO_1... |  | MCC | MCC | MCC | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
293 | SCM-61302 | - | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61302 (Sifter ) | - | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | 3 | - | - | - | C7 | S03, S06 | C7S03,06 (DI); C7S03,07 (DI); C7S06,17 (DO); C7S06,18 (DO) | SCM-61302_DI_2; SCM-61302_DI_1; SCM-61302_DO_1... |  | MCC | MCC | MCC | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
294 | DEDERT SUPPLY EQUIPMENT | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
295 | FT-60207 | FT-60701 | 325-01-602-PD-07 | Instr. Air Flow Transmitter for Camera #4 (ACAM-21) | Flow Transmitter | 4 - 20 mA | - | - | Endress+Hauser | t-mass F 300 / I 300 (Thermal Mass Flowmeter) | 6F3B / 6I3B Series | Flange Cl.150 or 1" NPT Compression | 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S12 | C2S12,00 (AI) | FT-60207_AI_1 | 1756-IF16-0 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
296 | PT-60207 | PT-60701 | 325-01-602-PD-07 | Instr. Air Pressure Transmitter for Camera #4 (ACAM-21) | Pressure Transmitter | 4 - 20 mA | - | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S13 | C2S13,03 (AI) | PT-60207_AI_1 | 1756-IF16-3 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
297 | SV-60240D | - | 325-01-602-PD-05 | PA On/Off Valve for Bag House Tank Valve (BGHS-21) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
298 | SV-60207 | SV-60701 | 325-01-602-PD-07 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) | On/Off Valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S03, S07 | C2S03,08 (DI); C2S03,09 (DI); C2S07,00 (DO) | SV-60207_DI_1; SV-60207_DI_2; SV-60207_DO_1 | 1756-IB32-8, 1756-IB32-9, 1756-OB32-0 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
299 | SV-60201 | - | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) | On/Off Valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S05, S08 | C1S05,19 (DI); C1S05,20 (DI); C1S08,16 (DO) | SV-60201_DI_1; SV-60201_DI_2; SV-60201_DO_1 | 1756-IB32-19, 1756-IB32-20, 1756-OB32-16 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
300 | SV-60202 | - | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) | On/Off Valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S05, S08 | C1S05,21 (DI); C1S05,22 (DI); C1S08,17 (DO) | SV-60202_DI_1; SV-60202_DI_2; SV-60202_DO_1 | 1756-IB32-21, 1756-IB32-22, 1756-OB32-17 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
301 | SV-60203 | - | 325-01-602-PD-08 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) | On/Off Valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C1 | S05, S08 | C1S05,23 (DI); C1S05,24 (DI); C1S08,19 (DO) | SV-60203_DI_1; SV-60203_DI_2; SV-60203_DO_1 | 1756-IB32-23, 1756-IB32-24, 1756-OB32-19 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
302 | SV-61304 | - | 325-01-613-PD-01 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) | On/Off Valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C3 | S02, S03 | C3S02,24 (DI); C3S02,25 (DI); C3S03,05 (DO) | SV-61304_DI_1; SV-61304_DI_2; SV-61304_DO_1 | 1756-IB32-24, 1756-IB32-25, 1756-OB32-5 | =CA1+MCP-M3 | JB-618 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
303 | TT-60207 | TT-60701 | 325-01-602-PD-07 | Instr. Air Temperature Transmitter for Air Manifold - Camera #4 (ACAM-21) | Temperature Transmitter | 4 - 20 mA | - | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | TMT71 + TM411 Head Assembly | Threaded 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C2 | S13 | C2S13,09 (AI) | TT-60207_AI_1 | 1756-IF16-9 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
304 | XV-60261FA | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | 1 | 2 | - | - | - | C2 | S03, S07 | C2S03,24 (DI); C2S03,25 (DI); C2S07,05 (DO) | XV-60261FA_DI_1; XV-60261FA_DI_2; XV-60261FA_DO_1 | 1756-IB32-24, 1756-IB32-25, 1756-OB32-5 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
305 | XV-60261FB | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | 1 | 2 | - | - | - | C2 | S03, S07 | C2S03,28 (DI); C2S03,29 (DI); C2S07,06 (DO) | XV-60261FB_DI_1; XV-60261FB_DI_2; XV-60261FB_DO_1 | 1756-IB32-28, 1756-IB32-29, 1756-OB32-6 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
306 | XV-60261FC | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | 1 | 2 | - | - | - | C2 | S04, S07 | C2S04,00 (DI); C2S04,01 (DI); C2S07,07 (DO) | XV-60261FC_DI_1; XV-60261FC_DI_2; XV-60261FC_DO_1 | 1756-IB32-0, 1756-IB32-1, 1756-OB32-7 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
307 | XV-60261FD | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | FD-H20 / FD-H32 / FD-HF | Clamp-on Sensor Head (External Pipe Mount) | 4-20mA + Pulse / 24VDC | 1 | 2 | - | - | - | C2 | S04, S07 | C2S04,04 (DI); C2S04,05 (DI); C2S07,08 (DO) | XV-60261FD_DI_1; XV-60261FD_DI_2; XV-60261FD_DO_1 | 1756-IB32-4, 1756-IB32-5, 1756-OB32-8 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
308 | XV-60261SA | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S04, S07 | C2S04,08 (DI); C2S04,09 (DI); C2S07,09 (DO) | XV-60261SA_DI_1; XV-60261SA_DI_2; XV-60261SA_DO_1 | 1756-IB32-8, 1756-IB32-9, 1756-OB32-9 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
309 | XV-60261SB | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S04, S07 | C2S04,10 (DI); C2S04,11 (DI); C2S07,10 (DO) | XV-60261SB_DI_1; XV-60261SB_DI_2; XV-60261SB_DO_1 | 1756-IB32-10, 1756-IB32-11, 1756-OB32-10 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
310 | XV-60261SC | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S04, S07 | C2S04,12 (DI); C2S04,13 (DI); C2S07,11 (DO) | XV-60261SC_DI_1; XV-60261SC_DI_2; XV-60261SC_DO_1 | 1756-IB32-12, 1756-IB32-13, 1756-OB32-11 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
311 | XV-60261SD | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S04, S07 | C2S04,14 (DI); C2S04,15 (DI); C2S07,12 (DO) | XV-60261SD_DI_1; XV-60261SD_DI_2; XV-60261SD_DO_1 | 1756-IB32-14, 1756-IB32-15, 1756-OB32-12 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
312 | XV-60262FE | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S04, S07 | C2S04,18 (DI); C2S04,19 (DI); C2S07,14 (DO) | XV-60262FE_DI_1; XV-60262FE_DI_2; XV-60262FE_DO_1 | 1756-IB32-18, 1756-IB32-19, 1756-OB32-14 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
313 | XV-60262FF | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S04, S07 | C2S04,20 (DI); C2S04,21 (DI); C2S07,15 (DO) | XV-60262FF_DI_1; XV-60262FF_DI_2; XV-60262FF_DO_1 | 1756-IB32-20, 1756-IB32-21, 1756-OB32-15 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
314 | XV-60262FG | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S04, S07 | C2S04,22 (DI); C2S04,23 (DI); C2S07,16 (DO) | XV-60262FG_DI_1; XV-60262FG_DI_2; XV-60262FG_DO_1 | 1756-IB32-22, 1756-IB32-23, 1756-OB32-16 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
315 | XV-60262FH | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S04, S07 | C2S04,24 (DI); C2S04,25 (DI); C2S07,17 (DO) | XV-60262FH_DI_1; XV-60262FH_DI_2; XV-60262FH_DO_1 | 1756-IB32-24, 1756-IB32-25, 1756-OB32-17 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
316 | XV-60262SE | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S04, S07 | C2S04,26 (DI); C2S04,27 (DI); C2S07,18 (DO) | XV-60262SE_DI_1; XV-60262SE_DI_2; XV-60262SE_DO_1 | 1756-IB32-26, 1756-IB32-27, 1756-OB32-18 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
317 | XV-60262SF | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S04, S07 | C2S04,28 (DI); C2S04,29 (DI); C2S07,19 (DO) | XV-60262SF_DI_1; XV-60262SF_DI_2; XV-60262SF_DO_1 | 1756-IB32-28, 1756-IB32-29, 1756-OB32-19 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
318 | XV-60262SG | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S04, S07 | C2S04,30 (DI); C2S04,31 (DI); C2S07,20 (DO) | XV-60262SG_DI_1; XV-60262SG_DI_2; XV-60262SG_DO_1 | 1756-IB32-30, 1756-IB32-31, 1756-OB32-20 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
319 | XV-60262SH | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S05, S07 | C2S05,00 (DI); C2S05,01 (DI); C2S07,21 (DO) | XV-60262SH_DI_1; XV-60262SH_DI_2; XV-60262SH_DO_1 | 1756-IB32-0, 1756-IB32-1, 1756-OB32-21 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
320 | XV-60263FJ | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S05, S07 | C2S05,04 (DI); C2S05,05 (DI); C2S07,23 (DO) | XV-60263FJ_DI_1; XV-60263FJ_DI_2; XV-60263FJ_DO_1 | 1756-IB32-4, 1756-IB32-5, 1756-OB32-23 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
321 | XV-60263FK | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S05, S07 | C2S05,06 (DI); C2S05,07 (DI); C2S07,24 (DO) | XV-60263FK_DI_1; XV-60263FK_DI_2; XV-60263FK_DO_1 | 1756-IB32-6, 1756-IB32-7, 1756-OB32-24 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
322 | XV-60263FL | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S05, S07 | C2S05,08 (DI); C2S05,09 (DI); C2S07,25 (DO) | XV-60263FL_DI_1; XV-60263FL_DI_2; XV-60263FL_DO_1 | 1756-IB32-8, 1756-IB32-9, 1756-OB32-25 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
323 | XV-60263FM | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S05, S07 | C2S05,10 (DI); C2S05,11 (DI); C2S07,26 (DO) | XV-60263FM_DI_1; XV-60263FM_DI_2; XV-60263FM_DO_1 | 1756-IB32-10, 1756-IB32-11, 1756-OB32-26 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
324 | XV-60263SJ | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S05, S07 | C2S05,12 (DI); C2S05,13 (DI); C2S07,27 (DO) | XV-60263SJ_DI_1; XV-60263SJ_DI_2; XV-60263SJ_DO_1 | 1756-IB32-12, 1756-IB32-13, 1756-OB32-27 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
325 | XV-60263SK | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S05, S07 | C2S05,14 (DI); C2S05,15 (DI); C2S07,28 (DO) | XV-60263SK_DI_1; XV-60263SK_DI_2; XV-60263SK_DO_1 | 1756-IB32-14, 1756-IB32-15, 1756-OB32-28 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
326 | XV-60263SL | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S05, S07 | C2S05,16 (DI); C2S05,17 (DI); C2S07,29 (DO) | XV-60263SL_DI_1; XV-60263SL_DI_2; XV-60263SL_DO_1 | 1756-IB32-16, 1756-IB32-17, 1756-OB32-29 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
327 | XV-60263SM | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S05, S07 | C2S05,18 (DI); C2S05,19 (DI); C2S07,30 (DO) | XV-60263SM_DI_1; XV-60263SM_DI_2; XV-60263SM_DO_1 | 1756-IB32-18, 1756-IB32-19, 1756-OB32-30 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
328 | XV-60264FN | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S03, S08 | C2S03,12 (DI); C2S03,13 (DI); C2S08,01 (DO) | XV-60264FN_DI_1; XV-60264FN_DI_2; XV-60264FN_DO_1 | 1756-IB32-12, 1756-IB32-13, 1756-OB32-1 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
329 | XV-60264FP | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S03, S08 | C2S03,14 (DI); C2S03,15 (DI); C2S08,02 (DO) | XV-60264FP_DI_1; XV-60264FP_DI_2; XV-60264FP_DO_1 | 1756-IB32-14, 1756-IB32-15, 1756-OB32-2 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
330 | XV-60264FQ | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S03, S08 | C2S03,18 (DI); C2S03,19 (DI); C2S08,03 (DO) | XV-60264FQ_DI_1; XV-60264FQ_DI_2; XV-60264FQ_DO_1 | 1756-IB32-18, 1756-IB32-19, 1756-OB32-3 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
331 | XV-60264FR | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S03, S08 | C2S03,22 (DI); C2S03,23 (DI); C2S08,04 (DO) | XV-60264FR_DI_1; XV-60264FR_DI_2; XV-60264FR_DO_1 | 1756-IB32-22, 1756-IB32-23, 1756-OB32-4 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
332 | XV-60264SN | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S03, S08 | C2S03,26 (DI); C2S03,27 (DI); C2S08,05 (DO) | XV-60264SN_DI_1; XV-60264SN_DI_2; XV-60264SN_DO_1 | 1756-IB32-26, 1756-IB32-27, 1756-OB32-5 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
333 | XV-60264SP | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S03, S08 | C2S03,30 (DI); C2S03,31 (DI); C2S08,06 (DO) | XV-60264SP_DI_1; XV-60264SP_DI_2; XV-60264SP_DO_1 | 1756-IB32-30, 1756-IB32-31, 1756-OB32-6 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
334 | XV-60264SQ | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S04, S08 | C2S04,02 (DI); C2S04,03 (DI); C2S08,07 (DO) | XV-60264SQ_DI_1; XV-60264SQ_DI_2; XV-60264SQ_DO_1 | 1756-IB32-2, 1756-IB32-3, 1756-OB32-7 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
335 | XV-60264SR | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S04, S08 | C2S04,06 (DI); C2S04,07 (DI); C2S08,08 (DO) | XV-60264SR_DI_1; XV-60264SR_DI_2; XV-60264SR_DO_1 | 1756-IB32-6, 1756-IB32-7, 1756-OB32-8 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
336 | XV-60261DA | - | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11A | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
337 | XV-60262DE | - | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11B | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
338 | XV-60263DN | - | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11C | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
339 | XV-60264DJ | - | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11D | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
340 | XV-60241 | - | 325-01-602-PD-05 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C2 | S02, S06 | C2S02,21 (DI); C2S02,22 (DI); C2S06,18 (DO) | XV-60241_DI_1; XV-60241_DI_2; XV-60241_DO_1 | 1756-IB32-21, 1756-IB32-22, 1756-OB32-18 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
341 | XA-60202A | - | 325-01-602-PD-08 | General Alarm Emergency Stop Actuation for XSUP-5601 (Supression Panel) | General Alarm Emergency Stop Actuation | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,00 (DI) | XA-60202A_DI_1 | 1756-IB32-0 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
342 | XA-60202B | - | 325-01-602-PD-08 | General Fault Controlled Stop for XSUP-5601 (Supression Panel) | General Fault Controlled Stop | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,01 (DI) | XA-60202B_DI_1 | 1756-IB32-1 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
343 | XA-60202C | - | 325-01-602-PD-08 | General Armed Status Indicator for XSUP-5601 (Supression Panel) | General Armed Status Indicator | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,02 (DI) | XA-60202C_DI_1 | 1756-IB32-2 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
344 | XA-60202D | - | 325-01-602-PD-08 | Power Fault Status Indicator for XSUP-5601 (Supression Panel) | Power Fault Status Indicator | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,03 (DI) | XA-60202D_DI_1 | 1756-IB32-3 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
345 | XA-60202E | - | 325-01-602-PD-08 | Dryer CHAM-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | Dryer CHAM-21 Emergency Stop Actuation | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,04 (DI) | XA-60202E_DI_1 | 1756-IB32-4 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
346 | XA-60202F | - | 325-01-602-PD-08 | CHAM-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CHAM-21 Controlled Stop Trouble (No Protection) | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,05 (DI) | XA-60202F_DI_1 | 1756-IB32-5 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
347 | XA-60202G | - | 325-01-602-PD-08 | CYCL-21/22 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-21/22 Emergency Stop Actuation | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,06 (DI) | XA-60202G_DI_1 | 1756-IB32-6 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
348 | XA-60202H | - | 325-01-602-PD-08 | CYCL-21/22 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-21/22 Controlled Stop Trouble (No Protection) | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,07 (DI) | XA-60202H_DI_1 | 1756-IB32-7 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
349 | XA-60202J | - | 325-01-602-PD-08 | BGHS-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | BGHS-21 Emergency Stop Actuation | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,09 (DI) | XA-60202J_DI_1 | 1756-IB32-9 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
350 | XA-60202K | - | 325-01-602-PD-08 | BGHS-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | BGHS-21 Controlled Stop Trouble (No Protection) | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,10 (DI) | XA-60202K_DI_1 | 1756-IB32-10 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
351 | XA-60202L | - | 325-01-602-PD-08 | CYCL-31 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-31 Emergency Stop Actuation | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,11 (DI) | XA-60202L_DI_1 | 1756-IB32-11 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
352 | XA-60202M | - | 325-01-602-PD-08 | CYCL-31 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-31 Controlled Stop Trouble (No Protection) | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,12 (DI) | XA-60202M_DI_1 | 1756-IB32-12 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
353 | XA-60261 | - | 325-01-602-PD-05 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Fire Deluge Fault (No Protection) | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C4 | S01 | C4S01,02 (DI) | XA-60261_DI_1 | 1756-IB32-2 | =CA1+MCP-M4 | JB-606 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
354 | XA-60262 | - | 325-01-602-PD-05 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Fire Deluge Alarm (Deluge Activated) | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C4 | S01 | C4S01,03 (DI) | XA-60262_DI_1 | 1756-IB32-3 | =CA1+MCP-M4 | JB-606 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
355 | XS-60260 | - | 325-01-602-PD-05 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C7 | S06 | C7S06,06 (DO) | XS-60260_DO_1 |  | MCC | MCC | MCC | CVV 3Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
356 | XV-60240 | - | 325-01-602-PD-08 | Powder On/Off Valve for Diverter Valve (DVTR-21) | On/Off Valve | 24 VDC energized | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
357 | Haver & Boecker. EQUIPMENT | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
358 | XA-61301A | - | 325-01-613-PD-02 | Request filter plant | Request filter plant | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C4 | S02 | C4S02,04 (DI) | XA-61301A_DI_1 | 1756-IB32-4 | =CA1+MCP-M4 | JB-612 | WIRED | MULTICORE LINK TO PLC | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
359 | XA-61301B | - | 325-01-613-PD-02 | Request material transport | Request material transport | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C4 | S02 | C4S02,05 (DI) | XA-61301B_DI_1 | 1756-IB32-5 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
360 | XA-61301C | - | 325-01-613-PD-02 | Request belt plant | Request belt plant | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C4 | S02 | C4S02,06 (DI) | XA-61301C_DI_1 | 1756-IB32-6 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
361 | XA-61301D | - | 325-01-613-PD-02 | Machine in operation | Machine in operation | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C4 | S02 | C4S02,07 (DI) | XA-61301D_DI_1 | 1756-IB32-7 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
362 | XA-61301E | - | 325-01-613-PD-02 | General Fault | General Fault | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C4 | S02 | C4S02,08 (DI) | XA-61301E_DI_1 | 1756-IB32-8 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
363 | XA-61301F | - | 325-01-613-PD-02 | Machine is ready | Machine is ready | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C4 | S02 | C4S02,09 (DI) | XA-61301F_DI_1 | 1756-IB32-9 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
364 | XA-61301G | - | 325-01-613-PD-02 | Emergency stop activated | Emergency stop activated | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C4 | S02 | C4S02,10 (DI) | XA-61301G_DI_1 | 1756-IB32-10 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
365 | XA-61301H | - | 325-01-613-PD-02 | Silo minimum | Silo minimum | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C4 | S02 | C4S02,11 (DI) | XA-61301H_DI_1 | 1756-IB32-11 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
366 | XA-61301J | - | 325-01-613-PD-02 | Silo maximum | Silo maximum | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C4 | S02 | C4S02,12 (DI) | XA-61301J_DI_1 | 1756-IB32-12 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
367 | XS-61301A | - | 325-01-613-PD-02 | Filter plant in operation | Filter plant in operation | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C4 | S04 | C4S04,23 (DO) | XS-61301A_DO_1 | 1756-OB32-23 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
368 | XS-61301B | - | 325-01-613-PD-02 | Material transport in operation | Material transport in operation | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C4 | S04 | C4S04,24 (DO) | XS-61301B_DO_1 | 1756-OB32-24 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
369 | XS-61301C | - | 325-01-613-PD-02 | Belt plant in operation | Belt plant in operation | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C4 | S04 | C4S04,25 (DO) | XS-61301C_DO_1 | 1756-OB32-25 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
370 | XS-61301D | - | 325-01-613-PD-02 | Sequence Stop | Sequence Stop | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C4 | S04 | C4S04,26 (DO) | XS-61301D_DO_1 | 1756-OB32-26 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
371 | XS-61301E | - | 325-01-613-PD-02 | Status from Customer Emergency stop | Status from Customer Emergency stop | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C4 | S04 | C4S04,27 (DO) | XS-61301E_DO_1 | 1756-OB32-27 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
372 | XS-61301F | - | 325-01-613-PD-02 | Operation Release | Operation Release | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C4 | S04 | C4S04,28 (DO) | XS-61301F_DO_1 | 1756-OB32-28 | =CA1+MCP-M4 | JB-612 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
373 | - | - | 325-01-613-PD-02 | Spare | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
374 | - | - | 325-01-613-PD-02 | Spare | - | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
375 | - | - | 325-01-613-PD-02 | Spare | - | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
376 | - | - | 325-01-613-PD-02 | Communication Signal | - | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | 1 | - | - | - | - | - | - | - | UNMAPPED | CAT 6 S/FTP Industrial Ethernet Cable / Belden 3105A RS-485 | 4 Pairs 24 AWG (Ethernet) / 1 Pair 22 AWG (RS-485) | Braided Shield + Foil Screen per Pair (S/FTP) | M20x1.5 Industrial RJ45 / Cable Gland | Fiber Optic Backbone / Industrial Ethernet Ring to CA1
377 | BGHS-21 Filter Control Panel | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
378 | XS-60240A | - | 325-01-602-PD-05 | Start / Stop Command for BGHS-21 (Bag House Air Pulsing) | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C7 | S06 | C7S06,02 (DO) | XS-60240A_DO_1 |  | MCC | MCC | MCC | MULTICORE LINK TO PLC | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
379 | XS-60240B | - | 325-01-602-PD-05 | Fan Command for BGHS-21 (Bag House Air Pulsing) | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C2 | S06 | C2S06,16 (DO) | XS-60240B_DO_1 | 1756-OB32-16 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
380 | XA-60240A | - | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S02 | C2S02,11 (DI) | XA-60240A_DI_1 | 1756-IB32-11 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
381 | XA-60240B | - | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S02 | C2S02,12 (DI) | XA-60240B_DI_1 | 1756-IB32-12 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
382 | DPI-60240 | - | 325-01-602-PD-05 | Gas Pressure Differntial Pressure (Bag House Air Pulsing) | - | 4 - 20 mA | - | - | Ashcroft | Model 1132 Differential Pressure Gauge | 1132 w/ V03 Manifold | 1/4" NPT Female | Local Mechanical Indication | - | - | - | 1 | - | C1 | S10 | C1S10,00 (AI) | DPI-60240_AI_1 | 1756-IF16-0 | =CA1+MCP-M1 | JB-601 | WIRED | LiY-CY TP 1Px1.0 | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
383 | HTRE-21 Heater Control Panel (TRACING) | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
384 | XS-60241A | - | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C7 | S06 | C7S06,03 (DO) | XS-60241A_DO_1 |  | MCC | MCC | MCC | MULTICORE LINK TO PLC | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
385 | XA-60241A | - | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S02 | C2S02,13 (DI) | XA-60241A_DI_1 | 1756-IB32-13 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
386 | XA-60241B | - | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S02 | C2S02,14 (DI) | XA-60241B_DI_1 | 1756-IB32-14 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
387 | TSH-60241A | - | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | 0 - 100 C | Ex d | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | TTR35 Series | 1/2" NPT w/ Hygienic Adapter | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C2 | S02 | C2S02,05 (DI) | TSH-60241A_DI_1 | 1756-IB32-5 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
388 | TSL-60241B | - | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | 0 - 100 C | Ex d | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | TTR35 Series | 1/2" NPT w/ Hygienic Adapter | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C2 | S02 | C2S02,08 (DI) | TSL-60241B_DI_1 | 1756-IB32-8 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
389 | HTRE-22 Heater Control Panel (TRACING) | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
390 | XS-60242A | - | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C7 | S06 | C7S06,04 (DO) | XS-60242A_DO_1 |  | MCC | MCC | MCC | MULTICORE LINK TO PLC | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
391 | XA-60242A | - | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S02 | C2S02,15 (DI) | XA-60242A_DI_1 | 1756-IB32-15 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
392 | XA-60242B | - | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S02 | C2S02,16 (DI) | XA-60242B_DI_1 | 1756-IB32-16 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
393 | TSH-60242A | - | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | 0 - 100 C | Ex d | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | TTR35 Series | 1/2" NPT w/ Hygienic Adapter | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C2 | S02 | C2S02,06 (DI) | TSH-60242A_DI_1 | 1756-IB32-6 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
394 | TSL-60242B | - | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | 0 - 100 C | Ex d | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | TTR35 Series | 1/2" NPT w/ Hygienic Adapter | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C2 | S02 | C2S02,09 (DI) | TSL-60242B_DI_1 | 1756-IB32-9 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
395 | HTRE-23 Heater Control Panel (TRACING) | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
396 | XS-60243A | - | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C7 | S06 | C7S06,04 (DO) | XS-60243A_DO_1 |  | MCC | MCC | MCC | MULTICORE LINK TO PLC | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
397 | XA-60243A | - | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S02 | C2S02,17 (DI) | XA-60243A_DI_1 | 1756-IB32-17 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
398 | XA-60243B | - | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S02 | C2S02,18 (DI) | XA-60243B_DI_1 | 1756-IB32-18 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
399 | TSH-60243A | - | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | 0 - 100 C | Ex d | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | TTR35 Series | 1/2" NPT w/ Hygienic Adapter | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C2 | S02 | C2S02,07 (DI) | TSH-60243A_DI_1 | 1756-IB32-7 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
400 | TSL-60243B | - | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | 0 - 100 C | Ex d | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | TTR35 Series | 1/2" NPT w/ Hygienic Adapter | 24VDC / Dry Contact Relay / PNP | - | 1 | - | - | - | C2 | S02 | C2S02,10 (DI) | TSL-60243B_DI_1 | 1756-IB32-10 | =CA1+MCP-M2 | JB-602 | WIRED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
401 | AHTR-21 Air Heater Control Panel | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
402 | XA-FH-60210A | - | 325-01-602-PD-06 | BMS PANEL POWER ON for AHTR-21 | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S03 | C2S03,00 (DI) | XA-FH-60210A_DI_1 | 1756-IB32-0 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 20C x 1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
403 | XA-FH-60210B | - | 325-01-602-PD-06 | BMS Burner High Fire Purge for AHTR-21 | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S03 | C2S03,01 (DI) | XA-FH-60210B_DI_1 | 1756-IB32-1 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
404 | XA-FH-60210C | - | 325-01-602-PD-06 | BMS Burner On for AHTR-21 | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S03 | C2S03,02 (DI) | XA-FH-60210C_DI_1 | 1756-IB32-2 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
405 | XA-FH-60210D | - | 325-01-602-PD-06 | BMS BMS Lockout for AHTR-21 | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S03 | C2S03,03 (DI) | XA-FH-60210D_DI_1 | 1756-IB32-3 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
406 | XA-FH-60210E | - | 325-01-602-PD-06 | BMS Remote Modet for AHTR-21 | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C2 | S03 | C2S03,04 (DI) | XA-FH-60210E_DI_1 | 1756-IB32-4 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
407 | XS-FH-60210A | - | 325-01-602-PD-06 | Start / Stop Command Burner Remote Start for AHTR-21 | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C7 | S06 | C7S06,08 (DO) | XS-FH-60210A_DO_1 |  | MCC | MCC | MCC | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
408 | XS-FH-60210B | - | 325-01-602-PD-06 | Start / Stop Command Dryer Interlocks for AHTR-21 | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C7 | S06 | C7S06,09 (DO) | XS-FH-60210B_DO_1 |  | MCC | MCC | MCC | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
409 | XS-FH-60210C | - | 325-01-602-PD-06 | Command Remote Reset for AHTR-21 | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C2 | S07 | C2S07,01 (DO) | XS-FH-60210C_DO_1 | 1756-OB32-1 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
410 | XS-FH-60210D | - | 325-01-602-PD-06 | Spare | - | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C2 | S07 | C2S07,02 (DO) | XS-FH-60210D_DO_1 | 1756-OB32-2 | =CA1+MCP-M2 | JB-607 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
411 | TI-FH-60210 | - | 325-01-602-PD-06 | Gas Burner Firing Rate Temp Signal to AHTR-21 | - | 4 - 20 mA | On-Off | - | Ashcroft | Model FI Bimetal Dial Thermometer | FI Series w/ Threaded Thermowell | 1/2" NPT Threaded Thermowell | Local Mechanical Indication | - | - | - | 1 | - | C2 | S13 | C2S13,06 (AI) | TI-FH-60210_AI_1 | 1756-IF16-6 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 3P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
412 | UY-FH-60210A | - | 325-01-602-PD-06 | Comb fan VFD Speed Control | - | 4 - 20 mA | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | 1 | - | C2 | S13 | C2S13,10 (AI) | UY-FH-60210A_AI_1 | 1756-IF16-10 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
413 | UY-FH-60210B | - | 325-01-602-PD-06 | Demand Signal | - | 4 - 20 mA | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | 1 | - | - | C3 | S13 | C3S13,04 (AO) | UY-FH-60210B_AO_1 | 1756-OF8-4 | =CA1+MCP-M2 | JB-607 | WIRED | LiY-CY TP 1Px1.0 | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
414 | COM-FH-60210B | - | 325-01-602-PD-06 | Communication Signal | - | Modbus RTU | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | 1 | C7 | S00 | C7S00,00 (BUS) | COM-FH-60210B_BUS_1 |  | MCC | JB-607 | MCC | CAT 6 S/FTP Industrial Ethernet Cable / Belden 3105A RS-485 (Ref: CAT 5e) | 4 Pairs 24 AWG (Ethernet) / 1 Pair 22 AWG (RS-485) | Braided Shield + Foil Screen per Pair (S/FTP) | M20x1.5 Industrial RJ45 / Cable Gland | Fiber Optic Backbone / Industrial Ethernet Ring to CA1
415 | TE-60212 | - | - | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Element | T/C Type K | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | LiY-CY TP 1P x1.0 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
416 | DPHL-60230 | - | - | Gas Pressure Differntial Switch Low for Exhaust Fan (FANE-21) | Pressure Differntial Switch Low | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
417 | DPSL-60211 | - | - | Gas Pressure Differential Switch Low for Combustion Fan (FANC-21) | Pressure Differential Switch Low | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
418 | FCV-60211B | - | - | Gas Flow Control Damper (Valve) for Burner Combustion Air Duct (DTCB-21) | Flow Control Damper (Valve) | - | - | - | Samson | Type 3241 Globe Valve + Trovis 3730-1 Positioner | 3241-ANSI + 3730-1 Positioner | Flange ASME B16.5 Cl.150/300 RF | 4-20mA Setpoint + 4-20mA Feedback | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | LiY-CY TP 2Px1.0 (Setpoint AO + Position Feedback AI) (Ref: LiY-CY TP 2P x1.0 , CVV 8Cx1) | 2 Pairs x 1.0 mm² (Individually & Overall Shielded) | Individual Foil Screen per Pair + Overall Tinned Copper Braid | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
419 | ZT-60211B | - | - | Gas Position Transmitter for Combustion Air Damper Actuator (DTCB-21) | Position Transmitter | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
420 | ZSL-60211B | - | - | Gas Position Switch Low for Combustion Air Damper Actuator (DTCB-21) | Position Switch Low | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
421 | ZSH-60211B | - | - | Gas Position Switch High for Combustion Air Damper Actuator (DTCB-21) | Position Switch High | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
422 | VJ-01 (24VDC) | - | - | Valve train J-BOX | Control Box | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | LiY-CY TP 2P x1.0 , CVV 17Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
423 | VJ-01 (220VAC) | - | - | Valve train J-BOX | Control Box | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
424 | UJ-01 (24VDC) | - | - | Valve train J-BOX | Control Box | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | LiY-CY TP 2P x1.0 , CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
425 | UJ-01 (220VAC) | - | - | Valve train J-BOX | Control Box | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 5Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
426 | PV-60210A | - | - | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | LiY-CY TP 1P x1.0 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
427 | PV-60210B | - | - | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | LiY-CY TP 1P x1.0 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
428 | DPT-60210 | - | - | Gas Pressure Differential Switch Low for Main Supply Air Fan (FANS-21) | Pressure Differential Switch Low | - | - | - | Endress+Hauser | Deltabar PMD55B (Diff. Pressure Transmitter) | PMD55B Series w/ 5-Valve Manifold | 1/4" NPT Female w/ 5-Valve Manifold DA63M | 2-wire 4-20mA HART / 24VDC | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | LiY-CY TP 1P x1.0 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
429 | DPSL-60210B | - | - | Gas Pressure Differential Switch Low for Air Heater (AHTR-21) | Pressure Differential Switch Low | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
430 | DPSH-60210C | - | - | Gas Pressure Differential Switch High for Air Heater (AHTR-21) | Pressure Differential Switch High | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
431 | BE-60210A | - | - | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
432 | BE-60210B | - | - | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
433 | IX-60210A | - | - | Gas Ignition Transformer for Air Heater (AHTR-21) | Ignition Transformer | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | LiY-CY TP 1P x1.0 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
434 | FCV-60210A | - | - | Gas Flow Control Valve for Air Heater Gas Train (GTRN-21) | Flow Control Valve | - | - | - | Samson | Type 3241 Globe Valve + Trovis 3730-1 Positioner | 3241-ANSI + 3730-1 Positioner | Flange ASME B16.5 Cl.150/300 RF | 4-20mA Setpoint + 4-20mA Feedback | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | LiY-CY TP 2Px1.0 (Setpoint AO + Position Feedback AI) (Ref: LiY-CY TP 2P x1.0 , CVV 8Cx1) | 2 Pairs x 1.0 mm² (Individually & Overall Shielded) | Individual Foil Screen per Pair + Overall Tinned Copper Braid | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
435 | ZSL-60210A | - | - | Gas Position Switch Low for Air Heater Gas Train (GTRN-21) | Position Switch Low | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
436 | ZT-60210A | - | - | Gas Position Transmitter for Air Heater Gas Train (GTRN-21) | Position Transmitter | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | LiY-CY TP 1P x1.0 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
437 | PSH-60210 | - | - | Gas Pressure Switch High for Air Heater Gas Train (GTRN-21) | Pressure Switch High | - | - | - | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | PTC31B Series | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Ref: CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
438 | BV-60210B | - | - | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | - | - | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
439 | ZSO-60210B | - | - | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
440 | ZSC-60210B | - | - | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
441 | VV-60210 | - | - | Gas Venting Valve (main gas) for Air Heater Gas Train (GTRN-21) | Venting Valve (main gas) | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
442 | ZSO-60210C | - | - | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
443 | ZSC-60210C | - | - | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
444 | PSL-60210 | - | - | Gas Pressure Switch Low for Air Heater Gas Train (GTRN-21) | Pressure Switch Low | - | - | - | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | PTC31B Series | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Ref: CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
445 | BV-60210A | - | - | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | - | - | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
446 | ZSO-60210A | - | - | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
447 | ZSC-60210A | - | - | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
448 | PUPD Pump Control Panel | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
449 | ES-60202 | - | 325-01-602-PD-01 | E-Stop for PUPD-11 (Positive Displacement Pump ) | E-Stop | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S05 | C1S05,16 (DI) | ES-60202_DI_1 | 1756-IB32-16 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
450 | PT-60205 | - | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter | 4 - 20 mA | - | - | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | - | - | C1 | S10 | C1S10,07 (AI) | PT-60205_AI_1 | 1756-IF16-7 | =CA1+MCP-M1 | JB-601 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
451 | FS-60205 | - | 325-01-602-PD-01 | Cooling Water Return Flow Switch for Positive Displacement Pump (PUPD-11) | Flow Switch | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C1 | S05 | C1S05,17 (DI) | FS-60205_DI_1 | 1756-IB32-17 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
452 | XS-60205 | - | 325-01-602-PD-01 | Start / Stop Command for PUPD-11 (Positive Displacement Pump ) | Start / Stop Command | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C7 | S05 | C7S05,29 (DO) | XS-60205_DO_1 |  | MCC | MCC | MCC | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
453 | VS-60205 | - | 325-01-602-PD-01 | Vibration Gear Box Vibration Switch for Switch Vibration for PUPD-11 (PUPD-11) | Vibration Switch | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | C1 | S05 | C1S05,25 (DI) | VS-60205_DI_1 | 1756-IB32-25 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 4Cx1 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
454 | XV-60205A | - | 325-01-602-PD-01 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) | On/Off Valve | 24 VDC energized,Dry Contact | On-Off | - | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | - | - | - | - | - | C1 | S06, S08 | C1S06,15 (DI); C1S06,16 (DI); C1S08,27 (DO) | XV-60205A_DI_1; XV-60205A_DI_2; XV-60205A_DO_1 | 1756-IB32-15, 1756-IB32-16, 1756-OB32-27 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
455 | YA-60205 | - | 325-01-602-PD-01 | Fault Command | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,21 (DI) | YA-60205_DI_1 | 1756-IB32-21 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
456 | YI-60205 | - | 325-01-602-PD-01 | Run Command | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C1 | S06 | C1S06,22 (DI) | YI-60205_DI_1 | 1756-IB32-22 | =CA1+MCP-M1 | JB-601 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
457 | Suppression Panel | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
458 | PSH-61301 | - | 325-01-613-PD-01 | Gas and Powder Pressure Switch High for Storage Bin Cyclone Inlet Duct (####-##) | Pressure Switch High | - | - | - | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | PTC31B Series | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
459 | PSH-60220 | - | 325-01-602-PD-04 | Gas Pressure Switch High for Spray Chamber (CHAM-21) | Pressure Switch High | - | - | - | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | PTC31B Series | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
460 | PSH-60230 | - | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-21) | Pressure Switch High | - | - | - | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | PTC31B Series | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
461 | PSH-60231 | - | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-22) | Pressure Switch High | - | - | - | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | PTC31B Series | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
462 | PSH-60224 | - | 325-01-602-PD-05 | Gas and Powder Pressure Switch High for Bag House (BGHS-21) | Pressure Switch High | - | - | - | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | PTC31B Series | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | - | - | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
463 | REMOTE I-O Area-200 | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
464 | HV-20204 | HV-2022 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C5 | S01 | C5S01,07 (DI) | HV-20204_DI_1 | 1756-IB32-7 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
465 | HV-20205 | HV-2024 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C5 | S01 | C5S01,08 (DI) | HV-20205_DI_1 | 1756-IB32-8 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
466 | HV-20206 | HV-2026 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C5 | S01 | C5S01,09 (DI) | HV-20206_DI_1 | 1756-IB32-9 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
467 | HV-20207 | HV-2030 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C5 | S01 | C5S01,10 (DI) | HV-20207_DI_1 | 1756-IB32-10 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
468 | HV-20208 | HV-2032 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C5 | S01 | C5S01,11 (DI) | HV-20208_DI_1 | 1756-IB32-11 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
469 | HV-20209 | HV-2035 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C5 | S01 | C5S01,12 (DI) | HV-20209_DI_1 | 1756-IB32-12 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
470 | HV-20210 | HV-2038 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | Dry Contact | On-Off | - | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | TF-20DFS + APL-210N Limit Switch | Flange Cl.150 RF / Manual Lever | Dry Contact Limit Switches (2x DI) | - | 1 | - | - | - | C5 | S01 | C5S01,13 (DI) | HV-20210_DI_1 | 1756-IB32-13 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 4 Cores x 1.0 mm² | Flame-Retardant Heavy-Duty PVC Outer Sheath | M20x1.5 / 1/2" NPT Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
471 | XV-20201 | - | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | Ex d | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C5 | S01, S03 | C5S01,26 (DI); C5S01,27 (DI); C5S03,01 (DO) | XV-20201_DI_1; XV-20201_DI_2; XV-20201_DO_1 | 1756-IB32-26, 1756-IB32-27, 1756-OB32-1 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
472 | XV-20202 | - | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | Ex d | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C5 | S01, S03 | C5S01,28 (DI); C5S01,29 (DI); C5S03,02 (DO) | XV-20202_DI_1; XV-20202_DI_2; XV-20202_DO_1 | 1756-IB32-28, 1756-IB32-29, 1756-OB32-2 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
473 | XV-20203 | - | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 24 VDC energized | On-Off | Ex d | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C5 | S01, S03 | C5S01,30 (DI); C5S01,31 (DI); C5S03,03 (DO) | XV-20203_DI_1; XV-20203_DI_2; XV-20203_DO_1 | 1756-IB32-30, 1756-IB32-31, 1756-OB32-3 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
474 | XV-20211 | - | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | Ex d | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C5 | S02, S03 | C5S02,00 (DI); C5S02,01 (DI); C5S03,04 (DO) | XV-20211_DI_1; XV-20211_DI_2; XV-20211_DO_1 | 1756-IB32-0, 1756-IB32-1, 1756-OB32-4 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
475 | XV-20212 | - | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | Ex d | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C5 | S02, S03 | C5S02,02 (DI); C5S02,03 (DI); C5S03,05 (DO) | XV-20212_DI_1; XV-20212_DI_2; XV-20212_DO_1 | 1756-IB32-2, 1756-IB32-3, 1756-OB32-5 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
476 | XV-20213 | - | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 24 VDC energized | On-Off | Ex d | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C5 | S02, S03 | C5S02,04 (DI); C5S02,05 (DI); C5S03,06 (DO) | XV-20213_DI_1; XV-20213_DI_2; XV-20213_DO_1 | 1756-IB32-4, 1756-IB32-5, 1756-OB32-6 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
477 | LS-814201 | LS-81001 | 325-01-814-PD-01 | Level alarm low | Level switch | Dry Contact | On-Off | Ex ic | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | FTL51B Series | Thread 3/4" NPT / Tri-Clamp | 24VDC / Relay Contact Output | - | 1 | - | - | - | - | - | - | - | - | - | - | UNMAPPED | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 3 Cores x 1.5 mm² | Heavy-Duty PVC Insulation & Outer Jacket | M20x1.5 Ex d/e Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
478 | PCM-20201 | PCM-2030 | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2030 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | - | C6 | S05, S06 | C6S05,00 (DO); C6S05,01 (DO); C6S06,00 (DI); C6S06,01 (DI) | PCM-2030_DO_1; PCM-2030_DO_2; PCM-2030_DI_1... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC 200 PANEL) | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
479 | PCM-2031 | - | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2031 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 2 | 2 | - | - | - | C6 | S05, S06 | C6S05,02 (DO); C6S05,03 (DO); C6S06,02 (DI); C6S06,03 (DI) | PCM-2031_DO_1; PCM-2031_DO_2; PCM-2031_DI_1... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
480 | PCY-814201 | PCY-81001 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81001 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C6, C7 | S00, S05, S06 | C6S05,04 (DO); C6S06,04 (DI); C6S06,05 (DI); C6S06,06 (DI)... | PCY-814201_DO_1; PCY-814201_DI_1; PCY-814201_DI_2... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC 810 PANEL) | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
481 | PCY-814202 | PCY-81002 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81002 | - | 24 VDC energized | On-Off | - | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | Centerline 2500 Draw-out Bucket | Terminal Block in MCC Compartment | 24VDC Interlock / 380VAC 3-Phase | 1 | 3 | - | - | 1 | C6, C7 | S00, S05, S06 | C6S05,05 (DO); C6S06,07 (DI); C6S06,08 (DI); C6S06,09 (DI)... | PCY-814202_DO_1; PCY-814202_DI_1; PCY-814202_DI_2... |  | MCC | MCC | MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 8 - 12 Cores x 1.5 mm² | Heavy-Duty PVC Control Cable | M25 / M32 Brass Industrial Gland | MCC Internal Wiring Duct / Multi-Core Interlock Trunk
482 | LPG Station | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
483 | FT-913201 | FT-80301 | 325-01-913-PD-02 | Flow outlet LPG line | Coriolis Flow Transmitter | 4 - 20 mA,Pulse | 0-1000kg/hr | Ex d | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | 8E3B50 Series | Flange ASME B16.5 Cl.150 RF, 316L | 4-20mA HART / 24VDC Loop/Aux | - | 1 | - | 2 | - | C5 | S01, S04 | C5S01,01 (DI); C5S04,01 (AI); C5S04,02 (AI) | FT-913201_DI_1; FT-913201_AI_1; FT-913201_AI_2 | 1756-IB32-1, 1756-IF16-1, 1756-IF16-2 | =CA1+MCP-M5 | RIO-200 | WIRED | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 3 Pairs x 1.0 mm² + 3 Cores x 1.5 mm² | Individually & Overall Shielded Twisted Pairs | M20x1.5 Brass Nickel-Plated Ex d/e Gland | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Trunk Cable to CA1
484 | LT-913201 | LT-80301 | 325-01-913-PD-01 | Level LPG in storage | Level transmitter | 4 - 20 mA | - | Ex ia | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic Level) | PMP43 Flush Diaphragm | Universal Clamp / Flush Mount | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C5 | S04 | C5S04,05 (AI) | LT-913201_AI_1 | 1756-IF16-5 | =CA1+MCP-M5 | RIO-200 | WIRED | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Polyamide Ex i (Blue) | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
485 | PT-913201 | PT-80302 | 325-01-913-PD-02 | Pressure outlet LPG line | Pressure Transmitter | 4 - 20 mA | 0 - 10 barg | Ex d | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | PMP51B / PMP43 Hygienic | 1/2" NPT Male / Tri-Clamp Clamp | 2-wire 4-20mA HART / 24VDC | - | - | - | 1 | - | C5 | S04 | C5S04,06 (AI) | PT-913201_AI_1 | 1756-IF16-6 | =CA1+MCP-M5 | RIO-200 | WIRED | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 1 Pair x 1.0 mm² | Al-Mylar Tape Screen + Tinned Copper Braid Shield (100% Coverage) | M20x1.5 Brass Nickel-Plated Ex d/e | LiY-CY(IS/OS) 16Px0.75 Multi-Pair Shielded Trunk Cable to CA1
486 | XV-913201 | - | 325-01-913-PD-02 | Outlet LPG line | Automatic on/off valve | 24 VDC energized | On-Off | Ex d | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | TF-20DFS + EL-O-Matic F + ESV Solenoid | Flange Cl.150 RF / 1/4" Air Supply | 24VDC Solenoid (DO) + Dry Contact LS (DI) | 1 | 2 | - | - | - | C5 | S02, S03, S04 | C5S02,06 (DI); C5S02,07 (DI); C5S03,07 (DO); C5S04,08 (AI) | XV-913201_DI_1; XV-913201_DI_1; XV-913201_DO_1... | 1756-IB32-6, 1756-IB32-7, 1756-IF16-8, 1756-OB32-7 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 3 Cores x 1.5 mm² + 4 Cores x 1.0 mm² | Heavy-Duty PVC Outer Sheath / Annealed Copper Conductors | M20x1.5 / 1/2" NPT Ex d Double Compression Gland | CVV 30Cx1.5 Multi-Core Control Trunk Cable to CA1
487 | Gas Vaporizer 5 | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
488 | XA-80305A | - | 325-01-803-PD-02 | Gas Vaporizer 5 control status | Gas vaporizer Ready | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C5 | S01 | C5S01,14 (DI) | XA-80305A_DI_1 | 1756-IB32-14 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 16Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
489 | XA-80305B | - | 325-01-803-PD-02 | Gas Vaporizer 5 control status | Gas vaporizer Run | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C5 | S01 | C5S01,15 (DI) | XA-80305B_DI_1 | 1756-IB32-15 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
490 | XA-80305C | - | 325-01-803-PD-02 | Gas Vaporizer 5 control status | Gas vaporizer Failed | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C5 | S01 | C5S01,16 (DI) | XA-80305C_DI_1 | 1756-IB32-16 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
491 | XA-80305D | - | 325-01-803-PD-02 | Gas Vaporizer 5 control status | Gas vaporizer Overheated | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C5 | S01 | C5S01,17 (DI) | XA-80305D_DI_1 | 1756-IB32-17 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
492 | XA-80305E | - | 325-01-803-PD-02 | Gas Vaporizer 5 control status | Gas vaporizer Excessive flow tripped | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C5 | S01 | C5S01,18 (DI) | XA-80305E_DI_1 | 1756-IB32-18 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
493 | XA-80305F | - | 325-01-803-PD-02 | Gas Vaporizer 5 control status | Gas vaporizer low water level | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C5 | S01 | C5S01,19 (DI) | XA-80305F_DI_1 | 1756-IB32-19 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
494 | XS-80305 | - | 325-01-803-PD-02 | Start / Stop Command for Gas Vaporizer 5 | Start / Stop Command | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C6 | S05 | C6S05,06 (DO) | XS-80305_DO_1 |  | MCC | MCC | MCC | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
495 | Gas Vaporizer 6 | - | - | - | - | - | - | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | - | - | - | - | - | - | - | - | - | - | - | LOCAL | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
496 | XA-80306A | - | 325-01-803-PD-02 | Gas Vaporizer 6 control status | Gas vaporizer Ready | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C5 | S01 | C5S01,20 (DI) | XA-80306A_DI_1 | 1756-IB32-20 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 16Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
497 | XA-80306B | - | 325-01-803-PD-02 | Gas Vaporizer 6 control status | Gas vaporizer Run | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C5 | S01 | C5S01,21 (DI) | XA-80306B_DI_1 | 1756-IB32-21 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
498 | XA-80306C | - | 325-01-803-PD-02 | Gas Vaporizer 6 control status | Gas vaporizer Failed | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C5 | S01 | C5S01,22 (DI) | XA-80306C_DI_1 | 1756-IB32-22 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
499 | XA-80306D | - | 325-01-803-PD-02 | Gas Vaporizer 6 control status | Gas vaporizer Overheated | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C5 | S01 | C5S01,23 (DI) | XA-80306D_DI_1 | 1756-IB32-23 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
500 | XA-80306E | - | 325-01-803-PD-02 | Gas Vaporizer 6 control status | Gas vaporizer Excessive flow tripped | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C5 | S01 | C5S01,24 (DI) | XA-80306E_DI_1 | 1756-IB32-24 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
501 | XA-80306F | - | 325-01-803-PD-02 | Gas Vaporizer 6 control status | Gas vaporizer low water level | Dry Contact | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | - | 1 | - | - | - | C5 | S01 | C5S01,25 (DI) | XA-80306F_DI_1 | 1756-IB32-25 | =CA1+MCP-M5 | RIO-200 | WIRED | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC
502 | XS-80306 | - | 325-01-803-PD-02 | Start / Stop Command for Gas Vaporizer 6 | Start / Stop Command | 24 VDC energized | On-Off | - | Industrial Process Equipment | Standard Process Field Device | - | Standard Process Connection | 24VDC / Dry Contact | 1 | - | - | - | - | C6 | S05 | C6S05,07 (DO) | XS-80306_DO_1 |  | MCC | MCC | MCC | CVV 3Cx1.5 | 3 Cores x 1.5 mm² | Standard PVC Control Cable | M20x1.5 Cable Gland | Multi-Core Trunk Cable to CA1 / MCC

## Channel_Point_IO_Map
INGREDION (THAILAND) CO., LTD. ¦ PROJECT JET COOKER ¦ CHANNEL-BY-CHANNEL PLC I/O MAP
1,210 I/O Channel Wiring Points Sorted by Chassis, Slot, Point with Instrument Models & Cable Suggestions
Seq No. | Chassis | Slot | Point | Channel Code | Terminal Block | PLC Card Model | I/O Type | Signal Level | PLC Tag Name | Instrument Tag | Instrument Description | Manufacturer | Model Series | Field Cable Suggestion | P&ID No. | Destination JB | Panel Enclosure | Status
1 | C1 | 3 | 0 | C1S03,00 | C1S03-X1 | 1756-IB32-0 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
2 | C1 | 3 | 1 | C1S03,01 | C1S03-X1 | 1756-IB32-1 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
3 | C1 | 3 | 2 | C1S03,02 | C1S03-X1 | 1756-IB32-2 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
4 | C1 | 3 | 3 | C1S03,03 | C1S03-X1 | 1756-IB32-3 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
5 | C1 | 3 | 4 | C1S03,04 | C1S03-X1 | 1756-IB32-4 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
6 | C1 | 3 | 5 | C1S03,05 | C1S03-X1 | 1756-IB32-5 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
7 | C1 | 3 | 6 | C1S03,06 | C1S03-X1 | 1756-IB32-6 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
8 | C1 | 3 | 7 | C1S03,07 | C1S03-X1 | 1756-IB32-7 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
9 | C1 | 3 | 8 | C1S03,08 | C1S03-X1 | 1756-IB32-8 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
10 | C1 | 3 | 9 | C1S03,09 | C1S03-X1 | 1756-IB32-9 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
11 | C1 | 3 | 10 | C1S03,10 | C1S03-X1 | 1756-IB32-10 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
12 | C1 | 3 | 11 | C1S03,11 | C1S03-X1 | 1756-IB32-11 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
13 | C1 | 3 | 12 | C1S03,12 | C1S03-X1 | 1756-IB32-12 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
14 | C1 | 3 | 13 | C1S03,13 | C1S03-X1 | 1756-IB32-13 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
15 | C1 | 3 | 14 | C1S03,14 | C1S03-X1 | 1756-IB32-14 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
16 | C1 | 3 | 15 | C1S03,15 | C1S03-X1 | 1756-IB32-15 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
17 | C1 | 3 | 16 | C1S03,16 | C1S03-X2 | 1756-IB32-16 | DI | Dry Contact | FSL-40201_DI_1 | FSL-40201 | Slurry low flow | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
18 | C1 | 3 | 17 | C1S03,17 | C1S03-X2 | 1756-IB32-17 | DI | Dry Contact | FSL-40202_DI_1 | FSL-40202 | Slurry low flow | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
19 | C1 | 3 | 18 | C1S03,18 | C1S03-X2 | 1756-IB32-18 | DI | 4 - 20 mA,Pulse | FT-40201_DI_1 | FT-40201 | Slurry flowrate & density check transfer line | Endress+Hauser | Promass E 300 (Coriolis Mass Flow) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
20 | C1 | 3 | 19 | C1S03,19 | C1S03-X2 | 1756-IB32-19 | DI | 4 - 20 mA,Pulse | FT-40202_DI_1 | FT-40202 | Feed Slurry Flow Transmitter for Pipe (PIPE) | Endress+Hauser | Promag P 300 (Electromagnetic Flow) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
21 | C1 | 3 | 20 | C1S03,20 | C1S03-X2 | 1756-IB32-20 | DI | Dry Contact | HV-40201_DI_1 | HV-40201 | Slurry Drain line | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
22 | C1 | 3 | 21 | C1S03,21 | C1S03-X2 | 1756-IB32-21 | DI | Dry Contact | HV-40202_DI_1 | HV-40202 | Slurry Drain line | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
23 | C1 | 3 | 22 | C1S03,22 | C1S03-X2 | 1756-IB32-22 | DI | Dry Contact | HV-40203_DI_1 | HV-40203 | Slurry Drain tank TS-40201 | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
24 | C1 | 3 | 23 | C1S03,23 | C1S03-X2 | 1756-IB32-23 | DI | Dry Contact | HV-40204_DI_1 | HV-40204 | Slurry Drain tank TS-40202 | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
25 | C1 | 3 | 24 | C1S03,24 | C1S03-X2 | 1756-IB32-24 | DI | Dry Contact | HV-40205_DI_1 | HV-40205 | Slurry Drain line | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
26 | C1 | 3 | 25 | C1S03,25 | C1S03-X2 | 1756-IB32-25 | DI | Dry Contact | HV-40206_DI_1 | HV-40206 | Slurry Drain tank TS-40203 | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
27 | C1 | 3 | 26 | C1S03,26 | C1S03-X2 | 1756-IB32-26 | DI | 24 VDC energized | XV-40201A_DI_1 | XV-40201A | Slurry feed-in pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
28 | C1 | 3 | 27 | C1S03,27 | C1S03-X2 | 1756-IB32-27 | DI | 24 VDC energized | XV-40201A_DI_2 | XV-40201A | Slurry feed-in pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
29 | C1 | 3 | 28 | C1S03,28 | C1S03-X2 | 1756-IB32-28 | DI | 24 VDC energized | XV-40201B_DI_1 | XV-40201B | Slurry feed-out pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
30 | C1 | 3 | 29 | C1S03,29 | C1S03-X2 | 1756-IB32-29 | DI | 24 VDC energized | XV-40201B_DI_2 | XV-40201B | Slurry feed-out pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
31 | C1 | 3 | 30 | C1S03,30 | C1S03-X2 | 1756-IB32-30 | DI | 24 VDC energized | XV-40201C_DI_1 | XV-40201C | Water washing line outlet pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
32 | C1 | 3 | 31 | C1S03,31 | C1S03-X2 | 1756-IB32-31 | DI | 24 VDC energized | XV-40201C_DI_2 | XV-40201C | Water washing line outlet pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
33 | C1 | 4 | 0 | C1S04,00 | C1S04-X1 | 1756-IB32-0 | DI | 24 VDC energized | XV-40201D_DI_1 | XV-40201D | Slurry circulation pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
34 | C1 | 4 | 1 | C1S04,01 | C1S04-X1 | 1756-IB32-1 | DI | 24 VDC energized | XV-40201D_DI_2 | XV-40201D | Slurry circulation pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
35 | C1 | 4 | 2 | C1S04,02 | C1S04-X1 | 1756-IB32-2 | DI | 24 VDC energized | XV-40201E_DI_1 | XV-40201E | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
36 | C1 | 4 | 3 | C1S04,03 | C1S04-X1 | 1756-IB32-3 | DI | 24 VDC energized | XV-40201E_DI_2 | XV-40201E | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
37 | C1 | 4 | 4 | C1S04,04 | C1S04-X1 | 1756-IB32-4 | DI | 24 VDC energized | XV-40201F_DI_1 | XV-40201F | Slurry feed-to spray dry tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
38 | C1 | 4 | 5 | C1S04,05 | C1S04-X1 | 1756-IB32-5 | DI | 24 VDC energized | XV-40201F_DI_2 | XV-40201F | Slurry feed-to spray dry tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
39 | C1 | 4 | 6 | C1S04,06 | C1S04-X1 | 1756-IB32-6 | DI | 24 VDC energized | XV-40201G_DI_1 | XV-40201G | CIP water washing pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
40 | C1 | 4 | 7 | C1S04,07 | C1S04-X1 | 1756-IB32-7 | DI | 24 VDC energized | XV-40201G_DI_2 | XV-40201G | CIP water washing pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
41 | C1 | 4 | 8 | C1S04,08 | C1S04-X1 | 1756-IB32-8 | DI | 24 VDC energized | XV-40201H_DI_1 | XV-40201H | CIP Hight pressure water washing pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
42 | C1 | 4 | 9 | C1S04,09 | C1S04-X1 | 1756-IB32-9 | DI | 24 VDC energized | XV-40201H_DI_2 | XV-40201H | CIP Hight pressure water washing pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
43 | C1 | 4 | 11 | C1S04,11 | C1S04-X1 | 1756-IB32-11 | DI | 24 VDC energized | XV-40202A_DI_2 | XV-40202A | Slurry feed-in pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
44 | C1 | 4 | 12 | C1S04,12 | C1S04-X1 | 1756-IB32-12 | DI | 24 VDC energized | XV-40202B_DI_1 | XV-40202B | Slurry feed-out pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
45 | C1 | 4 | 13 | C1S04,13 | C1S04-X1 | 1756-IB32-13 | DI | 24 VDC energized | XV-40202B_DI_2 | XV-40202B | Slurry feed-out pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
46 | C1 | 4 | 14 | C1S04,14 | C1S04-X1 | 1756-IB32-14 | DI | 24 VDC energized | XV-40202C_DI_1 | XV-40202C | Water washing line outlet pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
47 | C1 | 4 | 15 | C1S04,15 | C1S04-X1 | 1756-IB32-15 | DI | 24 VDC energized | XV-40202C_DI_2 | XV-40202C | Water washing line outlet pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
48 | C1 | 4 | 16 | C1S04,16 | C1S04-X2 | 1756-IB32-16 | DI | 24 VDC energized | XV-40202D_DI_1 | XV-40202D | Slurry circulation pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
49 | C1 | 4 | 17 | C1S04,17 | C1S04-X2 | 1756-IB32-17 | DI | 24 VDC energized | XV-40202D_DI_2 | XV-40202D | Slurry circulation pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
50 | C1 | 4 | 18 | C1S04,18 | C1S04-X2 | 1756-IB32-18 | DI | 24 VDC energized | XV-40202E_DI_1 | XV-40202E | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
51 | C1 | 4 | 19 | C1S04,19 | C1S04-X2 | 1756-IB32-19 | DI | 24 VDC energized | XV-40202A_DI_1 | XV-40202A | Slurry feed-in pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
52 | C1 | 4 | 19 | C1S04,19 | C1S04-X2 | 1756-IB32-19 | DI | 24 VDC energized | XV-40202E_DI_2 | XV-40202E | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
53 | C1 | 4 | 20 | C1S04,20 | C1S04-X2 | 1756-IB32-20 | DI | 24 VDC energized | XV-40202F_DI_1 | XV-40202F | Slurry feed-to spray dry tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
54 | C1 | 4 | 21 | C1S04,21 | C1S04-X2 | 1756-IB32-21 | DI | 24 VDC energized | XV-40202F_DI_2 | XV-40202F | Slurry feed-to spray dry tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
55 | C1 | 4 | 22 | C1S04,22 | C1S04-X2 | 1756-IB32-22 | DI | 24 VDC energized | XV-40202G_DI_1 | XV-40202G | CIP water washing pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
56 | C1 | 4 | 23 | C1S04,23 | C1S04-X2 | 1756-IB32-23 | DI | 24 VDC energized | XV-40202G_DI_2 | XV-40202G | CIP water washing pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
57 | C1 | 4 | 24 | C1S04,24 | C1S04-X2 | 1756-IB32-24 | DI | 24 VDC energized | XV-40202H_DI_1 | XV-40202H | CIP Hight pressure water washing pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
58 | C1 | 4 | 25 | C1S04,25 | C1S04-X2 | 1756-IB32-25 | DI | 24 VDC energized | XV-40202H_DI_2 | XV-40202H | CIP Hight pressure water washing pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
59 | C1 | 4 | 26 | C1S04,26 | C1S04-X2 | 1756-IB32-26 | DI | 24 VDC energized | XV-40203B_DI_1 | XV-40203B | Slurry feed-out Spray dryer infeed tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
60 | C1 | 4 | 27 | C1S04,27 | C1S04-X2 | 1756-IB32-27 | DI | 24 VDC energized | XV-40203B_DI_2 | XV-40203B | Slurry feed-out Spray dryer infeed tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
61 | C1 | 4 | 28 | C1S04,28 | C1S04-X2 | 1756-IB32-28 | DI | 24 VDC energized | XV-40203C_DI_1 | XV-40203C | Water washing line outlet Spray dryer infeed tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
62 | C1 | 4 | 29 | C1S04,29 | C1S04-X2 | 1756-IB32-29 | DI | 24 VDC energized | XV-40203C_DI_2 | XV-40203C | Water washing line outlet Spray dryer infeed tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
63 | C1 | 4 | 30 | C1S04,30 | C1S04-X2 | 1756-IB32-30 | DI | 24 VDC energized | XV-40203D_DI_1 | XV-40203D | CIP water washing Spray dryer infeed tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
64 | C1 | 4 | 31 | C1S04,31 | C1S04-X2 | 1756-IB32-31 | DI | 24 VDC energized | XV-40203D_DI_2 | XV-40203D | CIP water washing Spray dryer infeed tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
65 | C1 | 5 | 0 | C1S05,00 | C1S05-X1 | 1756-IB32-0 | DI | 24 VDC energized | XV-40203E_DI_1 | XV-40203E | CIP hight pressure water washing Spray dryer infeed tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
66 | C1 | 5 | 1 | C1S05,01 | C1S05-X1 | 1756-IB32-1 | DI | 24 VDC energized | XV-40203E_DI_2 | XV-40203E | CIP hight pressure water washing Spray dryer infeed tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
67 | C1 | 5 | 2 | C1S05,02 | C1S05-X1 | 1756-IB32-2 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
68 | C1 | 5 | 3 | C1S05,03 | C1S05-X1 | 1756-IB32-3 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
69 | C1 | 5 | 4 | C1S05,04 | C1S05-X1 | 1756-IB32-4 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
70 | C1 | 5 | 5 | C1S05,05 | C1S05-X1 | 1756-IB32-5 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
71 | C1 | 5 | 6 | C1S05,06 | C1S05-X1 | 1756-IB32-6 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
72 | C1 | 5 | 7 | C1S05,07 | C1S05-X1 | 1756-IB32-7 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
73 | C1 | 5 | 8 | C1S05,08 | C1S05-X1 | 1756-IB32-8 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
74 | C1 | 5 | 9 | C1S05,09 | C1S05-X1 | 1756-IB32-9 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
75 | C1 | 5 | 10 | C1S05,10 | C1S05-X1 | 1756-IB32-10 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
76 | C1 | 5 | 11 | C1S05,11 | C1S05-X1 | 1756-IB32-11 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
77 | C1 | 5 | 12 | C1S05,12 | C1S05-X1 | 1756-IB32-12 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
78 | C1 | 5 | 13 | C1S05,13 | C1S05-X1 | 1756-IB32-13 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
79 | C1 | 5 | 14 | C1S05,14 | C1S05-X1 | 1756-IB32-14 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
80 | C1 | 5 | 15 | C1S05,15 | C1S05-X1 | 1756-IB32-15 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
81 | C1 | 5 | 16 | C1S05,16 | C1S05-X2 | 1756-IB32-16 | DI | 0 | ES-60202_DI_1 | ES-60202 | E-Stop for PUPD-11 (Positive Displacement Pump ) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-01 | JB-601 | =CA1+MCP-M1 | ACTIVE
82 | C1 | 5 | 17 | C1S05,17 | C1S05-X2 | 1756-IB32-17 | DI | 0 | FS-60205_DI_1 | FS-60205 | Cooling Water Return Flow Switch for Positive Displacement Pump (PUPD-11) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-01 | JB-601 | =CA1+MCP-M1 | ACTIVE
83 | C1 | 5 | 18 | C1S05,18 | C1S05-X2 | 1756-IB32-18 | DI | Dry Contact | LSL-60201_DI_1 | LSL-60201 | Level low switch | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-11 | JB-601 | =CA1+MCP-M1 | ACTIVE
84 | C1 | 5 | 19 | C1S05,19 | C1S05-X2 | 1756-IB32-19 | DI | 24 VDC energized | SV-60201_DI_1 | SV-60201 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
85 | C1 | 5 | 20 | C1S05,20 | C1S05-X2 | 1756-IB32-20 | DI | 24 VDC energized | SV-60201_DI_2 | SV-60201 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
86 | C1 | 5 | 21 | C1S05,21 | C1S05-X2 | 1756-IB32-21 | DI | 24 VDC energized | SV-60202_DI_1 | SV-60202 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
87 | C1 | 5 | 22 | C1S05,22 | C1S05-X2 | 1756-IB32-22 | DI | 24 VDC energized | SV-60202_DI_2 | SV-60202 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
88 | C1 | 5 | 23 | C1S05,23 | C1S05-X2 | 1756-IB32-23 | DI | 24 VDC energized | SV-60203_DI_1 | SV-60203 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
89 | C1 | 5 | 24 | C1S05,24 | C1S05-X2 | 1756-IB32-24 | DI | 24 VDC energized | SV-60203_DI_2 | SV-60203 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
90 | C1 | 5 | 25 | C1S05,25 | C1S05-X2 | 1756-IB32-25 | DI | Dry Contact | VS-60205_DI_1 | VS-60205 | Vibration Gear Box Vibration Switch for Switch Vibration for PUPD-11 (PUPD-11) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-01 | JB-601 | =CA1+MCP-M1 | ACTIVE
91 | C1 | 5 | 26 | C1S05,26 | C1S05-X2 | 1756-IB32-26 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
92 | C1 | 5 | 27 | C1S05,27 | C1S05-X2 | 1756-IB32-27 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
93 | C1 | 5 | 28 | C1S05,28 | C1S05-X2 | 1756-IB32-28 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
94 | C1 | 5 | 29 | C1S05,29 | C1S05-X2 | 1756-IB32-29 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
95 | C1 | 5 | 30 | C1S05,30 | C1S05-X2 | 1756-IB32-30 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
96 | C1 | 5 | 31 | C1S05,31 | C1S05-X2 | 1756-IB32-31 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
97 | C1 | 6 | 0 | C1S06,00 | C1S06-X1 | 1756-IB32-0 | DI | Dry Contact | XA-60202A_DI_1 | XA-60202A | General Alarm Emergency Stop Actuation for XSUP-5601 (Supression Panel) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
98 | C1 | 6 | 1 | C1S06,01 | C1S06-X1 | 1756-IB32-1 | DI | Dry Contact | XA-60202B_DI_1 | XA-60202B | General Fault Controlled Stop for XSUP-5601 (Supression Panel) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
99 | C1 | 6 | 2 | C1S06,02 | C1S06-X1 | 1756-IB32-2 | DI | Dry Contact | XA-60202C_DI_1 | XA-60202C | General Armed Status Indicator for XSUP-5601 (Supression Panel) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
100 | C1 | 6 | 3 | C1S06,03 | C1S06-X1 | 1756-IB32-3 | DI | Dry Contact | XA-60202D_DI_1 | XA-60202D | Power Fault Status Indicator for XSUP-5601 (Supression Panel) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
101 | C1 | 6 | 4 | C1S06,04 | C1S06-X1 | 1756-IB32-4 | DI | Dry Contact | XA-60202E_DI_1 | XA-60202E | Dryer CHAM-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
102 | C1 | 6 | 5 | C1S06,05 | C1S06-X1 | 1756-IB32-5 | DI | Dry Contact | XA-60202F_DI_1 | XA-60202F | CHAM-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
103 | C1 | 6 | 6 | C1S06,06 | C1S06-X1 | 1756-IB32-6 | DI | Dry Contact | XA-60202G_DI_1 | XA-60202G | CYCL-21/22 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
104 | C1 | 6 | 7 | C1S06,07 | C1S06-X1 | 1756-IB32-7 | DI | Dry Contact | XA-60202H_DI_1 | XA-60202H | CYCL-21/22 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
105 | C1 | 6 | 8 | C1S06,08 | C1S06-X1 | 1756-IB32-8 | DI | - | XA-60202I_DI_1 | XA-60202I | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
106 | C1 | 6 | 9 | C1S06,09 | C1S06-X1 | 1756-IB32-9 | DI | Dry Contact | XA-60202J_DI_1 | XA-60202J | BGHS-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
107 | C1 | 6 | 10 | C1S06,10 | C1S06-X1 | 1756-IB32-10 | DI | Dry Contact | XA-60202K_DI_1 | XA-60202K | BGHS-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
108 | C1 | 6 | 11 | C1S06,11 | C1S06-X1 | 1756-IB32-11 | DI | Dry Contact | XA-60202L_DI_1 | XA-60202L | CYCL-31 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
109 | C1 | 6 | 12 | C1S06,12 | C1S06-X1 | 1756-IB32-12 | DI | Dry Contact | XA-60202M_DI_1 | XA-60202M | CYCL-31 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
110 | C1 | 6 | 13 | C1S06,13 | C1S06-X1 | 1756-IB32-13 | DI | 24 VDC energized | XV-60202_DI_1 | XV-60202 | High Pressure Water On/Off Valve for Drain Pipe | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-11 | JB-601 | =CA1+MCP-M1 | ACTIVE
111 | C1 | 6 | 14 | C1S06,14 | C1S06-X1 | 1756-IB32-14 | DI | 24 VDC energized | XV-60202_DI_2 | XV-60202 | High Pressure Water On/Off Valve for Drain Pipe | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-11 | JB-601 | =CA1+MCP-M1 | ACTIVE
112 | C1 | 6 | 15 | C1S06,15 | C1S06-X1 | 1756-IB32-15 | DI | 24 VDC energized,Dry Contact | XV-60205A_DI_1 | XV-60205A | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-01 | JB-601 | =CA1+MCP-M1 | ACTIVE
113 | C1 | 6 | 16 | C1S06,16 | C1S06-X2 | 1756-IB32-16 | DI | 24 VDC energized,Dry Contact | XV-60205A_DI_2 | XV-60205A | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-01 | JB-601 | =CA1+MCP-M1 | ACTIVE
114 | C1 | 6 | 17 | C1S06,17 | C1S06-X2 | 1756-IB32-17 | DI | - | XV-60240D_DI_1 | XV-60240D | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-05 | JB-601 | =CA1+MCP-M1 | ACTIVE
115 | C1 | 6 | 18 | C1S06,18 | C1S06-X2 | 1756-IB32-18 | DI | - | XV-60240D_DI_2 | XV-60240D | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 3-25-01-602-PD-05 | JB-601 | =CA1+MCP-M1 | ACTIVE
116 | C1 | 6 | 19 | C1S06,19 | C1S06-X2 | 1756-IB32-19 | DI | - | XV-60240D_DI_1 | XV-60240D | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-05 | JB-601 | =CA1+MCP-M1 | ACTIVE
117 | C1 | 6 | 20 | C1S06,20 | C1S06-X2 | 1756-IB32-20 | DI | - | XV-60240D_DI_2 | XV-60240D | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 3-25-01-602-PD-05 | JB-601 | =CA1+MCP-M1 | ACTIVE
118 | C1 | 6 | 21 | C1S06,21 | C1S06-X2 | 1756-IB32-21 | DI | 0 | YA-60205_DI_1 | YA-60205 | Fault Command | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-01 | JB-601 | =CA1+MCP-M1 | ACTIVE
119 | C1 | 6 | 22 | C1S06,22 | C1S06-X2 | 1756-IB32-22 | DI | 0 | YI-60205_DI_1 | YI-60205 | Run Command | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-01 | JB-601 | =CA1+MCP-M1 | ACTIVE
120 | C1 | 6 | 23 | C1S06,23 | C1S06-X2 | 1756-IB32-23 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
121 | C1 | 6 | 24 | C1S06,24 | C1S06-X2 | 1756-IB32-24 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
122 | C1 | 6 | 25 | C1S06,25 | C1S06-X2 | 1756-IB32-25 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
123 | C1 | 6 | 26 | C1S06,26 | C1S06-X2 | 1756-IB32-26 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
124 | C1 | 6 | 27 | C1S06,27 | C1S06-X2 | 1756-IB32-27 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
125 | C1 | 6 | 28 | C1S06,28 | C1S06-X2 | 1756-IB32-28 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
126 | C1 | 6 | 29 | C1S06,29 | C1S06-X2 | 1756-IB32-29 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
127 | C1 | 6 | 30 | C1S06,30 | C1S06-X2 | 1756-IB32-30 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
128 | C1 | 6 | 31 | C1S06,31 | C1S06-X2 | 1756-IB32-31 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
129 | C1 | 7 | 0 | C1S07,00 | C1S07-X1 | 1756-OB32-0 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
130 | C1 | 7 | 1 | C1S07,01 | C1S07-X1 | 1756-OB32-1 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
131 | C1 | 7 | 2 | C1S07,02 | C1S07-X1 | 1756-OB32-2 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
132 | C1 | 7 | 3 | C1S07,03 | C1S07-X1 | 1756-OB32-3 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
133 | C1 | 7 | 4 | C1S07,04 | C1S07-X1 | 1756-OB32-4 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
134 | C1 | 7 | 5 | C1S07,05 | C1S07-X1 | 1756-OB32-5 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
135 | C1 | 7 | 6 | C1S07,06 | C1S07-X1 | 1756-OB32-6 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
136 | C1 | 7 | 7 | C1S07,07 | C1S07-X1 | 1756-OB32-7 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
137 | C1 | 7 | 8 | C1S07,08 | C1S07-X1 | 1756-OB32-8 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
138 | C1 | 7 | 9 | C1S07,09 | C1S07-X1 | 1756-OB32-9 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
139 | C1 | 7 | 10 | C1S07,10 | C1S07-X1 | 1756-OB32-10 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
140 | C1 | 7 | 11 | C1S07,11 | C1S07-X1 | 1756-OB32-11 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
141 | C1 | 7 | 12 | C1S07,12 | C1S07-X1 | 1756-OB32-12 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
142 | C1 | 7 | 13 | C1S07,13 | C1S07-X1 | 1756-OB32-13 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
143 | C1 | 7 | 14 | C1S07,14 | C1S07-X1 | 1756-OB32-14 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
144 | C1 | 7 | 15 | C1S07,15 | C1S07-X1 | 1756-OB32-15 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | CA1 | =CA1+MCP-M1 | SPARE
145 | C1 | 7 | 16 | C1S07,16 | C1S07-X2 | 1756-OB32-16 | DO | 24 VDC energized | XV-40202E_DO_1 | XV-40202E | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
146 | C1 | 7 | 17 | C1S07,17 | C1S07-X2 | 1756-OB32-17 | DO | 24 VDC energized | XV-40202F_DO_1 | XV-40202F | Slurry feed-to spray dry tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
147 | C1 | 7 | 18 | C1S07,18 | C1S07-X2 | 1756-OB32-18 | DO | 24 VDC energized | XV-40202G_DO_1 | XV-40202G | CIP water washing pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
148 | C1 | 7 | 19 | C1S07,19 | C1S07-X2 | 1756-OB32-19 | DO | 24 VDC energized | XV-40202H_DO_1 | XV-40202H | CIP Hight pressure water washing pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
149 | C1 | 7 | 20 | C1S07,20 | C1S07-X2 | 1756-OB32-20 | DO | 24 VDC energized | XV-40203B_DO_1 | XV-40203B | Slurry feed-out Spray dryer infeed tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
150 | C1 | 7 | 21 | C1S07,21 | C1S07-X2 | 1756-OB32-21 | DO | 24 VDC energized | XV-40203C_DO_1 | XV-40203C | Water washing line outlet Spray dryer infeed tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
151 | C1 | 7 | 22 | C1S07,22 | C1S07-X2 | 1756-OB32-22 | DO | 24 VDC energized | XV-40203D_DO_1 | XV-40203D | CIP water washing Spray dryer infeed tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
152 | C1 | 7 | 23 | C1S07,23 | C1S07-X2 | 1756-OB32-23 | DO | 24 VDC energized | XV-40203E_DO_1 | XV-40203E | CIP hight pressure water washing Spray dryer infeed tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
153 | C1 | 7 | 24 | C1S07,24 | C1S07-X2 | 1756-OB32-24 | DO | 24 VDC energized | SV-40201_DO_1 | SV-40201 | Water service pH analyzer in pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
154 | C1 | 7 | 25 | C1S07,25 | C1S07-X2 | 1756-OB32-25 | DO | 24 VDC energized | SV-40202_DO_1 | SV-40202 | Water service pH analyzer in pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
155 | C1 | 7 | 26 | C1S07,26 | C1S07-X2 | 1756-OB32-26 | DO | 24 VDC energized | SV-40203_DO_1 | SV-40203 | Air service pH analyzer in pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
156 | C1 | 7 | 27 | C1S07,27 | C1S07-X2 | 1756-OB32-27 | DO | 24 VDC energized | SV-40204_DO_1 | SV-40204 | Air service pH analyzer in pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
157 | C1 | 7 | 28 | C1S07,28 | C1S07-X2 | 1756-OB32-28 | DO | 24 VDC energized | XV-40201A_DO_1 | XV-40201A | Slurry feed-in pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
158 | C1 | 7 | 29 | C1S07,29 | C1S07-X2 | 1756-OB32-29 | DO | 24 VDC energized | XV-40201B_DO_1 | XV-40201B | Slurry feed-out pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
159 | C1 | 7 | 30 | C1S07,30 | C1S07-X2 | 1756-OB32-30 | DO | 24 VDC energized | XV-40201C_DO_1 | XV-40201C | Water washing line outlet pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
160 | C1 | 7 | 31 | C1S07,31 | C1S07-X2 | 1756-OB32-31 | DO | 24 VDC energized | XV-40201D_DO_1 | XV-40201D | Slurry circulation pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
161 | C1 | 8 | 0 | C1S08,00 | C1S08-X1 | 1756-OB32-0 | DO | 24 VDC energized | XV-40201E_DO_1 | XV-40201E | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
162 | C1 | 8 | 1 | C1S08,01 | C1S08-X1 | 1756-OB32-1 | DO | 24 VDC energized | XV-40201F_DO_1 | XV-40201F | Slurry feed-to spray dry tank | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
163 | C1 | 8 | 2 | C1S08,02 | C1S08-X1 | 1756-OB32-2 | DO | 24 VDC energized | XV-40201G_DO_1 | XV-40201G | CIP water washing pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
164 | C1 | 8 | 3 | C1S08,03 | C1S08-X1 | 1756-OB32-3 | DO | 24 VDC energized | XV-40201H_DO_1 | XV-40201H | CIP Hight pressure water washing pH Adjustment tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
165 | C1 | 8 | 4 | C1S08,04 | C1S08-X1 | 1756-OB32-4 | DO | 24 VDC energized | XV-40202A_DO_1 | XV-40202A | Slurry feed-in pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
166 | C1 | 8 | 5 | C1S08,05 | C1S08-X1 | 1756-OB32-5 | DO | 24 VDC energized | XV-40202B_DO_1 | XV-40202B | Slurry feed-out pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
167 | C1 | 8 | 6 | C1S08,06 | C1S08-X1 | 1756-OB32-6 | DO | 24 VDC energized | XV-40202C_DO_1 | XV-40202C | Water washing line outlet pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
168 | C1 | 8 | 7 | C1S08,07 | C1S08-X1 | 1756-OB32-7 | DO | 24 VDC energized | XV-40202D_DO_1 | XV-40202D | Slurry circulation pH Adjustment tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
169 | C1 | 8 | 8 | C1S08,08 | C1S08-X1 | 1756-OB32-8 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
170 | C1 | 8 | 9 | C1S08,09 | C1S08-X1 | 1756-OB32-9 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
171 | C1 | 8 | 10 | C1S08,10 | C1S08-X1 | 1756-OB32-10 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
172 | C1 | 8 | 11 | C1S08,11 | C1S08-X1 | 1756-OB32-11 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
173 | C1 | 8 | 12 | C1S08,12 | C1S08-X1 | 1756-OB32-12 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
174 | C1 | 8 | 13 | C1S08,13 | C1S08-X1 | 1756-OB32-13 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
175 | C1 | 8 | 14 | C1S08,14 | C1S08-X1 | 1756-OB32-14 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
176 | C1 | 8 | 15 | C1S08,15 | C1S08-X1 | 1756-OB32-15 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
177 | C1 | 8 | 16 | C1S08,16 | C1S08-X2 | 1756-OB32-16 | DO | 24 VDC energized | SV-60201_DO_1 | SV-60201 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
178 | C1 | 8 | 17 | C1S08,17 | C1S08-X2 | 1756-OB32-17 | DO | 24 VDC energized | SV-60202_DO_1 | SV-60202 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
179 | C1 | 8 | 18 | C1S08,18 | C1S08-X2 | 1756-OB32-18 | DO | 24 VDC energized | SV-60230_DO_1 | SV-60230 | PA On/Off Valve for Cyclone Air Hammer 27 (CYCL-21) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-602-PD-04 | JB-601 | =CA1+MCP-M1 | ACTIVE
180 | C1 | 8 | 19 | C1S08,19 | C1S08-X2 | 1756-OB32-19 | DO | 24 VDC energized | SV-60203_DO_1 | SV-60203 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
181 | C1 | 8 | 20 | C1S08,20 | C1S08-X2 | 1756-OB32-20 | DO | 24 VDC energized | SV-60240A_DO_1 | SV-60240A | PA On/Off Valve for Cyclone Air Hammer 29A (BGHS-21) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-602-PD-05 | JB-601 | =CA1+MCP-M1 | ACTIVE
182 | C1 | 8 | 21 | C1S08,21 | C1S08-X2 | 1756-OB32-21 | DO | 24 VDC energized | SV-60231_DO_1 | SV-60231 | PA On/Off Valve for Cyclone Air Hammer 28 (CYCL-22) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-602-PD-04 | JB-601 | =CA1+MCP-M1 | ACTIVE
183 | C1 | 8 | 22 | C1S08,22 | C1S08-X2 | 1756-OB32-22 | DO | 24 VDC energized | SV-60240B_DO_1 | SV-60240B | PA On/Off Valve for Cyclone Air Hammer 29B (BGHS-21) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-602-PD-05 | JB-601 | =CA1+MCP-M1 | ACTIVE
184 | C1 | 8 | 23 | C1S08,23 | C1S08-X2 | 1756-OB32-23 | DO | 24 VDC energized | SV-60240C_DO_1 | SV-60240C | PA On/Off Valve for Cyclone Air Hammer 29C (BGHS-21) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-602-PD-05 | JB-601 | =CA1+MCP-M1 | ACTIVE
185 | C1 | 8 | 24 | C1S08,24 | C1S08-X2 | 1756-OB32-24 | DO | - | XV-60240D_DO_1 | XV-60240D | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-05 | JB-601 | =CA1+MCP-M1 | ACTIVE
186 | C1 | 8 | 25 | C1S08,25 | C1S08-X2 | 1756-OB32-25 | DO | 24 VDC energized | XV-60251_DO_1 | XV-60251 | Liquid On/Off Valve for Drain Pipe (PIPE) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-01 | JB-601 | =CA1+MCP-M1 | ACTIVE
187 | C1 | 8 | 26 | C1S08,26 | C1S08-X2 | 1756-OB32-26 | DO | 24 VDC energized | XV-60202_DO_1 | XV-60202 | High Pressure Water On/Off Valve for Drain Pipe | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-11 | JB-601 | =CA1+MCP-M1 | ACTIVE
188 | C1 | 8 | 27 | C1S08,27 | C1S08-X2 | 1756-OB32-27 | DO | 24 VDC energized,Dry Contact | XV-60205A_DO_1 | XV-60205A | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-01 | JB-601 | =CA1+MCP-M1 | ACTIVE
189 | C1 | 8 | 28 | C1S08,28 | C1S08-X2 | 1756-OB32-28 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
190 | C1 | 8 | 29 | C1S08,29 | C1S08-X2 | 1756-OB32-29 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
191 | C1 | 8 | 30 | C1S08,30 | C1S08-X2 | 1756-OB32-30 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
192 | C1 | 8 | 31 | C1S08,31 | C1S08-X2 | 1756-OB32-31 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
193 | C1 | 9 | 0 | C1S09,00 | C1S09-X1 | 1756-IF16-0 | AI | 4 - 20 mA,Pulse | FT-40201_AI_1 | FT-40201 | Slurry flowrate & density check transfer line | Endress+Hauser | Promass E 300 (Coriolis Mass Flow) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
194 | C1 | 9 | 1 | C1S09,01 | C1S09-X1 | 1756-IF16-1 | AI | 4 - 20 mA,Pulse | FT-40201_AI_2 | FT-40201 | Slurry flowrate & density check transfer line | Endress+Hauser | Promass E 300 (Coriolis Mass Flow) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
195 | C1 | 9 | 2 | C1S09,02 | C1S09-X1 | 1756-IF16-2 | AI | 4 - 20 mA,Pulse | FT-40202_AI_1 | FT-40202 | Feed Slurry Flow Transmitter for Pipe (PIPE) | Endress+Hauser | Promag P 300 (Electromagnetic Flow) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
196 | C1 | 9 | 3 | C1S09,03 | C1S09-X1 | 1756-IF16-3 | AI | 4 - 20 mA | LT-40203_AI_1 | LT-40203 | Level transmitter in Spray dryer infeed tank | Endress+Hauser | Micropilot FMR67B (80GHz Radar Level) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
197 | C1 | 9 | 4 | C1S09,04 | C1S09-X1 | 1756-IF16-4 | AI | 4 - 20 mA | LT-40201_AI_1 | LT-40201 | Level transmitter in pH Adjustment tank 1 | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic Level) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
198 | C1 | 9 | 5 | C1S09,05 | C1S09-X1 | 1756-IF16-5 | AI | 4 - 20 mA | LT-40202_AI_1 | LT-40202 | Level transmitter in pH Adjustment tank 2 | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic Level) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
199 | C1 | 9 | 6 | C1S09,06 | C1S09-X1 | 1756-IF16-6 | AI | 4 - 20 mA | pHT-40201_AI_1 | pHT-40201 | pH analyzer in pH Adjustment tank 1 | Mettler Toledo | M300G2 + InPro3250i (pH System) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
200 | C1 | 9 | 7 | C1S09,07 | C1S09-X1 | 1756-IF16-7 | AI | 4 - 20 mA | pHT-40202_AI_1 | pHT-40202 | pH analyzer in pH Adjustment tank 2 | Mettler Toledo | M300G2 + InPro3250i (pH System) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
201 | C1 | 9 | 8 | C1S09,08 | C1S09-X1 | 1756-IF16-8 | AI | 4 - 20 mA | PT-40201_AI_1 | PT-40201 | Pressure Transmitter for Inlet Filter Strainer (FSTR-11) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
202 | C1 | 9 | 9 | C1S09,09 | C1S09-X1 | 1756-IF16-9 | AI | 4 - 20 mA | PT-40202_AI_1 | PT-40202 | Feed Slurry Pressure Transmitter for Pipe (PIPE) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-402-PD-02 | JB-401 | =CA1+MCP-M1 | ACTIVE
203 | C1 | 9 | 10 | C1S09,10 | C1S09-X1 | 1756-IF16-10 | AI | 4 - 20 mA | PT-60202_AI_1 | PT-60202 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-01 | JB-401 | =CA1+MCP-M1 | ACTIVE
204 | C1 | 9 | 11 | C1S09,11 | C1S09-X1 | 1756-IF16-11 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
205 | C1 | 9 | 12 | C1S09,12 | C1S09-X1 | 1756-IF16-12 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
206 | C1 | 9 | 13 | C1S09,13 | C1S09-X1 | 1756-IF16-13 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
207 | C1 | 9 | 14 | C1S09,14 | C1S09-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
208 | C1 | 9 | 15 | C1S09,15 | C1S09-X1 | 1756-IF16-15 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-401 | =CA1+MCP-M1 | SPARE
209 | C1 | 10 | 0 | C1S10,00 | C1S10-X1 | 1756-IF16-0 | AI | 4 - 20 mA | DPI-60240_AI_1 | DPI-60240 | Gas Pressure Differntial Pressure (Bag House Air Pulsing) | Ashcroft | Model 1132 Differential Pressure Gauge | LiY-CY TP 1Px1.0 | 325-01-602-PD-05 | JB-601 | =CA1+MCP-M1 | ACTIVE
210 | C1 | 10 | 1 | C1S10,01 | C1S10-X1 | 1756-IF16-1 | AI | 4 - 20 mA | DPT-60202_AI_1 | DPT-60202 | Gas Pressure Differential Transmitter for Air Filter (FICA-31) | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
211 | C1 | 10 | 2 | C1S10,02 | C1S10-X1 | 1756-IF16-2 | AI | 4 - 20 mA | FT-60201_AI_1 | FT-60201 | Gas Flow Transmitter for Cooling Conveying Cold Air Duct (DTCA-32) | Endress+Hauser | t-mass I 300 (Thermal Mass Flow) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
212 | C1 | 10 | 3 | C1S10,03 | C1S10-X1 | 1756-IF16-3 | AI | 4 - 20 mA | FT-60204_AI_1 | FT-60204 | Compressed air Flow | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-602-PD-10 | JB-601 | =CA1+MCP-M1 | ACTIVE
213 | C1 | 10 | 4 | C1S10,04 | C1S10-X1 | 1756-IF16-4 | AI | 4 - 20 mA | FT-61307_AI_1 | FT-61307 | Compressed air Flow | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-04 | JB-601 | =CA1+MCP-M1 | ACTIVE
214 | C1 | 10 | 5 | C1S10,05 | C1S10-X1 | 1756-IF16-5 | AI | 4 - 20 mA | PT-60203_AI_1 | PT-60203 | Gas Pressure Transmitter for Cool Air Duct (DTCA-32) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-08 | JB-601 | =CA1+MCP-M1 | ACTIVE
215 | C1 | 10 | 6 | C1S10,06 | C1S10-X1 | 1756-IF16-6 | AI | 4 - 20 mA | PT-60204_AI_1 | PT-60204 | Pressure transmitter | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-10 | JB-601 | =CA1+MCP-M1 | ACTIVE
216 | C1 | 10 | 7 | C1S10,07 | C1S10-X1 | 1756-IF16-7 | AI | 4 - 20 mA | PT-60205_AI_1 | PT-60205 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-01 | JB-601 | =CA1+MCP-M1 | ACTIVE
217 | C1 | 10 | 8 | C1S10,08 | C1S10-X1 | 1756-IF16-8 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
218 | C1 | 10 | 9 | C1S10,09 | C1S10-X1 | 1756-IF16-9 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
219 | C1 | 10 | 10 | C1S10,10 | C1S10-X1 | 1756-IF16-10 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
220 | C1 | 10 | 11 | C1S10,11 | C1S10-X1 | 1756-IF16-11 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
221 | C1 | 10 | 12 | C1S10,12 | C1S10-X1 | 1756-IF16-12 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
222 | C1 | 10 | 13 | C1S10,13 | C1S10-X1 | 1756-IF16-13 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
223 | C1 | 10 | 14 | C1S10,14 | C1S10-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
224 | C1 | 10 | 15 | C1S10,15 | C1S10-X1 | 1756-IF16-15 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-601 | =CA1+MCP-M1 | SPARE
225 | C2 | 1 | 0 | C2S01,00 | C2S01-X1 | 1756-IB32-0 | DI | Dry Contact | FS-40204_DI_1 | FS-40204 | Jet Cooker | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-402-PD-01 | JB-402 | =CA1+MCP-M2 | ACTIVE
226 | C2 | 1 | 1 | C2S01,01 | C2S01-X1 | 1756-IB32-1 | DI | Dry Contact | FS-40205_DI_1 | FS-40205 | Jet Cooker | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
227 | C2 | 1 | 2 | C2S01,02 | C2S01-X1 | 1756-IB32-2 | DI | 4 - 20 mA,Pulse | FT-40221_DI_1 | FT-40221 | Jet Cooker | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
228 | C2 | 1 | 3 | C2S01,03 | C2S01-X1 | 1756-IB32-3 | DI | 4 - 20 mA,Pulse | FT-40222_DI_1 | FT-40222 | Jet Cooker | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
229 | C2 | 1 | 4 | C2S01,04 | C2S01-X1 | 1756-IB32-4 | DI | Dry Contact | HV-40207_DI_1 | HV-40207 | Jet Cooker | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-402-PD-01 | JB-402 | =CA1+MCP-M2 | ACTIVE
230 | C2 | 1 | 5 | C2S01,05 | C2S01-X1 | 1756-IB32-5 | DI | Dry Contact | HV-40208_DI_1 | HV-40208 | Jet Cooker | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-402-PD-01 | JB-402 | =CA1+MCP-M2 | ACTIVE
231 | C2 | 1 | 6 | C2S01,06 | C2S01-X1 | 1756-IB32-6 | DI | 24 VDC energized | XV-40203F_DI_1 | XV-40203F | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
232 | C2 | 1 | 7 | C2S01,07 | C2S01-X1 | 1756-IB32-7 | DI | 24 VDC energized | XV-40203F_DI_2 | XV-40203F | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
233 | C2 | 1 | 8 | C2S01,08 | C2S01-X1 | 1756-IB32-8 | DI | 24 VDC energized | XV-40204B_DI_1 | XV-40204B | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-402 | =CA1+MCP-M2 | ACTIVE
234 | C2 | 1 | 9 | C2S01,09 | C2S01-X1 | 1756-IB32-9 | DI | 24 VDC energized | XV-40204B_DI_2 | XV-40204B | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-402 | =CA1+MCP-M2 | ACTIVE
235 | C2 | 1 | 10 | C2S01,10 | C2S01-X1 | 1756-IB32-10 | DI | 24 VDC energized | XV-40204C_DI_1 | XV-40204C | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-402 | =CA1+MCP-M2 | ACTIVE
236 | C2 | 1 | 11 | C2S01,11 | C2S01-X1 | 1756-IB32-11 | DI | 24 VDC energized | XV-40204C_DI_2 | XV-40204C | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-402 | =CA1+MCP-M2 | ACTIVE
237 | C2 | 1 | 12 | C2S01,12 | C2S01-X1 | 1756-IB32-12 | DI | 24 VDC energized | XV-40205A_DI_1 | XV-40205A | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
238 | C2 | 1 | 13 | C2S01,13 | C2S01-X1 | 1756-IB32-13 | DI | 24 VDC energized | XV-40205A_DI_2 | XV-40205A | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
239 | C2 | 1 | 14 | C2S01,14 | C2S01-X1 | 1756-IB32-14 | DI | 24 VDC energized | XV-40205B_DI_1 | XV-40205B | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
240 | C2 | 1 | 15 | C2S01,15 | C2S01-X1 | 1756-IB32-15 | DI | 24 VDC energized | XV-40205B_DI_2 | XV-40205B | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
241 | C2 | 1 | 16 | C2S01,16 | C2S01-X2 | 1756-IB32-16 | DI | 24 VDC energized | XV-40205C_DI_1 | XV-40205C | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
242 | C2 | 1 | 17 | C2S01,17 | C2S01-X2 | 1756-IB32-17 | DI | 24 VDC energized | XV-40205C_DI_2 | XV-40205C | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
243 | C2 | 1 | 18 | C2S01,18 | C2S01-X2 | 1756-IB32-18 | DI | 24 VDC energized | XV-40205D_DI_1 | XV-40205D | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
244 | C2 | 1 | 19 | C2S01,19 | C2S01-X2 | 1756-IB32-19 | DI | 24 VDC energized | XV-40205D_DI_2 | XV-40205D | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
245 | C2 | 1 | 20 | C2S01,20 | C2S01-X2 | 1756-IB32-20 | DI | 24 VDC energized | XV-40205F_DI_1 | XV-40205F | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
246 | C2 | 1 | 21 | C2S01,21 | C2S01-X2 | 1756-IB32-21 | DI | 24 VDC energized | XV-40205F_DI_2 | XV-40205F | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
247 | C2 | 1 | 22 | C2S01,22 | C2S01-X2 | 1756-IB32-22 | DI | 24 VDC energized | XV-40222_DI_1 | XV-40222 | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
248 | C2 | 1 | 23 | C2S01,23 | C2S01-X2 | 1756-IB32-23 | DI | 24 VDC energized | XV-40222_DI_2 | XV-40222 | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
249 | C2 | 1 | 24 | C2S01,24 | C2S01-X2 | 1756-IB32-24 | DI | - | Spare_DI_2 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
250 | C2 | 1 | 25 | C2S01,25 | C2S01-X2 | 1756-IB32-25 | DI | - | Spare_DI_2 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
251 | C2 | 1 | 26 | C2S01,26 | C2S01-X2 | 1756-IB32-26 | DI | - | Spare_DI_2 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
252 | C2 | 1 | 27 | C2S01,27 | C2S01-X2 | 1756-IB32-27 | DI | - | Spare_DI_2 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
253 | C2 | 1 | 28 | C2S01,28 | C2S01-X2 | 1756-IB32-28 | DI | - | Spare_DI_2 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
254 | C2 | 1 | 29 | C2S01,29 | C2S01-X2 | 1756-IB32-29 | DI | - | Spare_DI_2 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
255 | C2 | 1 | 30 | C2S01,30 | C2S01-X2 | 1756-IB32-30 | DI | - | Spare_DI_2 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
256 | C2 | 1 | 31 | C2S01,31 | C2S01-X2 | 1756-IB32-31 | DI | - | Spare_DI_2 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
257 | C2 | 2 | 0 | C2S02,00 | C2S02-X1 | 1756-IB32-0 | DI | 4 - 20 mA | FT-60202_DI_1 | FT-60202 | Steam feed to Spray dryer | Endress+Hauser | Prowirl F 200 (Vortex Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2P x1.0) | 325-01-602-PD-09 | JB-602 | =CA1+MCP-M2 | ACTIVE
258 | C2 | 2 | 1 | C2S02,01 | C2S02-X1 | 1756-IB32-1 | DI | Dry Contact | LSH-60251_DI_1 | LSH-60251 | Water Level Switch High for Fire Deluge Pipe (FWDP-22) | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-04 | JB-602 | =CA1+MCP-M2 | ACTIVE
259 | C2 | 2 | 2 | C2S02,02 | C2S02-X1 | 1756-IB32-2 | DI | Dry Contact | PSL-60220_DI_1 | PSL-60220 | Gas Pressure Switch Low for Spray Chamber (CHAM-21) | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-04 | JB-602 | =CA1+MCP-M2 | ACTIVE
260 | C2 | 2 | 3 | C2S02,03 | C2S02-X1 | 1756-IB32-3 | DI | Dry Contact | TSH-60230_DI_1 | TSH-60230 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-04 | JB-602 | =CA1+MCP-M2 | ACTIVE
261 | C2 | 2 | 4 | C2S02,04 | C2S02-X1 | 1756-IB32-4 | DI | Dry Contact | TSH-60240_DI_1 | TSH-60240 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
262 | C2 | 2 | 5 | C2S02,05 | C2S02-X1 | 1756-IB32-5 | DI | Dry Contact | TSH-60241A_DI_1 | TSH-60241A | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
263 | C2 | 2 | 6 | C2S02,06 | C2S02-X1 | 1756-IB32-6 | DI | Dry Contact | TSH-60242A_DI_1 | TSH-60242A | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
264 | C2 | 2 | 7 | C2S02,07 | C2S02-X1 | 1756-IB32-7 | DI | Dry Contact | TSH-60243A_DI_1 | TSH-60243A | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
265 | C2 | 2 | 8 | C2S02,08 | C2S02-X1 | 1756-IB32-8 | DI | Dry Contact | TSL-60241B_DI_1 | TSL-60241B | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
266 | C2 | 2 | 9 | C2S02,09 | C2S02-X1 | 1756-IB32-9 | DI | Dry Contact | TSL-60242B_DI_1 | TSL-60242B | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
267 | C2 | 2 | 10 | C2S02,10 | C2S02-X1 | 1756-IB32-10 | DI | Dry Contact | TSL-60243B_DI_1 | TSL-60243B | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
268 | C2 | 2 | 11 | C2S02,11 | C2S02-X1 | 1756-IB32-11 | DI | Dry Contact | XA-60240A_DI_1 | XA-60240A | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
269 | C2 | 2 | 12 | C2S02,12 | C2S02-X1 | 1756-IB32-12 | DI | Dry Contact | XA-60240B_DI_1 | XA-60240B | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
270 | C2 | 2 | 13 | C2S02,13 | C2S02-X1 | 1756-IB32-13 | DI | Dry Contact | XA-60241A_DI_1 | XA-60241A | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
271 | C2 | 2 | 14 | C2S02,14 | C2S02-X1 | 1756-IB32-14 | DI | Dry Contact | XA-60241B_DI_1 | XA-60241B | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
272 | C2 | 2 | 15 | C2S02,15 | C2S02-X1 | 1756-IB32-15 | DI | Dry Contact | XA-60242A_DI_1 | XA-60242A | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
273 | C2 | 2 | 16 | C2S02,16 | C2S02-X2 | 1756-IB32-16 | DI | Dry Contact | XA-60242B_DI_1 | XA-60242B | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
274 | C2 | 2 | 17 | C2S02,17 | C2S02-X2 | 1756-IB32-17 | DI | Dry Contact | XA-60243A_DI_1 | XA-60243A | Alarm 1 for BGHS-21 (Bag House Air Pulsing) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
275 | C2 | 2 | 18 | C2S02,18 | C2S02-X2 | 1756-IB32-18 | DI | Dry Contact | XA-60243B_DI_1 | XA-60243B | Alarm 2 for BGHS-21 (Bag House Air Pulsing) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
276 | C2 | 2 | 19 | C2S02,19 | C2S02-X2 | 1756-IB32-19 | DI | 24 VDC energized | XV-60214_DI_1 | XV-60214 | Steam feed to Spray dryer | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
277 | C2 | 2 | 20 | C2S02,20 | C2S02-X2 | 1756-IB32-20 | DI | 24 VDC energized | XV-60214_DI_2 | XV-60214 | Steam feed to Spray dryer | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
278 | C2 | 2 | 21 | C2S02,21 | C2S02-X2 | 1756-IB32-21 | DI | 24 VDC energized,Dry Contact | XV-60241_DI_1 | XV-60241 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
279 | C2 | 2 | 22 | C2S02,22 | C2S02-X2 | 1756-IB32-22 | DI | 24 VDC energized,Dry Contact | XV-60241_DI_2 | XV-60241 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
280 | C2 | 2 | 23 | C2S02,23 | C2S02-X2 | 1756-IB32-23 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
281 | C2 | 2 | 24 | C2S02,24 | C2S02-X2 | 1756-IB32-24 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
282 | C2 | 2 | 25 | C2S02,25 | C2S02-X2 | 1756-IB32-25 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
283 | C2 | 2 | 26 | C2S02,26 | C2S02-X2 | 1756-IB32-26 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
284 | C2 | 2 | 27 | C2S02,27 | C2S02-X2 | 1756-IB32-27 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
285 | C2 | 2 | 28 | C2S02,28 | C2S02-X2 | 1756-IB32-28 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
286 | C2 | 2 | 29 | C2S02,29 | C2S02-X2 | 1756-IB32-29 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
287 | C2 | 2 | 30 | C2S02,30 | C2S02-X2 | 1756-IB32-30 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
288 | C2 | 2 | 31 | C2S02,31 | C2S02-X2 | 1756-IB32-31 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
289 | C2 | 3 | 0 | C2S03,00 | C2S03-X1 | 1756-IB32-0 | DI | Dry Contact | XA-FH-60210A_DI_1 | XA-FH-60210A | BMS PANEL POWER ON for AHTR-21 | Industrial Process Equipment | Standard Process Field Device | CVV 20C x 1 | 325-01-602-PD-06 | JB-607 | =CA1+MCP-M2 | ACTIVE
290 | C2 | 3 | 1 | C2S03,01 | C2S03-X1 | 1756-IB32-1 | DI | Dry Contact | XA-FH-60210B_DI_1 | XA-FH-60210B | BMS Burner High Fire Purge for AHTR-21 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-06 | JB-607 | =CA1+MCP-M2 | ACTIVE
291 | C2 | 3 | 2 | C2S03,02 | C2S03-X1 | 1756-IB32-2 | DI | Dry Contact | XA-FH-60210C_DI_1 | XA-FH-60210C | BMS Burner On for AHTR-21 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-06 | JB-607 | =CA1+MCP-M2 | ACTIVE
292 | C2 | 3 | 3 | C2S03,03 | C2S03-X1 | 1756-IB32-3 | DI | Dry Contact | XA-FH-60210D_DI_1 | XA-FH-60210D | BMS BMS Lockout for AHTR-21 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-06 | JB-607 | =CA1+MCP-M2 | ACTIVE
293 | C2 | 3 | 4 | C2S03,04 | C2S03-X1 | 1756-IB32-4 | DI | Dry Contact | XA-FH-60210E_DI_1 | XA-FH-60210E | BMS Remote Modet for AHTR-21 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-06 | JB-607 | =CA1+MCP-M2 | ACTIVE
294 | C2 | 3 | 8 | C2S03,08 | C2S03-X1 | 1756-IB32-8 | DI | 24 VDC energized | SV-60207_DI_1 | SV-60207 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-07 | JB-607 | =CA1+MCP-M2 | ACTIVE
295 | C2 | 3 | 9 | C2S03,09 | C2S03-X1 | 1756-IB32-9 | DI | 24 VDC energized | SV-60207_DI_2 | SV-60207 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-07 | JB-607 | =CA1+MCP-M2 | ACTIVE
296 | C2 | 3 | 10 | C2S03,10 | C2S03-X1 | 1756-IB32-10 | DI | - | XV-60264_DI_1 | XV-60264 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
297 | C2 | 3 | 11 | C2S03,11 | C2S03-X1 | 1756-IB32-11 | DI | - | XV-60264_DI_2 | XV-60264 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
298 | C2 | 3 | 12 | C2S03,12 | C2S03-X1 | 1756-IB32-12 | DI | 24 VDC energized,Dry Contact | XV-60264FN_DI_1 | XV-60264FN | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
299 | C2 | 3 | 13 | C2S03,13 | C2S03-X1 | 1756-IB32-13 | DI | 24 VDC energized,Dry Contact | XV-60264FN_DI_2 | XV-60264FN | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
300 | C2 | 3 | 14 | C2S03,14 | C2S03-X1 | 1756-IB32-14 | DI | 24 VDC energized,Dry Contact | XV-60264FP_DI_1 | XV-60264FP | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
301 | C2 | 3 | 15 | C2S03,15 | C2S03-X1 | 1756-IB32-15 | DI | 24 VDC energized,Dry Contact | XV-60264FP_DI_2 | XV-60264FP | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
302 | C2 | 3 | 16 | C2S03,16 | C2S03-X2 | 1756-IB32-16 | DI | 24 VDC energized | XV-60201_DI_1 | XV-60201 | Steam feed to Spray dryer | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
303 | C2 | 3 | 17 | C2S03,17 | C2S03-X2 | 1756-IB32-17 | DI | 24 VDC energized | XV-60201_DI_2 | XV-60201 | Steam feed to Spray dryer | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
304 | C2 | 3 | 18 | C2S03,18 | C2S03-X2 | 1756-IB32-18 | DI | 24 VDC energized,Dry Contact | XV-60264FQ_DI_1 | XV-60264FQ | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
305 | C2 | 3 | 19 | C2S03,19 | C2S03-X2 | 1756-IB32-19 | DI | 24 VDC energized,Dry Contact | XV-60264FQ_DI_2 | XV-60264FQ | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
306 | C2 | 3 | 20 | C2S03,20 | C2S03-X2 | 1756-IB32-20 | DI | - | XV-60261_DI_1 | XV-60261 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
307 | C2 | 3 | 21 | C2S03,21 | C2S03-X2 | 1756-IB32-21 | DI | - | XV-60261_DI_2 | XV-60261 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
308 | C2 | 3 | 22 | C2S03,22 | C2S03-X2 | 1756-IB32-22 | DI | 24 VDC energized,Dry Contact | XV-60264FR_DI_1 | XV-60264FR | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
309 | C2 | 3 | 23 | C2S03,23 | C2S03-X2 | 1756-IB32-23 | DI | 24 VDC energized,Dry Contact | XV-60264FR_DI_2 | XV-60264FR | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
310 | C2 | 3 | 24 | C2S03,24 | C2S03-X2 | 1756-IB32-24 | DI | 24 VDC energized,Dry Contact | XV-60261FA_DI_1 | XV-60261FA | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
311 | C2 | 3 | 25 | C2S03,25 | C2S03-X2 | 1756-IB32-25 | DI | 24 VDC energized,Dry Contact | XV-60261FA_DI_2 | XV-60261FA | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
312 | C2 | 3 | 26 | C2S03,26 | C2S03-X2 | 1756-IB32-26 | DI | 24 VDC energized,Dry Contact | XV-60264SN_DI_1 | XV-60264SN | Steam On/Off Valve for Nozzle #13 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
313 | C2 | 3 | 27 | C2S03,27 | C2S03-X2 | 1756-IB32-27 | DI | 24 VDC energized,Dry Contact | XV-60264SN_DI_2 | XV-60264SN | Steam On/Off Valve for Nozzle #13 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
314 | C2 | 3 | 28 | C2S03,28 | C2S03-X2 | 1756-IB32-28 | DI | 24 VDC energized,Dry Contact | XV-60261FB_DI_1 | XV-60261FB | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
315 | C2 | 3 | 29 | C2S03,29 | C2S03-X2 | 1756-IB32-29 | DI | 24 VDC energized,Dry Contact | XV-60261FB_DI_2 | XV-60261FB | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
316 | C2 | 3 | 30 | C2S03,30 | C2S03-X2 | 1756-IB32-30 | DI | 24 VDC energized,Dry Contact | XV-60264SP_DI_1 | XV-60264SP | Steam On/Off Valve for Nozzle #14 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
317 | C2 | 3 | 31 | C2S03,31 | C2S03-X2 | 1756-IB32-31 | DI | 24 VDC energized,Dry Contact | XV-60264SP_DI_2 | XV-60264SP | Steam On/Off Valve for Nozzle #14 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
318 | C2 | 4 | 0 | C2S04,00 | C2S04-X1 | 1756-IB32-0 | DI | 24 VDC energized,Dry Contact | XV-60261FC_DI_1 | XV-60261FC | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
319 | C2 | 4 | 1 | C2S04,01 | C2S04-X1 | 1756-IB32-1 | DI | 24 VDC energized,Dry Contact | XV-60261FC_DI_2 | XV-60261FC | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
320 | C2 | 4 | 2 | C2S04,02 | C2S04-X1 | 1756-IB32-2 | DI | 24 VDC energized,Dry Contact | XV-60264SQ_DI_1 | XV-60264SQ | Steam On/Off Valve for Nozzle #15 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
321 | C2 | 4 | 3 | C2S04,03 | C2S04-X1 | 1756-IB32-3 | DI | 24 VDC energized,Dry Contact | XV-60264SQ_DI_2 | XV-60264SQ | Steam On/Off Valve for Nozzle #15 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
322 | C2 | 4 | 4 | C2S04,04 | C2S04-X1 | 1756-IB32-4 | DI | 24 VDC energized,Dry Contact | XV-60261FD_DI_1 | XV-60261FD | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
323 | C2 | 4 | 5 | C2S04,05 | C2S04-X1 | 1756-IB32-5 | DI | 24 VDC energized,Dry Contact | XV-60261FD_DI_2 | XV-60261FD | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
324 | C2 | 4 | 6 | C2S04,06 | C2S04-X1 | 1756-IB32-6 | DI | 24 VDC energized,Dry Contact | XV-60264SR_DI_1 | XV-60264SR | Steam On/Off Valve for Nozzle #16 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
325 | C2 | 4 | 7 | C2S04,07 | C2S04-X1 | 1756-IB32-7 | DI | 24 VDC energized,Dry Contact | XV-60264SR_DI_2 | XV-60264SR | Steam On/Off Valve for Nozzle #16 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
326 | C2 | 4 | 8 | C2S04,08 | C2S04-X1 | 1756-IB32-8 | DI | 24 VDC energized,Dry Contact | XV-60261SA_DI_1 | XV-60261SA | Steam On/Off Valve for Nozzle #1 (ATVM-11A) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
327 | C2 | 4 | 9 | C2S04,09 | C2S04-X1 | 1756-IB32-9 | DI | 24 VDC energized,Dry Contact | XV-60261SA_DI_2 | XV-60261SA | Steam On/Off Valve for Nozzle #1 (ATVM-11A) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
328 | C2 | 4 | 10 | C2S04,10 | C2S04-X1 | 1756-IB32-10 | DI | 24 VDC energized,Dry Contact | XV-60261SB_DI_1 | XV-60261SB | Steam On/Off Valve for Nozzle #2 (ATVM-11A) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
329 | C2 | 4 | 11 | C2S04,11 | C2S04-X1 | 1756-IB32-11 | DI | 24 VDC energized,Dry Contact | XV-60261SB_DI_2 | XV-60261SB | Steam On/Off Valve for Nozzle #2 (ATVM-11A) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
330 | C2 | 4 | 12 | C2S04,12 | C2S04-X1 | 1756-IB32-12 | DI | 24 VDC energized,Dry Contact | XV-60261SC_DI_1 | XV-60261SC | Steam On/Off Valve for Nozzle #3 (ATVM-11A) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
331 | C2 | 4 | 13 | C2S04,13 | C2S04-X1 | 1756-IB32-13 | DI | 24 VDC energized,Dry Contact | XV-60261SC_DI_2 | XV-60261SC | Steam On/Off Valve for Nozzle #3 (ATVM-11A) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
332 | C2 | 4 | 14 | C2S04,14 | C2S04-X1 | 1756-IB32-14 | DI | 24 VDC energized,Dry Contact | XV-60261SD_DI_1 | XV-60261SD | Steam On/Off Valve for Nozzle #4 (ATVM-11A) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
333 | C2 | 4 | 15 | C2S04,15 | C2S04-X1 | 1756-IB32-15 | DI | 24 VDC energized,Dry Contact | XV-60261SD_DI_2 | XV-60261SD | Steam On/Off Valve for Nozzle #4 (ATVM-11A) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
334 | C2 | 4 | 16 | C2S04,16 | C2S04-X2 | 1756-IB32-16 | DI | - | XV-60262_DI_1 | XV-60262 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
335 | C2 | 4 | 17 | C2S04,17 | C2S04-X2 | 1756-IB32-17 | DI | - | XV-60262_DI_2 | XV-60262 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
336 | C2 | 4 | 18 | C2S04,18 | C2S04-X2 | 1756-IB32-18 | DI | 24 VDC energized,Dry Contact | XV-60262FE_DI_1 | XV-60262FE | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
337 | C2 | 4 | 19 | C2S04,19 | C2S04-X2 | 1756-IB32-19 | DI | 24 VDC energized,Dry Contact | XV-60262FE_DI_2 | XV-60262FE | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
338 | C2 | 4 | 20 | C2S04,20 | C2S04-X2 | 1756-IB32-20 | DI | 24 VDC energized,Dry Contact | XV-60262FF_DI_1 | XV-60262FF | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
339 | C2 | 4 | 21 | C2S04,21 | C2S04-X2 | 1756-IB32-21 | DI | 24 VDC energized,Dry Contact | XV-60262FF_DI_2 | XV-60262FF | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
340 | C2 | 4 | 22 | C2S04,22 | C2S04-X2 | 1756-IB32-22 | DI | 24 VDC energized,Dry Contact | XV-60262FG_DI_1 | XV-60262FG | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
341 | C2 | 4 | 23 | C2S04,23 | C2S04-X2 | 1756-IB32-23 | DI | 24 VDC energized,Dry Contact | XV-60262FG_DI_2 | XV-60262FG | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
342 | C2 | 4 | 24 | C2S04,24 | C2S04-X2 | 1756-IB32-24 | DI | 24 VDC energized,Dry Contact | XV-60262FH_DI_1 | XV-60262FH | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
343 | C2 | 4 | 25 | C2S04,25 | C2S04-X2 | 1756-IB32-25 | DI | 24 VDC energized,Dry Contact | XV-60262FH_DI_2 | XV-60262FH | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
344 | C2 | 4 | 26 | C2S04,26 | C2S04-X2 | 1756-IB32-26 | DI | 24 VDC energized,Dry Contact | XV-60262SE_DI_1 | XV-60262SE | Steam On/Off Valve for Nozzle #5 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
345 | C2 | 4 | 27 | C2S04,27 | C2S04-X2 | 1756-IB32-27 | DI | 24 VDC energized,Dry Contact | XV-60262SE_DI_2 | XV-60262SE | Steam On/Off Valve for Nozzle #5 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
346 | C2 | 4 | 28 | C2S04,28 | C2S04-X2 | 1756-IB32-28 | DI | 24 VDC energized,Dry Contact | XV-60262SF_DI_1 | XV-60262SF | Steam On/Off Valve for Nozzle #6 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
347 | C2 | 4 | 29 | C2S04,29 | C2S04-X2 | 1756-IB32-29 | DI | 24 VDC energized,Dry Contact | XV-60262SF_DI_2 | XV-60262SF | Steam On/Off Valve for Nozzle #6 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
348 | C2 | 4 | 30 | C2S04,30 | C2S04-X2 | 1756-IB32-30 | DI | 24 VDC energized,Dry Contact | XV-60262SG_DI_1 | XV-60262SG | Steam On/Off Valve for Nozzle #7 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
349 | C2 | 4 | 31 | C2S04,31 | C2S04-X2 | 1756-IB32-31 | DI | 24 VDC energized,Dry Contact | XV-60262SG_DI_2 | XV-60262SG | Steam On/Off Valve for Nozzle #7 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
350 | C2 | 5 | 0 | C2S05,00 | C2S05-X1 | 1756-IB32-0 | DI | 24 VDC energized,Dry Contact | XV-60262SH_DI_1 | XV-60262SH | Steam On/Off Valve for Nozzle #8 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
351 | C2 | 5 | 1 | C2S05,01 | C2S05-X1 | 1756-IB32-1 | DI | 24 VDC energized,Dry Contact | XV-60262SH_DI_2 | XV-60262SH | Steam On/Off Valve for Nozzle #8 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
352 | C2 | 5 | 2 | C2S05,02 | C2S05-X1 | 1756-IB32-2 | DI | - | XV-60263_DI_1 | XV-60263 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
353 | C2 | 5 | 3 | C2S05,03 | C2S05-X1 | 1756-IB32-3 | DI | - | XV-60263_DI_2 | XV-60263 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
354 | C2 | 5 | 4 | C2S05,04 | C2S05-X1 | 1756-IB32-4 | DI | 24 VDC energized,Dry Contact | XV-60263FJ_DI_1 | XV-60263FJ | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
355 | C2 | 5 | 5 | C2S05,05 | C2S05-X1 | 1756-IB32-5 | DI | 24 VDC energized,Dry Contact | XV-60263FJ_DI_2 | XV-60263FJ | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
356 | C2 | 5 | 6 | C2S05,06 | C2S05-X1 | 1756-IB32-6 | DI | 24 VDC energized,Dry Contact | XV-60263FK_DI_1 | XV-60263FK | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
357 | C2 | 5 | 7 | C2S05,07 | C2S05-X1 | 1756-IB32-7 | DI | 24 VDC energized,Dry Contact | XV-60263FK_DI_2 | XV-60263FK | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
358 | C2 | 5 | 8 | C2S05,08 | C2S05-X1 | 1756-IB32-8 | DI | 24 VDC energized,Dry Contact | XV-60263FL_DI_1 | XV-60263FL | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
359 | C2 | 5 | 9 | C2S05,09 | C2S05-X1 | 1756-IB32-9 | DI | 24 VDC energized,Dry Contact | XV-60263FL_DI_2 | XV-60263FL | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
360 | C2 | 5 | 10 | C2S05,10 | C2S05-X1 | 1756-IB32-10 | DI | 24 VDC energized,Dry Contact | XV-60263FM_DI_1 | XV-60263FM | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
361 | C2 | 5 | 11 | C2S05,11 | C2S05-X1 | 1756-IB32-11 | DI | 24 VDC energized,Dry Contact | XV-60263FM_DI_2 | XV-60263FM | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
362 | C2 | 5 | 12 | C2S05,12 | C2S05-X1 | 1756-IB32-12 | DI | 24 VDC energized,Dry Contact | XV-60263SJ_DI_1 | XV-60263SJ | Steam On/Off Valve for Nozzle #9 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
363 | C2 | 5 | 13 | C2S05,13 | C2S05-X1 | 1756-IB32-13 | DI | 24 VDC energized,Dry Contact | XV-60263SJ_DI_2 | XV-60263SJ | Steam On/Off Valve for Nozzle #9 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
364 | C2 | 5 | 14 | C2S05,14 | C2S05-X1 | 1756-IB32-14 | DI | 24 VDC energized,Dry Contact | XV-60263SK_DI_1 | XV-60263SK | Steam On/Off Valve for Nozzle #10 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
365 | C2 | 5 | 15 | C2S05,15 | C2S05-X1 | 1756-IB32-15 | DI | 24 VDC energized,Dry Contact | XV-60263SK_DI_2 | XV-60263SK | Steam On/Off Valve for Nozzle #10 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
366 | C2 | 5 | 16 | C2S05,16 | C2S05-X2 | 1756-IB32-16 | DI | 24 VDC energized,Dry Contact | XV-60263SL_DI_1 | XV-60263SL | Steam On/Off Valve for Nozzle #11 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
367 | C2 | 5 | 17 | C2S05,17 | C2S05-X2 | 1756-IB32-17 | DI | 24 VDC energized,Dry Contact | XV-60263SL_DI_2 | XV-60263SL | Steam On/Off Valve for Nozzle #11 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
368 | C2 | 5 | 18 | C2S05,18 | C2S05-X2 | 1756-IB32-18 | DI | 24 VDC energized,Dry Contact | XV-60263SM_DI_1 | XV-60263SM | Steam On/Off Valve for Nozzle #12 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
369 | C2 | 5 | 19 | C2S05,19 | C2S05-X2 | 1756-IB32-19 | DI | 24 VDC energized,Dry Contact | XV-60263SM_DI_2 | XV-60263SM | Steam On/Off Valve for Nozzle #12 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
370 | C2 | 5 | 20 | C2S05,20 | C2S05-X2 | 1756-IB32-20 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
371 | C2 | 5 | 21 | C2S05,21 | C2S05-X2 | 1756-IB32-21 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
372 | C2 | 5 | 22 | C2S05,22 | C2S05-X2 | 1756-IB32-22 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
373 | C2 | 5 | 23 | C2S05,23 | C2S05-X2 | 1756-IB32-23 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
374 | C2 | 5 | 24 | C2S05,24 | C2S05-X2 | 1756-IB32-24 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
375 | C2 | 5 | 25 | C2S05,25 | C2S05-X2 | 1756-IB32-25 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
376 | C2 | 5 | 26 | C2S05,26 | C2S05-X2 | 1756-IB32-26 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
377 | C2 | 5 | 27 | C2S05,27 | C2S05-X2 | 1756-IB32-27 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
378 | C2 | 5 | 28 | C2S05,28 | C2S05-X2 | 1756-IB32-28 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
379 | C2 | 5 | 29 | C2S05,29 | C2S05-X2 | 1756-IB32-29 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
380 | C2 | 5 | 30 | C2S05,30 | C2S05-X2 | 1756-IB32-30 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
381 | C2 | 5 | 31 | C2S05,31 | C2S05-X2 | 1756-IB32-31 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
382 | C2 | 6 | 0 | C2S06,00 | C2S06-X1 | 1756-OB32-0 | DO | 24 VDC energized | XV-40203F_DO_1 | XV-40203F | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
383 | C2 | 6 | 1 | C2S06,01 | C2S06-X1 | 1756-OB32-1 | DO | 24 VDC energized | XV-40204B_DO_1 | XV-40204B | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-402 | =CA1+MCP-M2 | ACTIVE
384 | C2 | 6 | 2 | C2S06,02 | C2S06-X1 | 1756-OB32-2 | DO | 24 VDC energized | XV-40204C_DO_1 | XV-40204C | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-01 | JB-402 | =CA1+MCP-M2 | ACTIVE
385 | C2 | 6 | 3 | C2S06,03 | C2S06-X1 | 1756-OB32-3 | DO | 24 VDC energized | XV-40205A_DO_1 | XV-40205A | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
386 | C2 | 6 | 4 | C2S06,04 | C2S06-X1 | 1756-OB32-4 | DO | 24 VDC energized | XV-40205B_DO_1 | XV-40205B | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
387 | C2 | 6 | 5 | C2S06,05 | C2S06-X1 | 1756-OB32-5 | DO | 24 VDC energized | XV-40205C_DO_1 | XV-40205C | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
388 | C2 | 6 | 6 | C2S06,06 | C2S06-X1 | 1756-OB32-6 | DO | 24 VDC energized | XV-40205D_DO_1 | XV-40205D | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
389 | C2 | 6 | 7 | C2S06,07 | C2S06-X1 | 1756-OB32-7 | DO | 24 VDC energized | XV-40205F_DO_1 | XV-40205F | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
390 | C2 | 6 | 8 | C2S06,08 | C2S06-X1 | 1756-OB32-8 | DO | 24 VDC energized | XV-40222_DO_1 | XV-40222 | Jet Cooker | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
391 | C2 | 6 | 9 | C2S06,09 | C2S06-X1 | 1756-OB32-9 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
392 | C2 | 6 | 10 | C2S06,10 | C2S06-X1 | 1756-OB32-10 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
393 | C2 | 6 | 11 | C2S06,11 | C2S06-X1 | 1756-OB32-11 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
394 | C2 | 6 | 12 | C2S06,12 | C2S06-X1 | 1756-OB32-12 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
395 | C2 | 6 | 13 | C2S06,13 | C2S06-X1 | 1756-OB32-13 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
396 | C2 | 6 | 14 | C2S06,14 | C2S06-X1 | 1756-OB32-14 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
397 | C2 | 6 | 15 | C2S06,15 | C2S06-X1 | 1756-OB32-15 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
398 | C2 | 6 | 16 | C2S06,16 | C2S06-X2 | 1756-OB32-16 | DO | Dry Contact | XS-60240B_DO_1 | XS-60240B | Fan Command for BGHS-21 (Bag House Air Pulsing) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
399 | C2 | 6 | 17 | C2S06,17 | C2S06-X2 | 1756-OB32-17 | DO | 24 VDC energized | XV-60214_DO_1 | XV-60214 | Steam feed to Spray dryer | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
400 | C2 | 6 | 18 | C2S06,18 | C2S06-X2 | 1756-OB32-18 | DO | 24 VDC energized,Dry Contact | XV-60241_DO_1 | XV-60241 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
401 | C2 | 6 | 19 | C2S06,19 | C2S06-X2 | 1756-OB32-19 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
402 | C2 | 6 | 20 | C2S06,20 | C2S06-X2 | 1756-OB32-20 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
403 | C2 | 6 | 21 | C2S06,21 | C2S06-X2 | 1756-OB32-21 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
404 | C2 | 6 | 22 | C2S06,22 | C2S06-X2 | 1756-OB32-22 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
405 | C2 | 6 | 23 | C2S06,23 | C2S06-X2 | 1756-OB32-23 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
406 | C2 | 6 | 24 | C2S06,24 | C2S06-X2 | 1756-OB32-24 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
407 | C2 | 6 | 25 | C2S06,25 | C2S06-X2 | 1756-OB32-25 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
408 | C2 | 6 | 26 | C2S06,26 | C2S06-X2 | 1756-OB32-26 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
409 | C2 | 6 | 27 | C2S06,27 | C2S06-X2 | 1756-OB32-27 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
410 | C2 | 6 | 28 | C2S06,28 | C2S06-X2 | 1756-OB32-28 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
411 | C2 | 6 | 29 | C2S06,29 | C2S06-X2 | 1756-OB32-29 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
412 | C2 | 6 | 30 | C2S06,30 | C2S06-X2 | 1756-OB32-30 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
413 | C2 | 6 | 31 | C2S06,31 | C2S06-X2 | 1756-OB32-31 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
414 | C2 | 7 | 0 | C2S07,00 | C2S07-X1 | 1756-OB32-0 | DO | 24 VDC energized | SV-60207_DO_1 | SV-60207 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-07 | JB-607 | =CA1+MCP-M2 | ACTIVE
415 | C2 | 7 | 1 | C2S07,01 | C2S07-X1 | 1756-OB32-1 | DO | Dry Contact | XS-FH-60210C_DO_1 | XS-FH-60210C | Command Remote Reset for AHTR-21 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-06 | JB-607 | =CA1+MCP-M2 | ACTIVE
416 | C2 | 7 | 2 | C2S07,02 | C2S07-X1 | 1756-OB32-2 | DO | Dry Contact | XS-FH-60210D_DO_1 | XS-FH-60210D | Spare | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-06 | JB-607 | =CA1+MCP-M2 | ACTIVE
417 | C2 | 7 | 3 | C2S07,03 | C2S07-X1 | 1756-OB32-3 | DO | 24 VDC energized | XV-60201_DO_1 | XV-60201 | Steam feed to Spray dryer | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
418 | C2 | 7 | 4 | C2S07,04 | C2S07-X1 | 1756-OB32-4 | DO | - | XV-60261_DO_1 | XV-60261 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
419 | C2 | 7 | 5 | C2S07,05 | C2S07-X1 | 1756-OB32-5 | DO | 24 VDC energized,Dry Contact | XV-60261FA_DO_1 | XV-60261FA | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
420 | C2 | 7 | 6 | C2S07,06 | C2S07-X1 | 1756-OB32-6 | DO | 24 VDC energized,Dry Contact | XV-60261FB_DO_1 | XV-60261FB | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
421 | C2 | 7 | 7 | C2S07,07 | C2S07-X1 | 1756-OB32-7 | DO | 24 VDC energized,Dry Contact | XV-60261FC_DO_1 | XV-60261FC | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
422 | C2 | 7 | 8 | C2S07,08 | C2S07-X1 | 1756-OB32-8 | DO | 24 VDC energized,Dry Contact | XV-60261FD_DO_1 | XV-60261FD | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
423 | C2 | 7 | 9 | C2S07,09 | C2S07-X1 | 1756-OB32-9 | DO | 24 VDC energized,Dry Contact | XV-60261SA_DO_1 | XV-60261SA | Steam On/Off Valve for Nozzle #1 (ATVM-11A) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
424 | C2 | 7 | 10 | C2S07,10 | C2S07-X1 | 1756-OB32-10 | DO | 24 VDC energized,Dry Contact | XV-60261SB_DO_1 | XV-60261SB | Steam On/Off Valve for Nozzle #2 (ATVM-11A) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
425 | C2 | 7 | 11 | C2S07,11 | C2S07-X1 | 1756-OB32-11 | DO | 24 VDC energized,Dry Contact | XV-60261SC_DO_1 | XV-60261SC | Steam On/Off Valve for Nozzle #3 (ATVM-11A) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
426 | C2 | 7 | 12 | C2S07,12 | C2S07-X1 | 1756-OB32-12 | DO | 24 VDC energized,Dry Contact | XV-60261SD_DO_1 | XV-60261SD | Steam On/Off Valve for Nozzle #4 (ATVM-11A) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
427 | C2 | 7 | 13 | C2S07,13 | C2S07-X1 | 1756-OB32-13 | DO | - | XV-60262_DO_1 | XV-60262 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
428 | C2 | 7 | 14 | C2S07,14 | C2S07-X1 | 1756-OB32-14 | DO | 24 VDC energized,Dry Contact | XV-60262FE_DO_1 | XV-60262FE | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
429 | C2 | 7 | 15 | C2S07,15 | C2S07-X1 | 1756-OB32-15 | DO | 24 VDC energized,Dry Contact | XV-60262FF_DO_1 | XV-60262FF | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
430 | C2 | 7 | 16 | C2S07,16 | C2S07-X2 | 1756-OB32-16 | DO | 24 VDC energized,Dry Contact | XV-60262FG_DO_1 | XV-60262FG | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
431 | C2 | 7 | 17 | C2S07,17 | C2S07-X2 | 1756-OB32-17 | DO | 24 VDC energized,Dry Contact | XV-60262FH_DO_1 | XV-60262FH | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
432 | C2 | 7 | 18 | C2S07,18 | C2S07-X2 | 1756-OB32-18 | DO | 24 VDC energized,Dry Contact | XV-60262SE_DO_1 | XV-60262SE | Steam On/Off Valve for Nozzle #5 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
433 | C2 | 7 | 19 | C2S07,19 | C2S07-X2 | 1756-OB32-19 | DO | 24 VDC energized,Dry Contact | XV-60262SF_DO_1 | XV-60262SF | Steam On/Off Valve for Nozzle #6 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
434 | C2 | 7 | 20 | C2S07,20 | C2S07-X2 | 1756-OB32-20 | DO | 24 VDC energized,Dry Contact | XV-60262SG_DO_1 | XV-60262SG | Steam On/Off Valve for Nozzle #7 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
435 | C2 | 7 | 21 | C2S07,21 | C2S07-X2 | 1756-OB32-21 | DO | 24 VDC energized,Dry Contact | XV-60262SH_DO_1 | XV-60262SH | Steam On/Off Valve for Nozzle #8 (ATVM-11B) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
436 | C2 | 7 | 22 | C2S07,22 | C2S07-X2 | 1756-OB32-22 | DO | - | XV-60263_DO_1 | XV-60263 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
437 | C2 | 7 | 23 | C2S07,23 | C2S07-X2 | 1756-OB32-23 | DO | 24 VDC energized,Dry Contact | XV-60263FJ_DO_1 | XV-60263FJ | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
438 | C2 | 7 | 24 | C2S07,24 | C2S07-X2 | 1756-OB32-24 | DO | 24 VDC energized,Dry Contact | XV-60263FK_DO_1 | XV-60263FK | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
439 | C2 | 7 | 25 | C2S07,25 | C2S07-X2 | 1756-OB32-25 | DO | 24 VDC energized,Dry Contact | XV-60263FL_DO_1 | XV-60263FL | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
440 | C2 | 7 | 26 | C2S07,26 | C2S07-X2 | 1756-OB32-26 | DO | 24 VDC energized,Dry Contact | XV-60263FM_DO_1 | XV-60263FM | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
441 | C2 | 7 | 27 | C2S07,27 | C2S07-X2 | 1756-OB32-27 | DO | 24 VDC energized,Dry Contact | XV-60263SJ_DO_1 | XV-60263SJ | Steam On/Off Valve for Nozzle #9 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
442 | C2 | 7 | 28 | C2S07,28 | C2S07-X2 | 1756-OB32-28 | DO | 24 VDC energized,Dry Contact | XV-60263SK_DO_1 | XV-60263SK | Steam On/Off Valve for Nozzle #10 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
443 | C2 | 7 | 29 | C2S07,29 | C2S07-X2 | 1756-OB32-29 | DO | 24 VDC energized,Dry Contact | XV-60263SL_DO_1 | XV-60263SL | Steam On/Off Valve for Nozzle #11 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
444 | C2 | 7 | 30 | C2S07,30 | C2S07-X2 | 1756-OB32-30 | DO | 24 VDC energized,Dry Contact | XV-60263SM_DO_1 | XV-60263SM | Steam On/Off Valve for Nozzle #12 (ATVM-11C) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
445 | C2 | 7 | 31 | C2S07,31 | C2S07-X2 | 1756-OB32-31 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
446 | C2 | 8 | 0 | C2S08,00 | C2S08-X1 | 1756-OB32-0 | DO | - | XV-60264_DO_1 | XV-60264 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
447 | C2 | 8 | 1 | C2S08,01 | C2S08-X1 | 1756-OB32-1 | DO | 24 VDC energized,Dry Contact | XV-60264FN_DO_1 | XV-60264FN | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
448 | C2 | 8 | 2 | C2S08,02 | C2S08-X1 | 1756-OB32-2 | DO | 24 VDC energized,Dry Contact | XV-60264FP_DO_1 | XV-60264FP | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
449 | C2 | 8 | 3 | C2S08,03 | C2S08-X1 | 1756-OB32-3 | DO | 24 VDC energized,Dry Contact | XV-60264FQ_DO_1 | XV-60264FQ | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
450 | C2 | 8 | 4 | C2S08,04 | C2S08-X1 | 1756-OB32-4 | DO | 24 VDC energized,Dry Contact | XV-60264FR_DO_1 | XV-60264FR | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
451 | C2 | 8 | 5 | C2S08,05 | C2S08-X1 | 1756-OB32-5 | DO | 24 VDC energized,Dry Contact | XV-60264SN_DO_1 | XV-60264SN | Steam On/Off Valve for Nozzle #13 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
452 | C2 | 8 | 6 | C2S08,06 | C2S08-X1 | 1756-OB32-6 | DO | 24 VDC energized,Dry Contact | XV-60264SP_DO_1 | XV-60264SP | Steam On/Off Valve for Nozzle #14 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
453 | C2 | 8 | 7 | C2S08,07 | C2S08-X1 | 1756-OB32-7 | DO | 24 VDC energized,Dry Contact | XV-60264SQ_DO_1 | XV-60264SQ | Steam On/Off Valve for Nozzle #15 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
454 | C2 | 8 | 8 | C2S08,08 | C2S08-X1 | 1756-OB32-8 | DO | 24 VDC energized,Dry Contact | XV-60264SR_DO_1 | XV-60264SR | Steam On/Off Valve for Nozzle #16 (ATVM-11D) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
455 | C2 | 8 | 9 | C2S08,09 | C2S08-X1 | 1756-OB32-9 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
456 | C2 | 8 | 10 | C2S08,10 | C2S08-X1 | 1756-OB32-10 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
457 | C2 | 8 | 11 | C2S08,11 | C2S08-X1 | 1756-OB32-11 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
458 | C2 | 8 | 12 | C2S08,12 | C2S08-X1 | 1756-OB32-12 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
459 | C2 | 8 | 13 | C2S08,13 | C2S08-X1 | 1756-OB32-13 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
460 | C2 | 8 | 14 | C2S08,14 | C2S08-X1 | 1756-OB32-14 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
461 | C2 | 8 | 15 | C2S08,15 | C2S08-X1 | 1756-OB32-15 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
462 | C2 | 8 | 16 | C2S08,16 | C2S08-X2 | 1756-OB32-16 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
463 | C2 | 8 | 17 | C2S08,17 | C2S08-X2 | 1756-OB32-17 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
464 | C2 | 8 | 18 | C2S08,18 | C2S08-X2 | 1756-OB32-18 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
465 | C2 | 8 | 19 | C2S08,19 | C2S08-X2 | 1756-OB32-19 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
466 | C2 | 8 | 20 | C2S08,20 | C2S08-X2 | 1756-OB32-20 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
467 | C2 | 8 | 21 | C2S08,21 | C2S08-X2 | 1756-OB32-21 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
468 | C2 | 8 | 22 | C2S08,22 | C2S08-X2 | 1756-OB32-22 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
469 | C2 | 8 | 23 | C2S08,23 | C2S08-X2 | 1756-OB32-23 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
470 | C2 | 8 | 24 | C2S08,24 | C2S08-X2 | 1756-OB32-24 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
471 | C2 | 8 | 25 | C2S08,25 | C2S08-X2 | 1756-OB32-25 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
472 | C2 | 8 | 26 | C2S08,26 | C2S08-X2 | 1756-OB32-26 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
473 | C2 | 8 | 27 | C2S08,27 | C2S08-X2 | 1756-OB32-27 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
474 | C2 | 8 | 28 | C2S08,28 | C2S08-X2 | 1756-OB32-28 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
475 | C2 | 8 | 29 | C2S08,29 | C2S08-X2 | 1756-OB32-29 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
476 | C2 | 8 | 30 | C2S08,30 | C2S08-X2 | 1756-OB32-30 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
477 | C2 | 8 | 31 | C2S08,31 | C2S08-X2 | 1756-OB32-31 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
478 | C2 | 9 | 0 | C2S09,00 | C2S09-X1 | 1756-IF16-0 | AI | 4 - 20 mA,Pulse | FT-40221_AI_1 | FT-40221 | Jet Cooker | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
479 | C2 | 9 | 1 | C2S09,01 | C2S09-X1 | 1756-IF16-1 | AI | 4 - 20 mA,Pulse | FT-40221_AI_2 | FT-40221 | Jet Cooker | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
480 | C2 | 9 | 2 | C2S09,02 | C2S09-X1 | 1756-IF16-2 | AI | 4 - 20 mA,Pulse | FT-40222_AI_1 | FT-40222 | Jet Cooker | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
481 | C2 | 9 | 3 | C2S09,03 | C2S09-X1 | 1756-IF16-3 | AI | 4 - 20 mA,Pulse | FT-40222_AI_2 | FT-40222 | Jet Cooker | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
482 | C2 | 9 | 4 | C2S09,04 | C2S09-X1 | 1756-IF16-4 | AI | 4 - 20 mA | PT-40222_AI_1 | PT-40222 | Jet Cooker | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
483 | C2 | 9 | 5 | C2S09,05 | C2S09-X1 | 1756-IF16-5 | AI | 4 - 20 mA | TT-40221_AI_1 | TT-40221 | Jet Cooker | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
484 | C2 | 9 | 6 | C2S09,06 | C2S09-X1 | 1756-IF16-6 | AI | 4 - 20 mA | TT-40222_AI_1 | TT-40222 | Jet Cooker | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
485 | C2 | 9 | 7 | C2S09,07 | C2S09-X1 | 1756-IF16-7 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
486 | C2 | 9 | 8 | C2S09,08 | C2S09-X1 | 1756-IF16-8 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
487 | C2 | 9 | 9 | C2S09,09 | C2S09-X1 | 1756-IF16-9 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
488 | C2 | 9 | 10 | C2S09,10 | C2S09-X1 | 1756-IF16-10 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
489 | C2 | 9 | 11 | C2S09,11 | C2S09-X1 | 1756-IF16-11 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
490 | C2 | 9 | 12 | C2S09,12 | C2S09-X1 | 1756-IF16-12 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
491 | C2 | 9 | 13 | C2S09,13 | C2S09-X1 | 1756-IF16-13 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
492 | C2 | 9 | 14 | C2S09,14 | C2S09-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
493 | C2 | 9 | 15 | C2S09,15 | C2S09-X1 | 1756-IF16-15 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-402 | =CA1+MCP-M2 | SPARE
494 | C2 | 10 | 0 | C2S10,00 | C2S10-X1 | 1756-IF16-0 | AI | 4 - 20 mA | AT-60241_AI_1 | AT-60241 | Dust Analyzer Transmitter for Exhaust Duct (DTEX-22) | ENVEA / PCME | PCME QAL 991 (Dust Analyzer) | LiY-CY TP 2Px1.0 (Signal + Alarm) + CVV 3Cx1.5 (24VDC Power) (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
495 | C2 | 10 | 1 | C2S10,01 | C2S10-X1 | 1756-IF16-1 | AI | 4 - 20 mA | DPT-60203_AI_1 | DPT-60203 | Gas Pressure Differential Transmitter for Air Filter (FICA-21) | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
496 | C2 | 10 | 2 | C2S10,02 | C2S10-X1 | 1756-IF16-2 | AI | 4 - 20 mA | FT-60202_AI_1 | FT-60202 | Steam feed to Spray dryer | Endress+Hauser | Prowirl F 200 (Vortex Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2P x1.0) | 325-01-602-PD-09 | JB-602 | =CA1+MCP-M2 | ACTIVE
497 | C2 | 10 | 3 | C2S10,03 | C2S10-X1 | 1756-IF16-3 | AI | 4 - 20 mA | PT-60210_AI_1 | PT-60210 | Gas Pressure Transmitter for Hot Air Duct (DTHA-21) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
498 | C2 | 10 | 4 | C2S10,04 | C2S10-X1 | 1756-IF16-4 | AI | 4 - 20 mA | PT-60215_AI_1 | PT-60215 | 15% Polypropylene Glycol Pressure Indicator Transmitter for Heat Recovery Pumping Skid (PUCF-21) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
499 | C2 | 10 | 5 | C2S10,05 | C2S10-X1 | 1756-IF16-5 | AI | 4 - 20 mA | PT-60216_AI_1 | PT-60216 | Gas Pressure Transmitter for Combustion Air Burner Duct (DTCB-21) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
500 | C2 | 10 | 6 | C2S10,06 | C2S10-X1 | 1756-IF16-6 | AI | 4 - 20 mA | PT-60240_AI_1 | PT-60240 | Gas Pressure Transmitter for Bag House Exhaust Duct (DTEX-22) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
501 | C2 | 10 | 7 | C2S10,07 | C2S10-X1 | 1756-IF16-7 | AI | 4 - 20 mA | PT-60241_AI_1 | PT-60241 | Gas Pressure Transmitter for Exhaust Fan (FANE-21) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
502 | C2 | 10 | 8 | C2S10,08 | C2S10-X1 | 1756-IF16-8 | AI | 4 - 20 mA | TT-60210_AI_1 | TT-60210 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
503 | C2 | 10 | 9 | C2S10,09 | C2S10-X1 | 1756-IF16-9 | AI | - | TT-60210A_AI_1 | TT-60210A | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
504 | C2 | 10 | 10 | C2S10,10 | C2S10-X1 | 1756-IF16-10 | AI | - | TT-60210B_AI_1 | TT-60210B | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
505 | C2 | 10 | 11 | C2S10,11 | C2S10-X1 | 1756-IF16-11 | AI | 4 - 20 mA | TT-60211_AI_1 | TT-60211 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
506 | C2 | 10 | 12 | C2S10,12 | C2S10-X1 | 1756-IF16-12 | AI | 4 - 20 mA | TT-60212A_AI_1 | TT-60212A | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
507 | C2 | 10 | 13 | C2S10,13 | C2S10-X1 | 1756-IF16-13 | AI | 4 - 20 mA | TT-60212B_AI_1 | TT-60212B | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
508 | C2 | 10 | 14 | C2S10,14 | C2S10-X1 | 1756-IF16-14 | AI | 4 - 20 mA | TT-60214_AI_1 | TT-60214 | Steam Temperature Transmitter for Cold Air Duct (DTCA-23) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
509 | C2 | 10 | 15 | C2S10,15 | C2S10-X1 | 1756-IF16-15 | AI | 4 - 20 mA | TT-60215A_AI_1 | TT-60215A | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
510 | C2 | 11 | 0 | C2S11,00 | C2S11-X1 | 1756-IF16-0 | AI | 4 - 20 mA | TT-60215B_AI_1 | TT-60215B | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
511 | C2 | 11 | 1 | C2S11,01 | C2S11-X1 | 1756-IF16-1 | AI | 4 - 20 mA | TT-60216_AI_1 | TT-60216 | Gas Temperature Transmitter for Combustion Air Burner Duct (DTCB-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
512 | C2 | 11 | 2 | C2S11,02 | C2S11-X1 | 1756-IF16-2 | AI | 4 - 20 mA | TT-60240_AI_1 | TT-60240 | Gas Temperature Transmitter for Exhaust Fan (FANE-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
513 | C2 | 11 | 3 | C2S11,03 | C2S11-X1 | 1756-IF16-3 | AI | 4 - 20 mA | TT-60241A_AI_1 | TT-60241A | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
514 | C2 | 11 | 4 | C2S11,04 | C2S11-X1 | 1756-IF16-4 | AI | 4 - 20 mA | TT-60241B_AI_1 | TT-60241B | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
515 | C2 | 11 | 5 | C2S11,05 | C2S11-X1 | 1756-IF16-5 | AI | 4 - 20 mA | VT-60210A_AI_1 | VT-60210A | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
516 | C2 | 11 | 6 | C2S11,06 | C2S11-X1 | 1756-IF16-6 | AI | 4 - 20 mA | VT-60210B_AI_1 | VT-60210B | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
517 | C2 | 11 | 7 | C2S11,07 | C2S11-X1 | 1756-IF16-7 | AI | 4 - 20 mA | VT-60241A_AI_1 | VT-60241A | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
518 | C2 | 11 | 8 | C2S11,08 | C2S11-X1 | 1756-IF16-8 | AI | 4 - 20 mA | VT-60241B_AI_1 | VT-60241B | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-05 | JB-602 | =CA1+MCP-M2 | ACTIVE
519 | C2 | 11 | 9 | C2S11,09 | C2S11-X1 | 1756-IF16-9 | AI | 4 - 20 mA | FT-60210_AI_1 | FT-60210 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) | Endress+Hauser | t-mass F 300 (Thermal Mass Flow) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
520 | C2 | 11 | 10 | C2S11,10 | C2S11-X1 | 1756-IF16-10 | AI | 4 - 20 mA | FT-60211_AI_1 | FT-60211 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) | Endress+Hauser | t-mass F 300 (Thermal Mass Flow) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
521 | C2 | 11 | 11 | C2S11,11 | C2S11-X1 | 1756-IF16-11 | AI | 4 - 20 mA | FT-60210_AI_2 | FT-60210 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) | Endress+Hauser | t-mass F 300 (Thermal Mass Flow) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
522 | C2 | 11 | 12 | C2S11,12 | C2S11-X1 | 1756-IF16-12 | AI | 4 - 20 mA | FT-60211_AI_2 | FT-60211 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) | Endress+Hauser | t-mass F 300 (Thermal Mass Flow) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
523 | C2 | 11 | 13 | C2S11,13 | C2S11-X1 | 1756-IF16-13 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
524 | C2 | 11 | 14 | C2S11,14 | C2S11-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
525 | C2 | 11 | 15 | C2S11,15 | C2S11-X1 | 1756-IF16-15 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-602 | =CA1+MCP-M2 | SPARE
526 | C2 | 12 | 0 | C2S12,00 | C2S12-X1 | 1756-IF16-0 | AI | 4 - 20 mA | FT-60207_AI_1 | FT-60207 | Instr. Air Flow Transmitter for Camera #4 (ACAM-21) | Endress+Hauser | t-mass F 300 / I 300 (Thermal Mass Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-07 | JB-607 | =CA1+MCP-M2 | ACTIVE
527 | C2 | 12 | 1 | C2S12,01 | C2S12-X1 | 1756-IF16-1 | AI | 4 - 20 mA | FT-60221_AI_1 | FT-60221 | Cool air Flow | Endress+Hauser | t-mass I 300 (Thermal Mass Flow) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | JB-607 | =CA1+MCP-M2 | ACTIVE
528 | C2 | 12 | 2 | C2S12,02 | C2S12-X1 | 1756-IF16-2 | AI | 4 - 20 mA | FT-60261FA_AI_1 | FT-60261FA | Feed Slurry Flow Transmitter for Nozzle #1 (AMTV-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
529 | C2 | 12 | 3 | C2S12,03 | C2S12-X1 | 1756-IF16-3 | AI | 4 - 20 mA | FT-60261FB_AI_1 | FT-60261FB | Feed Slurry Flow Transmitter for Nozzle #2 (AMTV-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
530 | C2 | 12 | 4 | C2S12,04 | C2S12-X1 | 1756-IF16-4 | AI | 4 - 20 mA | FT-60261FC_AI_1 | FT-60261FC | Feed Slurry Flow Transmitter for Nozzle #3 (AMTV-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
531 | C2 | 12 | 5 | C2S12,05 | C2S12-X1 | 1756-IF16-5 | AI | 4 - 20 mA | FT-60261FD_AI_1 | FT-60261FD | Feed Slurry Flow Transmitter for Nozzle #4 (AMTV-11A) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
532 | C2 | 12 | 6 | C2S12,06 | C2S12-X1 | 1756-IF16-6 | AI | 4 - 20 mA | FT-60262FE_AI_1 | FT-60262FE | Feed Slurry Flow Transmitter for Nozzle #5 (AMTV-11B) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
533 | C2 | 12 | 7 | C2S12,07 | C2S12-X1 | 1756-IF16-7 | AI | 4 - 20 mA | FT-60262FF_AI_1 | FT-60262FF | Feed Slurry Flow Transmitter for Nozzle #6 (AMTV-11B) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
534 | C2 | 12 | 8 | C2S12,08 | C2S12-X1 | 1756-IF16-8 | AI | 4 - 20 mA | FT-60262FG_AI_1 | FT-60262FG | Feed Slurry Flow Transmitter for Nozzle #7 (AMTV-11B) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
535 | C2 | 12 | 9 | C2S12,09 | C2S12-X1 | 1756-IF16-9 | AI | 4 - 20 mA | FT-60262FH_AI_1 | FT-60262FH | Feed Slurry Flow Transmitter for Nozzle #8 (AMTV-11B) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
536 | C2 | 12 | 10 | C2S12,10 | C2S12-X1 | 1756-IF16-10 | AI | 4 - 20 mA | FT-60263FJ_AI_1 | FT-60263FJ | Feed Slurry Flow Transmitter for Nozzle #9 (AMTV-11C) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
537 | C2 | 12 | 11 | C2S12,11 | C2S12-X1 | 1756-IF16-11 | AI | 4 - 20 mA | FT-60263FK_AI_1 | FT-60263FK | Feed Slurry Flow Transmitter for Nozzle #10 (AMTV-11C) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
538 | C2 | 12 | 12 | C2S12,12 | C2S12-X1 | 1756-IF16-12 | AI | 4 - 20 mA | FT-60263FL_AI_1 | FT-60263FL | Feed Slurry Flow Transmitter for Nozzle #11 (AMTV-11C) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
539 | C2 | 12 | 13 | C2S12,13 | C2S12-X1 | 1756-IF16-13 | AI | 4 - 20 mA | FT-60263FM_AI_1 | FT-60263FM | Feed Slurry Flow Transmitter for Nozzle #12 (AMTV-11C) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
540 | C2 | 12 | 14 | C2S12,14 | C2S12-X1 | 1756-IF16-14 | AI | 4 - 20 mA | FT-60264FN_AI_1 | FT-60264FN | Feed Slurry Flow Transmitter for Nozzle #13 (AMTV-11D) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
541 | C2 | 12 | 15 | C2S12,15 | C2S12-X1 | 1756-IF16-15 | AI | 4 - 20 mA | FT-60264FP_AI_1 | FT-60264FP | Feed Slurry Flow Transmitter for Nozzle #14 (AMTV-11D) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
542 | C2 | 13 | 0 | C2S13,00 | C2S13-X1 | 1756-IF16-0 | AI | 4 - 20 mA | FT-60264FQ_AI_1 | FT-60264FQ | Feed Slurry Flow Transmitter for Nozzle #15 (AMTV-11D) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
543 | C2 | 13 | 1 | C2S13,01 | C2S13-X1 | 1756-IF16-1 | AI | 4 - 20 mA | FT-60264FR_AI_1 | FT-60264FR | Feed Slurry Flow Transmitter for Nozzle #16 (AMTV-11D) | Keyence | FD-H Series (Clamp-on Ultrasonic Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
544 | C2 | 13 | 2 | C2S13,02 | C2S13-X1 | 1756-IF16-2 | AI | 4 - 20 mA | PT-60201_AI_1 | PT-60201 | Steam feed to Spray dryer | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
545 | C2 | 13 | 3 | C2S13,03 | C2S13-X1 | 1756-IF16-3 | AI | 4 - 20 mA | PT-60207_AI_1 | PT-60207 | Instr. Air Pressure Transmitter for Camera #4 (ACAM-21) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-07 | JB-607 | =CA1+MCP-M2 | ACTIVE
546 | C2 | 13 | 4 | C2S13,04 | C2S13-X1 | 1756-IF16-4 | AI | 4 - 20 mA | PT-60221_AI_1 | PT-60221 | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | JB-607 | =CA1+MCP-M2 | ACTIVE
547 | C2 | 13 | 5 | C2S13,05 | C2S13-X1 | 1756-IF16-5 | AI | 4 - 20 mA | PT-60221_AI_1 | PT-60221 | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | JB-607 | =CA1+MCP-M2 | ACTIVE
548 | C2 | 13 | 6 | C2S13,06 | C2S13-X1 | 1756-IF16-6 | AI | 4 - 20 mA | TI-FH-60210_AI_1 | TI-FH-60210 | Gas Burner Firing Rate Temp Signal to AHTR-21 | Ashcroft | Model FI Bimetal Dial Thermometer | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 3P x1.0) | 325-01-602-PD-06 | JB-607 | =CA1+MCP-M2 | ACTIVE
549 | C2 | 13 | 7 | C2S13,07 | C2S13-X1 | 1756-IF16-7 | AI | 4 - 20 mA | TT-60201_AI_1 | TT-60201 | Steam feed to Spray dryer | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
550 | C2 | 13 | 8 | C2S13,08 | C2S13-X1 | 1756-IF16-8 | AI | 4 - 20 mA | TT-60202_AI_1 | TT-60202 | Compress air temp to camera | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-07 | JB-607 | =CA1+MCP-M2 | ACTIVE
551 | C2 | 13 | 9 | C2S13,09 | C2S13-X1 | 1756-IF16-9 | AI | 4 - 20 mA | TT-60207_AI_1 | TT-60207 | Instr. Air Temperature Transmitter for Air Manifold - Camera #4 (ACAM-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-07 | JB-607 | =CA1+MCP-M2 | ACTIVE
552 | C2 | 13 | 10 | C2S13,10 | C2S13-X1 | 1756-IF16-10 | AI | 4 - 20 mA | UY-FH-60210A_AI_1 | UY-FH-60210A | Comb fan VFD Speed Control | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 | 325-01-602-PD-06 | JB-607 | =CA1+MCP-M2 | ACTIVE
553 | C2 | 13 | 11 | C2S13,11 | C2S13-X1 | 1756-IF16-11 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
554 | C2 | 13 | 12 | C2S13,12 | C2S13-X1 | 1756-IF16-12 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
555 | C2 | 13 | 13 | C2S13,13 | C2S13-X1 | 1756-IF16-13 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
556 | C2 | 13 | 14 | C2S13,14 | C2S13-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
557 | C2 | 13 | 15 | C2S13,15 | C2S13-X1 | 1756-IF16-15 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
558 | C3 | 1 | 0 | C3S01,00 | C3S01-X1 | 1756-IB32-0 | DI | - | AT-40201_DI_1 | AT-40201 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | - | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
559 | C3 | 1 | 1 | C3S01,01 | C3S01-X1 | 1756-IB32-1 | DI | - | AT-40202_DI_1 | AT-40202 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | - | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
560 | C3 | 1 | 2 | C3S01,02 | C3S01-X1 | 1756-IB32-2 | DI | - | AT-40203_DI_1 | AT-40203 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | - | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
561 | C3 | 1 | 3 | C3S01,03 | C3S01-X1 | 1756-IB32-3 | DI | Dry Contact | LSH-60230_DI_1 | LSH-60230 | Powder Level Switch High for Cyclone (CYCL-21) | Endress+Hauser | Soliphant FTM51 (Vibrating Fork for Solids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
562 | C3 | 1 | 4 | C3S01,04 | C3S01-X1 | 1756-IB32-4 | DI | Dry Contact | LSH-60231_DI_1 | LSH-60231 | Powder Level Switch High for Cyclone (CYCL-22) | Endress+Hauser | Soliphant FTM51 (Vibrating Fork for Solids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
563 | C3 | 1 | 5 | C3S01,05 | C3S01-X1 | 1756-IB32-5 | DI | Dry Contact | LSH-60240_DI_1 | LSH-60240 | Powder Level Switch High for Bag House (BGHS-21) | Endress+Hauser | Soliphant FTM51 (Vibrating Fork for Solids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-05 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
564 | C3 | 1 | 6 | C3S01,06 | C3S01-X1 | 1756-IB32-6 | DI | - | PD-60202_DI_1 | PD-60202 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | - | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
565 | C3 | 1 | 7 | C3S01,07 | C3S01-X1 | 1756-IB32-7 | DI | - | RV-60204_DI_1 | RV-60204 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | - | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
566 | C3 | 1 | 8 | C3S01,08 | C3S01-X1 | 1756-IB32-8 | DI | Dry Contact | ZS-60201C_DI_1 | ZS-60201C | Limit Switch for CHAM-21 (Spray Chamber) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
567 | C3 | 1 | 9 | C3S01,09 | C3S01-X1 | 1756-IB32-9 | DI | Dry Contact | ZS-60201D_DI_1 | ZS-60201D | Limit Switch for CHAM-21 (Spray Chamber) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
568 | C3 | 1 | 10 | C3S01,10 | C3S01-X1 | 1756-IB32-10 | DI | Dry Contact | ZS-60201E_DI_1 | ZS-60201E | Limit Switch for CHAM-21 (Spray Chamber) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
569 | C3 | 1 | 11 | C3S01,11 | C3S01-X1 | 1756-IB32-11 | DI | Dry Contact | ZS-60229_DI_1 | ZS-60229 | Limit Switch for CY-60230 (Door Service) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
570 | C3 | 1 | 12 | C3S01,12 | C3S01-X1 | 1756-IB32-12 | DI | Dry Contact | ZS-60230_DI_1 | ZS-60230 | Limit Switch for CY-60231 (Door Service) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
571 | C3 | 1 | 13 | C3S01,13 | C3S01-X1 | 1756-IB32-13 | DI | Dry Contact | ZS-60231A_DI_1 | ZS-60231A | Gas Limit Switch for DTEX-21 (Bag House Face Spectacle Inserted) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-05 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
572 | C3 | 1 | 14 | C3S01,14 | C3S01-X1 | 1756-IB32-14 | DI | Dry Contact | ZS-60231B_DI_1 | ZS-60231B | Gas Limit Switch for DTEX-21 (Bag House Face Blind Inserted) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-05 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
573 | C3 | 1 | 15 | C3S01,15 | C3S01-X1 | 1756-IB32-15 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-603 | =CA1+MCP-M3 | SPARE
574 | C3 | 1 | 16 | C3S01,16 | C3S01-X2 | 1756-IB32-16 | DI | 24 VDC energized | DV-61301_DI_1 | DV-61301 | On/Off Valve for Diverter Valve DV-61301 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1 / CVV 4Cx1 | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
575 | C3 | 1 | 17 | C3S01,17 | C3S01-X2 | 1756-IB32-17 | DI | 24 VDC energized | DV-61301_DI_2 | DV-61301 | On/Off Valve for Diverter Valve DV-61301 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1 / CVV 4Cx1 | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
576 | C3 | 1 | 18 | C3S01,18 | C3S01-X2 | 1756-IB32-18 | DI | 24 VDC energized | DV-61302_DI_1 | DV-61302 | On/Off Valve for Diverter Valve DV-61302 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1 / CVV 4Cx1 | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
577 | C3 | 1 | 19 | C3S01,19 | C3S01-X2 | 1756-IB32-19 | DI | 24 VDC energized | DV-61302_DI_2 | DV-61302 | On/Off Valve for Diverter Valve DV-61302 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1 / CVV 4Cx1 | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
578 | C3 | 1 | 20 | C3S01,20 | C3S01-X2 | 1756-IB32-20 | DI | Dry Contact | LS-61303_DI_1 | LS-61303 | Level switch | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
579 | C3 | 1 | 21 | C3S01,21 | C3S01-X2 | 1756-IB32-21 | DI | Dry Contact | PSL-61301_DI_1 | PSL-61301 | Pressure alarm low | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
580 | C3 | 1 | 22 | C3S01,22 | C3S01-X2 | 1756-IB32-22 | DI | Dry Contact | PSL-61302_DI_1 | PSL-61302 | Pressure alarm low | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
581 | C3 | 1 | 28 | C3S01,28 | C3S01-X2 | 1756-IB32-28 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
582 | C3 | 1 | 29 | C3S01,29 | C3S01-X2 | 1756-IB32-29 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
583 | C3 | 1 | 30 | C3S01,30 | C3S01-X2 | 1756-IB32-30 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
584 | C3 | 1 | 31 | C3S01,31 | C3S01-X2 | 1756-IB32-31 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
585 | C3 | 2 | 0 | C3S02,00 | C3S02-X1 | 1756-IB32-0 | DI | - | ISV-61301_DI_1 | ISV-61301 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
586 | C3 | 2 | 1 | C3S02,01 | C3S02-X1 | 1756-IB32-1 | DI | Dry Contact | LSH-61301_DI_1 | LSH-61301 | Level alarm high | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
587 | C3 | 2 | 2 | C3S02,02 | C3S02-X1 | 1756-IB32-2 | DI | - | LSH-61303_DI_1 | LSH-61303 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
588 | C3 | 2 | 3 | C3S02,03 | C3S02-X1 | 1756-IB32-3 | DI | Dry Contact | LSH-61306_DI_1 | LSH-61306 | Level alarm high | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
589 | C3 | 2 | 4 | C3S02,04 | C3S02-X1 | 1756-IB32-4 | DI | Dry Contact | LSH-61308_DI_1 | LSH-61308 | High Level alarm Cooling cyclone | Endress+Hauser | Soliphant FTM51 (Vibrating Fork for Solids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
590 | C3 | 2 | 5 | C3S02,05 | C3S02-X1 | 1756-IB32-5 | DI | Dry Contact | LSL-61302_DI_1 | LSL-61302 | Level alarm low | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
591 | C3 | 2 | 6 | C3S02,06 | C3S02-X1 | 1756-IB32-6 | DI | Dry Contact | PSE-61300_DI_1 | PSE-61300 | Explosion Vent PSE-61300 | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | CVV 4Cx1 | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
592 | C3 | 2 | 7 | C3S02,07 | C3S02-X1 | 1756-IB32-7 | DI | Dry Contact | PSE-61301_DI_1 | PSE-61301 | Explosion Vent PSE-61301 | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | CVV 4Cx1 | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
593 | C3 | 2 | 8 | C3S02,08 | C3S02-X1 | 1756-IB32-8 | DI | Dry Contact | PSE-61304_DI_1 | PSE-61304 | Explosion Vent PSE-61304 | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | CVV 4Cx1 | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
594 | C3 | 2 | 9 | C3S02,09 | C3S02-X1 | 1756-IB32-9 | DI | - | PSV-61301A_DI_1 | PSV-61301A | Position Brether Valve High Pressure PSV-61301 | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
595 | C3 | 2 | 10 | C3S02,10 | C3S02-X1 | 1756-IB32-10 | DI | - | PSV-61301B_DI_1 | PSV-61301B | Position Brether Valve Vacuum Pressure PSV-61301 | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
596 | C3 | 2 | 11 | C3S02,11 | C3S02-X1 | 1756-IB32-11 | DI | Dry Contact | ZS-61310_DI_1 | ZS-61310 | Position Magnet Door | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
597 | C3 | 2 | 12 | C3S02,12 | C3S02-X1 | 1756-IB32-12 | DI | Dry Contact | ZS-61311_DI_1 | ZS-61311 | Position Magnet Door | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
598 | C3 | 2 | 13 | C3S02,13 | C3S02-X1 | 1756-IB32-13 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
599 | C3 | 2 | 14 | C3S02,14 | C3S02-X1 | 1756-IB32-14 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
600 | C3 | 2 | 15 | C3S02,15 | C3S02-X1 | 1756-IB32-15 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
601 | C3 | 2 | 16 | C3S02,16 | C3S02-X2 | 1756-IB32-16 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
602 | C3 | 2 | 17 | C3S02,17 | C3S02-X2 | 1756-IB32-17 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
603 | C3 | 2 | 18 | C3S02,18 | C3S02-X2 | 1756-IB32-18 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
604 | C3 | 2 | 19 | C3S02,19 | C3S02-X2 | 1756-IB32-19 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
605 | C3 | 2 | 20 | C3S02,20 | C3S02-X2 | 1756-IB32-20 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
606 | C3 | 2 | 21 | C3S02,21 | C3S02-X2 | 1756-IB32-21 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
607 | C3 | 2 | 22 | C3S02,22 | C3S02-X2 | 1756-IB32-22 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
608 | C3 | 2 | 23 | C3S02,23 | C3S02-X2 | 1756-IB32-23 | DI | Dry Contact | PSL-61311_DI_1 | PSL-61311 | Pressure alarm low | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-04 | JB-618 | =CA1+MCP-M3 | ACTIVE
609 | C3 | 2 | 23 | C3S02,23 | C3S02-X2 | 1756-IB32-23 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
610 | C3 | 2 | 24 | C3S02,24 | C3S02-X2 | 1756-IB32-24 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
611 | C3 | 2 | 24 | C3S02,24 | C3S02-X2 | 1756-IB32-24 | DI | 24 VDC energized | SV-61304_DI_1 | SV-61304 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
612 | C3 | 2 | 25 | C3S02,25 | C3S02-X2 | 1756-IB32-25 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
613 | C3 | 2 | 25 | C3S02,25 | C3S02-X2 | 1756-IB32-25 | DI | 24 VDC energized | SV-61304_DI_2 | SV-61304 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
614 | C3 | 2 | 26 | C3S02,26 | C3S02-X2 | 1756-IB32-26 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
615 | C3 | 2 | 26 | C3S02,26 | C3S02-X2 | 1756-IB32-26 | DI | 24 VDC energized | XV-61301_DI_1 | XV-61301 | Product feed-out Packing silo | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
616 | C3 | 2 | 27 | C3S02,27 | C3S02-X2 | 1756-IB32-27 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
617 | C3 | 2 | 27 | C3S02,27 | C3S02-X2 | 1756-IB32-27 | DI | 24 VDC energized | XV-61301_DI_2 | XV-61301 | Product feed-out Packing silo | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
618 | C3 | 2 | 28 | C3S02,28 | C3S02-X2 | 1756-IB32-28 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
619 | C3 | 2 | 29 | C3S02,29 | C3S02-X2 | 1756-IB32-29 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
620 | C3 | 2 | 30 | C3S02,30 | C3S02-X2 | 1756-IB32-30 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
621 | C3 | 2 | 31 | C3S02,31 | C3S02-X2 | 1756-IB32-31 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | SPARE
622 | C3 | 3 | 0 | C3S03,00 | C3S03-X1 | 1756-OB32-0 | DO | 24 VDC energized | DV-61301_DO_1 | DV-61301 | On/Off Valve for Diverter Valve DV-61301 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1 / CVV 4Cx1 | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
623 | C3 | 3 | 1 | C3S03,01 | C3S03-X1 | 1756-OB32-1 | DO | 24 VDC energized | DV-61302_DO_1 | DV-61302 | On/Off Valve for Diverter Valve DV-61302 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1 / CVV 4Cx1 | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
624 | C3 | 3 | 2 | C3S03,02 | C3S03-X1 | 1756-OB32-2 | DO | 24 VDC energized | SV-61301_DO_1 | SV-61301 | Timer compress air pluse solenoid valve | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
625 | C3 | 3 | 3 | C3S03,03 | C3S03-X1 | 1756-OB32-3 | DO | 24 VDC energized | SV-61302_DO_1 | SV-61302 | Air service | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
626 | C3 | 3 | 4 | C3S03,04 | C3S03-X1 | 1756-OB32-4 | DO | 24 VDC energized | SV-61303_DO_1 | SV-61303 | Timer compress air pluse solenoid valve | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
627 | C3 | 3 | 5 | C3S03,05 | C3S03-X1 | 1756-OB32-5 | DO | 24 VDC energized | SV-61304_DO_1 | SV-61304 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
628 | C3 | 3 | 6 | C3S03,06 | C3S03-X1 | 1756-OB32-6 | DO | 24 VDC energized | SV-61305_DO_1 | SV-61305 | Air service | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
629 | C3 | 3 | 7 | C3S03,07 | C3S03-X1 | 1756-OB32-7 | DO | - | SV-61306_DO_1 | SV-61306 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 3-25-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
630 | C3 | 3 | 8 | C3S03,08 | C3S03-X1 | 1756-OB32-8 | DO | 24 VDC energized | XV-61301_DO_1 | XV-61301 | Product feed-out Packing silo | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
631 | C3 | 3 | 9 | C3S03,09 | C3S03-X1 | 1756-OB32-9 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
632 | C3 | 3 | 10 | C3S03,10 | C3S03-X1 | 1756-OB32-10 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
633 | C3 | 3 | 11 | C3S03,11 | C3S03-X1 | 1756-OB32-11 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
634 | C3 | 3 | 12 | C3S03,12 | C3S03-X1 | 1756-OB32-12 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
635 | C3 | 3 | 13 | C3S03,13 | C3S03-X1 | 1756-OB32-13 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
636 | C3 | 3 | 14 | C3S03,14 | C3S03-X1 | 1756-OB32-14 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
637 | C3 | 3 | 15 | C3S03,15 | C3S03-X1 | 1756-OB32-15 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
638 | C3 | 3 | 16 | C3S03,16 | C3S03-X2 | 1756-OB32-16 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
639 | C3 | 3 | 17 | C3S03,17 | C3S03-X2 | 1756-OB32-17 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
640 | C3 | 3 | 18 | C3S03,18 | C3S03-X2 | 1756-OB32-18 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
641 | C3 | 3 | 19 | C3S03,19 | C3S03-X2 | 1756-OB32-19 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
642 | C3 | 3 | 20 | C3S03,20 | C3S03-X2 | 1756-OB32-20 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
643 | C3 | 3 | 21 | C3S03,21 | C3S03-X2 | 1756-OB32-21 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
644 | C3 | 3 | 22 | C3S03,22 | C3S03-X2 | 1756-OB32-22 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
645 | C3 | 3 | 23 | C3S03,23 | C3S03-X2 | 1756-OB32-23 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
646 | C3 | 3 | 24 | C3S03,24 | C3S03-X2 | 1756-OB32-24 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
647 | C3 | 3 | 25 | C3S03,25 | C3S03-X2 | 1756-OB32-25 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
648 | C3 | 3 | 26 | C3S03,26 | C3S03-X2 | 1756-OB32-26 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
649 | C3 | 3 | 27 | C3S03,27 | C3S03-X2 | 1756-OB32-27 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
650 | C3 | 3 | 28 | C3S03,28 | C3S03-X2 | 1756-OB32-28 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
651 | C3 | 3 | 29 | C3S03,29 | C3S03-X2 | 1756-OB32-29 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
652 | C3 | 3 | 30 | C3S03,30 | C3S03-X2 | 1756-OB32-30 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
653 | C3 | 3 | 31 | C3S03,31 | C3S03-X2 | 1756-OB32-31 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-618 | =CA1+MCP-M3 | SPARE
654 | C3 | 4 | 0 | C3S04,00 | C3S04-X1 | 1756-IF16-0 | AI | 4 - 20 mA | PT-60230_AI_1 | PT-60230 | Gas Pressure Transmitter for Conveying Duct (DTCO-21) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
655 | C3 | 4 | 1 | C3S04,01 | C3S04-X1 | 1756-IF16-1 | AI | 4 - 20 mA | PT-60231_AI_1 | PT-60231 | Gas Pressure Transmitter for Cyclone Exhaust Duct (DTCE-21) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
656 | C3 | 4 | 2 | C3S04,02 | C3S04-X1 | 1756-IF16-2 | AI | 4 - 20 mA | TT-60224_AI_1 | TT-60224 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
657 | C3 | 4 | 3 | C3S04,03 | C3S04-X1 | 1756-IF16-3 | AI | 4 - 20 mA | TT-60225_AI_1 | TT-60225 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
658 | C3 | 4 | 4 | C3S04,04 | C3S04-X1 | 1756-IF16-4 | AI | 4 - 20 mA | TT-60226_AI_1 | TT-60226 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
659 | C3 | 4 | 5 | C3S04,05 | C3S04-X1 | 1756-IF16-5 | AI | 4 - 20 mA | TT-60227_AI_1 | TT-60227 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
660 | C3 | 4 | 6 | C3S04,06 | C3S04-X1 | 1756-IF16-6 | AI | 4 - 20 mA | TT-60230_AI_1 | TT-60230 | Gas and Powder Temperature Transmitter for Conveying Duct (DTCO-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | IS-JB-603 | =CA1+MCP-M3 | ACTIVE
661 | C3 | 4 | 7 | C3S04,07 | C3S04-X1 | 1756-IF16-7 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-603 | =CA1+MCP-M3 | SPARE
662 | C3 | 4 | 8 | C3S04,08 | C3S04-X1 | 1756-IF16-8 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-603 | =CA1+MCP-M3 | SPARE
663 | C3 | 4 | 9 | C3S04,09 | C3S04-X1 | 1756-IF16-9 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-603 | =CA1+MCP-M3 | SPARE
664 | C3 | 4 | 10 | C3S04,10 | C3S04-X1 | 1756-IF16-10 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-603 | =CA1+MCP-M3 | SPARE
665 | C3 | 4 | 11 | C3S04,11 | C3S04-X1 | 1756-IF16-11 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-603 | =CA1+MCP-M3 | SPARE
666 | C3 | 4 | 12 | C3S04,12 | C3S04-X1 | 1756-IF16-12 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-603 | =CA1+MCP-M3 | SPARE
667 | C3 | 4 | 13 | C3S04,13 | C3S04-X1 | 1756-IF16-13 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-603 | =CA1+MCP-M3 | SPARE
668 | C3 | 4 | 14 | C3S04,14 | C3S04-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-603 | =CA1+MCP-M3 | SPARE
669 | C3 | 4 | 15 | C3S04,15 | C3S04-X1 | 1756-IF16-15 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-603 | =CA1+MCP-M3 | SPARE
670 | C3 | 5 | 0 | C3S05,00 | C3S05-X1 | 1756-IF16-0 | AI | 4 - 20 mA | PT-61303_AI_1 | PT-61303 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
671 | C3 | 5 | 1 | C3S05,01 | C3S05-X1 | 1756-IF16-1 | AI | - | PT-61306_AI_1 | PT-61306 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 3-25-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
672 | C3 | 5 | 2 | C3S05,02 | C3S05-X1 | 1756-IF16-2 | AI | - | TT-61303_AI_1 | TT-61303 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 3-25-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
673 | C3 | 5 | 3 | C3S05,03 | C3S05-X1 | 1756-IF16-3 | AI | - | TT-61304_AI_1 | TT-61304 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 3-25-01-613-PD-01 | JB-618 | =CA1+MCP-M3 | ACTIVE
674 | C3 | 5 | 4 | C3S05,04 | C3S05-X1 | 1756-IF16-4 | AI | 4 - 20 mA | DPT-61301_AI_1 | DPT-61301 | Vent filter pressure | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
675 | C3 | 5 | 5 | C3S05,05 | C3S05-X1 | 1756-IF16-5 | AI | 4 - 20 mA | DPT-61302_AI_1 | DPT-61302 | Vent filter pressure | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
676 | C3 | 5 | 6 | C3S05,06 | C3S05-X1 | 1756-IF16-6 | AI | 4 - 20 mA | LT-61301_AI_1 | LT-61301 | Level powder in silo | Endress+Hauser | Micropilot FMR67B (80GHz Radar Level) | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
677 | C3 | 5 | 7 | C3S05,07 | C3S05-X1 | 1756-IF16-7 | AI | 4 - 20 mA | PT-61301_AI_1 | PT-61301 | Pressure in silo | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
678 | C3 | 5 | 8 | C3S05,08 | C3S05-X1 | 1756-IF16-8 | AI | 4 - 20 mA | PT-61303_AI_1 | PT-61303 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
679 | C3 | 5 | 9 | C3S05,09 | C3S05-X1 | 1756-IF16-9 | AI | 4 - 20 mA | PT-61304_AI_1 | PT-61304 | Gas Pressure Transmitter for Storage Bin Cyclone Inlet Duct (CYCL-31) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
680 | C3 | 5 | 10 | C3S05,10 | C3S05-X1 | 1756-IF16-10 | AI | 4 - 20 mA | PT-61305_AI_1 | PT-61305 | Gas Pressure Transmitter for Exhaust Duct (DTEX-31) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
681 | C3 | 5 | 11 | C3S05,11 | C3S05-X1 | 1756-IF16-11 | AI | 4 - 20 mA | TT-61301_AI_1 | TT-61301 | Gas Temperature Transmitter for Cold Air Duct (DTCA-32) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
682 | C3 | 5 | 12 | C3S05,12 | C3S05-X1 | 1756-IF16-12 | AI | 4 - 20 mA | TT-61302_AI_1 | TT-61302 | Gas and Powder Temperature Transmitter for Cooling Cyclone (CYCL-31) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-01 | IS-JB-618 | =CA1+MCP-M3 | ACTIVE
683 | C3 | 5 | 13 | C3S05,13 | C3S05-X1 | 1756-IF16-13 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-618 | =CA1+MCP-M3 | SPARE
684 | C3 | 5 | 14 | C3S05,14 | C3S05-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-618 | =CA1+MCP-M3 | SPARE
685 | C3 | 5 | 15 | C3S05,15 | C3S05-X1 | 1756-IF16-15 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-618 | =CA1+MCP-M3 | SPARE
686 | C3 | 13 | 0 | C3S13,00 | C3S13-X1 | 1756-OF8-0 | AO | 4 - 20 mA | TCV-40222_AO_1 | TCV-40222 | Jet Cooker | Samson | Type 3241 Globe Valve + Trovis 3730-1 Positioner | LiY-CY TP 2Px1.0 (Setpoint AO + Position Feedback AI) (Ref: LiY-CY TP 1P x1.0) | 325-01-402-PD-02 | JB-402 | =CA1+MCP-M2 | ACTIVE
687 | C3 | 13 | 1 | C3S13,01 | C3S13-X1 | 1756-OF8-1 | AO | - | TV-60202_AO_1 | TV-60202 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 3-25-01-602-PD-07 | JB-602 | =CA1+MCP-M2 | ACTIVE
688 | C3 | 13 | 2 | C3S13,02 | C3S13-X1 | 1756-OF8-2 | AO | - | TV-60214_AO_1 | TV-60214 | Steam Temperature Valve for Pre-Heat Steam Heat Exchanger (HXCH-21) | Samson | Type 3241 Globe Valve + Trovis 3730-1 Positioner | LiY-CY TP 2Px1.0 (Setpoint AO + Position Feedback AI) (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-03 | JB-602 | =CA1+MCP-M2 | ACTIVE
689 | C3 | 13 | 3 | C3S13,03 | C3S13-X1 | 1756-OF8-3 | AO | - | PV-60201_AO_1 | PV-60201 | Steam feed to Spray dryer | Samson | Type 3241 Globe Valve + Trovis 3730-1 Positioner | LiY-CY TP 2Px1.0 (Setpoint AO + Position Feedback AI) (Ref: LiY-CY TP 2P x1.0) | 325-01-602-PD-02 | JB-607 | =CA1+MCP-M2 | ACTIVE
690 | C3 | 13 | 4 | C3S13,04 | C3S13-X1 | 1756-OF8-4 | AO | 4 - 20 mA | UY-FH-60210B_AO_1 | UY-FH-60210B | Demand Signal | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 | 325-01-602-PD-06 | JB-607 | =CA1+MCP-M2 | ACTIVE
691 | C3 | 13 | 5 | C3S13,05 | C3S13-X1 | 1756-OF8-5 | AO | - | Spare_AO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
692 | C3 | 13 | 6 | C3S13,06 | C3S13-X1 | 1756-OF8-6 | AO | - | Spare_AO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
693 | C3 | 13 | 7 | C3S13,07 | C3S13-X1 | 1756-OF8-7 | AO | - | Spare_AO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-607 | =CA1+MCP-M2 | SPARE
694 | C4 | 1 | 0 | C4S01,00 | C4S01-X1 | 1756-IB32-0 | DI | 4 - 20 mA | FT-60203_DI_1 | FT-60203 | Culinary steam feed to Spray dryer | Endress+Hauser | Prowirl F 200 (Vortex Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2P x1.0) | 325-01-602-PD-09 | JB-606 | =CA1+MCP-M4 | ACTIVE
695 | C4 | 1 | 1 | C4S01,01 | C4S01-X1 | 1756-IB32-1 | DI | Dry Contact | LSH-60250_DI_1 | LSH-60250 | Water Level Switch High for Fire Deluge Pipe (FWDP-21) | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-602-PD-05 | JB-606 | =CA1+MCP-M4 | ACTIVE
696 | C4 | 1 | 2 | C4S01,02 | C4S01-X1 | 1756-IB32-2 | DI | Dry Contact | XA-60261_DI_1 | XA-60261 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-05 | JB-606 | =CA1+MCP-M4 | ACTIVE
697 | C4 | 1 | 3 | C4S01,03 | C4S01-X1 | 1756-IB32-3 | DI | Dry Contact | XA-60262_DI_1 | XA-60262 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-602-PD-05 | JB-606 | =CA1+MCP-M4 | ACTIVE
698 | C4 | 1 | 4 | C4S01,04 | C4S01-X1 | 1756-IB32-4 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
699 | C4 | 1 | 5 | C4S01,05 | C4S01-X1 | 1756-IB32-5 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
700 | C4 | 1 | 6 | C4S01,06 | C4S01-X1 | 1756-IB32-6 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
701 | C4 | 1 | 7 | C4S01,07 | C4S01-X1 | 1756-IB32-7 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
702 | C4 | 1 | 8 | C4S01,08 | C4S01-X1 | 1756-IB32-8 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
703 | C4 | 1 | 9 | C4S01,09 | C4S01-X1 | 1756-IB32-9 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
704 | C4 | 1 | 10 | C4S01,10 | C4S01-X1 | 1756-IB32-10 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
705 | C4 | 1 | 11 | C4S01,11 | C4S01-X1 | 1756-IB32-11 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
706 | C4 | 1 | 12 | C4S01,12 | C4S01-X1 | 1756-IB32-12 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
707 | C4 | 1 | 13 | C4S01,13 | C4S01-X1 | 1756-IB32-13 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
708 | C4 | 1 | 14 | C4S01,14 | C4S01-X1 | 1756-IB32-14 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
709 | C4 | 1 | 15 | C4S01,15 | C4S01-X1 | 1756-IB32-15 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
710 | C4 | 1 | 16 | C4S01,16 | C4S01-X2 | 1756-IB32-16 | DI | Dry Contact | ZS-60201A_DI_1 | ZS-60201A | Limit Switch for CHAM-21 (Spray Chamber) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-04 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
711 | C4 | 1 | 17 | C4S01,17 | C4S01-X2 | 1756-IB32-17 | DI | Dry Contact | ZS-60201B_DI_1 | ZS-60201B | Limit Switch for CHAM-21 (Spray Chamber) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-04 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
712 | C4 | 1 | 18 | C4S01,18 | C4S01-X2 | 1756-IB32-18 | DI | Dry Contact | ZS-60231C_DI_1 | ZS-60231C | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Spool Inserted) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-05 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
713 | C4 | 1 | 19 | C4S01,19 | C4S01-X2 | 1756-IB32-19 | DI | Dry Contact | ZS-60231D_DI_1 | ZS-60231D | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Blind Inserted) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-05 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
714 | C4 | 1 | 20 | C4S01,20 | C4S01-X2 | 1756-IB32-20 | DI | Dry Contact | ZS-60231E_DI_1 | ZS-60231E | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Spool Inserted) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-05 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
715 | C4 | 1 | 21 | C4S01,21 | C4S01-X2 | 1756-IB32-21 | DI | Dry Contact | ZS-60231F_DI_1 | ZS-60231F | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Blind Inserted) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-05 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
716 | C4 | 1 | 22 | C4S01,22 | C4S01-X2 | 1756-IB32-22 | DI | Dry Contact | ZS-60240_DI_1 | ZS-60240 | Limit Switch for FA-60240 (Door Service) | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-602-PD-05 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
717 | C4 | 1 | 23 | C4S01,23 | C4S01-X2 | 1756-IB32-23 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
718 | C4 | 1 | 24 | C4S01,24 | C4S01-X2 | 1756-IB32-24 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
719 | C4 | 1 | 25 | C4S01,25 | C4S01-X2 | 1756-IB32-25 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
720 | C4 | 1 | 26 | C4S01,26 | C4S01-X2 | 1756-IB32-26 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
721 | C4 | 1 | 27 | C4S01,27 | C4S01-X2 | 1756-IB32-27 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
722 | C4 | 1 | 28 | C4S01,28 | C4S01-X2 | 1756-IB32-28 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
723 | C4 | 1 | 29 | C4S01,29 | C4S01-X2 | 1756-IB32-29 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
724 | C4 | 1 | 30 | C4S01,30 | C4S01-X2 | 1756-IB32-30 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
725 | C4 | 1 | 31 | C4S01,31 | C4S01-X2 | 1756-IB32-31 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
726 | C4 | 2 | 0 | C4S02,00 | C4S02-X1 | 1756-IB32-0 | DI | Dry Contact | PSL-61305_DI_1 | PSL-61305 | Pressure alarm low | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-03 | JB-612 | =CA1+MCP-M4 | ACTIVE
727 | C4 | 2 | 1 | C4S02,01 | C4S02-X1 | 1756-IB32-1 | DI | Dry Contact | PSL-61306_DI_1 | PSL-61306 | Pressure alarm low | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-05 | JB-612 | =CA1+MCP-M4 | ACTIVE
728 | C4 | 2 | 2 | C4S02,02 | C4S02-X1 | 1756-IB32-2 | DI | - | PVM-61301_DI_1 | PVM-61301 | Start / Stop Command for FVNR PV-61301 (Vacuum Cleaning Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-03 | JB-612 | =CA1+MCP-M4 | ACTIVE
729 | C4 | 2 | 3 | C4S02,03 | C4S02-X1 | 1756-IB32-3 | DI | - | PVM-61301_DI_2 | PVM-61301 | Start / Stop Command for FVNR PV-61301 (Vacuum Cleaning Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-03 | JB-612 | =CA1+MCP-M4 | ACTIVE
730 | C4 | 2 | 4 | C4S02,04 | C4S02-X1 | 1756-IB32-4 | DI | Dry Contact | XA-61301A_DI_1 | XA-61301A | Request filter plant | Industrial Process Equipment | Standard Process Field Device | MULTICORE LINK TO PLC | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
731 | C4 | 2 | 5 | C4S02,05 | C4S02-X1 | 1756-IB32-5 | DI | Dry Contact | XA-61301B_DI_1 | XA-61301B | Request material transport | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
732 | C4 | 2 | 6 | C4S02,06 | C4S02-X1 | 1756-IB32-6 | DI | Dry Contact | XA-61301C_DI_1 | XA-61301C | Request belt plant | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
733 | C4 | 2 | 7 | C4S02,07 | C4S02-X1 | 1756-IB32-7 | DI | Dry Contact | XA-61301D_DI_1 | XA-61301D | Machine in operation | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
734 | C4 | 2 | 8 | C4S02,08 | C4S02-X1 | 1756-IB32-8 | DI | Dry Contact | XA-61301E_DI_1 | XA-61301E | General Fault | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
735 | C4 | 2 | 9 | C4S02,09 | C4S02-X1 | 1756-IB32-9 | DI | Dry Contact | XA-61301F_DI_1 | XA-61301F | Machine is ready | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
736 | C4 | 2 | 10 | C4S02,10 | C4S02-X1 | 1756-IB32-10 | DI | Dry Contact | XA-61301G_DI_1 | XA-61301G | Emergency stop activated | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
737 | C4 | 2 | 11 | C4S02,11 | C4S02-X1 | 1756-IB32-11 | DI | Dry Contact | XA-61301H_DI_1 | XA-61301H | Silo minimum | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
738 | C4 | 2 | 12 | C4S02,12 | C4S02-X1 | 1756-IB32-12 | DI | Dry Contact | XA-61301J_DI_1 | XA-61301J | Silo maximum | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
739 | C4 | 2 | 13 | C4S02,13 | C4S02-X1 | 1756-IB32-13 | DI | 24 VDC energized | XV-61302_DI_1 | XV-61302 | Dust collector feed vent | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
740 | C4 | 2 | 14 | C4S02,14 | C4S02-X1 | 1756-IB32-14 | DI | 24 VDC energized | XV-61302_DI_2 | XV-61302 | Dust collector feed vent | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
741 | C4 | 2 | 15 | C4S02,15 | C4S02-X1 | 1756-IB32-15 | DI | 24 VDC energized | XV-61303_DI_1 | XV-61303 | Dust collector feed from packer | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
742 | C4 | 2 | 16 | C4S02,16 | C4S02-X2 | 1756-IB32-16 | DI | 24 VDC energized | XV-61303_DI_2 | XV-61303 | Dust collector feed from packer | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
743 | C4 | 2 | 17 | C4S02,17 | C4S02-X2 | 1756-IB32-17 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
744 | C4 | 2 | 18 | C4S02,18 | C4S02-X2 | 1756-IB32-18 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
745 | C4 | 2 | 19 | C4S02,19 | C4S02-X2 | 1756-IB32-19 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
746 | C4 | 2 | 20 | C4S02,20 | C4S02-X2 | 1756-IB32-20 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
747 | C4 | 2 | 21 | C4S02,21 | C4S02-X2 | 1756-IB32-21 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
748 | C4 | 2 | 22 | C4S02,22 | C4S02-X2 | 1756-IB32-22 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
749 | C4 | 2 | 23 | C4S02,23 | C4S02-X2 | 1756-IB32-23 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
750 | C4 | 2 | 24 | C4S02,24 | C4S02-X2 | 1756-IB32-24 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
751 | C4 | 2 | 25 | C4S02,25 | C4S02-X2 | 1756-IB32-25 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
752 | C4 | 2 | 26 | C4S02,26 | C4S02-X2 | 1756-IB32-26 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
753 | C4 | 2 | 27 | C4S02,27 | C4S02-X2 | 1756-IB32-27 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
754 | C4 | 2 | 28 | C4S02,28 | C4S02-X2 | 1756-IB32-28 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
755 | C4 | 2 | 29 | C4S02,29 | C4S02-X2 | 1756-IB32-29 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
756 | C4 | 2 | 30 | C4S02,30 | C4S02-X2 | 1756-IB32-30 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
757 | C4 | 2 | 31 | C4S02,31 | C4S02-X2 | 1756-IB32-31 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
758 | C4 | 3 | 0 | C4S03,00 | C4S03-X1 | 1756-IB32-0 | DI | Dry Contact | ISV-61303_DI_1 | ISV-61303 | Explosion isolation flap valve ISV-61303 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 4Cx1) | 325-01-613-PD-03 | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
759 | C4 | 3 | 1 | C4S03,01 | C4S03-X1 | 1756-IB32-1 | DI | Dry Contact | ISV-61304_DI_1 | ISV-61304 | Explosion isolation flap valve ISV-61304 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 4Cx1) | 325-01-613-PD-05 | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
760 | C4 | 3 | 2 | C4S03,02 | C4S03-X1 | 1756-IB32-2 | DI | Dry Contact | LSH-61304_DI_1 | LSH-61304 | Big bag level alarm high | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-03 | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
761 | C4 | 3 | 3 | C4S03,03 | C4S03-X1 | 1756-IB32-3 | DI | Dry Contact | LSH-61305_DI_1 | LSH-61305 | Big bag level alarm high | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-05 | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
762 | C4 | 3 | 4 | C4S03,04 | C4S03-X1 | 1756-IB32-4 | DI | Dry Contact | LSH-61307_DI_1 | LSH-61307 | High Level alarm reject screen | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-01 | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
763 | C4 | 3 | 5 | C4S03,05 | C4S03-X1 | 1756-IB32-5 | DI | Dry Contact | LSH-61312_DI_1 | LSH-61312 | Level alarm high | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-613-PD-05 | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
764 | C4 | 3 | 6 | C4S03,06 | C4S03-X1 | 1756-IB32-6 | DI | Dry Contact | PSE-61302_DI_1 | PSE-61302 | Explosion Vent PSE-61302 | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | CVV 4Cx1 | 325-01-613-PD-03 | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
765 | C4 | 3 | 7 | C4S03,07 | C4S03-X1 | 1756-IB32-7 | DI | Dry Contact | PSE-61303_DI_1 | PSE-61303 | Explosion Vent PSE-61303 | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | CVV 4Cx1 | 325-01-613-PD-05 | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
766 | C4 | 3 | 9 | C4S03,09 | C4S03-X1 | 1756-IB32-9 | DI | - | RV-61301_DI_1 | RV-61301 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | - | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
767 | C4 | 3 | 10 | C4S03,10 | C4S03-X1 | 1756-IB32-10 | DI | - | RV-61304_DI_1 | RV-61304 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | - | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
768 | C4 | 3 | 11 | C4S03,11 | C4S03-X1 | 1756-IB32-11 | DI | - | RV-61305_DI_1 | RV-61305 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | - | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
769 | C4 | 3 | 12 | C4S03,12 | C4S03-X1 | 1756-IB32-12 | DI | - | SC-61301_DI_1 | SC-61301 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | - | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
770 | C4 | 3 | 13 | C4S03,13 | C4S03-X1 | 1756-IB32-13 | DI | - | SC-61302_DI_1 | SC-61302 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | - | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
771 | C4 | 3 | 14 | C4S03,14 | C4S03-X1 | 1756-IB32-14 | DI | Dry Contact | ZS-61312_DI_1 | ZS-61312 | Position Magnet Door | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-613-PD-01 | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
772 | C4 | 3 | 15 | C4S03,15 | C4S03-X1 | 1756-IB32-15 | DI | Dry Contact | ZS-61313_DI_1 | ZS-61313 | Position Magnet Door | APL-HKC | APL-210N / APL-510N Valve Position Monitor | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-613-PD-01 | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
773 | C4 | 3 | 16 | C4S03,16 | C4S03-X2 | 1756-IB32-16 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
774 | C4 | 3 | 17 | C4S03,17 | C4S03-X2 | 1756-IB32-17 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
775 | C4 | 3 | 18 | C4S03,18 | C4S03-X2 | 1756-IB32-18 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
776 | C4 | 3 | 19 | C4S03,19 | C4S03-X2 | 1756-IB32-19 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
777 | C4 | 3 | 20 | C4S03,20 | C4S03-X2 | 1756-IB32-20 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
778 | C4 | 3 | 21 | C4S03,21 | C4S03-X2 | 1756-IB32-21 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
779 | C4 | 3 | 22 | C4S03,22 | C4S03-X2 | 1756-IB32-22 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
780 | C4 | 3 | 23 | C4S03,23 | C4S03-X2 | 1756-IB32-23 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
781 | C4 | 3 | 24 | C4S03,24 | C4S03-X2 | 1756-IB32-24 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
782 | C4 | 3 | 25 | C4S03,25 | C4S03-X2 | 1756-IB32-25 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
783 | C4 | 3 | 26 | C4S03,26 | C4S03-X2 | 1756-IB32-26 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
784 | C4 | 3 | 27 | C4S03,27 | C4S03-X2 | 1756-IB32-27 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
785 | C4 | 3 | 28 | C4S03,28 | C4S03-X2 | 1756-IB32-28 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
786 | C4 | 3 | 29 | C4S03,29 | C4S03-X2 | 1756-IB32-29 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
787 | C4 | 3 | 30 | C4S03,30 | C4S03-X2 | 1756-IB32-30 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
788 | C4 | 3 | 31 | C4S03,31 | C4S03-X2 | 1756-IB32-31 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
789 | C4 | 4 | 0 | C4S04,00 | C4S04-X1 | 1756-OB32-0 | DO | 24 VDC energized | SV-60220_DO_1 | SV-60220 | PA On/Off Valve for Chamber PSE purge air (CHAM-21) | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-602-PD-04 | JB-606 | =CA1+MCP-M4 | ACTIVE
790 | C4 | 4 | 1 | C4S04,01 | C4S04-X1 | 1756-OB32-1 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
791 | C4 | 4 | 2 | C4S04,02 | C4S04-X1 | 1756-OB32-2 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
792 | C4 | 4 | 3 | C4S04,03 | C4S04-X1 | 1756-OB32-3 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
793 | C4 | 4 | 4 | C4S04,04 | C4S04-X1 | 1756-OB32-4 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
794 | C4 | 4 | 5 | C4S04,05 | C4S04-X1 | 1756-OB32-5 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
795 | C4 | 4 | 6 | C4S04,06 | C4S04-X1 | 1756-OB32-6 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
796 | C4 | 4 | 7 | C4S04,07 | C4S04-X1 | 1756-OB32-7 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-606 | =CA1+MCP-M4 | SPARE
797 | C4 | 4 | 8 | C4S04,08 | C4S04-X1 | 1756-OB32-8 | DO | 4 - 20 mA | XA-60201_DO_1 | XA-60201 | LEL gas Buzzer Alarm | Industrial Process Equipment | Standard Process Field Device | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-03 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
798 | C4 | 4 | 9 | C4S04,09 | C4S04-X1 | 1756-OB32-9 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
799 | C4 | 4 | 10 | C4S04,10 | C4S04-X1 | 1756-OB32-10 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
800 | C4 | 4 | 11 | C4S04,11 | C4S04-X1 | 1756-OB32-11 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
801 | C4 | 4 | 12 | C4S04,12 | C4S04-X1 | 1756-OB32-12 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
802 | C4 | 4 | 13 | C4S04,13 | C4S04-X1 | 1756-OB32-13 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
803 | C4 | 4 | 14 | C4S04,14 | C4S04-X1 | 1756-OB32-14 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
804 | C4 | 4 | 15 | C4S04,15 | C4S04-X1 | 1756-OB32-15 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
805 | C4 | 4 | 16 | C4S04,16 | C4S04-X2 | 1756-OB32-16 | DO | - | PVM-61301_DO_1 | PVM-61301 | Start / Stop Command for FVNR PV-61301 (Vacuum Cleaning Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-03 | JB-612 | =CA1+MCP-M4 | ACTIVE
806 | C4 | 4 | 17 | C4S04,17 | C4S04-X2 | 1756-OB32-17 | DO | - | PVM-61301_DO_2 | PVM-61301 | Start / Stop Command for FVNR PV-61301 (Vacuum Cleaning Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-03 | JB-612 | =CA1+MCP-M4 | ACTIVE
807 | C4 | 4 | 18 | C4S04,18 | C4S04-X2 | 1756-OB32-18 | DO | - | SV-61307_DO_1 | SV-61307 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 3-25-01-613-PD-01 | JB-612 | =CA1+MCP-M4 | ACTIVE
808 | C4 | 4 | 19 | C4S04,19 | C4S04-X2 | 1756-OB32-19 | DO | 24 VDC energized | SV-61308_DO_1 | SV-61308 | Timer compress air pluse solenoid valve | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-613-PD-03 | JB-612 | =CA1+MCP-M4 | ACTIVE
809 | C4 | 4 | 20 | C4S04,20 | C4S04-X2 | 1756-OB32-20 | DO | 24 VDC energized | SV-61309_DO_1 | SV-61309 | Air service | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-613-PD-03 | JB-612 | =CA1+MCP-M4 | ACTIVE
810 | C4 | 4 | 21 | C4S04,21 | C4S04-X2 | 1756-OB32-21 | DO | 24 VDC energized | SV-61310_DO_1 | SV-61310 | Timer compress air pluse solenoid valve | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-613-PD-05 | JB-612 | =CA1+MCP-M4 | ACTIVE
811 | C4 | 4 | 22 | C4S04,22 | C4S04-X2 | 1756-OB32-22 | DO | 24 VDC energized | SV-61311_DO_1 | SV-61311 | Air service | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 2Cx1) | 325-01-613-PD-05 | JB-612 | =CA1+MCP-M4 | ACTIVE
812 | C4 | 4 | 23 | C4S04,23 | C4S04-X2 | 1756-OB32-23 | DO | 24 VDC energized | XS-61301A_DO_1 | XS-61301A | Filter plant in operation | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
813 | C4 | 4 | 24 | C4S04,24 | C4S04-X2 | 1756-OB32-24 | DO | 24 VDC energized | XS-61301B_DO_1 | XS-61301B | Material transport in operation | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
814 | C4 | 4 | 25 | C4S04,25 | C4S04-X2 | 1756-OB32-25 | DO | 24 VDC energized | XS-61301C_DO_1 | XS-61301C | Belt plant in operation | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
815 | C4 | 4 | 26 | C4S04,26 | C4S04-X2 | 1756-OB32-26 | DO | 24 VDC energized | XS-61301D_DO_1 | XS-61301D | Sequence Stop | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
816 | C4 | 4 | 27 | C4S04,27 | C4S04-X2 | 1756-OB32-27 | DO | 24 VDC energized | XS-61301E_DO_1 | XS-61301E | Status from Customer Emergency stop | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
817 | C4 | 4 | 28 | C4S04,28 | C4S04-X2 | 1756-OB32-28 | DO | 24 VDC energized | XS-61301F_DO_1 | XS-61301F | Operation Release | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
818 | C4 | 4 | 29 | C4S04,29 | C4S04-X2 | 1756-OB32-29 | DO | 24 VDC energized | XV-61302_DO_1 | XV-61302 | Dust collector feed vent | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
819 | C4 | 4 | 30 | C4S04,30 | C4S04-X2 | 1756-OB32-30 | DO | 24 VDC energized | XV-61303_DO_1 | XV-61303 | Dust collector feed from packer | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-613-PD-02 | JB-612 | =CA1+MCP-M4 | ACTIVE
820 | C4 | 4 | 31 | C4S04,31 | C4S04-X2 | 1756-OB32-31 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
821 | C4 | 5 | 0 | C4S05,00 | C4S05-X1 | 1756-IF16-0 | AI | 4 - 20 mA | DPT-60201_AI_1 | DPT-60201 | Steam filter pressure | Endress+Hauser | Deltabar PMD55B (Diff. Pressure Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-09 | JB-606 | =CA1+MCP-M4 | ACTIVE
822 | C4 | 5 | 1 | C4S05,01 | C4S05-X1 | 1756-IF16-1 | AI | 4 - 20 mA | FT-60203_AI_1 | FT-60203 | Culinary steam feed to Spray dryer | Endress+Hauser | Prowirl F 200 (Vortex Flowmeter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 2P x1.0) | 325-01-602-PD-09 | JB-606 | =CA1+MCP-M4 | ACTIVE
823 | C4 | 5 | 2 | C4S05,02 | C4S05-X1 | 1756-IF16-2 | AI | 4 - 20 mA | TT-60245_AI_1 | TT-60245 | Gas Temperature Transmitter for Exhaust Stack (DTXS-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-05 | JB-608 | =CA1+MCP-M4 | ACTIVE
824 | C4 | 5 | 3 | C4S05,03 | C4S05-X1 | 1756-IF16-3 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-608 | =CA1+MCP-M4 | SPARE
825 | C4 | 5 | 4 | C4S05,04 | C4S05-X1 | 1756-IF16-4 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-608 | =CA1+MCP-M4 | SPARE
826 | C4 | 5 | 5 | C4S05,05 | C4S05-X1 | 1756-IF16-5 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-608 | =CA1+MCP-M4 | SPARE
827 | C4 | 5 | 6 | C4S05,06 | C4S05-X1 | 1756-IF16-6 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-608 | =CA1+MCP-M4 | SPARE
828 | C4 | 5 | 6 | C4S05,06 | C4S05-X1 | 1756-IF16-6 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
829 | C4 | 5 | 7 | C4S05,07 | C4S05-X1 | 1756-IF16-7 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-608 | =CA1+MCP-M4 | SPARE
830 | C4 | 5 | 7 | C4S05,07 | C4S05-X1 | 1756-IF16-7 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-608 | =CA1+MCP-M4 | SPARE
831 | C4 | 5 | 8 | C4S05,08 | C4S05-X1 | 1756-IF16-8 | AI | 4 - 20 mA | PT-61302_AI_1 | PT-61302 | Pressure in vacuum line | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-03 | JB-612 | =CA1+MCP-M4 | ACTIVE
832 | C4 | 5 | 9 | C4S05,09 | C4S05-X1 | 1756-IF16-9 | AI | 4 - 20 mA | PT-61309_AI_1 | PT-61309 | Pressure transmitter | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-04 | JB-612 | =CA1+MCP-M4 | ACTIVE
833 | C4 | 5 | 10 | C4S05,10 | C4S05-X1 | 1756-IF16-10 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
834 | C4 | 5 | 11 | C4S05,11 | C4S05-X1 | 1756-IF16-11 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
835 | C4 | 5 | 12 | C4S05,12 | C4S05-X1 | 1756-IF16-12 | AI | 4 - 20 mA | PT-61302_AI_1 | PT-61302 | Pressure in vacuum line | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-03 | JB-612 | =CA1+MCP-M4 | ACTIVE
836 | C4 | 5 | 13 | C4S05,13 | C4S05-X1 | 1756-IF16-13 | AI | 4 - 20 mA | PT-61309_AI_1 | PT-61309 | Pressure transmitter | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-04 | JB-612 | =CA1+MCP-M4 | ACTIVE
837 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
838 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
839 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
840 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
841 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
842 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
843 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
844 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
845 | C4 | 5 | 14 | C4S05,14 | C4S05-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | IS-JB-612 | =CA1+MCP-M4 | SPARE
846 | C4 | 5 | 15 | C4S05,15 | C4S05-X1 | 1756-IF16-15 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | JB-612 | =CA1+MCP-M4 | SPARE
847 | C4 | 6 | 0 | C4S06,00 | C4S06-X1 | 1756-IF16-0 | AI | 4 - 20 mA | PT-60220_AI_1 | PT-60220 | Gas Pressure Transmitter for Chamber (CHAM-21) | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
848 | C4 | 6 | 1 | C4S06,01 | C4S06-X1 | 1756-IF16-1 | AI | 4 - 20 mA | TT-60220_AI_1 | TT-60220 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
849 | C4 | 6 | 2 | C4S06,02 | C4S06-X1 | 1756-IF16-2 | AI | 4 - 20 mA | TT-60221_AI_1 | TT-60221 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
850 | C4 | 6 | 3 | C4S06,03 | C4S06-X1 | 1756-IF16-3 | AI | 4 - 20 mA | TT-60222_AI_1 | TT-60222 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
851 | C4 | 6 | 4 | C4S06,04 | C4S06-X1 | 1756-IF16-4 | AI | 4 - 20 mA | TT-60223_AI_1 | TT-60223 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD Transmitter) | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-602-PD-04 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
852 | C4 | 6 | 5 | C4S06,05 | C4S06-X1 | 1756-IF16-5 | AI | 4 - 20 mA | XT-60201_AI_1 | XT-60201 | LEL gas analyzer | Industrial Process Equipment | Standard Process Field Device | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-402-PD-03 | IS-JB-608 | =CA1+MCP-M4 | ACTIVE
853 | C4 | 6 | 6 | C4S06,06 | C4S06-X1 | 1756-IF16-6 | AI | 4 - 20 mA | DPT-61310_AI_1 | DPT-61310 | Vent filter pressure | Endress+Hauser | Deltabar PMD55B (Diff. Pressure Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-03 | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
854 | C4 | 6 | 7 | C4S06,07 | C4S06-X1 | 1756-IF16-7 | AI | - | DPT-61312_AI_1 | DPT-61312 | Vent filter pressure | Endress+Hauser | Deltabar PMD55B (Diff. Pressure Transmitter) | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-613-PD-05 | IS-JB-612 | =CA1+MCP-M4 | ACTIVE
855 | C5 | 1 | 0 | C5S01,00 | C5S01-X1 | 1756-IB32-0 | DI | - | FS-20201_DI_1 | FS-20201 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 3-25-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
856 | C5 | 1 | 1 | C5S01,01 | C5S01-X1 | 1756-IB32-1 | DI | 4 - 20 mA,Pulse | FT-913201_DI_1 | FT-913201 | Flow outlet LPG line | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 325-01-913-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
857 | C5 | 1 | 2 | C5S01,02 | C5S01-X1 | 1756-IB32-2 | DI | 4 - 20 mA,Pulse | FT-936201_DI_1 | FT-936201 | Process Water | Endress+Hauser | Promag P 300 (Electromagnetic Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-930-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
858 | C5 | 1 | 3 | C5S01,03 | C5S01-X1 | 1756-IB32-3 | DI | 4 - 20 mA,Pulse | FT-936202_DI_1 | FT-936202 | Process Water | Endress+Hauser | Promag P 300 (Electromagnetic Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-930-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
859 | C5 | 1 | 4 | C5S01,04 | C5S01-X1 | 1756-IB32-4 | DI | Dry Contact | LSL-814201_DI_1 | LSL-814201 | Low Level alarm | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork for Liquids) | CVV 3Cx1.5 (Ref: CVV 3Cx1.5 , CVV 4Cx1) | 325-01-814-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
860 | C5 | 1 | 5 | C5S01,05 | C5S01-X1 | 1756-IB32-5 | DI | - | PK-913201_DI_1 | PK-913201 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | - | RIO-200 | =CA1+MCP-M5 | ACTIVE
861 | C5 | 1 | 6 | C5S01,06 | C5S01-X1 | 1756-IB32-6 | DI | - | PK-913202_DI_1 | PK-913202 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | - | RIO-200 | =CA1+MCP-M5 | ACTIVE
862 | C5 | 1 | 7 | C5S01,07 | C5S01-X1 | 1756-IB32-7 | DI | Dry Contact | HV-20204_DI_1 | HV-20204 | Slurry Drain line | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
863 | C5 | 1 | 8 | C5S01,08 | C5S01-X1 | 1756-IB32-8 | DI | Dry Contact | HV-20205_DI_1 | HV-20205 | Slurry Drain line | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
864 | C5 | 1 | 9 | C5S01,09 | C5S01-X1 | 1756-IB32-9 | DI | Dry Contact | HV-20206_DI_1 | HV-20206 | Slurry Drain line | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
865 | C5 | 1 | 10 | C5S01,10 | C5S01-X1 | 1756-IB32-10 | DI | Dry Contact | HV-20207_DI_1 | HV-20207 | Slurry Drain line | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
866 | C5 | 1 | 11 | C5S01,11 | C5S01-X1 | 1756-IB32-11 | DI | Dry Contact | HV-20208_DI_1 | HV-20208 | Slurry Drain line | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-202-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
867 | C5 | 1 | 12 | C5S01,12 | C5S01-X1 | 1756-IB32-12 | DI | Dry Contact | HV-20209_DI_1 | HV-20209 | Slurry Drain line | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-202-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
868 | C5 | 1 | 13 | C5S01,13 | C5S01-X1 | 1756-IB32-13 | DI | Dry Contact | HV-20210_DI_1 | HV-20210 | Slurry Drain line | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N/510N Switch Box | CVV 4Cx1.0 (Ref: CVV 4Cx1) | 325-01-202-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
869 | C5 | 1 | 14 | C5S01,14 | C5S01-X1 | 1756-IB32-14 | DI | Dry Contact | XA-80305A_DI_1 | XA-80305A | Gas Vaporizer 5 control status | Industrial Process Equipment | Standard Process Field Device | CVV 16Cx1.5 | 325-01-803-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
870 | C5 | 1 | 15 | C5S01,15 | C5S01-X1 | 1756-IB32-15 | DI | Dry Contact | XA-80305B_DI_1 | XA-80305B | Gas Vaporizer 5 control status | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-803-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
871 | C5 | 1 | 16 | C5S01,16 | C5S01-X2 | 1756-IB32-16 | DI | Dry Contact | XA-80305C_DI_1 | XA-80305C | Gas Vaporizer 5 control status | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-803-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
872 | C5 | 1 | 17 | C5S01,17 | C5S01-X2 | 1756-IB32-17 | DI | Dry Contact | XA-80305D_DI_1 | XA-80305D | Gas Vaporizer 5 control status | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-803-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
873 | C5 | 1 | 18 | C5S01,18 | C5S01-X2 | 1756-IB32-18 | DI | Dry Contact | XA-80305E_DI_1 | XA-80305E | Gas Vaporizer 5 control status | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-803-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
874 | C5 | 1 | 19 | C5S01,19 | C5S01-X2 | 1756-IB32-19 | DI | Dry Contact | XA-80305F_DI_1 | XA-80305F | Gas Vaporizer 5 control status | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-803-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
875 | C5 | 1 | 20 | C5S01,20 | C5S01-X2 | 1756-IB32-20 | DI | Dry Contact | XA-80306A_DI_1 | XA-80306A | Gas Vaporizer 6 control status | Industrial Process Equipment | Standard Process Field Device | CVV 16Cx1.5 | 325-01-803-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
876 | C5 | 1 | 21 | C5S01,21 | C5S01-X2 | 1756-IB32-21 | DI | Dry Contact | XA-80306B_DI_1 | XA-80306B | Gas Vaporizer 6 control status | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-803-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
877 | C5 | 1 | 22 | C5S01,22 | C5S01-X2 | 1756-IB32-22 | DI | Dry Contact | XA-80306C_DI_1 | XA-80306C | Gas Vaporizer 6 control status | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-803-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
878 | C5 | 1 | 23 | C5S01,23 | C5S01-X2 | 1756-IB32-23 | DI | Dry Contact | XA-80306D_DI_1 | XA-80306D | Gas Vaporizer 6 control status | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-803-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
879 | C5 | 1 | 24 | C5S01,24 | C5S01-X2 | 1756-IB32-24 | DI | Dry Contact | XA-80306E_DI_1 | XA-80306E | Gas Vaporizer 6 control status | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-803-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
880 | C5 | 1 | 25 | C5S01,25 | C5S01-X2 | 1756-IB32-25 | DI | Dry Contact | XA-80306F_DI_1 | XA-80306F | Gas Vaporizer 6 control status | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-803-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
881 | C5 | 1 | 26 | C5S01,26 | C5S01-X2 | 1756-IB32-26 | DI | 24 VDC energized | XV-20201_DI_1 | XV-20201 | Slurry Preparation Tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
882 | C5 | 1 | 27 | C5S01,27 | C5S01-X2 | 1756-IB32-27 | DI | 24 VDC energized | XV-20201_DI_2 | XV-20201 | Slurry Preparation Tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
883 | C5 | 1 | 28 | C5S01,28 | C5S01-X2 | 1756-IB32-28 | DI | 24 VDC energized | XV-20202_DI_1 | XV-20202 | Slurry Preparation Tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
884 | C5 | 1 | 29 | C5S01,29 | C5S01-X2 | 1756-IB32-29 | DI | 24 VDC energized | XV-20202_DI_2 | XV-20202 | Slurry Preparation Tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
885 | C5 | 1 | 30 | C5S01,30 | C5S01-X2 | 1756-IB32-30 | DI | 24 VDC energized | XV-20203_DI_1 | XV-20203 | Slurry Preparation Tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
886 | C5 | 1 | 31 | C5S01,31 | C5S01-X2 | 1756-IB32-31 | DI | 24 VDC energized | XV-20203_DI_2 | XV-20203 | Slurry Preparation Tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
887 | C5 | 2 | 0 | C5S02,00 | C5S02-X1 | 1756-IB32-0 | DI | 24 VDC energized | XV-20211_DI_1 | XV-20211 | Slurry Preparation Tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
888 | C5 | 2 | 1 | C5S02,01 | C5S02-X1 | 1756-IB32-1 | DI | 24 VDC energized | XV-20211_DI_2 | XV-20211 | Slurry Preparation Tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
889 | C5 | 2 | 2 | C5S02,02 | C5S02-X1 | 1756-IB32-2 | DI | 24 VDC energized | XV-20212_DI_1 | XV-20212 | Slurry Preparation Tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
890 | C5 | 2 | 3 | C5S02,03 | C5S02-X1 | 1756-IB32-3 | DI | 24 VDC energized | XV-20212_DI_2 | XV-20212 | Slurry Preparation Tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
891 | C5 | 2 | 4 | C5S02,04 | C5S02-X1 | 1756-IB32-4 | DI | 24 VDC energized | XV-20213_DI_1 | XV-20213 | Slurry Preparation Tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
892 | C5 | 2 | 5 | C5S02,05 | C5S02-X1 | 1756-IB32-5 | DI | 24 VDC energized | XV-20213_DI_2 | XV-20213 | Slurry Preparation Tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
893 | C5 | 2 | 6 | C5S02,06 | C5S02-X1 | 1756-IB32-6 | DI | 24 VDC energized | XV-913201_DI_1 | XV-913201 | Outlet LPG line | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-913-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
894 | C5 | 2 | 7 | C5S02,07 | C5S02-X1 | 1756-IB32-7 | DI | 24 VDC energized | XV-913201_DI_1 | XV-913201 | Outlet LPG line | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-913-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
895 | C5 | 2 | 8 | C5S02,08 | C5S02-X1 | 1756-IB32-8 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
896 | C5 | 2 | 9 | C5S02,09 | C5S02-X1 | 1756-IB32-9 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
897 | C5 | 2 | 10 | C5S02,10 | C5S02-X1 | 1756-IB32-10 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
898 | C5 | 2 | 11 | C5S02,11 | C5S02-X1 | 1756-IB32-11 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
899 | C5 | 2 | 12 | C5S02,12 | C5S02-X1 | 1756-IB32-12 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
900 | C5 | 2 | 13 | C5S02,13 | C5S02-X1 | 1756-IB32-13 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
901 | C5 | 2 | 14 | C5S02,14 | C5S02-X1 | 1756-IB32-14 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
902 | C5 | 2 | 15 | C5S02,15 | C5S02-X1 | 1756-IB32-15 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
903 | C5 | 2 | 16 | C5S02,16 | C5S02-X2 | 1756-IB32-16 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
904 | C5 | 2 | 17 | C5S02,17 | C5S02-X2 | 1756-IB32-17 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
905 | C5 | 2 | 18 | C5S02,18 | C5S02-X2 | 1756-IB32-18 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
906 | C5 | 2 | 19 | C5S02,19 | C5S02-X2 | 1756-IB32-19 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
907 | C5 | 2 | 20 | C5S02,20 | C5S02-X2 | 1756-IB32-20 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
908 | C5 | 2 | 21 | C5S02,21 | C5S02-X2 | 1756-IB32-21 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
909 | C5 | 2 | 22 | C5S02,22 | C5S02-X2 | 1756-IB32-22 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
910 | C5 | 2 | 23 | C5S02,23 | C5S02-X2 | 1756-IB32-23 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
911 | C5 | 2 | 24 | C5S02,24 | C5S02-X2 | 1756-IB32-24 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
912 | C5 | 2 | 25 | C5S02,25 | C5S02-X2 | 1756-IB32-25 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
913 | C5 | 2 | 26 | C5S02,26 | C5S02-X2 | 1756-IB32-26 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
914 | C5 | 2 | 27 | C5S02,27 | C5S02-X2 | 1756-IB32-27 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
915 | C5 | 2 | 28 | C5S02,28 | C5S02-X2 | 1756-IB32-28 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
916 | C5 | 2 | 29 | C5S02,29 | C5S02-X2 | 1756-IB32-29 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
917 | C5 | 2 | 30 | C5S02,30 | C5S02-X2 | 1756-IB32-30 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
918 | C5 | 2 | 31 | C5S02,31 | C5S02-X2 | 1756-IB32-31 | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
919 | C5 | 3 | 0 | C5S03,00 | C5S03-X1 | 1756-OB32-0 | DO | 4 - 20 mA | XA-92201_DO_1 | XA-92201 | LEL gas Buzzer Alarm | Industrial Process Equipment | Standard Process Field Device | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-923-PD-03 | RIO-200 | =CA1+MCP-M5 | ACTIVE
920 | C5 | 3 | 1 | C5S03,01 | C5S03-X1 | 1756-OB32-1 | DO | 24 VDC energized | XV-20201_DO_1 | XV-20201 | Slurry Preparation Tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
921 | C5 | 3 | 2 | C5S03,02 | C5S03-X1 | 1756-OB32-2 | DO | 24 VDC energized | XV-20202_DO_1 | XV-20202 | Slurry Preparation Tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
922 | C5 | 3 | 3 | C5S03,03 | C5S03-X1 | 1756-OB32-3 | DO | 24 VDC energized | XV-20203_DO_1 | XV-20203 | Slurry Preparation Tank 1 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
923 | C5 | 3 | 4 | C5S03,04 | C5S03-X1 | 1756-OB32-4 | DO | 24 VDC energized | XV-20211_DO_1 | XV-20211 | Slurry Preparation Tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
924 | C5 | 3 | 5 | C5S03,05 | C5S03-X1 | 1756-OB32-5 | DO | 24 VDC energized | XV-20212_DO_1 | XV-20212 | Slurry Preparation Tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
925 | C5 | 3 | 6 | C5S03,06 | C5S03-X1 | 1756-OB32-6 | DO | 24 VDC energized | XV-20213_DO_1 | XV-20213 | Slurry Preparation Tank 2 | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-202-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
926 | C5 | 3 | 7 | C5S03,07 | C5S03-X1 | 1756-OB32-7 | DO | 24 VDC energized | XV-913201_DO_1 | XV-913201 | Outlet LPG line | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-913-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
927 | C5 | 3 | 8 | C5S03,08 | C5S03-X1 | 1756-OB32-8 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
928 | C5 | 3 | 9 | C5S03,09 | C5S03-X1 | 1756-OB32-9 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
929 | C5 | 3 | 10 | C5S03,10 | C5S03-X1 | 1756-OB32-10 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
930 | C5 | 3 | 11 | C5S03,11 | C5S03-X1 | 1756-OB32-11 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
931 | C5 | 3 | 12 | C5S03,12 | C5S03-X1 | 1756-OB32-12 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
932 | C5 | 3 | 13 | C5S03,13 | C5S03-X1 | 1756-OB32-13 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
933 | C5 | 3 | 14 | C5S03,14 | C5S03-X1 | 1756-OB32-14 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
934 | C5 | 3 | 15 | C5S03,15 | C5S03-X1 | 1756-OB32-15 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
935 | C5 | 3 | 16 | C5S03,16 | C5S03-X2 | 1756-OB32-16 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
936 | C5 | 3 | 17 | C5S03,17 | C5S03-X2 | 1756-OB32-17 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
937 | C5 | 3 | 18 | C5S03,18 | C5S03-X2 | 1756-OB32-18 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
938 | C5 | 3 | 19 | C5S03,19 | C5S03-X2 | 1756-OB32-19 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
939 | C5 | 3 | 20 | C5S03,20 | C5S03-X2 | 1756-OB32-20 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
940 | C5 | 3 | 21 | C5S03,21 | C5S03-X2 | 1756-OB32-21 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
941 | C5 | 3 | 22 | C5S03,22 | C5S03-X2 | 1756-OB32-22 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
942 | C5 | 3 | 23 | C5S03,23 | C5S03-X2 | 1756-OB32-23 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
943 | C5 | 3 | 24 | C5S03,24 | C5S03-X2 | 1756-OB32-24 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
944 | C5 | 3 | 25 | C5S03,25 | C5S03-X2 | 1756-OB32-25 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
945 | C5 | 3 | 26 | C5S03,26 | C5S03-X2 | 1756-OB32-26 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
946 | C5 | 3 | 27 | C5S03,27 | C5S03-X2 | 1756-OB32-27 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
947 | C5 | 3 | 28 | C5S03,28 | C5S03-X2 | 1756-OB32-28 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
948 | C5 | 3 | 29 | C5S03,29 | C5S03-X2 | 1756-OB32-29 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
949 | C5 | 3 | 30 | C5S03,30 | C5S03-X2 | 1756-OB32-30 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
950 | C5 | 3 | 31 | C5S03,31 | C5S03-X2 | 1756-OB32-31 | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
951 | C5 | 4 | 0 | C5S04,00 | C5S04-X1 | 1756-IF16-0 | AI | - | EXT-BIILER_AI_1 | EXT-BIILER | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | External Remote Setpoint | RIO-200 | =CA1+MCP-M5 | ACTIVE
952 | C5 | 4 | 1 | C5S04,01 | C5S04-X1 | 1756-IF16-1 | AI | 4 - 20 mA,Pulse | FT-913201_AI_1 | FT-913201 | Flow outlet LPG line | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 325-01-913-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
953 | C5 | 4 | 2 | C5S04,02 | C5S04-X1 | 1756-IF16-2 | AI | 4 - 20 mA,Pulse | FT-913201_AI_2 | FT-913201 | Flow outlet LPG line | Endress+Hauser | Promass E 300 (Coriolis Mass Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 3Px1.0 , CVV 3Cx1.5) | 325-01-913-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
954 | C5 | 4 | 3 | C5S04,03 | C5S04-X1 | 1756-IF16-3 | AI | 4 - 20 mA,Pulse | FT-936201_AI_1 | FT-936201 | Process Water | Endress+Hauser | Promag P 300 (Electromagnetic Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-930-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
955 | C5 | 4 | 4 | C5S04,04 | C5S04-X1 | 1756-IF16-4 | AI | 4 - 20 mA,Pulse | FT-936202_AI_1 | FT-936202 | Process Water | Endress+Hauser | Promag P 300 (Electromagnetic Flowmeter) | LiY-CY TP 3Px1.0 (Mass Flow, Density, Status) + CVV 3Cx1.5 (Power) (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-930-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
956 | C5 | 4 | 5 | C5S04,05 | C5S04-X1 | 1756-IF16-5 | AI | 4 - 20 mA | LT-913201_AI_1 | LT-913201 | Level LPG in storage | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic Level) | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-913-PD-01 | RIO-200 | =CA1+MCP-M5 | ACTIVE
957 | C5 | 4 | 6 | C5S04,06 | C5S04-X1 | 1756-IF16-6 | AI | 4 - 20 mA | PT-913201_AI_1 | PT-913201 | Pressure outlet LPG line | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | LiY-CY TP 1Px1.0 (Ref: LiY-CY TP 1P x1.0) | 325-01-913-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
958 | C5 | 4 | 7 | C5S04,07 | C5S04-X1 | 1756-IF16-7 | AI | 4 - 20 mA | XT-92201_AI_1 | XT-92201 | LEL gas analyzer | Industrial Process Equipment | Standard Process Field Device | LiY-CY(EB) 1Px1.0 (Ref: LiY-CY TP 2Px1.0 , CVV 3Cx1.5) | 325-01-923-PD-03 | RIO-200 | =CA1+MCP-M5 | ACTIVE
959 | C5 | 4 | 8 | C5S04,08 | C5S04-X1 | 1756-IF16-8 | AI | 24 VDC energized | XV-913201_AI_1 | XV-913201 | Outlet LPG line | TeroFox / El-O-Matic / Power-Genex | TF-20DFS Valve + F-Series Actuator + ESV Solenoid | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) or CVV 5Cx1.5 (Ref: CVV 3Cx1 / CVV 4Cx1) | 325-01-913-PD-02 | RIO-200 | =CA1+MCP-M5 | ACTIVE
960 | C5 | 4 | 9 | C5S04,09 | C5S04-X1 | 1756-IF16-9 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-913-PD-02 | RIO-200 | =CA1+MCP-M5 | SPARE
961 | C5 | 4 | 10 | C5S04,10 | C5S04-X1 | 1756-IF16-10 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-913-PD-02 | RIO-200 | =CA1+MCP-M5 | SPARE
962 | C5 | 4 | 11 | C5S04,11 | C5S04-X1 | 1756-IF16-11 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-913-PD-02 | RIO-200 | =CA1+MCP-M5 | SPARE
963 | C5 | 4 | 12 | C5S04,12 | C5S04-X1 | 1756-IF16-12 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-913-PD-02 | RIO-200 | =CA1+MCP-M5 | SPARE
964 | C5 | 4 | 13 | C5S04,13 | C5S04-X1 | 1756-IF16-13 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-913-PD-02 | RIO-200 | =CA1+MCP-M5 | SPARE
965 | C5 | 4 | 14 | C5S04,14 | C5S04-X1 | 1756-IF16-14 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
966 | C5 | 4 | 15 | C5S04,15 | C5S04-X1 | 1756-IF16-15 | AI | - | Spare_AI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | RIO-200 | =CA1+MCP-M5 | SPARE
967 | C6 | 5 | 0 | C6S05,00 | C6S05- | - | DO | - | PCM-2030_DO_1 | PCM-2030 | Start / Stop Command for FVNR PC-2030 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC 200 PANEL) | 325-01-202-PD-01 | MCC | MCC | ACTIVE
968 | C6 | 5 | 1 | C6S05,01 | C6S05- | - | DO | - | PCM-2030_DO_2 | PCM-2030 | Start / Stop Command for FVNR PC-2030 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC 200 PANEL) | 325-01-202-PD-01 | MCC | MCC | ACTIVE
969 | C6 | 5 | 2 | C6S05,02 | C6S05- | - | DO | 24 VDC energized | PCM-2031_DO_1 | PCM-2031 | Start / Stop Command for FVNR PC-2031 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-202-PD-01 | MCC | MCC | ACTIVE
970 | C6 | 5 | 3 | C6S05,03 | C6S05- | - | DO | 24 VDC energized | PCM-2031_DO_2 | PCM-2031 | Start / Stop Command for FVNR PC-2031 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-202-PD-01 | MCC | MCC | ACTIVE
971 | C6 | 5 | 4 | C6S05,04 | C6S05- | - | DO | 24 VDC energized | PCY-814201_DO_1 | PCY-814201 | Start / Stop Command to VSD PC-81001 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC 810 PANEL) | 325-01-814-PD-01 | MCC | MCC | ACTIVE
972 | C6 | 5 | 5 | C6S05,05 | C6S05- | - | DO | 24 VDC energized | PCY-814202_DO_1 | PCY-814202 | Start / Stop Command to VSD PC-81002 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-814-PD-01 | MCC | MCC | ACTIVE
973 | C6 | 5 | 6 | C6S05,06 | C6S05- | - | DO | 24 VDC energized | XS-80305_DO_1 | XS-80305 | Start / Stop Command for Gas Vaporizer 5 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-803-PD-02 | MCC | MCC | ACTIVE
974 | C6 | 5 | 7 | C6S05,07 | C6S05- | - | DO | 24 VDC energized | XS-80306_DO_1 | XS-80306 | Start / Stop Command for Gas Vaporizer 6 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-803-PD-02 | MCC | MCC | ACTIVE
975 | C6 | 6 | 0 | C6S06,00 | C6S06- | - | DI | - | PCM-2030_DI_1 | PCM-2030 | Start / Stop Command for FVNR PC-2030 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC 200 PANEL) | 325-01-202-PD-01 | MCC | MCC | ACTIVE
976 | C6 | 6 | 1 | C6S06,01 | C6S06- | - | DI | - | PCM-2030_DI_2 | PCM-2030 | Start / Stop Command for FVNR PC-2030 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC 200 PANEL) | 325-01-202-PD-01 | MCC | MCC | ACTIVE
977 | C6 | 6 | 2 | C6S06,02 | C6S06- | - | DI | 24 VDC energized | PCM-2031_DI_1 | PCM-2031 | Start / Stop Command for FVNR PC-2031 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-202-PD-01 | MCC | MCC | ACTIVE
978 | C6 | 6 | 3 | C6S06,03 | C6S06- | - | DI | 24 VDC energized | PCM-2031_DI_2 | PCM-2031 | Start / Stop Command for FVNR PC-2031 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-202-PD-01 | MCC | MCC | ACTIVE
979 | C6 | 6 | 4 | C6S06,04 | C6S06- | - | DI | 24 VDC energized | PCY-814201_DI_1 | PCY-814201 | Start / Stop Command to VSD PC-81001 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC 810 PANEL) | 325-01-814-PD-01 | MCC | MCC | ACTIVE
980 | C6 | 6 | 5 | C6S06,05 | C6S06- | - | DI | 24 VDC energized | PCY-814201_DI_2 | PCY-814201 | Start / Stop Command to VSD PC-81001 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC 810 PANEL) | 325-01-814-PD-01 | MCC | MCC | ACTIVE
981 | C6 | 6 | 6 | C6S06,06 | C6S06- | - | DI | 24 VDC energized | PCY-814201_DI_3 | PCY-814201 | Start / Stop Command to VSD PC-81001 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC 810 PANEL) | 325-01-814-PD-01 | MCC | MCC | ACTIVE
982 | C6 | 6 | 7 | C6S06,07 | C6S06- | - | DI | 24 VDC energized | PCY-814202_DI_1 | PCY-814202 | Start / Stop Command to VSD PC-81002 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-814-PD-01 | MCC | MCC | ACTIVE
983 | C6 | 6 | 8 | C6S06,08 | C6S06- | - | DI | 24 VDC energized | PCY-814202_DI_2 | PCY-814202 | Start / Stop Command to VSD PC-81002 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-814-PD-01 | MCC | MCC | ACTIVE
984 | C6 | 6 | 9 | C6S06,09 | C6S06- | - | DI | 24 VDC energized | PCY-814202_DI_3 | PCY-814202 | Start / Stop Command to VSD PC-81002 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-814-PD-01 | MCC | MCC | ACTIVE
985 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | ATY-40201_BUS_1 | ATY-40201 | Start / Stop Command for VSD AT-40201 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC PANEL) | 325-01-402-PD-01 | MCC | MCC | ACTIVE
986 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | ATY-40202_BUS_1 | ATY-40202 | Start / Stop Command for VSD AT-40202 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
987 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | ATY-40203_BUS_1 | ATY-40203 | Start / Stop Command for VSD AT-40203 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-02 | MCC | MCC | ACTIVE
988 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60206_BUS_1 | BFY-60206 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
989 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60210_BUS_1 | BFY-60210 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-03 | MCC | MCC | ACTIVE
990 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60211_BUS_1 | BFY-60211 | Start / Stop Command for VSD FANC-21 (Combustion Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-03 | MCC | MCC | ACTIVE
991 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60220_BUS_1 | BFY-60220 | Start / Stop Command for VSD FANS-22 (Cooling Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-04 | MCC | MCC | ACTIVE
992 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-60240_BUS_1 | BFY-60240 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-05 | MCC | MCC | ACTIVE
993 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-61301_BUS_1 | BFY-61301 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
994 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-61302_BUS_1 | BFY-61302 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-05 | MCC | MCC | ACTIVE
995 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | BFY-61303_BUS_1 | BFY-61303 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
996 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | COM-FH-60210B_BUS_1 | COM-FH-60210B | Communication Signal | Industrial Process Equipment | Standard Process Field Device | CAT 6 S/FTP Industrial Ethernet Cable / Belden 3105A RS-485 (Ref: CAT 5e) | 325-01-602-PD-06 | JB-607 | MCC | ACTIVE
997 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | Communication Signal_BUS_1 | Communication Signal | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-613-PD-02 | JB-612 | MCC | ACTIVE
998 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-40201_BUS_1 | PCY-40201 | Start / Stop Command for VSD PC-40201 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
999 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-40202_BUS_1 | PCY-40202 | Start / Stop Command for VSD PC-40202 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1000 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-40203_BUS_1 | PCY-40203 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-02 | MCC | MCC | ACTIVE
1001 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-60205_BUS_1 | PCY-60205 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | JB-601 | MCC | ACTIVE
1002 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-60215_BUS_1 | PCY-60215 | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-03 | MCC | MCC | ACTIVE
1003 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-814201_BUS_1 | PCY-814201 | Start / Stop Command to VSD PC-81001 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC 810 PANEL) | 325-01-814-PD-01 | MCC | MCC | ACTIVE
1004 | C7 | 0 | 0 | C7S00,00 | C7S00- | - | BUS | BUS | PCY-814202_BUS_1 | PCY-814202 | Start / Stop Command to VSD PC-81002 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-814-PD-01 | MCC | MCC | ACTIVE
1005 | C7 | 1 | 0 | C7S01,00 | C7S01- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1006 | C7 | 1 | 1 | C7S01,01 | C7S01- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1007 | C7 | 1 | 2 | C7S01,02 | C7S01- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1008 | C7 | 1 | 3 | C7S01,03 | C7S01- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1009 | C7 | 1 | 4 | C7S01,04 | C7S01- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1010 | C7 | 1 | 5 | C7S01,05 | C7S01- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1011 | C7 | 1 | 6 | C7S01,06 | C7S01- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1012 | C7 | 1 | 7 | C7S01,07 | C7S01- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1013 | C7 | 1 | 8 | C7S01,08 | C7S01- | - | DI | 24 VDC energized | ATY-40201_DI_1 | ATY-40201 | Start / Stop Command for VSD AT-40201 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC PANEL) | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1014 | C7 | 1 | 9 | C7S01,09 | C7S01- | - | DI | 24 VDC energized | ATY-40201_DI_2 | ATY-40201 | Start / Stop Command for VSD AT-40201 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC PANEL) | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1015 | C7 | 1 | 10 | C7S01,10 | C7S01- | - | DI | 24 VDC energized | ATY-40201_DI_3 | ATY-40201 | Start / Stop Command for VSD AT-40201 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC PANEL) | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1016 | C7 | 1 | 11 | C7S01,11 | C7S01- | - | DI | 24 VDC energized | ATY-40202_DI_1 | ATY-40202 | Start / Stop Command for VSD AT-40202 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1017 | C7 | 1 | 12 | C7S01,12 | C7S01- | - | DI | 24 VDC energized | ATY-40202_DI_2 | ATY-40202 | Start / Stop Command for VSD AT-40202 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1018 | C7 | 1 | 13 | C7S01,13 | C7S01- | - | DI | 24 VDC energized | ATY-40202_DI_3 | ATY-40202 | Start / Stop Command for VSD AT-40202 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1019 | C7 | 1 | 14 | C7S01,14 | C7S01- | - | DI | 24 VDC energized | ATY-40203_DI_1 | ATY-40203 | Start / Stop Command for VSD AT-40203 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-02 | MCC | MCC | ACTIVE
1020 | C7 | 1 | 15 | C7S01,15 | C7S01- | - | DI | 24 VDC energized | ATY-40203_DI_2 | ATY-40203 | Start / Stop Command for VSD AT-40203 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-02 | MCC | MCC | ACTIVE
1021 | C7 | 1 | 16 | C7S01,16 | C7S01- | - | DI | 24 VDC energized | ATY-40203_DI_3 | ATY-40203 | Start / Stop Command for VSD AT-40203 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-02 | MCC | MCC | ACTIVE
1022 | C7 | 1 | 17 | C7S01,17 | C7S01- | - | DI | 24 VDC energized | PCY-40201_DI_1 | PCY-40201 | Start / Stop Command for VSD PC-40201 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1023 | C7 | 1 | 18 | C7S01,18 | C7S01- | - | DI | 24 VDC energized | PCY-40201_DI_2 | PCY-40201 | Start / Stop Command for VSD PC-40201 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1024 | C7 | 1 | 19 | C7S01,19 | C7S01- | - | DI | 24 VDC energized | PCY-40201_DI_3 | PCY-40201 | Start / Stop Command for VSD PC-40201 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1025 | C7 | 1 | 20 | C7S01,20 | C7S01- | - | DI | 24 VDC energized | PCY-40202_DI_1 | PCY-40202 | Start / Stop Command for VSD PC-40202 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1026 | C7 | 1 | 21 | C7S01,21 | C7S01- | - | DI | 24 VDC energized | PCY-40202_DI_2 | PCY-40202 | Start / Stop Command for VSD PC-40202 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1027 | C7 | 1 | 22 | C7S01,22 | C7S01- | - | DI | 24 VDC energized | PCY-40202_DI_3 | PCY-40202 | Start / Stop Command for VSD PC-40202 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1028 | C7 | 1 | 23 | C7S01,23 | C7S01- | - | DI | 24 VDC energized | PCY-40203_DI_1 | PCY-40203 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-02 | MCC | MCC | ACTIVE
1029 | C7 | 1 | 24 | C7S01,24 | C7S01- | - | DI | 24 VDC energized | PCY-40203_DI_2 | PCY-40203 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-02 | MCC | MCC | ACTIVE
1030 | C7 | 1 | 25 | C7S01,25 | C7S01- | - | DI | 24 VDC energized | PCY-40203_DI_3 | PCY-40203 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-02 | MCC | MCC | ACTIVE
1031 | C7 | 1 | 26 | C7S01,26 | C7S01- | - | DI | 24 VDC energized | BFY-60206_DI_1 | BFY-60206 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1032 | C7 | 1 | 27 | C7S01,27 | C7S01- | - | DI | - | PCM-60205-2_DI_1 | PCM-60205-2 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1033 | C7 | 1 | 28 | C7S01,28 | C7S01- | - | DI | - | PCM-60205-2_DI_2 | PCM-60205-2 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1034 | C7 | 1 | 29 | C7S01,29 | C7S01- | - | DI | - | PCM-60205-3_DI_1 | PCM-60205-3 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1035 | C7 | 1 | 30 | C7S01,30 | C7S01- | - | DI | - | PCM-60205-3_DI_2 | PCM-60205-3 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1036 | C7 | 1 | 31 | C7S01,31 | C7S01- | - | DI | - | PCM-60205-4_DI_1 | PCM-60205-4 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1037 | C7 | 2 | 0 | C7S02,00 | C7S02- | - | DI | - | PCM-60205-4_DI_2 | PCM-60205-4 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1038 | C7 | 2 | 1 | C7S02,01 | C7S02- | - | DI | - | PCM-60205-5_DI_1 | PCM-60205-5 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1039 | C7 | 2 | 2 | C7S02,02 | C7S02- | - | DI | - | PCM-60205-5_DI_2 | PCM-60205-5 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1040 | C7 | 2 | 3 | C7S02,03 | C7S02- | - | DI | - | PCY-60205_DI_1 | PCY-60205 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | JB-601 | MCC | ACTIVE
1041 | C7 | 2 | 4 | C7S02,04 | C7S02- | - | DI | - | PCY-60205_DI_2 | PCY-60205 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | JB-601 | MCC | ACTIVE
1042 | C7 | 2 | 5 | C7S02,05 | C7S02- | - | DI | 24 VDC energized | RVM-60201_DI_1 | RVM-60201 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1043 | C7 | 2 | 6 | C7S02,06 | C7S02- | - | DI | 24 VDC energized | RVM-60201_DI_2 | RVM-60201 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1044 | C7 | 2 | 7 | C7S02,07 | C7S02- | - | DI | 24 VDC energized | RVM-60202_DI_1 | RVM-60202 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1045 | C7 | 2 | 8 | C7S02,08 | C7S02- | - | DI | 24 VDC energized | RVM-60202_DI_2 | RVM-60202 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1046 | C7 | 2 | 9 | C7S02,09 | C7S02- | - | DI | 24 VDC energized | RVM-60203_DI_1 | RVM-60203 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1047 | C7 | 2 | 10 | C7S02,10 | C7S02- | - | DI | 24 VDC energized | RVM-60203_DI_2 | RVM-60203 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1048 | C7 | 2 | 11 | C7S02,11 | C7S02- | - | DI | 24 VDC energized | BFY-60210_DI_1 | BFY-60210 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-03 | MCC | MCC | ACTIVE
1049 | C7 | 2 | 12 | C7S02,12 | C7S02- | - | DI | 24 VDC energized | BFY-60211_DI_1 | BFY-60211 | Start / Stop Command for VSD FANC-21 (Combustion Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-03 | MCC | MCC | ACTIVE
1050 | C7 | 2 | 13 | C7S02,13 | C7S02- | - | DI | 24 VDC energized | BFY-60240_DI_1 | BFY-60240 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-05 | MCC | MCC | ACTIVE
1051 | C7 | 2 | 14 | C7S02,14 | C7S02- | - | DI | 24 VDC energized | PCY-60215_DI_1 | PCY-60215 | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-03 | MCC | MCC | ACTIVE
1052 | C7 | 2 | 15 | C7S02,15 | C7S02- | - | DI | 24 VDC energized | PCY-60215_DI_2 | PCY-60215 | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-03 | MCC | MCC | ACTIVE
1053 | C7 | 2 | 16 | C7S02,16 | C7S02- | - | DI | 24 VDC energized | PCY-60215_DI_3 | PCY-60215 | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-03 | MCC | MCC | ACTIVE
1054 | C7 | 2 | 17 | C7S02,17 | C7S02- | - | DI | 24 VDC energized | BFY-60220_DI_1 | BFY-60220 | Start / Stop Command for VSD FANS-22 (Cooling Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-04 | MCC | MCC | ACTIVE
1055 | C7 | 2 | 18 | C7S02,18 | C7S02- | - | DI | 24 VDC energized | BFY-61302_DI_1 | BFY-61302 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-05 | MCC | MCC | ACTIVE
1056 | C7 | 2 | 19 | C7S02,19 | C7S02- | - | DI | Dry Contact | HS-61307F_DI_1 | HS-61307F | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1057 | C7 | 2 | 20 | C7S02,20 | C7S02- | - | DI | Dry Contact | HS-61307G_DI_1 | HS-61307G | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1058 | C7 | 2 | 21 | C7S02,21 | C7S02- | - | DI | Dry Contact | HS-61307H_DI_1 | HS-61307H | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1059 | C7 | 2 | 22 | C7S02,22 | C7S02- | - | DI | Dry Contact | HS-61307I_DI_1 | HS-61307I | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1060 | C7 | 2 | 23 | C7S02,23 | C7S02- | - | DI | Dry Contact | HS-61307J_DI_1 | HS-61307J | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1061 | C7 | 2 | 24 | C7S02,24 | C7S02- | - | DI | Dry Contact | HS-61307K_DI_1 | HS-61307K | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1062 | C7 | 2 | 25 | C7S02,25 | C7S02- | - | DI | Dry Contact | HS-61307L_DI_1 | HS-61307L | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1063 | C7 | 2 | 26 | C7S02,26 | C7S02- | - | DI | Dry Contact | HS-61307M_DI_1 | HS-61307M | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1064 | C7 | 2 | 27 | C7S02,27 | C7S02- | - | DI | Dry Contact | HS-61307N_DI_1 | HS-61307N | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1065 | C7 | 2 | 28 | C7S02,28 | C7S02- | - | DI | Dry Contact | HS-61307O_DI_1 | HS-61307O | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1066 | C7 | 2 | 29 | C7S02,29 | C7S02- | - | DI | Dry Contact | HS-61307P_DI_1 | HS-61307P | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1067 | C7 | 2 | 30 | C7S02,30 | C7S02- | - | DI | Dry Contact | HS-61307Q_DI_1 | HS-61307Q | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1068 | C7 | 2 | 31 | C7S02,31 | C7S02- | - | DI | Dry Contact | HS-61307R_DI_1 | HS-61307R | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1069 | C7 | 3 | 0 | C7S03,00 | C7S03- | - | DI | 24 VDC energized | RVM-61302_DI_1 | RVM-61302 | Start / Stop Command for FVNR RV-61302 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1070 | C7 | 3 | 1 | C7S03,01 | C7S03- | - | DI | 24 VDC energized | RVM-61302_DI_2 | RVM-61302 | Start / Stop Command for FVNR RV-61302 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1071 | C7 | 3 | 2 | C7S03,02 | C7S03- | - | DI | 24 VDC energized | RVM-61303_DI_1 | RVM-61303 | Start / Stop Command for FVNR RV-61303 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-05 | MCC | MCC | ACTIVE
1072 | C7 | 3 | 3 | C7S03,03 | C7S03- | - | DI | 24 VDC energized | RVM-61303_DI_2 | RVM-61303 | Start / Stop Command for FVNR RV-61303 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-05 | MCC | MCC | ACTIVE
1073 | C7 | 3 | 4 | C7S03,04 | C7S03- | - | DI | 24 VDC energized | SCM-61301_DI_1 | SCM-61301 | Start / Stop Command for FVNR SC-61301 (Sifter ) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1074 | C7 | 3 | 5 | C7S03,05 | C7S03- | - | DI | 24 VDC energized | SCM-61301_DI_2 | SCM-61301 | Start / Stop Command for FVNR SC-61301 (Sifter ) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1075 | C7 | 3 | 6 | C7S03,06 | C7S03- | - | DI | 24 VDC energized | SCM-61302_DI_2 | SCM-61302 | Start / Stop Command for FVNR SC-61302 (Sifter ) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1076 | C7 | 3 | 7 | C7S03,07 | C7S03- | - | DI | 24 VDC energized | SCM-61302_DI_1 | SCM-61302 | Start / Stop Command for FVNR SC-61302 (Sifter ) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1077 | C7 | 3 | 8 | C7S03,08 | C7S03- | - | DI | 24 VDC energized | BFY-61301_DI_1 | BFY-61301 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1078 | C7 | 3 | 9 | C7S03,09 | C7S03- | - | DI | 24 VDC energized | BFY-61303_DI_1 | BFY-61303 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1079 | C7 | 3 | 10 | C7S03,10 | C7S03- | - | DI | 24 VDC energized | BLM-61302_DI_1 | BLM-61302 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1080 | C7 | 3 | 11 | C7S03,11 | C7S03- | - | DI | 24 VDC energized | BLM-61302_DI_2 | BLM-61302 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1081 | C7 | 3 | 12 | C7S03,12 | C7S03- | - | DI | Dry Contact | HS-61307A_DI_1 | HS-61307A | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1082 | C7 | 3 | 13 | C7S03,13 | C7S03- | - | DI | Dry Contact | HS-61307B_DI_1 | HS-61307B | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1083 | C7 | 3 | 14 | C7S03,14 | C7S03- | - | DI | Dry Contact | HS-61307C_DI_1 | HS-61307C | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1084 | C7 | 3 | 15 | C7S03,15 | C7S03- | - | DI | Dry Contact | HS-61307D_DI_1 | HS-61307D | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1085 | C7 | 3 | 16 | C7S03,16 | C7S03- | - | DI | Dry Contact | HS-61307E_DI_1 | HS-61307E | Start/Stop | Industrial Process Equipment | Standard Process Field Device | CVV 4Cx1 | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1086 | C7 | 3 | 17 | C7S03,17 | C7S03- | - | DI | 24 VDC energized | RVM-60204_DI_1 | RVM-60204 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1087 | C7 | 3 | 18 | C7S03,18 | C7S03- | - | DI | 24 VDC energized | RVM-60204_DI_2 | RVM-60204 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1088 | C7 | 3 | 19 | C7S03,19 | C7S03- | - | DI | 24 VDC energized | RVM-61301_DI_1 | RVM-61301 | Start / Stop Command for FVNR RV-61301 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1089 | C7 | 3 | 20 | C7S03,20 | C7S03- | - | DI | 24 VDC energized | RVM-61301_DI_2 | RVM-61301 | Start / Stop Command for FVNR RV-61301 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1090 | C7 | 3 | 21 | C7S03,21 | C7S03- | - | DI | 24 VDC energized | RVM-61304_DI_1 | RVM-61304 | Start / Stop Command for FVNR RV-61304 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1091 | C7 | 3 | 22 | C7S03,22 | C7S03- | - | DI | 24 VDC energized | RVM-61304_DI_2 | RVM-61304 | Start / Stop Command for FVNR RV-61304 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1092 | C7 | 3 | 23 | C7S03,23 | C7S03- | - | DI | 24 VDC energized | RVM-61305_DI_1 | RVM-61305 | Start / Stop Command for FVNR RV-61305 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1093 | C7 | 3 | 24 | C7S03,24 | C7S03- | - | DI | 24 VDC energized | RVM-61305_DI_2 | RVM-61305 | Start / Stop Command for FVNR RV-61305 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1094 | C7 | 3 | 25 | C7S03,25 | C7S03- | - | DI | - | PCY-60205_DI_3 | PCY-60205 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | JB-601 | MCC | ACTIVE
1095 | C7 | 4 | 4 | C7S04,04 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1096 | C7 | 4 | 5 | C7S04,05 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1097 | C7 | 4 | 6 | C7S04,06 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1098 | C7 | 4 | 7 | C7S04,07 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1099 | C7 | 4 | 8 | C7S04,08 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1100 | C7 | 4 | 9 | C7S04,09 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1101 | C7 | 4 | 10 | C7S04,10 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1102 | C7 | 4 | 11 | C7S04,11 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1103 | C7 | 4 | 12 | C7S04,12 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1104 | C7 | 4 | 13 | C7S04,13 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1105 | C7 | 4 | 14 | C7S04,14 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1106 | C7 | 4 | 15 | C7S04,15 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1107 | C7 | 4 | 16 | C7S04,16 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1108 | C7 | 4 | 17 | C7S04,17 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1109 | C7 | 4 | 18 | C7S04,18 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1110 | C7 | 4 | 19 | C7S04,19 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1111 | C7 | 4 | 20 | C7S04,20 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1112 | C7 | 4 | 21 | C7S04,21 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1113 | C7 | 4 | 22 | C7S04,22 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1114 | C7 | 4 | 23 | C7S04,23 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1115 | C7 | 4 | 24 | C7S04,24 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1116 | C7 | 4 | 25 | C7S04,25 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1117 | C7 | 4 | 26 | C7S04,26 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1118 | C7 | 4 | 27 | C7S04,27 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1119 | C7 | 4 | 28 | C7S04,28 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1120 | C7 | 4 | 29 | C7S04,29 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1121 | C7 | 4 | 30 | C7S04,30 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1122 | C7 | 4 | 31 | C7S04,31 | C7S04- | - | DI | - | Spare_DI_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1123 | C7 | 5 | 0 | C7S05,00 | C7S05- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1124 | C7 | 5 | 1 | C7S05,01 | C7S05- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1125 | C7 | 5 | 2 | C7S05,02 | C7S05- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1126 | C7 | 5 | 3 | C7S05,03 | C7S05- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1127 | C7 | 5 | 4 | C7S05,04 | C7S05- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1128 | C7 | 5 | 5 | C7S05,05 | C7S05- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1129 | C7 | 5 | 6 | C7S05,06 | C7S05- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1130 | C7 | 5 | 7 | C7S05,07 | C7S05- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | 3-25-01-402-PD-01 | MCC | MCC | SPARE
1131 | C7 | 5 | 8 | C7S05,08 | C7S05- | - | DO | 24 VDC energized | ATY-40201_DO_1 | ATY-40201 | Start / Stop Command for VSD AT-40201 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable (Ref: MULTICORE LINK TO MCC PANEL) | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1132 | C7 | 5 | 9 | C7S05,09 | C7S05- | - | DO | 24 VDC energized | ATY-40202_DO_1 | ATY-40202 | Start / Stop Command for VSD AT-40202 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1133 | C7 | 5 | 10 | C7S05,10 | C7S05- | - | DO | 24 VDC energized | ATY-40203_DO_1 | ATY-40203 | Start / Stop Command for VSD AT-40203 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-02 | MCC | MCC | ACTIVE
1134 | C7 | 5 | 11 | C7S05,11 | C7S05- | - | DO | 24 VDC energized | PCY-40201_DO_1 | PCY-40201 | Start / Stop Command for VSD PC-40201 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1135 | C7 | 5 | 12 | C7S05,12 | C7S05- | - | DO | 24 VDC energized | PCY-40202_DO_1 | PCY-40202 | Start / Stop Command for VSD PC-40202 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-01 | MCC | MCC | ACTIVE
1136 | C7 | 5 | 13 | C7S05,13 | C7S05- | - | DO | 24 VDC energized | PCY-40203_DO_1 | PCY-40203 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-402-PD-02 | MCC | MCC | ACTIVE
1137 | C7 | 5 | 14 | C7S05,14 | C7S05- | - | DO | 24 VDC energized | BFY-60206_DO_1 | BFY-60206 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1138 | C7 | 5 | 15 | C7S05,15 | C7S05- | - | DO | - | PCM-60205-2_DO_1 | PCM-60205-2 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1139 | C7 | 5 | 16 | C7S05,16 | C7S05- | - | DO | - | PCM-60205-2_DO_2 | PCM-60205-2 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1140 | C7 | 5 | 17 | C7S05,17 | C7S05- | - | DO | - | PCM-60205-3_DO_1 | PCM-60205-3 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1141 | C7 | 5 | 18 | C7S05,18 | C7S05- | - | DO | - | PCM-60205-3_DO_2 | PCM-60205-3 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1142 | C7 | 5 | 19 | C7S05,19 | C7S05- | - | DO | - | PCM-60205-4_DO_1 | PCM-60205-4 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1143 | C7 | 5 | 20 | C7S05,20 | C7S05- | - | DO | - | PCM-60205-4_DO_2 | PCM-60205-4 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1144 | C7 | 5 | 21 | C7S05,21 | C7S05- | - | DO | - | PCM-60205-5_DO_1 | PCM-60205-5 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1145 | C7 | 5 | 22 | C7S05,22 | C7S05- | - | DO | - | PCM-60205-5_DO_2 | PCM-60205-5 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | MCC | MCC | ACTIVE
1146 | C7 | 5 | 23 | C7S05,23 | C7S05- | - | DO | 24 VDC energized | RVM-60201_DO_1 | RVM-60201 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1147 | C7 | 5 | 24 | C7S05,24 | C7S05- | - | DO | 24 VDC energized | RVM-60201_DO_2 | RVM-60201 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1148 | C7 | 5 | 25 | C7S05,25 | C7S05- | - | DO | 24 VDC energized | RVM-60202_DO_1 | RVM-60202 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1149 | C7 | 5 | 26 | C7S05,26 | C7S05- | - | DO | 24 VDC energized | RVM-60202_DO_2 | RVM-60202 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1150 | C7 | 5 | 27 | C7S05,27 | C7S05- | - | DO | 24 VDC energized | RVM-60203_DO_1 | RVM-60203 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1151 | C7 | 5 | 28 | C7S05,28 | C7S05- | - | DO | 24 VDC energized | RVM-60203_DO_2 | RVM-60203 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1152 | C7 | 5 | 29 | C7S05,29 | C7S05- | - | DO | 0 | XS-60205_DO_1 | XS-60205 | Start / Stop Command for PUPD-11 (Positive Displacement Pump ) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-01 | MCC | MCC | ACTIVE
1153 | C7 | 5 | 30 | C7S05,30 | C7S05- | - | DO | 24 VDC energized | BFY-60210_DO_1 | BFY-60210 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-03 | MCC | MCC | ACTIVE
1154 | C7 | 5 | 31 | C7S05,31 | C7S05- | - | DO | 24 VDC energized | BFY-60211_DO_1 | BFY-60211 | Start / Stop Command for VSD FANC-21 (Combustion Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-03 | MCC | MCC | ACTIVE
1155 | C7 | 6 | 0 | C7S06,00 | C7S06- | - | DO | 24 VDC energized | BFY-60240_DO_1 | BFY-60240 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-05 | MCC | MCC | ACTIVE
1156 | C7 | 6 | 1 | C7S06,01 | C7S06- | - | DO | 24 VDC energized | PCY-60215_DO_1 | PCY-60215 | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-03 | MCC | MCC | ACTIVE
1157 | C7 | 6 | 2 | C7S06,02 | C7S06- | - | DO | Dry Contact | XS-60240A_DO_1 | XS-60240A | Start / Stop Command for BGHS-21 (Bag House Air Pulsing) | Industrial Process Equipment | Standard Process Field Device | MULTICORE LINK TO PLC | 325-01-602-PD-05 | MCC | MCC | ACTIVE
1158 | C7 | 6 | 3 | C7S06,03 | C7S06- | - | DO | Dry Contact | XS-60241A_DO_1 | XS-60241A | Start / Stop Command for HTRE-21 (Heater Control Panel) | Industrial Process Equipment | Standard Process Field Device | MULTICORE LINK TO PLC | 325-01-602-PD-05 | MCC | MCC | ACTIVE
1159 | C7 | 6 | 4 | C7S06,04 | C7S06- | - | DO | Dry Contact | XS-60242A_DO_1 | XS-60242A | Start / Stop Command for HTRE-21 (Heater Control Panel) | Industrial Process Equipment | Standard Process Field Device | MULTICORE LINK TO PLC | 325-01-602-PD-05 | MCC | MCC | ACTIVE
1160 | C7 | 6 | 4 | C7S06,04 | C7S06- | - | DO | Dry Contact | XS-60243A_DO_1 | XS-60243A | Start / Stop Command for HTRE-21 (Heater Control Panel) | Industrial Process Equipment | Standard Process Field Device | MULTICORE LINK TO PLC | 325-01-602-PD-05 | MCC | MCC | ACTIVE
1161 | C7 | 6 | 6 | C7S06,06 | C7S06- | - | DO | 24 VDC energized | XS-60260_DO_1 | XS-60260 | Start / Stop Command for FWDP-21 (Fire Deluge) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1 | 325-01-602-PD-05 | MCC | MCC | ACTIVE
1162 | C7 | 6 | 7 | C7S06,07 | C7S06- | - | DO | 24 VDC energized | BFY-60220_DO_1 | BFY-60220 | Start / Stop Command for VSD FANS-22 (Cooling Fan) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-04 | MCC | MCC | ACTIVE
1163 | C7 | 6 | 8 | C7S06,08 | C7S06- | - | DO | Dry Contact | XS-FH-60210A_DO_1 | XS-FH-60210A | Start / Stop Command Burner Remote Start for AHTR-21 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-06 | MCC | MCC | ACTIVE
1164 | C7 | 6 | 9 | C7S06,09 | C7S06- | - | DO | Dry Contact | XS-FH-60210B_DO_1 | XS-FH-60210B | Start / Stop Command Dryer Interlocks for AHTR-21 | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-602-PD-06 | MCC | MCC | ACTIVE
1165 | C7 | 6 | 10 | C7S06,10 | C7S06- | - | DO | 24 VDC energized | BFY-61302_DO_1 | BFY-61302 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-05 | MCC | MCC | ACTIVE
1166 | C7 | 6 | 11 | C7S06,11 | C7S06- | - | DO | 24 VDC energized | RVM-61302_DO_1 | RVM-61302 | Start / Stop Command for FVNR RV-61302 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1167 | C7 | 6 | 12 | C7S06,12 | C7S06- | - | DO | 24 VDC energized | RVM-61302_DO_2 | RVM-61302 | Start / Stop Command for FVNR RV-61302 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-03 | MCC | MCC | ACTIVE
1168 | C7 | 6 | 13 | C7S06,13 | C7S06- | - | DO | 24 VDC energized | RVM-61303_DO_1 | RVM-61303 | Start / Stop Command for FVNR RV-61303 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-05 | MCC | MCC | ACTIVE
1169 | C7 | 6 | 14 | C7S06,14 | C7S06- | - | DO | 24 VDC energized | RVM-61303_DO_2 | RVM-61303 | Start / Stop Command for FVNR RV-61303 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-05 | MCC | MCC | ACTIVE
1170 | C7 | 6 | 15 | C7S06,15 | C7S06- | - | DO | 24 VDC energized | SCM-61301_DO_1 | SCM-61301 | Start / Stop Command for FVNR SC-61301 (Sifter ) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1171 | C7 | 6 | 16 | C7S06,16 | C7S06- | - | DO | 24 VDC energized | SCM-61301_DO_2 | SCM-61301 | Start / Stop Command for FVNR SC-61301 (Sifter ) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1172 | C7 | 6 | 17 | C7S06,17 | C7S06- | - | DO | 24 VDC energized | SCM-61302_DO_1 | SCM-61302 | Start / Stop Command for FVNR SC-61302 (Sifter ) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1173 | C7 | 6 | 18 | C7S06,18 | C7S06- | - | DO | 24 VDC energized | SCM-61302_DO_2 | SCM-61302 | Start / Stop Command for FVNR SC-61302 (Sifter ) | Industrial Process Equipment | Standard Process Field Device | CVV 3Cx1.5 | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1174 | C7 | 6 | 19 | C7S06,19 | C7S06- | - | DO | 24 VDC energized | BFY-61301_DO_1 | BFY-61301 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1175 | C7 | 6 | 20 | C7S06,20 | C7S06- | - | DO | 24 VDC energized | BFY-61303_DO_1 | BFY-61303 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1176 | C7 | 6 | 21 | C7S06,21 | C7S06- | - | DO | 24 VDC energized | BLM-61302_DO_1 | BLM-61302 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1177 | C7 | 6 | 22 | C7S06,22 | C7S06- | - | DO | 24 VDC energized | BLM-61302_DO_2 | BLM-61302 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1178 | C7 | 6 | 23 | C7S06,23 | C7S06- | - | DO | 24 VDC energized | RVM-60204_DO_1 | RVM-60204 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1179 | C7 | 6 | 24 | C7S06,24 | C7S06- | - | DO | 24 VDC energized | RVM-60204_DO_2 | RVM-60204 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-602-PD-08 | MCC | MCC | ACTIVE
1180 | C7 | 6 | 25 | C7S06,25 | C7S06- | - | DO | 24 VDC energized | RVM-61301_DO_1 | RVM-61301 | Start / Stop Command for FVNR RV-61301 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1181 | C7 | 6 | 26 | C7S06,26 | C7S06- | - | DO | 24 VDC energized | RVM-61301_DO_2 | RVM-61301 | Start / Stop Command for FVNR RV-61301 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1182 | C7 | 6 | 27 | C7S06,27 | C7S06- | - | DO | 24 VDC energized | RVM-61304_DO_1 | RVM-61304 | Start / Stop Command for FVNR RV-61304 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1183 | C7 | 6 | 28 | C7S06,28 | C7S06- | - | DO | 24 VDC energized | RVM-61304_DO_2 | RVM-61304 | Start / Stop Command for FVNR RV-61304 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1184 | C7 | 6 | 29 | C7S06,29 | C7S06- | - | DO | 24 VDC energized | RVM-61305_DO_1 | RVM-61305 | Start / Stop Command for FVNR RV-61305 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1185 | C7 | 6 | 30 | C7S06,30 | C7S06- | - | DO | 24 VDC energized | RVM-61305_DO_2 | RVM-61305 | Start / Stop Command for FVNR RV-61305 | Rockwell Automation | Allen-Bradley PowerFlex VSD / E300 Relay in MCC | CVV 8Cx1.5 / CVV 12Cx1.5 Control Cable | 325-01-613-PD-01 | MCC | MCC | ACTIVE
1186 | C7 | 6 | 31 | C7S06,31 | C7S06- | - | DO | - | PCY-60205_DO_1 | PCY-60205 | - | Rockwell / Automation Field Equipment | Standard Loop Device | LiY-CY TP 1Px1.0 / CVV | 325-01-600-PD-01 | JB-601 | MCC | ACTIVE
1187 | C7 | 7 | 8 | C7S07,08 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1188 | C7 | 7 | 9 | C7S07,09 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1189 | C7 | 7 | 10 | C7S07,10 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1190 | C7 | 7 | 11 | C7S07,11 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1191 | C7 | 7 | 12 | C7S07,12 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1192 | C7 | 7 | 13 | C7S07,13 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1193 | C7 | 7 | 14 | C7S07,14 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1194 | C7 | 7 | 15 | C7S07,15 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1195 | C7 | 7 | 16 | C7S07,16 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1196 | C7 | 7 | 17 | C7S07,17 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1197 | C7 | 7 | 18 | C7S07,18 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1198 | C7 | 7 | 19 | C7S07,19 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1199 | C7 | 7 | 20 | C7S07,20 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1200 | C7 | 7 | 21 | C7S07,21 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1201 | C7 | 7 | 22 | C7S07,22 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1202 | C7 | 7 | 23 | C7S07,23 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1203 | C7 | 7 | 24 | C7S07,24 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1204 | C7 | 7 | 25 | C7S07,25 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1205 | C7 | 7 | 26 | C7S07,26 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1206 | C7 | 7 | 27 | C7S07,27 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1207 | C7 | 7 | 28 | C7S07,28 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1208 | C7 | 7 | 29 | C7S07,29 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1209 | C7 | 7 | 30 | C7S07,30 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE
1210 | C7 | 7 | 31 | C7S07,31 | C7S07- | - | DO | - | Spare_DO_0 | Spare | Spare I/O Terminal Point | - | - | - | - | MCC | MCC | SPARE

## Instrument_Catalog_Reference
INGREDION (THAILAND) CO., LTD. ¦ PROJECT JET COOKER ¦ INSTRUMENT CATALOG REFERENCE
Master Index of Equipment Packages, Manufacturer Manuals, Process Connections & Cable Standards in Folder
Package Directory | Equipment Type | Manufacturer | Product Series / Model | Key Technical Data Sheet | Process Connection | Electrical Standard | Suggested Field Cable
CS-DS-01 Dust Analyzer | Particulate / Dust Transmitter | ENVEA / PCME | PCME QAL 991 | 6626013-33-201-001_Dust Analyzer Data Sheets Rev.0.pdf | DN100 Flange w/ Purge Air | 4-20mA Output + Alarm Relay / 24VDC | LiY-CY TP 2Px1.0 + CVV 3Cx1.5 (Pwr)
CS-DS-01 LEL gas Analyzer | Combustible Gas Detector | Sensidyne / SmartGas | 925FGD Explosionproof | 6626014-33-204-001_General Arrangement Drawing_Rev.0.pdf | 3/4" NPT Conduit Entry | 4-20mA + Alarm Relays / 24VDC | LiY-CY TP 2Px1.0 (Ex d)
CS-DS-01 pH Analyzer | pH Analytical Loop | Mettler Toledo | M300G2 4-Wire + InPro3250i | DS_pH_InPro3250i_PA2097EN_RevA.pdf / TD_THO_Meter_M300G2.pdf | DN25 Weld-in Socket / InTrac 777P | 4-20mA HART + Relays / 24VDC | LiY-CY TP 2Px1.0 + CVV 3Cx1.5 (Pwr)
CS-DS-02 Diff Pressure Gauge | Diff. Pressure Indicator | Ashcroft | Model 1132 | datasheet-differential-1132-pressure-gauge.pdf | 1/4" NPT Female w/ V03 Manifold | Local Mechanical Dial | None (Mechanical)
CS-DS-03Diff Pressure Transmitter | Diff. Pressure Transmitter | Endress+Hauser | Deltabar PMD55B | Spec. Dif. Pressure_R3 19122025.pdf / TI PMD55B.pdf | 1/4" NPT w/ 5-Valve Manifold DA63M | 2-wire 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded)
CS-DS-05 Flow meter (Coriolis) | Coriolis Mass Flowmeter | Endress+Hauser | Promass E 300 (8E3B50) | Spec. Flow_R4 12192025.pdf / TI E300.pdf | DN50 Cl.150 RF Flange | 4-20mA HART (Mass/Dens) / 24VDC | LiY-CY TP 3Px1.0 + CVV 3Cx1.5 (Pwr)
CS-DS-05 Flow meter (Magmeter) | Electromagnetic Flowmeter | Endress+Hauser | Promag P 300 (5P3B50/80/1H) | Spec. Flow_R4 12192025.pdf / TI P300.pdf | DN50/80/100 Cl.150 Flange | 4-20mA HART / 24VDC | LiY-CY TP 2Px1.0 + CVV 3Cx1.5 (Pwr)
CS-DS-05 Flow meter (Vortex) | Vortex Steam Flowmeter | Endress+Hauser | Prowirl F 200 (7F2C80/1H) | Spec. Flow_R4 12192025.pdf / TI F200.pdf | DN80/100 Cl.300 RF Flange | 4-20mA HART + Pulse / 24VDC | LiY-CY TP 1Px1.0 (Shielded)
CS-DS-05 Flow meter (Thermal) | Thermal Mass Gas Flowmeter | Endress+Hauser | t-mass F 300 / I 300 (6F3B/6I3B) | Spec. Flow_R4 12192025.pdf / TI T-Mass F300.pdf | DN100 Flange / 1" NPT Insertion | 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded)
CS-DS-05 Ultra Sonic Flow meter | Clamp-on Ultrasonic Flow | Keyence | FD-H Series (FD-H20/H32) | FD-H Instruction manual TH.pdf | External Clamp-on Sensor | 4-20mA + Pulse / 24VDC | LiY-CY TP 2Px1.0 (Shielded)
CS-DS-07 Hand valve w/ Switch | Manual Valve Position Box | TeroFox / APL-HKC | TF-20DFS + APL-210N | APL-Series IOM.pdf / General Ball Valves Catalogue.pdf | Flange Cl.150 RF, SS316 | 2x DI Dry Contact Limit Switches | CVV 4Cx1.0 (Control Cable)
CS-DS-09 Level switch (Liquid) | Vibrating Fork Level Switch | Endress+Hauser | Liquiphant FTL51B | TI FTL51B.pdf | 3/4" NPT Threaded / Tri-Clamp | 24VDC / Relay Contact Output | CVV 3Cx1.5 (Control Cable)
CS-DS-09 Level switch (Solid) | Vibrating Fork Powder Switch | Endress+Hauser | Soliphant FTM51 | TI FTM51.pdf | 1-1/2" NPT Threaded / Flange | 24VDC / Relay Contact Output | CVV 3Cx1.5 (Control Cable)
CS-DS-10 Level transmitter | Radar Level Transmitter | Endress+Hauser | Micropilot FMR67B (80GHz) | TI FMR67B.pdf / TI PMD78B.pdf | DN80 3" Cl.150 Flange | 2-wire 4-20mA HART / 24VDC | LiY-CY(EB) 1Px1.0 (Blue IS Sheath)
CS-DS-11 Pressure Gauge | Pressure Indicator | Ashcroft | Model T5500 | DS-T5500-EN-2.pdf / datasheet-1098-1100-siphon.pdf | 1/2" NPT Male w/ Siphon | Local Mechanical Dial | None (Mechanical)
CS-DS-12 Pressure Switch | Electronic Pressure Switch | Endress+Hauser | Ceraphant PTC31B | TI PTC31B.pdf | 1/2" NPT Male Thread | 24VDC / Dry Contact Relay / PNP | CVV 3Cx1.5 (Control Cable)
CS-DS-13 Pressure Transmitter | Pressure Transmitter | Endress+Hauser | Cerabar PMP51B / PMC51B / PMP43 | TI PMP51B.pdf / TI PMC51B.pdf / TI PMP43.pdf | 1/2" NPT Male / Tri-Clamp | 2-wire 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded)
CS-DS-15 Temp gauge | Bimetal Thermometer | Ashcroft | Model FI + Thermowell | Datasheet_FI_EN_RevB.pdf / datasheet-threaded-thermowell.pdf | 1/2" NPT Threaded Thermowell | Local Mechanical Dial | None (Mechanical)
CS-DS-16 Temp transmitter | RTD Temperature Transmitter | Endress+Hauser | iTEMP TMT71 + TM411 (Pt100) | TI TM411.pdf / TI TMT71.pdf | 1/2" NPT w/ Threaded Thermowell | 2-wire 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded)
CS-DS-17 Pneumatic on-off valve | Pneumatic On-Off Valve | TeroFox / El-O-Matic | TF-20DFS + F-Series + ESV | EL-O-MATIC complete data sheet.pdf / 2023ESV.pdf | Flange Cl.150 RF, SS316 | 24VDC DO + 2x DI Limit Sw. | CVV 3Cx1.5 (Sol) + CVV 4Cx1.0 (Limit)
CS-DS-20 Control valve Sanmax | Globe Control Valve | Samson | Type 3241 + Trovis 3730-1 | 3241-ANSI.pdf / TI-Trovis 3730-1.pdf | Flange ASME B16.5 Cl.150/300 RF | 4-20mA Setpoint + Position Feedback | LiY-CY TP 2Px1.0 (Dual Shielded)
Pneumatic Vibrating | Pneumatic Turbine Vibrator | Netter Vibration | NCT 5 Vibrator | KBA_NCT_NCB_NCR-1882EN.pdf / NCT5 Technical data.jpg | G 1/8" BSP Port | 24VDC Solenoid Valve DO | CVV 3Cx1.5 (Solenoid Control)