## Executive_Summary
KALASIN STARCH PLANT --- JET COOKER AUTOMATION SYSTEM (xCIP-1545, Ref: x2608003)
MASTER ELECTRICAL POWER SUPPLY & DISTRIBUTION CALCULATION REPORT (ALL PANELS)
1. EXECUTIVE PROJECT OVERVIEW
Panel Tag | Panel Description & Location | Racks / Equipment | 24VDC Load (A) | Design 24VDC (A) | 24VDC Power Supply Configuration | PSU Load (%) | 220VAC Power (VA) | Mains Breaker | Recommended Online UPS | Heat Load (BTU/hr)
CA1 | Main Control Automation Cabinet (CA1) - Main Control Room (MCP) | C1, C2 | 14.1 | 18.33 | 2x QUINT4-PS/1AC/24DC/40 (1+1 Redundant) | 45.8% | 972.2 | 16A / 2P Type C | 3000 VA (32.4% load) | 1051
CA-RIO-1 | Field Remote I/O Cabinet 1 (RIO-1) - Spray Dryer 3rd/7th Floor | C3 | 6.28 | 8.16 | 2x QUINT4-PS/1AC/24DC/20 (1+1 Redundant) | 40.8% | 610.9 | 10A / 2P Type C | 1500 VA (40.7% load) | 495
CA-RIO-2 | Field Remote I/O Cabinet 2 (RIO-2) - Spray Dryer 6th/8th Floor | C4 | 4.48 | 5.83 | 2x QUINT4-PS/1AC/24DC/20 (1+1 Redundant) | 29.1% | 527.5 | 10A / 2P Type C | 1500 VA (35.2% load) | 372
CA-RIO-200 | Slurry Out-Building Remote Cabinet (RIO-200) - Slurry Building 2nd Floor | C5 | 4.1 | 5.34 | 2x QUINT4-PS/1AC/24DC/10 (1+1 Redundant) | 53.4% | 500.6 | 6A / 2P Type C | 1000 VA (50.1% load) | 315
CA-MCC | Motor Control Center Interface Panel (MCC) - MCC Room Ground Floor | C6, C7 | 10.11 | 13.14 | 2x QUINT4-PS/1AC/24DC/40 (1+1 Redundant) | 32.9% | 801.9 | 16A / 2P Type C | 2000 VA (40.1% load) | 814
CA-IS | Intrinsically Safe Marshaling Enclosure (IS-CAB) - Field Ex Area Boundary (Spray Dryer) | C8 (IS) | 6.24 | 8.11 | 2x QUINT4-PS/1AC/24DC/20 (1+1 Redundant) | 40.5% | 580.5 | 10A / 2P Type C | 1500 VA (38.7% load) | 415
SYSTEM TOTALS | All 6 Plant Automation Cabinets | 8 Chassis Racks | 45.31 | 58.9 | 12x QUINT4 PSUs Total | OK (N+1) | 3993.6 | Main Feeders | 10.5 kVA Total UPS | 3463
2. KEY ENGINEERING DESIGN BASIS & COMPLIANCE SUMMARY
• Redundancy Philosophy: All panel 24VDC systems employ 1+1 redundant Phoenix Contact QUINT4 industrial power supplies coupled via active diode modules (QUINT4-DIODE).
• N+1 Reliability: In the event of a primary power supply failure, the secondary redundant power supply automatically supports 100% of full rated operating current without voltage drop.
• ControlLogix Backplane Safety: All 1756-A13 and 1756-A7 chassis racks are powered by dedicated 1756-PA75 power supplies. Backplane utilization remains safely under 35% on all racks (maximum capacity: 75W).
• Digital Output Relay Protection: All 1756-OB32 sourcing outputs drive Phoenix Contact PLC-RSC-24DC/21 SPDT interface relays, preventing inductive flyback surges from entering the PLC backplane.
• Uninterruptible Power Supply (UPS): Online double-conversion UPS units are sized for each cabinet to provide >30 minutes continuous battery runtime upon main grid blackout.
• Environmental & Heat Management: Total internal cabinet heat dissipation is computed for ventilation exhaust fan and enclosure air conditioner sizing to maintain <40°C internal ambient.

## Backplane_Power_Details
ALLEN-BRADLEY CONTROLLOGIX 1756 CHASSIS BACKPLANE POWER BUDGET (C1 - C5)
Chassis | Slot No | Module Catalog | Module Description | Signal Family | 5.1VDC Current (A) | 24VDC Current (A) | Power (Watts) | Supply Headroom Check
C1 | Slot 0 | 1756-L950TPSXT | ControlLogix 5580 Controller (40MB, Conformal Coated) | L950TPSXT | 1.2 | 0.005 | 6.24 | PASS (OK)
C1 | Slot 1 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | EN4TR | 1 | 0.003 | 5.17 | PASS (OK)
C1 | Slot 2 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | EN4TR | 1 | 0.003 | 5.17 | PASS (OK)
C1 | Slot 3 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | EN4TR | 1 | 0.003 | 5.17 | PASS (OK)
C1 | Slot 4 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C1 | Slot 5 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C1 | Slot 6 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C1 | Slot 7 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C1 | Slot 8 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | OB32 | 0.28 | 0.003 | 1.5 | PASS (OK)
C1 | Slot 9 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | OB32 | 0.28 | 0.003 | 1.5 | PASS (OK)
C1 | Slot 10 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | IF16 | 0.15 | 0.065 | 2.33 | PASS (OK)
C1 | Slot 11 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | IF16 | 0.15 | 0.065 | 2.33 | PASS (OK)
C1 | Slot 12 | 1756-N2 | Slot Filler / Blanking Plate | N2 | 0 | 0 | 0 | PASS (OK)
SUBTOTAL C1 | 1756-PA75 PSU | Capacity: 75.0 W | 5.1V Max: 13.0A ¦ 24V Max: 2.8A | Util: 42.7% | 5.54 | 0.16 | 32.05 | PASS (42.7%)
C2 | Slot 0 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | EN4TR | 1 | 0.003 | 5.17 | PASS (OK)
C2 | Slot 1 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C2 | Slot 2 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C2 | Slot 3 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C2 | Slot 4 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C2 | Slot 5 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C2 | Slot 6 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | OB32 | 0.28 | 0.003 | 1.5 | PASS (OK)
C2 | Slot 7 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | OB32 | 0.28 | 0.003 | 1.5 | PASS (OK)
C2 | Slot 8 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | OB32 | 0.28 | 0.003 | 1.5 | PASS (OK)
C2 | Slot 9 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | IF16 | 0.15 | 0.065 | 2.33 | PASS (OK)
C2 | Slot 10 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | IF16 | 0.15 | 0.065 | 2.33 | PASS (OK)
C2 | Slot 11 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | IF16 | 0.15 | 0.065 | 2.33 | PASS (OK)
C2 | Slot 12 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | IF16 | 0.15 | 0.065 | 2.33 | PASS (OK)
SUBTOTAL C2 | 1756-PA75 PSU | Capacity: 75.0 W | 5.1V Max: 13.0A ¦ 24V Max: 2.8A | Util: 29.7% | 3.04 | 0.28 | 22.27 | PASS (29.7%)
C3 | Slot 0 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | EN4TR | 1 | 0.003 | 5.17 | PASS (OK)
C3 | Slot 1 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C3 | Slot 2 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C3 | Slot 3 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C3 | Slot 4 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | OB32 | 0.28 | 0.003 | 1.5 | PASS (OK)
C3 | Slot 5 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | OB32 | 0.28 | 0.003 | 1.5 | PASS (OK)
C3 | Slot 6 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | IF16 | 0.15 | 0.065 | 2.33 | PASS (OK)
C3 | Slot 7 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | IF16 | 0.15 | 0.065 | 2.33 | PASS (OK)
C3 | Slot 8 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | IF16 | 0.15 | 0.065 | 2.33 | PASS (OK)
C3 | Slot 9 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | IF16 | 0.15 | 0.065 | 2.33 | PASS (OK)
C3 | Slot 10 | 1756-N2 | Slot Filler / Blanking Plate | N2 | 0 | 0 | 0 | PASS (OK)
C3 | Slot 11 | 1756-N2 | Slot Filler / Blanking Plate | N2 | 0 | 0 | 0 | PASS (OK)
C3 | Slot 12 | 1756-OF8 | 8-Point Analog Output Module (4-20mA) | OF8 | 0.15 | 0.21 | 5.8 | PASS (OK)
SUBTOTAL C3 | 1756-PA75 PSU | Capacity: 75.0 W | 5.1V Max: 13.0A ¦ 24V Max: 2.8A | Util: 33.7% | 2.67 | 0.48 | 25.26 | PASS (33.7%)
C4 | Slot 0 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | EN4TR | 1 | 0.003 | 5.17 | PASS (OK)
C4 | Slot 1 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C4 | Slot 2 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C4 | Slot 3 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C4 | Slot 4 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | OB32 | 0.28 | 0.003 | 1.5 | PASS (OK)
C4 | Slot 5 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | IF16 | 0.15 | 0.065 | 2.33 | PASS (OK)
C4 | Slot 6 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | IF16 | 0.15 | 0.065 | 2.33 | PASS (OK)
C4 | Slot 7 | 1756-N2 | Slot Filler / Blanking Plate | N2 | 0 | 0 | 0 | PASS (OK)
C4 | Slot 8 | 1756-N2 | Slot Filler / Blanking Plate | N2 | 0 | 0 | 0 | PASS (OK)
C4 | Slot 9 | 1756-N2 | Slot Filler / Blanking Plate | N2 | 0 | 0 | 0 | PASS (OK)
C4 | Slot 10 | 1756-N2 | Slot Filler / Blanking Plate | N2 | 0 | 0 | 0 | PASS (OK)
C4 | Slot 11 | 1756-N2 | Slot Filler / Blanking Plate | N2 | 0 | 0 | 0 | PASS (OK)
C4 | Slot 12 | 1756-N2 | Slot Filler / Blanking Plate | N2 | 0 | 0 | 0 | PASS (OK)
SUBTOTAL C4 | 1756-PA75 PSU | Capacity: 75.0 W | 5.1V Max: 13.0A ¦ 24V Max: 2.8A | Util: 17.7% | 1.94 | 0.14 | 13.3 | PASS (17.7%)
C5 | Slot 0 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | EN4TR | 1 | 0.003 | 5.17 | PASS (OK)
C5 | Slot 1 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C5 | Slot 2 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | IB32 | 0.12 | 0.002 | 0.66 | PASS (OK)
C5 | Slot 3 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | OB32 | 0.28 | 0.003 | 1.5 | PASS (OK)
C5 | Slot 4 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | IF16 | 0.15 | 0.065 | 2.33 | PASS (OK)
SUBTOTAL C5 | 1756-PA75 PSU | Capacity: 75.0 W | 5.1V Max: 13.0A ¦ 24V Max: 2.8A | Util: 13.8% | 1.67 | 0.07 | 10.32 | PASS (13.8%)

## 24VDC_Field_Load_Details
24VDC POWER DISTRIBUTION & INSTRUMENTATION LOOP LOAD CALCULATIONS
Panel Tag | Panel Location | DI Loop Current (A) | DO Relay Coils (A) | DO Solenoids (A) | AI 4-20mA Loops (A) | AO 4-20mA Loops (A) | Network Switches (A) | Auxiliaries (A) | Operating Current (A) | Design Load +30% (A)
CA1 | Main Control Room (MCP) | 1.18 | 0.55 | 4.4 | 0.84 | 0 | 4 | 3.12 | 14.1 | 18.33
CA-RIO-1 | Spray Dryer 3rd/7th Floor | 0.18 | 0.16 | 1.25 | 1.02 | 0 | 2 | 1.67 | 6.28 | 8.16
CA-RIO-2 | Spray Dryer 6th/8th Floor | 0.28 | 0.01 | 0.05 | 0.48 | 0 | 2 | 1.67 | 4.48 | 5.83
CA-RIO-200 | Slurry Building 2nd Floor | 0.22 | 0.05 | 0.4 | 0.18 | 0 | 2 | 1.25 | 4.1 | 5.34
CA-MCC | MCC Room Ground Floor | 0.24 | 0.24 | 1.9 | 0.4 | 0 | 4 | 3.33 | 10.11 | 13.14
CA-IS | Field Ex Area Boundary (Spray Dryer) | 0.86 | 0 | 0.48 | 1.44 | 0 | 2 | 1.46 | 6.24 | 8.11
TOTALS | System Total 24VDC Current | 2.96 | 1.01 | 8.48 | 4.36 | 0 | 16 | 12.5 | 45.31 | 58.9

## AC_Mains_and_UPS_Sizing
PANEL AC MAINS INFEED, HEAT DISSIPATION & UPS BACKUP POWER SIZING
Panel Tag | Mains Voltage | Active Power (Watts) | Apparent Power (VA) | 220VAC Current (A) | Recommended MCB | Heat Load (Watts) | Heat Load (BTU/hr) | Cooling Method | Online UPS Model & Rating
CA1 | 220VAC 1-Ph 50Hz | 615.9 | 972.2 | 4.42 | 16A / 2P Type C | 308 | 1051 | Air Conditioned (Control Room) | APC Smart-UPS RT 3000VA (SRT3000XLI, Online Double-Conversion)
CA-RIO-1 | 220VAC 1-Ph 50Hz | 282.2 | 610.9 | 2.78 | 10A / 2P Type C | 145.1 | 495 | Fan Filter Unit (IP54) | APC Smart-UPS RT 1500VA (SRT1500XLI, Online Double-Conversion)
CA-RIO-2 | 220VAC 1-Ph 50Hz | 207 | 527.5 | 2.4 | 10A / 2P Type C | 109.1 | 372 | Fan Filter Unit (IP54) | APC Smart-UPS RT 1500VA (SRT1500XLI, Online Double-Conversion)
CA-RIO-200 | 220VAC 1-Ph 50Hz | 182.1 | 500.6 | 2.28 | 6A / 2P Type C | 92.4 | 315 | Fan Filter Unit (IP54) | APC Smart-UPS RT 1000VA (SRT1000XLI, Online Double-Conversion)
CA-MCC | 220VAC 1-Ph 50Hz | 459.2 | 801.9 | 3.65 | 16A / 2P Type C | 238.5 | 814 | Fan Filter Unit (IP54) | APC Smart-UPS RT 2200VA (SRT2200XLI, Online Double-Conversion)
CA-IS | 220VAC 1-Ph 50Hz | 257.9 | 580.5 | 2.64 | 10A / 2P Type C | 121.8 | 415 | Fan Filter Unit (IP54) | APC Smart-UPS RT 1500VA (SRT1500XLI, Online Double-Conversion)

## Power_Equipment_BOM
BILL OF MATERIALS (BOM) --- POWER SUPPLIES, REDUNDANCY & UPS EQUIPMENT
Item | Model / Catalog | Manufacturer | Part Number | Description & Technical Specifications | Qty | Panel Allocation | Application / Function
1 | QUINT4-PS/1AC/24DC/40 | Phoenix Contact | 2904603 | Primary Switched Redundant 24VDC 40A Power Supply, SFB Technology | 4 | CA1 (2), CA-MCC (2) | Redundant 24VDC Main DC Bus
2 | QUINT4-PS/1AC/24DC/20 | Phoenix Contact | 2904602 | Primary Switched Redundant 24VDC 20A Power Supply, SFB Technology | 6 | RIO-1 (2), RIO-2 (2), IS (2) | Redundant 24VDC Field DC Bus
3 | QUINT4-PS/1AC/24DC/10 | Phoenix Contact | 2904601 | Primary Switched Redundant 24VDC 10A Power Supply, SFB Technology | 2 | CA-RIO-200 (2) | Redundant 24VDC Remote Bus
4 | QUINT4-DIODE/48 | Phoenix Contact | 2907714 | Redundancy Decoupling Diode Module (2x 20A / 1x 40A, 12-24VDC) | 2 | CA1 (1), CA-MCC (1) | Decouples Primary/Secondary 40A PSUs
5 | QUINT4-DIODE/40 | Phoenix Contact | 2907713 | Redundancy Decoupling Diode Module (2x 20A / 1x 40A, 12-24VDC) | 3 | RIO-1 (1), RIO-2 (1), IS (1) | Decouples Primary/Secondary 20A PSUs
6 | QUINT4-DIODE/12 | Phoenix Contact | 2907712 | Redundancy Decoupling Diode Module (2x 10A / 1x 20A, 12-24VDC) | 1 | CA-RIO-200 (1) | Decouples Primary/Secondary 10A PSUs
7 | 1756-PA75 | Rockwell Automation | 1756-PA75 | ControlLogix AC Chassis Power Supply (85-265VAC Input, 75W Output) | 8 | C1, C2, C3, C4, C5, C6, C7 | PLC Chassis Backplane Power
8 | PLC-RSC-24DC/21 | Phoenix Contact | 2966171 | Interface Relay, DIN Rail, 24VDC Coil, SPDT 1 C/O Contact (6A 250VAC) | 288 | All DO Cards (C1-C5, MCC) | Interposing Relay Isolation
9 | SRT3000XLI | Schneider APC | SRT3000XLI | Smart-UPS On-Line RT 3000VA / 2700W 230V Double Conversion UPS | 1 | Control Room MCP (CA1) | 30-min Battery Autonomy
10 | SRT2200XLI | Schneider APC | SRT2200XLI | Smart-UPS On-Line RT 2200VA / 1980W 230V Double Conversion UPS | 1 | MCC Room (CA-MCC) | 30-min Battery Autonomy
11 | SRT1500XLI | Schneider APC | SRT1500XLI | Smart-UPS On-Line RT 1500VA / 1350W 230V Double Conversion UPS | 3 | RIO-1, RIO-2, IS-CAB | 30-min Battery Autonomy
12 | SRT1000XLI | Schneider APC | SRT1000XLI | Smart-UPS On-Line RT 1000VA / 900W 230V Double Conversion UPS | 1 | Slurry Building (RIO-200) | 30-min Battery Autonomy
13 | VAL-MS 230/3+1 | Phoenix Contact | 2838209 | Type 2 Surge Protection Device (SPD) for 230/400V Mains Feeder | 6 | All 6 Automation Panels | Mains Lightning & Surge Protection
14 | C60H-DC 2P | Schneider Electric | MGN61420 | 2-Pole DC Miniature Circuit Breaker (C-Curve, 10A / 16A / 20A) | 24 | All Panels DC Distribution | DC Branch Feeder Protection

## TRIO_Quotation_Design
PHOENIX CONTACT TRIO POWER (2903151) SIZING & VERIFICATION --- JW TECH QUOTATION REF: QJP-260901724-R0
1. PROCUREMENT & COMMERCIAL METADATA (QUOTATION QJP-260901724-R0)
Quotation Number | QJP-260901724-R0 |  |  | Supplier / Vendor | JW TECH., LTD. (เลขที่ 226 ซอยศูนย์การค้าแฮปปี้แลนด์ 1 บางกะปิ กรุงเทพฯ)
Quotation Date | 11 กันยายน 2026 (11 Sep 2026) |  |  | Vendor Contact | นางสาวจิรัชยา โพธิ์งาม (Tel: +66863101172, nidda@jwtech.co.th)
Buyer / Client | บริษัท อีโคแมกซ์ เอ็นจิเนียริ่ง ซัพพลายแอนด์ เซอร์วิส จำกัด |  |  | Attention | Khun Surachet Jumpit (Tel: 089-8926578, info.ecomax3@gmail.com)
Item Description | Power supply unit, primary-switched, 1-phase AC, 24VDC, 20A |  |  | Part Number / Model | 2903151 --- TRIO-PS-2G/1AC/24DC/20
Quoted Quantity | 5 EA (In Stock) |  |  | Unit Price (THB) | 7,260.00 THB / EA
Subtotal Amount | 36,300.00 THB |  |  | Grand Total (+7% VAT) | 38,841.00 THB (Payment: Cash, Warranty: 1 Year)
2. TECHNICAL PARAMETERS OF PHOENIX CONTACT TRIO-PS-2G/1AC/24DC/20 (2903151)
Nominal AC Input Voltage | 100 V AC ... 240 V AC (-15% / +10%) |  | Efficiency @ 230VAC | > 93.0% (Typical) |  | Heat Dissipation (Max) | 36.0 W @ 20A full load
AC Input Voltage Range | 85 V AC ... 264 V AC (45 ... 65 Hz) |  | Power Factor (cos phi) | 0.95 (Built-in active PFC) |  | Inrush Current | < 15 A @ 230VAC (Cold Start)
Nominal Output Voltage | 24 V DC (Adjustable 24 ... 28 V DC) |  | Push-in Conductor Size | 0.2 ... 4 mm² (In), 0.2 ... 10 mm² (Out) |  | Housing Dimensions | 68 x 130 x 160 mm (W x H x D)
Nominal Output Current | 20.0 A continuous (-25°C ... +60°C) |  | Dynamic Boost (150%) | 30.0 A for 5 seconds (heavy startup) |  | Status Contact | DC OK Floating Relay (30V, 100mA)
3. SIZING & LOADING ANALYSIS --- 5 QUOTED UNITS ALLOCATION OPTIONS
OPTION A: DEDICATED PER-CHASSIS DC DOMAIN (1x 20A TRIO PSU Per ControlLogix Chassis C1 to C5) --- RECOMMENDED
Unit # | Target Chassis | Panel & Location | 24VDC Oper. Load (A) | Design Load +30% (A) | TRIO Rated (A) | TRIO Utilization (%) | Dynamic Boost (5s) | Thermal Loss (W) | Engineering Sizing Verdict
Unit 1 | Chassis C1 | CA1 (Main Control Room) | 6.12 | 7.96 | 20 | 39.8% | 30.0 A (150%) | 14.4 | PASS (Optimal Load <40%)
Unit 2 | Chassis C2 | CA1 (Main Control Room) | 7.36 | 9.57 | 20 | 47.8% | 30.0 A (150%) | 17.3 | PASS (Optimal Load <50%)
Unit 3 | Chassis C3 | CA-RIO-1 (Spray Dryer 3F/7F) | 6.11 | 7.94 | 20 | 39.7% | 30.0 A (150%) | 14.3 | PASS (Optimal Load <40%)
Unit 4 | Chassis C4 | CA-RIO-2 (Spray Dryer 6F/8F) | 4.32 | 5.62 | 20 | 28.1% | 30.0 A (150%) | 10.1 | PASS (Generous Headroom)
Unit 5 | Chassis C5 | CA-RIO-200 (Slurry Building 2F) | 4.05 | 5.27 | 20 | 26.3% | 30.0 A (150%) | 9.5 | PASS (Generous Headroom)
OPTION B: PANEL-LEVEL REDUNDANT BUS (2x 20A in CA1 + 1x 20A in each Remote Panel) --- ALTERNATIVE
Unit Allocation | Target Panel | Location & Role | Total 24VDC Load (A) | Design Load +30% (A) | Bus Capacity (A) | Redundancy / Mode | Single PSU Load | Thermal Loss (W) | Engineering Sizing Verdict
Units 1 & 2 (2 EA) | Panel CA1 | Main Control Room (C1 + C2) | 13.48 | 17.52 | 40 | 2x 20A Parallel / Redundant | 87.6% (Single) / 43.8% (Dual) | 31.7 | PASS (True N+1 Redundancy)
Unit 3 (1 EA) | Panel CA-RIO-1 | Spray Dryer 3F/7F (C3) | 6.11 | 7.94 | 20 | Single Switched Mode | 39.7% of nominal 20A | 14.3 | PASS (Optimal Load <40%)
Unit 4 (1 EA) | Panel CA-RIO-2 | Spray Dryer 6F/8F (C4) | 4.32 | 5.62 | 20 | Single Switched Mode | 28.1% of nominal 20A | 10.1 | PASS (Generous Headroom)
Unit 5 (1 EA) | Panel CA-RIO-200 | Slurry Building 2F (C5) | 4.05 | 5.27 | 20 | Single Switched Mode | 26.3% of nominal 20A | 9.5 | PASS (Generous Headroom)
4. SWITCHGEAR PROTECTION & PLC SCADA INTEGRATION DESIGN
AC Mains Infeed Protection | Each TRIO 20A unit must be protected by an upstream 2-Pole Miniature Circuit Breaker rated 10A (or 6A), Characteristic C (e.g. Schneider Acti9 iC60N 2P 10A C). Inrush current is <15A, well below the C-curve magnetic trip threshold (50-100A).
DC Output Distribution | Branch feeds from each 24VDC TRIO power supply should be segregated using multi-channel electronic circuit breakers (Phoenix Contact PTCB or C60H-DC) to ensure selective trip during field sensor/solenoid short circuits without collapsing the 24V bus.
DC OK Contact Supervision | The integrated floating relay contact (terminals 13/14, 30V AC/DC, 100mA) on each TRIO unit shall be hardwired directly into a spare channel on the 1756-IB32 digital input card (e.g. Tag: 'PSU_HEALTHY_CHx').
SCADA Alarm Logic | FactoryTalk View SE will display a yellow banner alarm if 'PSU_HEALTHY' de-energizes, alerting operators to power supply derating, AC line loss, or output under-voltage (<21.5V) prior to PLC brownout.
Push-in Terminal Cabling | AC Input: 2.5 mm² multi-strand copper (THW / H07V-K) with insulated ferrule. DC Output: 6.0 mm² or 10.0 mm² copper (Red/Black) to main 24VDC terminal blocks Px-TBDC(+) and Px-TBDC(-).