## 00_Executive_Summary
KALASIN ENGINEERING ¦ xCIP-1545 AUTOMATION SYSTEM (Ref: x2608003)
MASTER PLC I/O MAPPING & HARDWARE ALLOCATION REPORT — SPRINT 18K TPA SPRAY DRYER / JET COOKER
TOTAL INSTRUMENTS |  | PHYSICAL PLC CHANNELS |  | ACTIVE PROCESS I/O |  | SPARE CAPACITY |  | COMMON / INTERNAL |  | NETWORK REDUNDANCY
560 |  | 1,466 |  | 746 |  | 561 |  | 159 |  | 1Gbps DLR RING
Rev 3.6a Master Client Schedule |  | 5 Chassis (C1-C5), 57 Slots |  | Assigned to Process Instruments |  | 38.3% Expansion Margin (>20% Req) |  | Power Commons, CPU & Comm Ports |  | EtherNet/IP Device Level Ring CA1-RIO
1. CONTROLLOGIX 1756 CHASSIS HARDWARE & UTILIZATION DIRECTORY
Chassis Code | Overview Sheet | Chassis & Function Description | Physical Location | Hardware Model | Mounted Slots | Total Channels | Active Channels | Spare Channels | Spare Margin % | Main Power Supply | Network Link | Cabinet / Panel
C1 | C1SlotConfig | Main Controller Rack (1756-L950TPSXT CPU) | Control Cabinet CA1 (Main Control Room MCP) | 1756-A13 (13-Slot ControlLogix Chassis) | 13 Slots (S0..S12) | 306 | 174 | 103 | 33.7% | 1756-PA75 (85-265VAC) | 1Gbps DLR Ring + SCADA Uplink | CA1 (Main Control Room MCP)
C2 | C2SlotConfig | Main Expansion Rack (High-Density Field I/O) | Control Cabinet CA1 (Main Control Room MCP) | 1756-A13 (13-Slot ControlLogix Chassis) | 13 Slots (S0..S12) | 436 | 230 | 164 | 37.6% | 1756-PA75 (85-265VAC) | Internal Backplane Bridge | CA1 (Main Control Room MCP)
C3 | C3SlotConfig | Remote I/O Rack 1 (Spray Dryer / Packing Tower) | Field RIO Cabinet (Spray Dryer / Packing Tower) | 1756-A13 (13-Slot ControlLogix Chassis) | 13 Slots (S0..S12) | 350 | 169 | 135 | 38.6% | 1756-PA75 (85-265VAC) | 1Gbps DLR Fiber Ring Ring Port 1/2 | Field RIO Cabinet (Spray Dryer)
C4 | C4SlotConfig | Remote I/O Rack 2 (Upper Spray Dryer 6th/8th Floor) | Field RIO Cabinet (Spray Dryer 6th/8th Floor) | 1756-A13 (13-Slot ControlLogix Chassis) | 13 Slots (S0..S12) | 226 | 103 | 95 | 42.0% | 1756-PA75 (85-265VAC) | 1Gbps DLR Copper Ring Port 1/2 | Field RIO Cabinet (6th/8th Fl)
C5 | C5SlotConfig | Remote I/O Station 5 (Slurry Building RIO-200) | Slurry Building 2nd Floor (RIO-200) | 1756-A7 (7-Slot ControlLogix Chassis) | 5 Slots (S0..S4) | 148 | 70 | 64 | 43.2% | 1756-PB75 (24VDC Redundant) | 1Gbps DLR Copper Ring (Slurry Bldg) | Slurry Bldg 2nd Fl (RIO-200)
TOTAL SYSTEM CAPACITY (5 CHASSIS) | [5 empty] | 1466 | 746 | 561 | 38.3% | - | - | -
2. I/O SIGNAL FAMILY & MODULE SCHEDULE | [6 empty] | 3. CLIENT INSTRUMENT SCOPE & DESTINATION SUMMARY
Signal Family | Module Hardware | Signal Type | Total Pts | Active Pts | Spare Pts |  | Scope Destination | Primary Wiring Target | Loop Count | Active Pts | Typical Cable | Interface Remark
DI (24VDC Digital Input) | 1756-IB32 (32-Pt Sink/Source) | 24VDC Dry Contact / PNP | 612 | 334 | 210 |  | Direct to Main PLC (CA1/RIO) | Chassis C1, C2, C3, C4 | 454 | 676 | LiY-CY TP 1Px1.0 / CVV | Main Process Automation
DO (24VDC Digital Output) | 1756-OB32 (32-Pt Source Transistor) | 24VDC Energized Solenoids | 324 | 122 | 184 |  | Slurry Bldg RIO-200 | Chassis C5 (Slurry 2nd Fl) | 36 | 70 | LiY-CY TP / CVV Multi-core | Slurry Preparation Area
AI (4-20mA / RTD / Volts) | 1756-IF16 (16-Pt Single-Ended / Diff) | 4-20mA HART Transmitter | 468 | 252 | 164 |  | Air Heater Panel (AHTR) | AHTR Package Control Panel | 22 | 0 | Package Vendor Cables | Dryer Air Heater Skid
AO (4-20mA Analog Output) | 1756-OF8 (8-Pt Voltage / Current) | 4-20mA Control Valves (CV) | 20 | 5 | 3 |  | Heat Control Panel (HCP) | HCP Control Panel | 11 | 0 | Package Vendor Cables | Burner / Heat Package
CPU (Main Controller) | 1756-L950TPSXT (ControlLogix 5580) | Process Controller & SD/USB | 5 | 5 | 0 |  | Fire Deluge / Suppression | Suppression / Deluge Skid | 7 | 0 | Fire Rated Cable | Safety & Fire Interlock
COMM (EtherNet/IP) | 1756-EN4TR (1Gbps 2-Port DLR) | DLR Device Level Ring | 28 | 28 | 0 |  | Local Mechanical Instruments | Local Pipe / Equipment Dial | 23 | 0 | None (Direct Reading) | Pressure Gauges & Sight Glass
EMPTY (Chassis Slot Reserve) | 1756-N2 (Slot Filler Blank Plate) | Future Hardware Expansion | 9 | 0 | 0 |  | Other Package / MCC | MCC / Heat Control HTRE | 7 | 0 | Vendor / Hardwire Interlock | VSD / Motor Feeders

## 01_Instrument_IO_Mapping
KALASIN ENGINEERING ¦ MASTER INSTRUMENT SPECIFICATION & PLC I/O MAPPING
Loop-by-Loop Instrument Engineering Master (Client Rev.3.6a) Cross-Referenced to ControlLogix 1756 Standardized Slots
Item | Tag No. (Rev 3.6) | Legacy Tag | P&ID No. | Instrument Description | Instrument Type / Name | Signal Type | Signal To | Calibrated Range | Protection Class | DO | DI | AO | AI | Bus | PLC Chassis | Slot Tag(s) | PLC Module(s) | Channel Point(s) | Terminal Pin(s) | Marshaling Terminal ID(s) | Wire Mark (PLC Side) | Wire Mark (Terminal Side) | PLC Tag Name(s) | Destination Area(s) | Suggested Field Cable | Mapping Status
1 | AT-60241 | - | 325-01-602-PD-05 | Dust Analyzer Transmitter for Exhaust Duct (DTEX-22) | Dust Analyzer Transmitter | 4 - 20 mA | PLC | 5000 mg | - | - | - | - | 1 | - | C2 | C2S10 | 1756-IF16 | i RTN-0, IN-0 | 1, 2 | P2-TBAI2-1(B), P2-TBAI2-1(A) | C2S10-1/P2-TBAI2-1(B), C2S10-2/P2-TBAI2-1(A) | P2-TBAI2-1(B)/C2S10-1, P2-TBAI2-1(A)/C2S10-2 | AT-60241_AI_1, AT-60241_AI_1 | JB-602 | LiY-CY TP 2Px1.0 (Signal) + CVV 3Cx1.5 (24VDC Power) | MAPPED_PLC
2 | DPT-60201 | DPT-60901 | 325-01-602-PD-09 | Steam filter pressure | Differential Pressure Transmitter | 4 - 20 mA | PLC | 0-1 barg | - | - | - | - | 1 | - | C3 | C3S6 | 1756-IF16 | i RTN-14, IN-14 | 33, 34 | P3-TBAI1-15(B), P3-TBAI1-15(A) | C3S6-33/P3-TBAI1-15(B), C3S6-34/P3-TBAI1-15(A) | P3-TBAI1-15(B)/C3S6-33, P3-TBAI1-15(A)/C3S6-34 | DPT-60201_AI_1, DPT-60201_AI_1 | JB-606 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
3 | DPT-61301 | - | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | 4 - 20 mA | PLC | - | Ex t/d | - | - | - | 1 | - | C4 | C4S6 | 1756-IF16 | i RTN-4, IN-4 | 11, 12 | P4-TBAI2-5(B), P4-TBAI2-5(A) | C4S6-11/P4-TBAI2-5(B), C4S6-12/P4-TBAI2-5(A) | P4-TBAI2-5(B)/C4S6-11, P4-TBAI2-5(A)/C4S6-12 | DPT-61301_AI_1, DPT-61301_AI_1 | IS-JB-618 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
4 | DPT-61302 | - | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | 4 - 20 mA | PLC | - | Ex t/d | - | - | - | 1 | - | C4 | C4S6 | 1756-IF16 | i RTN-5, IN-5 | 13, 14 | P4-TBAI2-6(B), P4-TBAI2-6(A) | C4S6-13/P4-TBAI2-6(B), C4S6-14/P4-TBAI2-6(A) | P4-TBAI2-6(B)/C4S6-13, P4-TBAI2-6(A)/C4S6-14 | DPT-61302_AI_1, DPT-61302_AI_1 | IS-JB-618 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
5 | DPT-61310 | - | 325-01-613-PD-03 | Vent filter pressure | Differential Pressure Transmitter | 4 - 20 mA | PLC | - | Ex t/d | - | - | - | 1 | - | C4 | C4S6 | 1756-IF16 | i RTN-0, IN-0 | 1, 2 | P4-TBAI2-1(B), P4-TBAI2-1(A) | C4S6-1/P4-TBAI2-1(B), C4S6-2/P4-TBAI2-1(A) | P4-TBAI2-1(B)/C4S6-1, P4-TBAI2-1(A)/C4S6-2 | DPT-61310_AI_1, DPT-61310_AI_1 | IS-JB-612 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
6 | DPT-61312 | - | 325-01-613-PD-05 | Vent filter pressure | Differential Pressure Transmitter | 4 - 20 mA | PLC | - | Ex t/d | - | - | - | 1 | - | C4 | C4S6 | 1756-IF16 | i RTN-1, IN-1 | 3, 4 | P4-TBAI2-2(B), P4-TBAI2-2(A) | C4S6-3/P4-TBAI2-2(B), C4S6-4/P4-TBAI2-2(A) | P4-TBAI2-2(B)/C4S6-3, P4-TBAI2-2(A)/C4S6-4 | DPT-61312_AI_1, DPT-61312_AI_1 | IS-JB-612 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
7 | DPT-60202 | - | 325-01-602-PD-08 | Gas Pressure Differential Transmitter for Air Filter (FICA-31) | Differential Pressure Transmitter | 4 - 20 mA | PLC | -100 to 500 mBar | - | - | - | - | 1 | - | C1 | C1S11 | 1756-IF16 | i RTN-1, IN-1 | 3, 4 | P1-TBAI2-2(B), P1-TBAI2-2(A) | C1S11-3/P1-TBAI2-2(B), C1S11-4/P1-TBAI2-2(A) | P1-TBAI2-2(B)/C1S11-3, P1-TBAI2-2(A)/C1S11-4 | DPT-60202_AI_1, DPT-60202_AI_1 | JB-601 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
8 | DPT-60203 | - | 325-01-602-PD-03 | Gas Pressure Differential Transmitter for Air Filter (FICA-21) | Differential Pressure Transmitter | 4 - 20 mA | PLC | -100 to 500 mBar | - | - | - | - | 1 | - | C2 | C2S10 | 1756-IF16 | i RTN-1, IN-1 | 3, 4 | P2-TBAI2-2(B), P2-TBAI2-2(A) | C2S10-3/P2-TBAI2-2(B), C2S10-4/P2-TBAI2-2(A) | P2-TBAI2-2(B)/C2S10-3, P2-TBAI2-2(A)/C2S10-4 | DPT-60203_AI_1, DPT-60203_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
9 | FSL-20201 | - | 325-01-202-PD-01 | Slurry low flow | Flow Switch | Dry Contact | PLC | - | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-0 | 1 | P5-TBDI1-1 | C5S1-1/P5-TBDI1-1 | P5-TBDI1-1/C5S1-1 | FS-20201_DI_1 | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_RIO200
10 | FSL-40201 | - | 325-01-402-PD-01 | Slurry low flow | Flow Switch | Dry Contact | PLC | - | - | - | 1 | - | - | - | C1 | C1S4 | 1756-IB32 | IN-16 | 19 | P1-TBDI1-17 | C1S4-19/P1-TBDI1-17 | P1-TBDI1-17/C1S4-19 | FSL-40201_DI_1 | JB-401 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
11 | FSL-40202 | - | 325-01-402-PD-01 | Slurry low flow | Flow Switch | Dry Contact | PLC | - | - | - | 1 | - | - | - | C1 | C1S4 | 1756-IB32 | IN-17 | 20 | P1-TBDI1-18 | C1S4-20/P1-TBDI1-18 | P1-TBDI1-18/C1S4-20 | FSL-40202_DI_1 | JB-401 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
12 | FS-40204 | - | 325-01-402-PD-01 | Jet Cooker | Flow Switch | Dry Contact | PLC | - | - | - | 1 | - | - | - | C2 | C2S1 | 1756-IB32 | IN-0 | 1 | P2-TBDI1-1 | C2S1-1/P2-TBDI1-1 | P2-TBDI1-1/C2S1-1 | FS-40204_DI_1 | JB-402 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
13 | FS-40205 | - | 325-01-402-PD-02 | Jet Cooker | Flow Switch | Dry Contact | PLC | - | - | - | 1 | - | - | - | C2 | C2S1 | 1756-IB32 | IN-1 | 2 | P2-TBDI1-2 | C2S1-2/P2-TBDI1-2 | P2-TBDI1-2/C2S1-2 | FS-40205_DI_1 | JB-402 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
14 | FT-40201 | - | 325-01-402-PD-02 | Slurry flowrate & density check transfer line | Coriolis Flow Transmitter | 4 - 20 mA,Pulse | PLC | 0-15 m³/hr | - | - | 1 | - | 2 | - | C1 | C1S10, C1S4 | 1756-IB32, 1756-IF16 | IN-18, i RTN-0, IN-0, i RTN-1, IN-1 | 21, 1, 2, 3, 4 | P1-TBDI1-19, P1-TBAI1-1(B), P1-TBAI1-1(A), P1-TBAI1-2(B), P1-TBAI1-2(A) | C1S4-21/P1-TBDI1-19, C1S10-1/P1-TBAI1-1(B), C1S10-2/P1-TBAI1-1(A)... | P1-TBDI1-19/C1S4-21, P1-TBAI1-1(B)/C1S10-1, P1-TBAI1-1(A)/C1S10-2... | FT-40201_DI_1, FT-40201_AI_1, FT-40201_AI_1, FT-40201_AI_2, FT-40201_AI_2 | JB-401 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
15 | FT-40202 | - | 325-01-402-PD-02 | Feed Slurry Flow Transmitter for Pipe (PIPE) | Magnetic Flow Transmitter | 4 - 20 mA,Pulse | PLC | 0 to 8,000 m³/hr | - | - | 1 | - | 1 | - | C1 | C1S10, C1S4 | 1756-IB32, 1756-IF16 | IN-19, i RTN-2, IN-2 | 22, 5, 6 | P1-TBDI1-20, P1-TBAI1-3(B), P1-TBAI1-3(A) | C1S4-22/P1-TBDI1-20, C1S10-5/P1-TBAI1-3(B), C1S10-6/P1-TBAI1-3(A) | P1-TBDI1-20/C1S4-22, P1-TBAI1-3(B)/C1S10-5, P1-TBAI1-3(A)/C1S10-6 | FT-40202_DI_1, FT-40202_AI_1, FT-40202_AI_1 | JB-401 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
16 | FT-40221 | - | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter | 4 - 20 mA,Pulse | PLC | 0-6 m³/hr | - | - | 1 | - | 2 | - | C2 | C2S1, C2S9 | 1756-IB32, 1756-IF16 | IN-2, i RTN-0, IN-0, i RTN-1, IN-1 | 3, 1, 2, 3, 4 | P2-TBDI1-3, P2-TBAI1-1(B), P2-TBAI1-1(A), P2-TBAI1-2(B), P2-TBAI1-2(A) | C2S1-3/P2-TBDI1-3, C2S9-1/P2-TBAI1-1(B), C2S9-2/P2-TBAI1-1(A)... | P2-TBDI1-3/C2S1-3, P2-TBAI1-1(B)/C2S9-1, P2-TBAI1-1(A)/C2S9-2... | FT-40221_DI_1, FT-40221_AI_1, FT-40221_AI_1, FT-40221_AI_2, FT-40221_AI_2 | JB-402 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
17 | FT-40222 | - | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter | 4 - 20 mA,Pulse | PLC | 0-850 kg/hr | - | - | 1 | - | 2 | - | C2 | C2S1, C2S9 | 1756-IB32, 1756-IF16 | IN-3, i RTN-2, IN-2, i RTN-3, IN-3 | 4, 5, 6, 7, 8 | P2-TBDI1-4, P2-TBAI1-3(B), P2-TBAI1-3(A), P2-TBAI1-4(B), P2-TBAI1-4(A) | C2S1-4/P2-TBDI1-4, C2S9-5/P2-TBAI1-3(B), C2S9-6/P2-TBAI1-3(A)... | P2-TBDI1-4/C2S1-4, P2-TBAI1-3(B)/C2S9-5, P2-TBAI1-3(A)/C2S9-6... | FT-40222_DI_1, FT-40222_AI_1, FT-40222_AI_1, FT-40222_AI_2, FT-40222_AI_2 | JB-402 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
18 | FT-60221 | - | 325-01-602-PD-04 | Cool air Flow | Thermal Mass Flow Transmitter | 4 - 20 mA | PLC | 2500 m3/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-1, IN-1 | 3, 4 | P3-TBAI2-2(B), P3-TBAI2-2(A) | C3S7-3/P3-TBAI2-2(B), C3S7-4/P3-TBAI2-2(A) | P3-TBAI2-2(B)/C3S7-3, P3-TBAI2-2(A)/C3S7-4 | FT-60221_AI_1, FT-60221_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
19 | FT-60201 | - | 325-01-602-PD-08 | Gas Flow Transmitter for Cooling Conveying Cold Air Duct (DTCA-32) | Thermal Mass Flow Transmitter | 4 - 20 mA | PLC | 70000 m3/h | - | - | - | - | 1 | - | C1 | C1S11 | 1756-IF16 | i RTN-2, IN-2 | 5, 6 | P1-TBAI2-3(B), P1-TBAI2-3(A) | C1S11-5/P1-TBAI2-3(B), C1S11-6/P1-TBAI2-3(A) | P1-TBAI2-3(B)/C1S11-5, P1-TBAI2-3(A)/C1S11-6 | FT-60201_AI_1, FT-60201_AI_1 | JB-601 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
20 | FT-60210 | - | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) | Thermal Mass Flow Transmitter | 4 - 20 mA | PLC | 126000 m3/h | - | - | - | - | 2 | - | C3 | C3S6 | 1756-IF16 | i RTN-9, IN-9, i RTN-11, IN-11 | 21, 22, 25, 26 | P3-TBAI1-10(B), P3-TBAI1-10(A), P3-TBAI1-12(B), P3-TBAI1-12(A) | C3S6-21/P3-TBAI1-10(B), C3S6-22/P3-TBAI1-10(A), C3S6-25/P3-TBAI1-12(B)... | P3-TBAI1-10(B)/C3S6-21, P3-TBAI1-10(A)/C3S6-22, P3-TBAI1-12(B)/C3S6-25... | FT-60210_AI_1, FT-60210_AI_1, FT-60210_AI_2, FT-60210_AI_2 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
21 | FT-60211 | - | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) | Thermal Mass Flow Transmitter | 4 - 20 mA | PLC | 126000 m3/h | - | - | - | - | 2 | - | C3 | C3S6 | 1756-IF16 | i RTN-10, IN-10, i RTN-12, IN-12 | 23, 24, 29, 30 | P3-TBAI1-11(B), P3-TBAI1-11(A), P3-TBAI1-13(B), P3-TBAI1-13(A) | C3S6-23/P3-TBAI1-11(B), C3S6-24/P3-TBAI1-11(A), C3S6-29/P3-TBAI1-13(B)... | P3-TBAI1-11(B)/C3S6-23, P3-TBAI1-11(A)/C3S6-24, P3-TBAI1-13(B)/C3S6-29... | FT-60211_AI_1, FT-60211_AI_1, FT-60211_AI_2, FT-60211_AI_2 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
22 | FT-60261FA | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #1 (AMTV-11A) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-2, IN-2 | 5, 6 | P3-TBAI2-3(B), P3-TBAI2-3(A) | C3S7-5/P3-TBAI2-3(B), C3S7-6/P3-TBAI2-3(A) | P3-TBAI2-3(B)/C3S7-5, P3-TBAI2-3(A)/C3S7-6 | FT-60261FA_AI_1, FT-60261FA_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
23 | FT-60261FB | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #2 (AMTV-11A) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-3, IN-3 | 7, 8 | P3-TBAI2-4(B), P3-TBAI2-4(A) | C3S7-7/P3-TBAI2-4(B), C3S7-8/P3-TBAI2-4(A) | P3-TBAI2-4(B)/C3S7-7, P3-TBAI2-4(A)/C3S7-8 | FT-60261FB_AI_1, FT-60261FB_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
24 | FT-60261FC | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #3 (AMTV-11A) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-4, IN-4 | 11, 12 | P3-TBAI2-5(B), P3-TBAI2-5(A) | C3S7-11/P3-TBAI2-5(B), C3S7-12/P3-TBAI2-5(A) | P3-TBAI2-5(B)/C3S7-11, P3-TBAI2-5(A)/C3S7-12 | FT-60261FC_AI_1, FT-60261FC_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
25 | FT-60261FD | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #4 (AMTV-11A) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-5, IN-5 | 13, 14 | P3-TBAI2-6(B), P3-TBAI2-6(A) | C3S7-13/P3-TBAI2-6(B), C3S7-14/P3-TBAI2-6(A) | P3-TBAI2-6(B)/C3S7-13, P3-TBAI2-6(A)/C3S7-14 | FT-60261FD_AI_1, FT-60261FD_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
26 | FT-60262FE | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #5 (AMTV-11B) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-6, IN-6 | 15, 16 | P3-TBAI2-7(B), P3-TBAI2-7(A) | C3S7-15/P3-TBAI2-7(B), C3S7-16/P3-TBAI2-7(A) | P3-TBAI2-7(B)/C3S7-15, P3-TBAI2-7(A)/C3S7-16 | FT-60262FE_AI_1, FT-60262FE_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
27 | FT-60262FF | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #6 (AMTV-11B) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-7, IN-7 | 17, 18 | P3-TBAI2-8(B), P3-TBAI2-8(A) | C3S7-17/P3-TBAI2-8(B), C3S7-18/P3-TBAI2-8(A) | P3-TBAI2-8(B)/C3S7-17, P3-TBAI2-8(A)/C3S7-18 | FT-60262FF_AI_1, FT-60262FF_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
28 | FT-60262FG | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #7 (AMTV-11B) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-8, IN-8 | 19, 20 | P3-TBAI2-9(B), P3-TBAI2-9(A) | C3S7-19/P3-TBAI2-9(B), C3S7-20/P3-TBAI2-9(A) | P3-TBAI2-9(B)/C3S7-19, P3-TBAI2-9(A)/C3S7-20 | FT-60262FG_AI_1, FT-60262FG_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
29 | FT-60262FH | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #8 (AMTV-11B) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-9, IN-9 | 21, 22 | P3-TBAI2-10(B), P3-TBAI2-10(A) | C3S7-21/P3-TBAI2-10(B), C3S7-22/P3-TBAI2-10(A) | P3-TBAI2-10(B)/C3S7-21, P3-TBAI2-10(A)/C3S7-22 | FT-60262FH_AI_1, FT-60262FH_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
30 | FT-60263FJ | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #9 (AMTV-11C) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-10, IN-10 | 23, 24 | P3-TBAI2-11(B), P3-TBAI2-11(A) | C3S7-23/P3-TBAI2-11(B), C3S7-24/P3-TBAI2-11(A) | P3-TBAI2-11(B)/C3S7-23, P3-TBAI2-11(A)/C3S7-24 | FT-60263FJ_AI_1, FT-60263FJ_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
31 | FT-60263FK | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #10 (AMTV-11C) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-11, IN-11 | 25, 26 | P3-TBAI2-12(B), P3-TBAI2-12(A) | C3S7-25/P3-TBAI2-12(B), C3S7-26/P3-TBAI2-12(A) | P3-TBAI2-12(B)/C3S7-25, P3-TBAI2-12(A)/C3S7-26 | FT-60263FK_AI_1, FT-60263FK_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
32 | FT-60263FL | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #11 (AMTV-11C) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-12, IN-12 | 29, 30 | P3-TBAI2-13(B), P3-TBAI2-13(A) | C3S7-29/P3-TBAI2-13(B), C3S7-30/P3-TBAI2-13(A) | P3-TBAI2-13(B)/C3S7-29, P3-TBAI2-13(A)/C3S7-30 | FT-60263FL_AI_1, FT-60263FL_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
33 | FT-60263FM | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #12 (AMTV-11C) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-13, IN-13 | 31, 32 | P3-TBAI2-14(B), P3-TBAI2-14(A) | C3S7-31/P3-TBAI2-14(B), C3S7-32/P3-TBAI2-14(A) | P3-TBAI2-14(B)/C3S7-31, P3-TBAI2-14(A)/C3S7-32 | FT-60263FM_AI_1, FT-60263FM_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
34 | FT-60264FN | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #13 (AMTV-11D) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-14, IN-14 | 33, 34 | P3-TBAI2-15(B), P3-TBAI2-15(A) | C3S7-33/P3-TBAI2-15(B), C3S7-34/P3-TBAI2-15(A) | P3-TBAI2-15(B)/C3S7-33, P3-TBAI2-15(A)/C3S7-34 | FT-60264FN_AI_1, FT-60264FN_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
35 | FT-60264FP | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #14 (AMTV-11D) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-15, IN-15 | 35, 36 | P3-TBAI2-16(B), P3-TBAI2-16(A) | C3S7-35/P3-TBAI2-16(B), C3S7-36/P3-TBAI2-16(A) | P3-TBAI2-16(B)/C3S7-35, P3-TBAI2-16(A)/C3S7-36 | FT-60264FP_AI_1, FT-60264FP_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
36 | FT-60264FQ | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #15 (AMTV-11D) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S8 | 1756-IF16 | i RTN-0, IN-0 | 1, 2 | P3-TBAI3-1(B), P3-TBAI3-1(A) | C3S8-1/P3-TBAI3-1(B), C3S8-2/P3-TBAI3-1(A) | P3-TBAI3-1(B)/C3S8-1, P3-TBAI3-1(A)/C3S8-2 | FT-60264FQ_AI_1, FT-60264FQ_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
37 | FT-60264FR | - | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #16 (AMTV-11D) | Ultrasonic Flow Transmitter | 4 - 20 mA | PLC | 0 to 100 l/h | - | - | - | - | 1 | - | C3 | C3S8 | 1756-IF16 | i RTN-1, IN-1 | 3, 4 | P3-TBAI3-2(B), P3-TBAI3-2(A) | C3S8-3/P3-TBAI3-2(B), C3S8-4/P3-TBAI3-2(A) | P3-TBAI3-2(B)/C3S8-3, P3-TBAI3-2(A)/C3S8-4 | FT-60264FR_AI_1, FT-60264FR_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
38 | FT-61307 | - | 325-01-613-PD-04 | Compressed air Flow | Thermal Mass Flow Transmitter | 4 - 20 mA | PLC | 0 - 1000 m3/hr | - | - | - | - | 1 | - | C1 | C1S11 | 1756-IF16 | i RTN-4, IN-4 | 11, 12 | P1-TBAI2-5(B), P1-TBAI2-5(A) | C1S11-11/P1-TBAI2-5(B), C1S11-12/P1-TBAI2-5(A) | P1-TBAI2-5(B)/C1S11-11, P1-TBAI2-5(A)/C1S11-12 | FT-61307_AI_1, FT-61307_AI_1 | JB-601 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
39 | FT-60203 | FT-60901 | 325-01-602-PD-09 | Culinary steam feed to Spray dryer | Vortex Flow Transmitter | 4 - 20 mA | PLC | 0 - 7000 kg/hr | - | - | 1 | - | 1 | - | C3 | C3S1, C3S6 | 1756-IB32, 1756-IF16 | IN-16, i RTN-15, IN-15 | 19, 35, 36 | P3-TBDI1-17, P3-TBAI1-16(B), P3-TBAI1-16(A) | C3S1-19/P3-TBDI1-17, C3S6-35/P3-TBAI1-16(B), C3S6-36/P3-TBAI1-16(A) | P3-TBDI1-17/C3S1-19, P3-TBAI1-16(B)/C3S6-35, P3-TBAI1-16(A)/C3S6-36 | FT-60203_DI_1, FT-60203_AI_1, FT-60203_AI_1 | JB-606 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
40 | FT-60202 | FT-60902 | 325-01-602-PD-09 | Steam feed to Spray dryer | Vortex Flow Transmitter | 4 - 20 mA | PLC | 0 - 2000 kg/hr | - | - | 1 | - | 1 | - | C2 | C2S10, C2S2 | 1756-IB32, 1756-IF16 | IN-0, i RTN-2, IN-2 | 1, 5, 6 | P2-TBDI2-1, P2-TBAI2-3(B), P2-TBAI2-3(A) | C2S2-1/P2-TBDI2-1, C2S10-5/P2-TBAI2-3(B), C2S10-6/P2-TBAI2-3(A) | P2-TBDI2-1/C2S2-1, P2-TBAI2-3(B)/C2S10-5, P2-TBAI2-3(A)/C2S10-6 | FT-60202_DI_1, FT-60202_AI_1, FT-60202_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
41 | FT-60204 | FT-61101 | 325-01-602-PD-10 | Compressed air Flow | Thermal Mass Flow Transmitter | 4 - 20 mA | PLC | 0 - 1000 m3/hr | - | - | - | - | 1 | - | C1 | C1S11 | 1756-IF16 | i RTN-3, IN-3 | 7, 8 | P1-TBAI2-4(B), P1-TBAI2-4(A) | C1S11-7/P1-TBAI2-4(B), C1S11-8/P1-TBAI2-4(A) | P1-TBAI2-4(B)/C1S11-7, P1-TBAI2-4(A)/C1S11-8 | FT-60204_AI_1, FT-60204_AI_1 | JB-601 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
42 | FT-936201 | FT-90301 | 325-01-930-PD-01 | Process Water | Magnetic Flow Transmitter | 4 - 20 mA,Pulse | PLC | 0-1000kg/m³ | - | - | 1 | - | 1 | - | C5 | C5S1, C5S4 | 1756-IB32, 1756-IF16 | IN-2, i RTN-3, IN-3 | 3, 7, 8 | P5-TBDI1-3, P5-TBAI1-4(B), P5-TBAI1-4(A) | C5S1-3/P5-TBDI1-3, C5S4-7/P5-TBAI1-4(B), C5S4-8/P5-TBAI1-4(A) | P5-TBDI1-3/C5S1-3, P5-TBAI1-4(B)/C5S4-7, P5-TBAI1-4(A)/C5S4-8 | FT-936201_DI_1, FT-936201_AI_1, FT-936201_AI_1 | RIO-200 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_RIO200
43 | FT-936202 | FT-93001 | 325-01-930-PD-02 | Process Water | Magnetic Flow Transmitter | 4 - 20 mA,Pulse | PLC | 0 - 20 m3/ hr | - | - | 1 | - | 1 | - | C5 | C5S1, C5S4 | 1756-IB32, 1756-IF16 | IN-3, i RTN-4, IN-4 | 4, 11, 12 | P5-TBDI1-4, P5-TBAI1-5(B), P5-TBAI1-5(A) | C5S1-4/P5-TBDI1-4, C5S4-11/P5-TBAI1-5(B), C5S4-12/P5-TBAI1-5(A) | P5-TBDI1-4/C5S1-4, P5-TBAI1-5(B)/C5S4-11, P5-TBAI1-5(A)/C5S4-12 | FT-936202_DI_1, FT-936202_AI_1, FT-936202_AI_1 | RIO-200 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_RIO200
44 | HS-61307A | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
45 | HS-61307B | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
46 | HS-61307C | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
47 | HS-61307D | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
48 | HS-61307E | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
49 | HS-61307F | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
50 | HS-61307G | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
51 | HS-61307H | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
52 | HS-61307I | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
53 | HS-61307J | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
54 | HS-61307K | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
55 | HS-61307L | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
56 | HS-61307M | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
57 | HS-61307N | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
58 | HS-61307O | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
59 | HS-61307P | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
60 | HS-61307Q | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
61 | HS-61307R | - | 325-01-613-PD-03 | Start/Stop | Hand Switch | Dry Contact | PLC | - | Ex d | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
62 | HV-40203 | HV-4106 | 325-01-402-PD-01 | Slurry Drain tank TS-40201 | Valve With Position Switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S4 | 1756-IB32 | IN-22 | 25 | P1-TBDI1-23 | C1S4-25/P1-TBDI1-23 | P1-TBDI1-23/C1S4-25 | HV-40203_DI_1 | JB-401 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
63 | HV-40201 | HV-4108 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S4 | 1756-IB32 | IN-20 | 23 | P1-TBDI1-21 | C1S4-23/P1-TBDI1-21 | P1-TBDI1-21/C1S4-23 | HV-40201_DI_1 | JB-401 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
64 | HV-40204 | HV-4126 | 325-01-402-PD-01 | Slurry Drain tank TS-40202 | Valve With Position Switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S4 | 1756-IB32 | IN-23 | 26 | P1-TBDI1-24 | C1S4-26/P1-TBDI1-24 | P1-TBDI1-24/C1S4-26 | HV-40204_DI_1 | JB-401 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
65 | HV-40202 | HV-4128 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S4 | 1756-IB32 | IN-21 | 24 | P1-TBDI1-22 | C1S4-24/P1-TBDI1-22 | P1-TBDI1-22/C1S4-24 | HV-40202_DI_1 | JB-401 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
66 | HV-40206 | HV-4208 | 325-01-402-PD-01 | Slurry Drain tank TS-40203 | Valve With Position Switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S4 | 1756-IB32 | IN-25 | 28 | P1-TBDI1-26 | C1S4-28/P1-TBDI1-26 | P1-TBDI1-26/C1S4-28 | HV-40206_DI_1 | JB-401 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
67 | HV-40205 | HV-4210 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S4 | 1756-IB32 | IN-24 | 27 | P1-TBDI1-25 | C1S4-27/P1-TBDI1-25 | P1-TBDI1-25/C1S4-27 | HV-40205_DI_1 | JB-401 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
68 | HV-40207 | - | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S1 | 1756-IB32 | IN-4 | 5 | P2-TBDI1-5 | C2S1-5/P2-TBDI1-5 | P2-TBDI1-5/C2S1-5 | HV-40207_DI_1 | JB-402 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
69 | HV-40208 | - | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S1 | 1756-IB32 | IN-5 | 6 | P2-TBDI1-6 | C2S1-6/P2-TBDI1-6 | P2-TBDI1-6/C2S1-6 | HV-40208_DI_1 | JB-402 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
70 | LSH-60230 | - | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-21) | Level switch | Dry Contact | PLC | - | Ex t/d | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-3 | 4 | P4-TBDI1-4 | C4S1-4/P4-TBDI1-4 | P4-TBDI1-4/C4S1-4 | LSH-60230_DI_1 | IS-JB-603 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
71 | LSH-60231 | - | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-22) | Level switch | Dry Contact | PLC | - | Ex t/d | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-4 | 5 | P4-TBDI1-5 | C4S1-5/P4-TBDI1-5 | P4-TBDI1-5/C4S1-5 | LSH-60231_DI_1 | IS-JB-603 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
72 | LSH-60240 | - | 325-01-602-PD-05 | Powder Level Switch High for Bag House (BGHS-21) | Level switch | Dry Contact | PLC | - | Ex t/d | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-5 | 6 | P4-TBDI1-6 | C4S1-6/P4-TBDI1-6 | P4-TBDI1-6/C4S1-6 | LSH-60240_DI_1 | IS-JB-603 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
73 | LSH-60250 | - | 325-01-602-PD-05 | Water Level Switch High for Fire Deluge Pipe (FWDP-21) | Level switch | Dry Contact | PLC | - | - | - | 1 | - | - | - | C3 | C3S1 | 1756-IB32 | IN-17 | 20 | P3-TBDI1-18 | C3S1-20/P3-TBDI1-18 | P3-TBDI1-18/C3S1-20 | LSH-60250_DI_1 | JB-606 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
74 | LSH-60251 | - | 325-01-602-PD-04 | Water Level Switch High for Fire Deluge Pipe (FWDP-22) | Level switch | Dry Contact | PLC | - | - | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-1 | 2 | P2-TBDI2-2 | C2S2-2/P2-TBDI2-2 | P2-TBDI2-2/C2S2-2 | LSH-60251_DI_1 | JB-602 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
75 | LSL-60201 | LSL-61101 | 325-01-602-PD-11 | Level low switch | Level switch | Dry Contact | PLC | - | - | - | 1 | - | - | - | C1 | C1S6 | 1756-IB32 | IN-18 | 21 | P1-TBDI3-19 | C1S6-21/P1-TBDI3-19 | P1-TBDI3-19/C1S6-21 | LSL-60201_DI_1 | JB-601 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
76 | LSH-61301 | - | 325-01-613-PD-01 | Level alarm high | Level switch | Dry Contact | PLC | - | Ex t/d | - | 1 | - | - | - | C4 | C4S3 | 1756-IB32 | IN-1 | 2 | P4-TBDI3-2 | C4S3-2/P4-TBDI3-2 | P4-TBDI3-2/C4S3-2 | LSH-61301_DI_1 | IS-JB-618 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
77 | LSL-61302 | - | 325-01-613-PD-01 | Level alarm low | Level switch | Dry Contact | PLC | - | Ex t/d | - | 1 | - | - | - | C4 | C4S3 | 1756-IB32 | IN-5 | 6 | P4-TBDI3-6 | C4S3-6/P4-TBDI3-6 | P4-TBDI3-6/C4S3-6 | LSL-61302_DI_1 | IS-JB-618 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
78 | LS-61303 | - | 325-01-613-PD-01 | Level switch | Level switch | Dry Contact | PLC | - | Ex t/d | - | 1 | - | - | - | C3 | C3S3 | 1756-IB32 | IN-4 | 5 | P3-TBDI3-5 | C3S3-5/P3-TBDI3-5 | P3-TBDI3-5/C3S3-5 | LS-61303_DI_1 | JB-618 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
79 | LSH-61304 | - | 325-01-613-PD-03 | Big bag level alarm high | Level switch | Dry Contact | PLC | - | Ex t/d | - | 1 | - | - | - | C4 | C4S2 | 1756-IB32 | IN-2 | 3 | P4-TBDI2-3 | C4S2-3/P4-TBDI2-3 | P4-TBDI2-3/C4S2-3 | LSH-61304_DI_1 | IS-JB-612 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
80 | LSH-61305 | - | 325-01-613-PD-05 | Big bag level alarm high | Level switch | Dry Contact | PLC | - | Ex t/d | - | 1 | - | - | - | C4 | C4S2 | 1756-IB32 | IN-3 | 4 | P4-TBDI2-4 | C4S2-4/P4-TBDI2-4 | P4-TBDI2-4/C4S2-4 | LSH-61305_DI_1 | IS-JB-612 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
81 | LSH-61306 | - | 325-01-613-PD-01 | Level alarm high | Level switch | Dry Contact | PLC | - | Ex t/d | - | 1 | - | - | - | C4 | C4S3 | 1756-IB32 | IN-3 | 4 | P4-TBDI3-4 | C4S3-4/P4-TBDI3-4 | P4-TBDI3-4/C4S3-4 | LSH-61306_DI_1 | IS-JB-618 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
82 | LSH-61307 | - | 325-01-613-PD-01 | High Level alarm reject screen | Level switch | Dry Contact | PLC | - | Ex t/d | - | 1 | - | - | - | C4 | C4S2 | 1756-IB32 | IN-4 | 5 | P4-TBDI2-5 | C4S2-5/P4-TBDI2-5 | P4-TBDI2-5/C4S2-5 | LSH-61307_DI_1 | IS-JB-612 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
83 | LSH-61308 | - | 325-01-613-PD-01 | High Level alarm Cooling cyclone | Level switch | Dry Contact | PLC | - | Ex t/d | - | 1 | - | - | - | C4 | C4S3 | 1756-IB32 | IN-4 | 5 | P4-TBDI3-5 | C4S3-5/P4-TBDI3-5 | P4-TBDI3-5/C4S3-5 | LSH-61308_DI_1 | IS-JB-618 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
84 | LSH-61312 | - | 325-01-613-PD-05 | Level alarm high | Level switch | Dry Contact | PLC | - | Ex t/d | - | 1 | - | - | - | C4 | C4S2 | 1756-IB32 | IN-5 | 6 | P4-TBDI2-6 | C4S2-6/P4-TBDI2-6 | P4-TBDI2-6/C4S2-6 | LSH-61312_DI_1 | IS-JB-612 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
85 | LSL-814201 | LSL-81001 | 325-01-814-PD-01 | Low Level alarm |  | Dry Contact | PLC | - | Ex t/d | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-4 | 5 | P5-TBDI1-5 | C5S1-5/P5-TBDI1-5 | P5-TBDI1-5/C5S1-5 | LSL-814201_DI_1 | RIO-200 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_RIO200
86 | LT-40201 | LT-40101 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 1 | Level transmitter | 4 - 20 mA | PLC | 0 - 10 m. | - | - | - | - | 1 | - | C1 | C1S10 | 1756-IF16 | i RTN-4, IN-4 | 11, 12 | P1-TBAI1-5(B), P1-TBAI1-5(A) | C1S10-11/P1-TBAI1-5(B), C1S10-12/P1-TBAI1-5(A) | P1-TBAI1-5(B)/C1S10-11, P1-TBAI1-5(A)/C1S10-12 | LT-40201_AI_1, LT-40201_AI_1 | JB-401 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
87 | LT-40202 | LT-40102 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 2 | Level transmitter | 4 - 20 mA | PLC | 0 - 10 m. | - | - | - | - | 1 | - | C1 | C1S10 | 1756-IF16 | i RTN-5, IN-5 | 13, 14 | P1-TBAI1-6(B), P1-TBAI1-6(A) | C1S10-13/P1-TBAI1-6(B), C1S10-14/P1-TBAI1-6(A) | P1-TBAI1-6(B)/C1S10-13, P1-TBAI1-6(A)/C1S10-14 | LT-40202_AI_1, LT-40202_AI_1 | JB-401 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
88 | LT-40203 | LT-40201 | 325-01-402-PD-02 | Level transmitter in Spray dryer infeed tank | Level transmitter | 4 - 20 mA | PLC | 0 - 10 m. | - | - | - | - | 1 | - | C1 | C1S10 | 1756-IF16 | i RTN-3, IN-3 | 7, 8 | P1-TBAI1-4(B), P1-TBAI1-4(A) | C1S10-7/P1-TBAI1-4(B), C1S10-8/P1-TBAI1-4(A) | P1-TBAI1-4(B)/C1S10-7, P1-TBAI1-4(A)/C1S10-8 | LT-40203_AI_1, LT-40203_AI_1 | JB-401 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
89 | LT-61301 | - | 325-01-613-PD-01 | Level powder in silo | Level transmitter | 4 - 20 mA | PLC | - | Ex ia | - | - | - | 1 | - | C4 | C4S6 | 1756-IF16 | i RTN-6, IN-6 | 15, 16 | P4-TBAI2-7(B), P4-TBAI2-7(A) | C4S6-15/P4-TBAI2-7(B), C4S6-16/P4-TBAI2-7(A) | P4-TBAI2-7(B)/C4S6-15, P4-TBAI2-7(A)/C4S6-16 | LT-61301_AI_1, LT-61301_AI_1 | IS-JB-618 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
90 | pHT-40201 | pHT-40101 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 1 | pH Analyzer | 4 - 20 mA | PLC | 0-14 | - | - | 1 | - | 1 | - | C1 | C1S10 | 1756-IF16 | i RTN-6, IN-6 | 15, 16 | P1-TBAI1-7(B), P1-TBAI1-7(A) | C1S10-15/P1-TBAI1-7(B), C1S10-16/P1-TBAI1-7(A) | P1-TBAI1-7(B)/C1S10-15, P1-TBAI1-7(A)/C1S10-16 | pHT-40201_AI_1, pHT-40201_AI_1 | JB-401 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
91 | pHT-40202 | pHT-40102 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 2 | pH Analyzer | 4 - 20 mA | PLC | 0-14 | - | - | 1 | - | 1 | - | C1 | C1S10 | 1756-IF16 | i RTN-7, IN-7 | 17, 18 | P1-TBAI1-8(B), P1-TBAI1-8(A) | C1S10-17/P1-TBAI1-8(B), C1S10-18/P1-TBAI1-8(A) | P1-TBAI1-8(B)/C1S10-17, P1-TBAI1-8(A)/C1S10-18 | pHT-40202_AI_1, pHT-40202_AI_1 | JB-401 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
92 | PSL-60220 | - | 325-01-602-PD-04 | Gas Pressure Switch Low for Spray Chamber (CHAM-21) | Pressure switch | Dry Contact | Hard Wired to MCC FANE-21 | -0.01 mbar | - | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-2 | 3 | P2-TBDI2-3 | C2S2-3/P2-TBDI2-3 | P2-TBDI2-3/C2S2-3 | PSL-60220_DI_1 | JB-602 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
93 | PSL-61301 | - | 325-01-613-PD-01 | Pressure alarm low | Pressure switch | Dry Contact | PLC | 0.3-0.7barg | - | - | 1 | - | - | - | C3 | C3S3 | 1756-IB32 | IN-5 | 6 | P3-TBDI3-6 | C3S3-6/P3-TBDI3-6 | P3-TBDI3-6/C3S3-6 | PSL-61301_DI_1 | JB-618 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
94 | PSL-61302 | - | 325-01-613-PD-01 | Pressure alarm low | Pressure switch | Dry Contact | PLC | 40 mbarg | - | - | 1 | - | - | - | C3 | C3S3 | 1756-IB32 | IN-6 | 7 | P3-TBDI3-7 | C3S3-7/P3-TBDI3-7 | P3-TBDI3-7/C3S3-7 | PSL-61302_DI_1 | JB-618 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
95 | PSL-61305 | - | 325-01-613-PD-03 | Pressure alarm low | Pressure switch | Dry Contact | PLC | - | - | - | 1 | - | - | - | C3 | C3S2 | 1756-IB32 | IN-0 | 1 | P3-TBDI2-1 | C3S2-1/P3-TBDI2-1 | P3-TBDI2-1/C3S2-1 | PSL-61305_DI_1 | JB-612 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
96 | PSL-61306 | - | 325-01-613-PD-05 | Pressure alarm low | Pressure switch | Dry Contact | PLC | - | - | - | 1 | - | - | - | C3 | C3S2 | 1756-IB32 | IN-1 | 2 | P3-TBDI2-2 | C3S2-2/P3-TBDI2-2 | P3-TBDI2-2/C3S2-2 | PSL-61306_DI_1 | JB-612 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
97 | PSL-61311 | - | 325-01-613-PD-04 | Pressure alarm low | Pressure switch | Dry Contact | PLC | - | - | - | 1 | - | - | - | C3 | C3S3 | 1756-IB32 | IN-7 | 8 | P3-TBDI3-8 | C3S3-8/P3-TBDI3-8 | P3-TBDI3-8/C3S3-8 | PSL-61311_DI_1 | JB-618 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
98 | PT-40201 | - | 325-01-402-PD-02 | Pressure Transmitter for Inlet Filter Strainer (FSTR-11) | Pressure Transmitter | 4 - 20 mA | PLC | -100 to 500 mBar | - | - | - | - | 1 | - | C1 | C1S10 | 1756-IF16 | i RTN-8, IN-8 | 19, 20 | P1-TBAI1-9(B), P1-TBAI1-9(A) | C1S10-19/P1-TBAI1-9(B), C1S10-20/P1-TBAI1-9(A) | P1-TBAI1-9(B)/C1S10-19, P1-TBAI1-9(A)/C1S10-20 | PT-40201_AI_1, PT-40201_AI_1 | JB-401 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
99 | PT-40202 | - | 325-01-402-PD-02 | Feed Slurry Pressure Transmitter for Pipe (PIPE) | Pressure Transmitter | 4 - 20 mA | PLC | 0 - 10'barg | - | - | - | - | 1 | - | C1 | C1S10 | 1756-IF16 | i RTN-9, IN-9 | 21, 22 | P1-TBAI1-10(B), P1-TBAI1-10(A) | C1S10-21/P1-TBAI1-10(B), C1S10-22/P1-TBAI1-10(A) | P1-TBAI1-10(B)/C1S10-21, P1-TBAI1-10(A)/C1S10-22 | PT-40202_AI_1, PT-40202_AI_1 | JB-401 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
100 | PT-40222 | - | 325-01-402-PD-02 | Jet Cooker | Pressure Transmitter | 4 - 20 mA | PLC | 0 - 12'barg | - | - | - | - | 1 | - | C2 | C2S9 | 1756-IF16 | i RTN-4, IN-4 | 11, 12 | P2-TBAI1-5(B), P2-TBAI1-5(A) | C2S9-11/P2-TBAI1-5(B), C2S9-12/P2-TBAI1-5(A) | P2-TBAI1-5(B)/C2S9-11, P2-TBAI1-5(A)/C2S9-12 | PT-40222_AI_1, PT-40222_AI_1 | JB-402 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
101 | PT-60201 | - | 325-01-602-PD-02 | Steam feed to Spray dryer | Pressure Transmitter | 4 - 20 mA | PLC | 0 - 20 bar | - | - | - | - | 1 | - | C3 | C3S8 | 1756-IF16 | i RTN-2, IN-2 | 5, 6 | P3-TBAI3-3(B), P3-TBAI3-3(A) | C3S8-5/P3-TBAI3-3(B), C3S8-6/P3-TBAI3-3(A) | P3-TBAI3-3(B)/C3S8-5, P3-TBAI3-3(A)/C3S8-6 | PT-60201_AI_1, PT-60201_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
102 | PT-60202 | PT-60202 | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter | 4 - 20 mA | PLC | 0 to 500 bar | - | - | - | - | 1 | - | C1 | C1S10 | 1756-IF16 | i RTN-10, IN-10 | 23, 24 | P1-TBAI1-11(B), P1-TBAI1-11(A) | C1S10-23/P1-TBAI1-11(B), C1S10-24/P1-TBAI1-11(A) | P1-TBAI1-11(B)/C1S10-23, P1-TBAI1-11(A)/C1S10-24 | PT-60202_AI_1, PT-60202_AI_1 | JB-401 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
103 | PT-60203 | - | 325-01-602-PD-08 | Gas Pressure Transmitter for Cool Air Duct (DTCA-32) | Pressure Transmitter | 4 - 20 mA | PLC | 0 - 0.1 mbar | - | - | - | - | 1 | - | C1 | C1S11 | 1756-IF16 | i RTN-5, IN-5 | 13, 14 | P1-TBAI2-6(B), P1-TBAI2-6(A) | C1S11-13/P1-TBAI2-6(B), C1S11-14/P1-TBAI2-6(A) | P1-TBAI2-6(B)/C1S11-13, P1-TBAI2-6(A)/C1S11-14 | PT-60203_AI_1, PT-60203_AI_1 | JB-601 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
104 | PT-60210 | - | 325-01-602-PD-03 | Gas Pressure Transmitter for Hot Air Duct (DTHA-21) | Pressure Transmitter | 4 - 20 mA | PLC | 0 - 0.1 mbar | - | - | - | - | 1 | - | C2 | C2S10 | 1756-IF16 | i RTN-3, IN-3 | 7, 8 | P2-TBAI2-4(B), P2-TBAI2-4(A) | C2S10-7/P2-TBAI2-4(B), C2S10-8/P2-TBAI2-4(A) | P2-TBAI2-4(B)/C2S10-7, P2-TBAI2-4(A)/C2S10-8 | PT-60210_AI_1, PT-60210_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
105 | PT-60215 | - | 325-01-602-PD-03 | 15% Polypropylene Glycol Pressure Indicator Transmitter for Heat Recovery Pumping Skid (PUCF-21) | Pressure Transmitter | 4 - 20 mA | PLC | 0 - 6 bar | - | - | - | - | 1 | - | C2 | C2S10 | 1756-IF16 | i RTN-4, IN-4 | 11, 12 | P2-TBAI2-5(B), P2-TBAI2-5(A) | C2S10-11/P2-TBAI2-5(B), C2S10-12/P2-TBAI2-5(A) | P2-TBAI2-5(B)/C2S10-11, P2-TBAI2-5(A)/C2S10-12 | PT-60215_AI_1, PT-60215_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
106 | PT-60216 | - | 325-01-602-PD-03 | Gas Pressure Transmitter for Combustion Air Burner Duct (DTCB-21) | Pressure Transmitter | 4 - 20 mA | PLC | 0 - 100 mbar | - | - | - | - | 1 | - | C2 | C2S10 | 1756-IF16 | i RTN-5, IN-5 | 13, 14 | P2-TBAI2-6(B), P2-TBAI2-6(A) | C2S10-13/P2-TBAI2-6(B), C2S10-14/P2-TBAI2-6(A) | P2-TBAI2-6(B)/C2S10-13, P2-TBAI2-6(A)/C2S10-14 | PT-60216_AI_1, PT-60216_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
107 | PT-60220 | - | 325-01-602-PD-04 | Gas Pressure Transmitter for Chamber (CHAM-21) | Pressure Transmitter | 4 - 20 mA | PLC | -100 - 100 mbar | Ex ic | - | - | - | 1 | - | C4 | C4S5 | 1756-IF16 | i RTN-8, IN-8 | 19, 20 | P4-TBAI1-9(B), P4-TBAI1-9(A) | C4S5-19/P4-TBAI1-9(B), C4S5-20/P4-TBAI1-9(A) | P4-TBAI1-9(B)/C4S5-19, P4-TBAI1-9(A)/C4S5-20 | PT-60220_AI_1, PT-60220_AI_1 | IS-JB-608 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
108 | PT-60221 | - | 325-01-602-PD-04 | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25) | Pressure Transmitter | 4 - 20 mA | PLC | 0 - 0.1 mbar | - | - | - | - | 1 | - | C3 | C3S8 | 1756-IF16 | i RTN-4, IN-4, i RTN-5, IN-5 | 11, 12, 13, 14 | P3-TBAI3-5(B), P3-TBAI3-5(A), P3-TBAI3-6(B), P3-TBAI3-6(A) | C3S8-11/P3-TBAI3-5(B), C3S8-12/P3-TBAI3-5(A), C3S8-13/P3-TBAI3-6(B)... | P3-TBAI3-5(B)/C3S8-11, P3-TBAI3-5(A)/C3S8-12, P3-TBAI3-6(B)/C3S8-13... | PT-60221_AI_1, PT-60221_AI_1, PT-60221_AI_1, PT-60221_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
109 | PT-60230 | - | 325-01-602-PD-04 | Gas Pressure Transmitter for Conveying Duct (DTCO-21) | Pressure Transmitter | 4 - 20 mA | PLC | 0 - 0.1 mbar | Ex ic | - | - | - | 1 | - | C4 | C4S5 | 1756-IF16 | i RTN-0, IN-0 | 1, 2 | P4-TBAI1-1(B), P4-TBAI1-1(A) | C4S5-1/P4-TBAI1-1(B), C4S5-2/P4-TBAI1-1(A) | P4-TBAI1-1(B)/C4S5-1, P4-TBAI1-1(A)/C4S5-2 | PT-60230_AI_1, PT-60230_AI_1 | IS-JB-603 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
110 | PT-60231 | - | 325-01-602-PD-04 | Gas Pressure Transmitter for Cyclone Exhaust Duct (DTCE-21) | Pressure Transmitter | 4 - 20 mA | PLC | -100 to 200 mbar | Ex ic | - | - | - | 1 | - | C4 | C4S5 | 1756-IF16 | i RTN-1, IN-1 | 3, 4 | P4-TBAI1-2(B), P4-TBAI1-2(A) | C4S5-3/P4-TBAI1-2(B), C4S5-4/P4-TBAI1-2(A) | P4-TBAI1-2(B)/C4S5-3, P4-TBAI1-2(A)/C4S5-4 | PT-60231_AI_1, PT-60231_AI_1 | IS-JB-603 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
111 | PT-60240 | - | 325-01-602-PD-05 | Gas Pressure Transmitter for Bag House Exhaust Duct (DTEX-22) | Pressure Transmitter | 4 - 20 mA | PLC | -100 to 200 mbar | - | - | - | - | 1 | - | C2 | C2S10 | 1756-IF16 | i RTN-6, IN-6 | 15, 16 | P2-TBAI2-7(B), P2-TBAI2-7(A) | C2S10-15/P2-TBAI2-7(B), C2S10-16/P2-TBAI2-7(A) | P2-TBAI2-7(B)/C2S10-15, P2-TBAI2-7(A)/C2S10-16 | PT-60240_AI_1, PT-60240_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
112 | PT-60241 | - | 325-01-602-PD-05 | Gas Pressure Transmitter for Exhaust Fan (FANE-21) | Pressure Transmitter | 4 - 20 mA | PLC | 0 - 0.1 mbar | - | - | - | - | 1 | - | C2 | C2S10 | 1756-IF16 | i RTN-7, IN-7 | 17, 18 | P2-TBAI2-8(B), P2-TBAI2-8(A) | C2S10-17/P2-TBAI2-8(B), C2S10-18/P2-TBAI2-8(A) | P2-TBAI2-8(B)/C2S10-17, P2-TBAI2-8(A)/C2S10-18 | PT-60241_AI_1, PT-60241_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
113 | PT-60204 | PT-61101 | 325-01-602-PD-10 | Pressure transmitter | Pressure Transmitter | 4 - 20 mA | PLC | 0 - 10 barg | - | - | - | - | 1 | - | C1 | C1S11 | 1756-IF16 | i RTN-6, IN-6 | 15, 16 | P1-TBAI2-7(B), P1-TBAI2-7(A) | C1S11-15/P1-TBAI2-7(B), C1S11-16/P1-TBAI2-7(A) | P1-TBAI2-7(B)/C1S11-15, P1-TBAI2-7(A)/C1S11-16 | PT-60204_AI_1, PT-60204_AI_1 | JB-601 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
114 | PT-61301 | - | 325-01-613-PD-01 | Pressure in silo | Pressure Transmitter | 4 - 20 mA | PLC | 0 - 1 barg | Ex ic | - | - | - | 1 | - | C4 | C4S6 | 1756-IF16 | i RTN-7, IN-7 | 17, 18 | P4-TBAI2-8(B), P4-TBAI2-8(A) | C4S6-17/P4-TBAI2-8(B), C4S6-18/P4-TBAI2-8(A) | P4-TBAI2-8(B)/C4S6-17, P4-TBAI2-8(A)/C4S6-18 | PT-61301_AI_1, PT-61301_AI_1 | IS-JB-618 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
115 | PT-61302 | - | 325-01-613-PD-03 | Pressure in vacuum line | Pressure Transmitter | 4 - 20 mA | PLC | -100 - 100 mbarg | - | - | - | - | 1 | - | C3 | C3S9 | 1756-IF16 | i RTN-8, IN-8, i RTN-12, IN-12 | 19, 20, 29, 30 | P3-TBAI4-9(B), P3-TBAI4-9(A), P3-TBAI4-13(B), P3-TBAI4-13(A) | C3S9-19/P3-TBAI4-9(B), C3S9-20/P3-TBAI4-9(A), C3S9-29/P3-TBAI4-13(B)... | P3-TBAI4-9(B)/C3S9-19, P3-TBAI4-9(A)/C3S9-20, P3-TBAI4-13(B)/C3S9-29... | PT-61302_AI_1, PT-61302_AI_1, PT-61302_AI_1, PT-61302_AI_1 | JB-612 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
116 | PT-61303 | - | 325-01-613-PD-01 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) | Pressure Transmitter | 4 - 20 mA | PLC | -100 to 200 mbar | Ex ic | - | - | - | 1 | - | C3, C4 | C3S9, C4S6 | 1756-IF16 | i RTN-0, IN-0, i RTN-8, IN-8 | 1, 2, 19, 20 | P3-TBAI4-1(B), P3-TBAI4-1(A), P4-TBAI2-9(B), P4-TBAI2-9(A) | C3S9-1/P3-TBAI4-1(B), C3S9-2/P3-TBAI4-1(A), C4S6-19/P4-TBAI2-9(B)... | P3-TBAI4-1(B)/C3S9-1, P3-TBAI4-1(A)/C3S9-2, P4-TBAI2-9(B)/C4S6-19... | PT-61303_AI_1, PT-61303_AI_1, PT-61303_AI_1, PT-61303_AI_1 | IS-JB-618, JB-618 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
117 | PT-61304 | - | 325-01-613-PD-01 | Gas Pressure Transmitter for Storage Bin Cyclone Inlet Duct (CYCL-31) | Pressure Transmitter | 4 - 20 mA | PLC | -100 to 200 mbar | Ex ic | - | - | - | 1 | - | C4 | C4S6 | 1756-IF16 | i RTN-9, IN-9 | 21, 22 | P4-TBAI2-10(B), P4-TBAI2-10(A) | C4S6-21/P4-TBAI2-10(B), C4S6-22/P4-TBAI2-10(A) | P4-TBAI2-10(B)/C4S6-21, P4-TBAI2-10(A)/C4S6-22 | PT-61304_AI_1, PT-61304_AI_1 | IS-JB-618 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
118 | PT-61305 | - | 325-01-613-PD-01 | Gas Pressure Transmitter for Exhaust Duct (DTEX-31) | Pressure Transmitter | 4 - 20 mA | PLC | -100 to 200 mbar | Ex ic | - | - | - | 1 | - | C4 | C4S6 | 1756-IF16 | i RTN-10, IN-10 | 23, 24 | P4-TBAI2-11(B), P4-TBAI2-11(A) | C4S6-23/P4-TBAI2-11(B), C4S6-24/P4-TBAI2-11(A) | P4-TBAI2-11(B)/C4S6-23, P4-TBAI2-11(A)/C4S6-24 | PT-61305_AI_1, PT-61305_AI_1 | IS-JB-618 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
119 | PT-61309 | - | 325-01-613-PD-04 | Pressure transmitter | Pressure Transmitter | 4 - 20 mA | PLC | 0 - 10 barg | - | - | - | - | 1 | - | C3 | C3S9 | 1756-IF16 | i RTN-9, IN-9, i RTN-13, IN-13 | 21, 22, 31, 32 | P3-TBAI4-10(B), P3-TBAI4-10(A), P3-TBAI4-14(B), P3-TBAI4-14(A) | C3S9-21/P3-TBAI4-10(B), C3S9-22/P3-TBAI4-10(A), C3S9-31/P3-TBAI4-14(B)... | P3-TBAI4-10(B)/C3S9-21, P3-TBAI4-10(A)/C3S9-22, P3-TBAI4-14(B)/C3S9-31... | PT-61309_AI_1, PT-61309_AI_1, PT-61309_AI_1, PT-61309_AI_1 | JB-612 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
120 | PCV-60201 | PV-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic Control valve | 4 - 20 mA | PLC | 0 - 100% | - | - | - | 1 | - | - | C3 | C3S12 | 1756-OF8 | IOUT-3 | 19 | P3-TBAO1-4 | C3S12-19/P3-TBAO1-4 | P3-TBAO1-4/C3S12-19 | PV-60201_AO_1 | JB-607 | LiY-CY TP 2Px1.0 (Setpoint AO + Feedback AI) | MAPPED_PLC
121 | SV-40201 | SV-40101 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 1 | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C1 | C1S8 | 1756-OB32 | OUT-24 | 27 | P1-TBRL1-25 | C1S8-27/P1-TBRL1-25 | P1-TBRL1-25/C1S8-27 | SV-40201_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
122 | SV-40202 | SV-40102 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 2 | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C1 | C1S8 | 1756-OB32 | OUT-25 | 28 | P1-TBRL1-26 | C1S8-28/P1-TBRL1-26 | P1-TBRL1-26/C1S8-28 | SV-40202_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
123 | SV-40203 | SV-40103 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 1 | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C1 | C1S8 | 1756-OB32 | OUT-26 | 29 | P1-TBRL1-27 | C1S8-29/P1-TBRL1-27 | P1-TBRL1-27/C1S8-29 | SV-40203_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
124 | SV-40204 | SV-40104 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 2 | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C1 | C1S8 | 1756-OB32 | OUT-27 | 30 | P1-TBRL1-28 | C1S8-30/P1-TBRL1-28 | P1-TBRL1-28/C1S8-30 | SV-40204_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
125 | SV-60220 | - | 325-01-602-PD-04 | PA On/Off Valve for Chamber PSE purge air (CHAM-21) | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C3 | C3S4 | 1756-OB32 | OUT-8 | 9 | P3-TBRL1-9 | C3S4-9/P3-TBRL1-9 | P3-TBRL1-9/C3S4-9 | SV-60220_DO_1 | JB-606 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
126 | SV-60230 | - | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 27 (CYCL-21) | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C1 | C1S9 | 1756-OB32 | OUT-18 | 21 | P1-TBRL2-19 | C1S9-21/P1-TBRL2-19 | P1-TBRL2-19/C1S9-21 | SV-60230_DO_1 | JB-601 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
127 | SV-60231 | - | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 28 (CYCL-22) | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C1 | C1S9 | 1756-OB32 | OUT-21 | 24 | P1-TBRL2-22 | C1S9-24/P1-TBRL2-22 | P1-TBRL2-22/C1S9-24 | SV-60231_DO_1 | JB-601 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
128 | SV-60240A | - | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29A (BGHS-21) | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C1 | C1S9 | 1756-OB32 | OUT-20 | 23 | P1-TBRL2-21 | C1S9-23/P1-TBRL2-21 | P1-TBRL2-21/C1S9-23 | SV-60240A_DO_1 | JB-601 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
129 | SV-60240B | - | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29B (BGHS-21) | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C1 | C1S9 | 1756-OB32 | OUT-22 | 25 | P1-TBRL2-23 | C1S9-25/P1-TBRL2-23 | P1-TBRL2-23/C1S9-25 | SV-60240B_DO_1 | JB-601 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
130 | SV-60240C | - | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29C (BGHS-21) | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C1 | C1S9 | 1756-OB32 | OUT-23 | 26 | P1-TBRL2-24 | C1S9-26/P1-TBRL2-24 | P1-TBRL2-24/C1S9-26 | SV-60240C_DO_1 | JB-601 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
131 | SV-61301 | - | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve | 24 VDC energized | PLC | On-Off | - | - | - | - | - | - | C3 | C3S5 | 1756-OB32 | OUT-2 | 3 | P3-TBRL2-3 | C3S5-3/P3-TBRL2-3 | P3-TBRL2-3/C3S5-3 | SV-61301_DO_1 | JB-618 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
132 | SV-61302 | - | 325-01-613-PD-01 | Air service | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C3 | C3S5 | 1756-OB32 | OUT-3 | 4 | P3-TBRL2-4 | C3S5-4/P3-TBRL2-4 | P3-TBRL2-4/C3S5-4 | SV-61302_DO_1 | JB-618 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
132 | SV-61306 | - | 325-01-613-PD-01 | Air service | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C3 | C3S5 | 1756-OB32 | OUT-7 | 8 | P3-TBRL2-8 | C3S5-8/P3-TBRL2-8 | P3-TBRL2-8/C3S5-8 | SV-61306_DO_1 | JB-618 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
133 | SV-61303 | - | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve | 24 VDC energized | PLC | On-Off | - | - | - | - | - | - | C3 | C3S5 | 1756-OB32 | OUT-4 | 5 | P3-TBRL2-5 | C3S5-5/P3-TBRL2-5 | P3-TBRL2-5/C3S5-5 | SV-61303_DO_1 | JB-618 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
134 | SV-61305 | - | 325-01-613-PD-01 | Air service | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C3 | C3S5 | 1756-OB32 | OUT-6 | 7 | P3-TBRL2-7 | C3S5-7/P3-TBRL2-7 | P3-TBRL2-7/C3S5-7 | SV-61305_DO_1 | JB-618 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
135 | SV-61308 | - | 325-01-613-PD-03 | Timer compress air pluse solenoid valve | Solenoid valve | 24 VDC energized | PLC | On-Off | - | - | - | - | - | - | C3 | C3S4 | 1756-OB32 | OUT-19 | 22 | P3-TBRL1-20 | C3S4-22/P3-TBRL1-20 | P3-TBRL1-20/C3S4-22 | SV-61308_DO_1 | JB-612 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
136 | SV-61309 | - | 325-01-613-PD-03 | Air service | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C3 | C3S4 | 1756-OB32 | OUT-20 | 23 | P3-TBRL1-21 | C3S4-23/P3-TBRL1-21 | P3-TBRL1-21/C3S4-23 | SV-61309_DO_1 | JB-612 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
137 | SV-61310 | - | 325-01-613-PD-05 | Timer compress air pluse solenoid valve | Solenoid valve | 24 VDC energized | PLC | On-Off | - | - | - | - | - | - | C3 | C3S4 | 1756-OB32 | OUT-21 | 24 | P3-TBRL1-22 | C3S4-24/P3-TBRL1-22 | P3-TBRL1-22/C3S4-24 | SV-61310_DO_1 | JB-612 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
138 | SV-61311 | - | 325-01-613-PD-05 | Air service | Solenoid valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C3 | C3S4 | 1756-OB32 | OUT-22 | 25 | P3-TBRL1-23 | C3S4-25/P3-TBRL1-23 | P3-TBRL1-23/C3S4-25 | SV-61311_DO_1 | JB-612 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
139 | TSH-60230 | - | 325-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | Temperature Switch | Dry Contact | PLC | 0 - 140 C | Ex d | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-3 | 4 | P2-TBDI2-4 | C2S2-4/P2-TBDI2-4 | P2-TBDI2-4/C2S2-4 | TSH-60230_DI_1 | JB-602 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
140 | TSH-60240 | - | 325-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | Temperature Switch | Dry Contact | PLC | 0 - 140 C | Ex d | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-4 | 5 | P2-TBDI2-5 | C2S2-5/P2-TBDI2-5 | P2-TBDI2-5/C2S2-5 | TSH-60240_DI_1 | JB-602 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
141 | TT-40221 | - | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 120 C | - | - | - | - | 1 | - | C2 | C2S9 | 1756-IF16 | i RTN-5, IN-5 | 13, 14 | P2-TBAI1-6(B), P2-TBAI1-6(A) | C2S9-13/P2-TBAI1-6(B), C2S9-14/P2-TBAI1-6(A) | P2-TBAI1-6(B)/C2S9-13, P2-TBAI1-6(A)/C2S9-14 | TT-40221_AI_1, TT-40221_AI_1 | JB-402 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
142 | TT-40222 | - | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 200 C | - | - | - | - | 1 | - | C2 | C2S9 | 1756-IF16 | i RTN-6, IN-6 | 15, 16 | P2-TBAI1-7(B), P2-TBAI1-7(A) | C2S9-15/P2-TBAI1-7(B), C2S9-16/P2-TBAI1-7(A) | P2-TBAI1-7(B)/C2S9-15, P2-TBAI1-7(A)/C2S9-16 | TT-40222_AI_1, TT-40222_AI_1 | JB-402 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
143 | TT-60201 | - | 325-01-602-PD-02 | Steam feed to Spray dryer | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 300 C | - | - | - | - | 1 | - | C3 | C3S8 | 1756-IF16 | i RTN-7, IN-7 | 17, 18 | P3-TBAI3-8(B), P3-TBAI3-8(A) | C3S8-17/P3-TBAI3-8(B), C3S8-18/P3-TBAI3-8(A) | P3-TBAI3-8(B)/C3S8-17, P3-TBAI3-8(A)/C3S8-18 | TT-60201_AI_1, TT-60201_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
144 | TT-60210 | - | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | - | - | - | - | 1 | - | C2 | C2S10 | 1756-IF16 | i RTN-8, IN-8 | 19, 20 | P2-TBAI2-9(B), P2-TBAI2-9(A) | C2S10-19/P2-TBAI2-9(B), C2S10-20/P2-TBAI2-9(A) | P2-TBAI2-9(B)/C2S10-19, P2-TBAI2-9(A)/C2S10-20 | TT-60210_AI_1, TT-60210_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
145 | TT-60210A | TT-60212A | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 100 C | - | - | - | - | 1 | - | C2 | C2S10 | 1756-IF16 | i RTN-9, IN-9 | 21, 22 | P2-TBAI2-10(B), P2-TBAI2-10(A) | C2S10-21/P2-TBAI2-10(B), C2S10-22/P2-TBAI2-10(A) | P2-TBAI2-10(B)/C2S10-21, P2-TBAI2-10(A)/C2S10-22 | TT-60210A_AI_1, TT-60210A_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
146 | TT-60210B | TT-60212B | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 100 C | - | - | - | - | 1 | - | C2 | C2S10 | 1756-IF16 | i RTN-10, IN-10 | 23, 24 | P2-TBAI2-11(B), P2-TBAI2-11(A) | C2S10-23/P2-TBAI2-11(B), C2S10-24/P2-TBAI2-11(A) | P2-TBAI2-11(B)/C2S10-23, P2-TBAI2-11(A)/C2S10-24 | TT-60210B_AI_1, TT-60210B_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
147 | TT-60211 | - | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | - | - | - | - | 1 | - | C2 | C2S10 | 1756-IF16 | i RTN-11, IN-11 | 25, 26 | P2-TBAI2-12(B), P2-TBAI2-12(A) | C2S10-25/P2-TBAI2-12(B), C2S10-26/P2-TBAI2-12(A) | P2-TBAI2-12(B)/C2S10-25, P2-TBAI2-12(A)/C2S10-26 | TT-60211_AI_1, TT-60211_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
148 | TT-60214 | - | 325-01-602-PD-03 | Steam Temperature Transmitter for Cold Air Duct (DTCA-23) | Temperature Transmitter | 4 - 20 mA | PLC | -10 to 250°C | - | - | - | - | 1 | - | C2 | C2S10 | 1756-IF16 | i RTN-14, IN-14 | 33, 34 | P2-TBAI2-15(B), P2-TBAI2-15(A) | C2S10-33/P2-TBAI2-15(B), C2S10-34/P2-TBAI2-15(A) | P2-TBAI2-15(B)/C2S10-33, P2-TBAI2-15(A)/C2S10-34 | TT-60214_AI_1, TT-60214_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
149 | TT-60215A | - | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter | 4 - 20 mA | PLC | -10 to 150°C | - | - | - | - | 1 | - | C2 | C2S10 | 1756-IF16 | i RTN-15, IN-15 | 35, 36 | P2-TBAI2-16(B), P2-TBAI2-16(A) | C2S10-35/P2-TBAI2-16(B), C2S10-36/P2-TBAI2-16(A) | P2-TBAI2-16(B)/C2S10-35, P2-TBAI2-16(A)/C2S10-36 | TT-60215A_AI_1, TT-60215A_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
150 | TT-60215B | - | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter | 4 - 20 mA | PLC | -10 to 150°C | - | - | - | - | 1 | - | C3 | C3S6 | 1756-IF16 | i RTN-0, IN-0 | 1, 2 | P3-TBAI1-1(B), P3-TBAI1-1(A) | C3S6-1/P3-TBAI1-1(B), C3S6-2/P3-TBAI1-1(A) | P3-TBAI1-1(B)/C3S6-1, P3-TBAI1-1(A)/C3S6-2 | TT-60215B_AI_1, TT-60215B_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
151 | TT-60216 | - | 325-01-602-PD-03 | Gas Temperature Transmitter for Combustion Air Burner Duct (DTCB-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 200'°C | - | - | - | - | 1 | - | C3 | C3S6 | 1756-IF16 | i RTN-1, IN-1 | 3, 4 | P3-TBAI1-2(B), P3-TBAI1-2(A) | C3S6-3/P3-TBAI1-2(B), C3S6-4/P3-TBAI1-2(A) | P3-TBAI1-2(B)/C3S6-3, P3-TBAI1-2(A)/C3S6-4 | TT-60216_AI_1, TT-60216_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
152 | TT-60220 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | Ex ic | - | - | - | 1 | - | C4 | C4S5 | 1756-IF16 | i RTN-9, IN-9 | 21, 22 | P4-TBAI1-10(B), P4-TBAI1-10(A) | C4S5-21/P4-TBAI1-10(B), C4S5-22/P4-TBAI1-10(A) | P4-TBAI1-10(B)/C4S5-21, P4-TBAI1-10(A)/C4S5-22 | TT-60220_AI_1, TT-60220_AI_1 | IS-JB-608 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
153 | TT-60221 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | Ex ic | - | - | - | 1 | - | C4 | C4S5 | 1756-IF16 | i RTN-10, IN-10 | 23, 24 | P4-TBAI1-11(B), P4-TBAI1-11(A) | C4S5-23/P4-TBAI1-11(B), C4S5-24/P4-TBAI1-11(A) | P4-TBAI1-11(B)/C4S5-23, P4-TBAI1-11(A)/C4S5-24 | TT-60221_AI_1, TT-60221_AI_1 | IS-JB-608 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
154 | TT-60222 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | Ex ic | - | - | - | 1 | - | C4 | C4S5 | 1756-IF16 | i RTN-11, IN-11 | 25, 26 | P4-TBAI1-12(B), P4-TBAI1-12(A) | C4S5-25/P4-TBAI1-12(B), C4S5-26/P4-TBAI1-12(A) | P4-TBAI1-12(B)/C4S5-25, P4-TBAI1-12(A)/C4S5-26 | TT-60222_AI_1, TT-60222_AI_1 | IS-JB-608 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
155 | TT-60223 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | Ex ic | - | - | - | 1 | - | C4 | C4S5 | 1756-IF16 | i RTN-12, IN-12 | 29, 30 | P4-TBAI1-13(B), P4-TBAI1-13(A) | C4S5-29/P4-TBAI1-13(B), C4S5-30/P4-TBAI1-13(A) | P4-TBAI1-13(B)/C4S5-29, P4-TBAI1-13(A)/C4S5-30 | TT-60223_AI_1, TT-60223_AI_1 | IS-JB-608 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
156 | TT-60224 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | Ex ic | - | - | - | 1 | - | C4 | C4S5 | 1756-IF16 | i RTN-2, IN-2 | 5, 6 | P4-TBAI1-3(B), P4-TBAI1-3(A) | C4S5-5/P4-TBAI1-3(B), C4S5-6/P4-TBAI1-3(A) | P4-TBAI1-3(B)/C4S5-5, P4-TBAI1-3(A)/C4S5-6 | TT-60224_AI_1, TT-60224_AI_1 | IS-JB-603 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
157 | TT-60225 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | Ex ic | - | - | - | 1 | - | C4 | C4S5 | 1756-IF16 | i RTN-3, IN-3 | 7, 8 | P4-TBAI1-4(B), P4-TBAI1-4(A) | C4S5-7/P4-TBAI1-4(B), C4S5-8/P4-TBAI1-4(A) | P4-TBAI1-4(B)/C4S5-7, P4-TBAI1-4(A)/C4S5-8 | TT-60225_AI_1, TT-60225_AI_1 | IS-JB-603 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
158 | TT-60226 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | Ex ic | - | - | - | 1 | - | C4 | C4S5 | 1756-IF16 | i RTN-4, IN-4 | 11, 12 | P4-TBAI1-5(B), P4-TBAI1-5(A) | C4S5-11/P4-TBAI1-5(B), C4S5-12/P4-TBAI1-5(A) | P4-TBAI1-5(B)/C4S5-11, P4-TBAI1-5(A)/C4S5-12 | TT-60226_AI_1, TT-60226_AI_1 | IS-JB-603 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
159 | TT-60227 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | Ex ic | - | - | - | 1 | - | C4 | C4S5 | 1756-IF16 | i RTN-5, IN-5 | 13, 14 | P4-TBAI1-6(B), P4-TBAI1-6(A) | C4S5-13/P4-TBAI1-6(B), C4S5-14/P4-TBAI1-6(A) | P4-TBAI1-6(B)/C4S5-13, P4-TBAI1-6(A)/C4S5-14 | TT-60227_AI_1, TT-60227_AI_1 | IS-JB-603 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
160 | TT-60230 | - | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Conveying Duct (DTCO-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | Ex ic | - | - | - | 1 | - | C4 | C4S5 | 1756-IF16 | i RTN-6, IN-6 | 15, 16 | P4-TBAI1-7(B), P4-TBAI1-7(A) | C4S5-15/P4-TBAI1-7(B), C4S5-16/P4-TBAI1-7(A) | P4-TBAI1-7(B)/C4S5-15, P4-TBAI1-7(A)/C4S5-16 | TT-60230_AI_1, TT-60230_AI_1 | IS-JB-603 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
161 | TT-60240 | - | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Fan (FANE-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | - | - | - | - | 1 | - | C3 | C3S6 | 1756-IF16 | i RTN-2, IN-2 | 5, 6 | P3-TBAI1-3(B), P3-TBAI1-3(A) | C3S6-5/P3-TBAI1-3(B), C3S6-6/P3-TBAI1-3(A) | P3-TBAI1-3(B)/C3S6-5, P3-TBAI1-3(A)/C3S6-6 | TT-60240_AI_1, TT-60240_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
162 | TT-60241A | - | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 100 C | - | - | - | - | 1 | - | C3 | C3S6 | 1756-IF16 | i RTN-3, IN-3 | 7, 8 | P3-TBAI1-4(B), P3-TBAI1-4(A) | C3S6-7/P3-TBAI1-4(B), C3S6-8/P3-TBAI1-4(A) | P3-TBAI1-4(B)/C3S6-7, P3-TBAI1-4(A)/C3S6-8 | TT-60241A_AI_1, TT-60241A_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
163 | TT-60241B | - | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 100 C | - | - | - | - | 1 | - | C3 | C3S6 | 1756-IF16 | i RTN-4, IN-4 | 11, 12 | P3-TBAI1-5(B), P3-TBAI1-5(A) | C3S6-11/P3-TBAI1-5(B), C3S6-12/P3-TBAI1-5(A) | P3-TBAI1-5(B)/C3S6-11, P3-TBAI1-5(A)/C3S6-12 | TT-60241B_AI_1, TT-60241B_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
164 | TT-60245 | - | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Stack (DTXS-21) | Temperature Transmitter | 4 - 20 mA | PLC | -10 to 150°C | - | - | - | - | 1 | - | C3 | C3S8 | 1756-IF16 | i RTN-15, IN-15 | 35, 36 | P3-TBAI3-16(B), P3-TBAI3-16(A) | C3S8-35/P3-TBAI3-16(B), C3S8-36/P3-TBAI3-16(A) | P3-TBAI3-16(B)/C3S8-35, P3-TBAI3-16(A)/C3S8-36 | TT-60245_AI_1, TT-60245_AI_1 | JB-608 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
165 | TT-60202 | TT-60702 | 325-01-602-PD-07 | Compress air temp to camera | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 40 C | - | - | - | - | 1 | - | C3 | C3S8 | 1756-IF16 | i RTN-8, IN-8 | 19, 20 | P3-TBAI3-9(B), P3-TBAI3-9(A) | C3S8-19/P3-TBAI3-9(B), C3S8-20/P3-TBAI3-9(A) | P3-TBAI3-9(B)/C3S8-19, P3-TBAI3-9(A)/C3S8-20 | TT-60202_AI_1, TT-60202_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
166 | TT-61301 | - | 325-01-613-PD-01 | Gas Temperature Transmitter for Cold Air Duct (DTCA-32) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | Ex ic | - | - | - | 1 | - | C4 | C4S6 | 1756-IF16 | i RTN-11, IN-11 | 25, 26 | P4-TBAI2-12(B), P4-TBAI2-12(A) | C4S6-25/P4-TBAI2-12(B), C4S6-26/P4-TBAI2-12(A) | P4-TBAI2-12(B)/C4S6-25, P4-TBAI2-12(A)/C4S6-26 | TT-61301_AI_1, TT-61301_AI_1 | IS-JB-618 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
167 | TT-61302 | - | 325-01-613-PD-01 | Gas and Powder Temperature Transmitter for Cooling Cyclone (CYCL-31) | Temperature Transmitter | 4 - 20 mA | PLC | 0 - 400'°C | Ex ic | - | - | - | 1 | - | C4 | C4S6 | 1756-IF16 | i RTN-12, IN-12 | 29, 30 | P4-TBAI2-13(B), P4-TBAI2-13(A) | C4S6-29/P4-TBAI2-13(B), C4S6-30/P4-TBAI2-13(A) | P4-TBAI2-13(B)/C4S6-29, P4-TBAI2-13(A)/C4S6-30 | TT-61302_AI_1, TT-61302_AI_1 | IS-JB-618 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
168 | TCV-40222 | - | 325-01-402-PD-02 | Jet Cooker | Automatic Control valve | 4 - 20 mA | PLC | 0 - 100% | - | - | - | 1 | - | - | C3 | C3S12 | 1756-OF8 | IOUT-0 | 3 | P3-TBAO1-1 | C3S12-3/P3-TBAO1-1 | P3-TBAO1-1/C3S12-3 | TCV-40222_AO_1 | JB-402 | LiY-CY TP 2Px1.0 (Setpoint AO + Feedback AI) | MAPPED_PLC
169 | TCV-60214 | TV-60214 | 325-01-602-PD-03 | Steam Temperature Valve for Pre-Heat Steam Heat Exchanger (HXCH-21) | Automatic Control valve | 4 - 20 mA | PLC | 0 - 100% | - | - | - | 1 | - | - | C3 | C3S12 | 1756-OF8 | IOUT-2 | 13 | P3-TBAO1-3 | C3S12-13/P3-TBAO1-3 | P3-TBAO1-3/C3S12-13 | TV-60214_AO_1 | JB-602 | LiY-CY TP 2Px1.0 (Setpoint AO + Feedback AI) | MAPPED_PLC
170 | TCV-60202 | TV-60702 | 325-01-602-PD-07 | Chiller water control valve | 3-way Control valve | 4 - 20 mA | PLC | 0 - 100% | - | - | - | 1 | - | - | C3 | C3S12 | 1756-OF8 | IOUT-1 | 9 | P3-TBAO1-2 | C3S12-9/P3-TBAO1-2 | P3-TBAO1-2/C3S12-9 | TV-60202_AO_1 | JB-602 | LiY-CY TP 2Px1.0 (Setpoint AO + Feedback AI) | MAPPED_PLC
171 | VT-60210A | - | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter | 4 - 20 mA | PLC | mm/sec | - | - | - | - | 1 | - | C3 | C3S6 | 1756-IF16 | i RTN-5, IN-5 | 13, 14 | P3-TBAI1-6(B), P3-TBAI1-6(A) | C3S6-13/P3-TBAI1-6(B), C3S6-14/P3-TBAI1-6(A) | P3-TBAI1-6(B)/C3S6-13, P3-TBAI1-6(A)/C3S6-14 | VT-60210A_AI_1, VT-60210A_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
172 | VT-60210B | - | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter | 4 - 20 mA | PLC | mm/sec | - | - | - | - | 1 | - | C3 | C3S6 | 1756-IF16 | i RTN-6, IN-6 | 15, 16 | P3-TBAI1-7(B), P3-TBAI1-7(A) | C3S6-15/P3-TBAI1-7(B), C3S6-16/P3-TBAI1-7(A) | P3-TBAI1-7(B)/C3S6-15, P3-TBAI1-7(A)/C3S6-16 | VT-60210B_AI_1, VT-60210B_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
173 | VT-60241A | - | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter | 4 - 20 mA | PLC | mm/sec | - | - | - | - | 1 | - | C3 | C3S6 | 1756-IF16 | i RTN-7, IN-7 | 17, 18 | P3-TBAI1-8(B), P3-TBAI1-8(A) | C3S6-17/P3-TBAI1-8(B), C3S6-18/P3-TBAI1-8(A) | P3-TBAI1-8(B)/C3S6-17, P3-TBAI1-8(A)/C3S6-18 | VT-60241A_AI_1, VT-60241A_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
174 | VT-60241B | - | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter | 4 - 20 mA | PLC | mm/sec | - | - | - | - | 1 | - | C3 | C3S6 | 1756-IF16 | i RTN-8, IN-8 | 19, 20 | P3-TBAI1-9(B), P3-TBAI1-9(A) | C3S6-19/P3-TBAI1-9(B), C3S6-20/P3-TBAI1-9(A) | P3-TBAI1-9(B)/C3S6-19, P3-TBAI1-9(A)/C3S6-20 | VT-60241B_AI_1, VT-60241B_AI_1 | JB-602 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
175 | XT-60201 | XT-60301 | 325-01-402-PD-03 | LEL gas analyzer | Gas detector | 4 - 20 mA | PLC | 0-10%LEL | Ex ic | - | - | - | 1 | - | C4 | C4S5 | 1756-IF16 | i RTN-13, IN-13 | 31, 32 | P4-TBAI1-14(B), P4-TBAI1-14(A) | C4S5-31/P4-TBAI1-14(B), C4S5-32/P4-TBAI1-14(A) | P4-TBAI1-14(B)/C4S5-31, P4-TBAI1-14(A)/C4S5-32 | XT-60201_AI_1, XT-60201_AI_1 | IS-JB-608 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
176 | XA-60201 | XA-60301 | 325-01-402-PD-03 | LEL gas Buzzer Alarm | Gas detector | 4 - 20 mA | PLC | 0-10%LEL | Ex ic | 1 | - | - | - | - | C4 | C4S4 | 1756-OB32 | OUT-8 | 9 | P4-TBRL1-9 | C4S4-9/P4-TBRL1-9 | P4-TBRL1-9/C4S4-9 | XA-60201_DO_1 | IS-JB-608 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_PLC
177 | XT-92201 | - | 325-01-923-PD-03 | LEL gas analyzer | Gas detector | 4 - 20 mA | PLC | 0-10%LEL | Ex ic | - | - | - | 1 | - | C5 | C5S4 | 1756-IF16 | i RTN-7, IN-7 | 17, 18 | P5-TBAI1-8(B), P5-TBAI1-8(A) | C5S4-17/P5-TBAI1-8(B), C5S4-18/P5-TBAI1-8(A) | P5-TBAI1-8(B)/C5S4-17, P5-TBAI1-8(A)/C5S4-18 | XT-92201_AI_1, XT-92201_AI_1 | RIO-200 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_RIO200
178 | XA-92201 | - | 325-01-923-PD-03 | LEL gas Buzzer Alarm | Gas detector | 4 - 20 mA | PLC | 0-10%LEL | Ex ic | 1 | - | - | - | - | C5 | C5S3 | 1756-OB32 | OUT-0 | 1 | P5-TBRL1-1 | C5S3-1/P5-TBRL1-1 | P5-TBRL1-1/C5S3-1 | XA-92201_DO_1 | RIO-200 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_RIO200
179 | XV-40201A | XV-40101A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S4, C1S8 | 1756-IB32, 1756-OB32 | IN-26, IN-27, OUT-28 | 29, 30, 31 | P1-TBDI1-27, P1-TBDI1-28, P1-TBRL1-29 | C1S4-29/P1-TBDI1-27, C1S4-30/P1-TBDI1-28, C1S8-31/P1-TBRL1-29 | P1-TBDI1-27/C1S4-29, P1-TBDI1-28/C1S4-30, P1-TBRL1-29/C1S8-31 | XV-40201A_DI_1, XV-40201A_DI_2, XV-40201A_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
180 | XV-40201B | XV-40101B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S4, C1S8 | 1756-IB32, 1756-OB32 | IN-28, IN-29, OUT-29 | 31, 32, 32 | P1-TBDI1-29, P1-TBDI1-30, P1-TBRL1-30 | C1S4-31/P1-TBDI1-29, C1S4-32/P1-TBDI1-30, C1S8-32/P1-TBRL1-30 | P1-TBDI1-29/C1S4-31, P1-TBDI1-30/C1S4-32, P1-TBRL1-30/C1S8-32 | XV-40201B_DI_1, XV-40201B_DI_2, XV-40201B_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
181 | XV-40201C | XV-40101C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S4, C1S8 | 1756-IB32, 1756-OB32 | IN-30, IN-31, OUT-30 | 33, 34, 33 | P1-TBDI1-31, P1-TBDI1-32, P1-TBRL1-31 | C1S4-33/P1-TBDI1-31, C1S4-34/P1-TBDI1-32, C1S8-33/P1-TBRL1-31 | P1-TBDI1-31/C1S4-33, P1-TBDI1-32/C1S4-34, P1-TBRL1-31/C1S8-33 | XV-40201C_DI_1, XV-40201C_DI_2, XV-40201C_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
182 | XV-40201D | XV-40101D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S8 | 1756-IB32, 1756-OB32 | IN-0, IN-1, OUT-31 | 1, 2, 34 | P1-TBDI2-1, P1-TBDI2-2, P1-TBRL1-32 | C1S5-1/P1-TBDI2-1, C1S5-2/P1-TBDI2-2, C1S8-34/P1-TBRL1-32 | P1-TBDI2-1/C1S5-1, P1-TBDI2-2/C1S5-2, P1-TBRL1-32/C1S8-34 | XV-40201D_DI_1, XV-40201D_DI_2, XV-40201D_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
183 | XV-40201E | XV-40101E | 325-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S9 | 1756-IB32, 1756-OB32 | IN-2, IN-3, OUT-0 | 3, 4, 1 | P1-TBDI2-3, P1-TBDI2-4, P1-TBRL2-1 | C1S5-3/P1-TBDI2-3, C1S5-4/P1-TBDI2-4, C1S9-1/P1-TBRL2-1 | P1-TBDI2-3/C1S5-3, P1-TBDI2-4/C1S5-4, P1-TBRL2-1/C1S9-1 | XV-40201E_DI_1, XV-40201E_DI_2, XV-40201E_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
184 | XV-40201F | XV-40101F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S9 | 1756-IB32, 1756-OB32 | IN-4, IN-5, OUT-1 | 5, 6, 2 | P1-TBDI2-5, P1-TBDI2-6, P1-TBRL2-2 | C1S5-5/P1-TBDI2-5, C1S5-6/P1-TBDI2-6, C1S9-2/P1-TBRL2-2 | P1-TBDI2-5/C1S5-5, P1-TBDI2-6/C1S5-6, P1-TBRL2-2/C1S9-2 | XV-40201F_DI_1, XV-40201F_DI_2, XV-40201F_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
185 | XV-40201G | XV-40101G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S9 | 1756-IB32, 1756-OB32 | IN-6, IN-7, OUT-2 | 7, 8, 3 | P1-TBDI2-7, P1-TBDI2-8, P1-TBRL2-3 | C1S5-7/P1-TBDI2-7, C1S5-8/P1-TBDI2-8, C1S9-3/P1-TBRL2-3 | P1-TBDI2-7/C1S5-7, P1-TBDI2-8/C1S5-8, P1-TBRL2-3/C1S9-3 | XV-40201G_DI_1, XV-40201G_DI_2, XV-40201G_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
186 | XV-40201H | XV-40101H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S9 | 1756-IB32, 1756-OB32 | IN-8, IN-9, OUT-3 | 9, 10, 4 | P1-TBDI2-9, P1-TBDI2-10, P1-TBRL2-4 | C1S5-9/P1-TBDI2-9, C1S5-10/P1-TBDI2-10, C1S9-4/P1-TBRL2-4 | P1-TBDI2-9/C1S5-9, P1-TBDI2-10/C1S5-10, P1-TBRL2-4/C1S9-4 | XV-40201H_DI_1, XV-40201H_DI_2, XV-40201H_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
187 | XV-40202A | XV-40102A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S9 | 1756-IB32, 1756-OB32 | IN-10, IN-18, OUT-4 | 11, 21, 5 | P1-TBDI2-11, P1-TBDI2-19, P1-TBRL2-5 | C1S5-11/P1-TBDI2-11, C1S5-21/P1-TBDI2-19, C1S9-5/P1-TBRL2-5 | P1-TBDI2-11/C1S5-11, P1-TBDI2-19/C1S5-21, P1-TBRL2-5/C1S9-5 | XV-40202A_DI_2, XV-40202A_DI_1, XV-40202A_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
188 | XV-40202B | XV-40102B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S9 | 1756-IB32, 1756-OB32 | IN-11, IN-12, OUT-5 | 12, 13, 6 | P1-TBDI2-12, P1-TBDI2-13, P1-TBRL2-6 | C1S5-12/P1-TBDI2-12, C1S5-13/P1-TBDI2-13, C1S9-6/P1-TBRL2-6 | P1-TBDI2-12/C1S5-12, P1-TBDI2-13/C1S5-13, P1-TBRL2-6/C1S9-6 | XV-40202B_DI_1, XV-40202B_DI_2, XV-40202B_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
189 | XV-40202C | XV-40102C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S9 | 1756-IB32, 1756-OB32 | IN-13, IN-14, OUT-6 | 14, 15, 7 | P1-TBDI2-14, P1-TBDI2-15, P1-TBRL2-7 | C1S5-14/P1-TBDI2-14, C1S5-15/P1-TBDI2-15, C1S9-7/P1-TBRL2-7 | P1-TBDI2-14/C1S5-14, P1-TBDI2-15/C1S5-15, P1-TBRL2-7/C1S9-7 | XV-40202C_DI_1, XV-40202C_DI_2, XV-40202C_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
190 | XV-40202D | XV-40102D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S9 | 1756-IB32, 1756-OB32 | IN-15, IN-16, OUT-7 | 16, 19, 8 | P1-TBDI2-16, P1-TBDI2-17, P1-TBRL2-8 | C1S5-16/P1-TBDI2-16, C1S5-19/P1-TBDI2-17, C1S9-8/P1-TBRL2-8 | P1-TBDI2-16/C1S5-16, P1-TBDI2-17/C1S5-19, P1-TBRL2-8/C1S9-8 | XV-40202D_DI_1, XV-40202D_DI_2, XV-40202D_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
191 | XV-40202E | XV-40102E | 325-01-402-PD-01 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S8 | 1756-IB32, 1756-OB32 | IN-17, IN-19, OUT-16 | 20, 22, 19 | P1-TBDI2-18, P1-TBDI2-20, P1-TBRL1-17 | C1S5-20/P1-TBDI2-18, C1S5-22/P1-TBDI2-20, C1S8-19/P1-TBRL1-17 | P1-TBDI2-18/C1S5-20, P1-TBDI2-20/C1S5-22, P1-TBRL1-17/C1S8-19 | XV-40202E_DI_1, XV-40202E_DI_2, XV-40202E_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
192 | XV-40202F | XV-40102F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S8 | 1756-IB32, 1756-OB32 | IN-20, IN-21, OUT-17 | 23, 24, 20 | P1-TBDI2-21, P1-TBDI2-22, P1-TBRL1-18 | C1S5-23/P1-TBDI2-21, C1S5-24/P1-TBDI2-22, C1S8-20/P1-TBRL1-18 | P1-TBDI2-21/C1S5-23, P1-TBDI2-22/C1S5-24, P1-TBRL1-18/C1S8-20 | XV-40202F_DI_1, XV-40202F_DI_2, XV-40202F_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
193 | XV-40202G | XV-40102G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S8 | 1756-IB32, 1756-OB32 | IN-22, IN-23, OUT-18 | 25, 26, 21 | P1-TBDI2-23, P1-TBDI2-24, P1-TBRL1-19 | C1S5-25/P1-TBDI2-23, C1S5-26/P1-TBDI2-24, C1S8-21/P1-TBRL1-19 | P1-TBDI2-23/C1S5-25, P1-TBDI2-24/C1S5-26, P1-TBRL1-19/C1S8-21 | XV-40202G_DI_1, XV-40202G_DI_2, XV-40202G_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
194 | XV-40202H | XV-40102H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 2 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S8 | 1756-IB32, 1756-OB32 | IN-24, IN-25, OUT-19 | 27, 28, 22 | P1-TBDI2-25, P1-TBDI2-26, P1-TBRL1-20 | C1S5-27/P1-TBDI2-25, C1S5-28/P1-TBDI2-26, C1S8-22/P1-TBRL1-20 | P1-TBDI2-25/C1S5-27, P1-TBDI2-26/C1S5-28, P1-TBRL1-20/C1S8-22 | XV-40202H_DI_1, XV-40202H_DI_2, XV-40202H_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
195 | XV-40203B | XV-40201B | 325-01-402-PD-02 | Slurry feed-out Spray dryer infeed tank | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S8 | 1756-IB32, 1756-OB32 | IN-26, IN-27, OUT-20 | 29, 30, 23 | P1-TBDI2-27, P1-TBDI2-28, P1-TBRL1-21 | C1S5-29/P1-TBDI2-27, C1S5-30/P1-TBDI2-28, C1S8-23/P1-TBRL1-21 | P1-TBDI2-27/C1S5-29, P1-TBDI2-28/C1S5-30, P1-TBRL1-21/C1S8-23 | XV-40203B_DI_1, XV-40203B_DI_2, XV-40203B_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
196 | XV-40203C | XV-40201C | 325-01-402-PD-02 | Water washing line outlet Spray dryer infeed tank | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S8 | 1756-IB32, 1756-OB32 | IN-28, IN-29, OUT-21 | 31, 32, 24 | P1-TBDI2-29, P1-TBDI2-30, P1-TBRL1-22 | C1S5-31/P1-TBDI2-29, C1S5-32/P1-TBDI2-30, C1S8-24/P1-TBRL1-22 | P1-TBDI2-29/C1S5-31, P1-TBDI2-30/C1S5-32, P1-TBRL1-22/C1S8-24 | XV-40203C_DI_1, XV-40203C_DI_2, XV-40203C_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
197 | XV-40203D | XV-40201D | 325-01-402-PD-02 | CIP water washing Spray dryer infeed tank | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S5, C1S8 | 1756-IB32, 1756-OB32 | IN-30, IN-31, OUT-22 | 33, 34, 25 | P1-TBDI2-31, P1-TBDI2-32, P1-TBRL1-23 | C1S5-33/P1-TBDI2-31, C1S5-34/P1-TBDI2-32, C1S8-25/P1-TBRL1-23 | P1-TBDI2-31/C1S5-33, P1-TBDI2-32/C1S5-34, P1-TBRL1-23/C1S8-25 | XV-40203D_DI_1, XV-40203D_DI_2, XV-40203D_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
198 | XV-40203E | XV-40201E | 325-01-402-PD-02 | CIP hight pressure water washing Spray dryer infeed tank | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S6, C1S8 | 1756-IB32, 1756-OB32 | IN-0, IN-1, OUT-23 | 1, 2, 26 | P1-TBDI3-1, P1-TBDI3-2, P1-TBRL1-24 | C1S6-1/P1-TBDI3-1, C1S6-2/P1-TBDI3-2, C1S8-26/P1-TBRL1-24 | P1-TBDI3-1/C1S6-1, P1-TBDI3-2/C1S6-2, P1-TBRL1-24/C1S8-26 | XV-40203E_DI_1, XV-40203E_DI_2, XV-40203E_DO_1 | JB-401 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
199 | XV-40203F | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S1, C2S6 | 1756-IB32, 1756-OB32 | IN-6, IN-7, OUT-0 | 7, 8, 1 | P2-TBDI1-7, P2-TBDI1-8, P2-TBRL1-1 | C2S1-7/P2-TBDI1-7, C2S1-8/P2-TBDI1-8, C2S6-1/P2-TBRL1-1 | P2-TBDI1-7/C2S1-7, P2-TBDI1-8/C2S1-8, P2-TBRL1-1/C2S6-1 | XV-40203F_DI_1, XV-40203F_DI_2, XV-40203F_DO_1 | JB-402 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
200 | XV-40204B | - | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S1, C2S6 | 1756-IB32, 1756-OB32 | IN-8, IN-9, OUT-1 | 9, 10, 2 | P2-TBDI1-9, P2-TBDI1-10, P2-TBRL1-2 | C2S1-9/P2-TBDI1-9, C2S1-10/P2-TBDI1-10, C2S6-2/P2-TBRL1-2 | P2-TBDI1-9/C2S1-9, P2-TBDI1-10/C2S1-10, P2-TBRL1-2/C2S6-2 | XV-40204B_DI_1, XV-40204B_DI_2, XV-40204B_DO_1 | JB-402 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
201 | XV-40204C | - | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S1, C2S6 | 1756-IB32, 1756-OB32 | IN-10, IN-11, OUT-2 | 11, 12, 3 | P2-TBDI1-11, P2-TBDI1-12, P2-TBRL1-3 | C2S1-11/P2-TBDI1-11, C2S1-12/P2-TBDI1-12, C2S6-3/P2-TBRL1-3 | P2-TBDI1-11/C2S1-11, P2-TBDI1-12/C2S1-12, P2-TBRL1-3/C2S6-3 | XV-40204C_DI_1, XV-40204C_DI_2, XV-40204C_DO_1 | JB-402 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
202 | XV-40205A | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S1, C2S6 | 1756-IB32, 1756-OB32 | IN-12, IN-13, OUT-3 | 13, 14, 4 | P2-TBDI1-13, P2-TBDI1-14, P2-TBRL1-4 | C2S1-13/P2-TBDI1-13, C2S1-14/P2-TBDI1-14, C2S6-4/P2-TBRL1-4 | P2-TBDI1-13/C2S1-13, P2-TBDI1-14/C2S1-14, P2-TBRL1-4/C2S6-4 | XV-40205A_DI_1, XV-40205A_DI_2, XV-40205A_DO_1 | JB-402 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
203 | XV-40205B | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S1, C2S6 | 1756-IB32, 1756-OB32 | IN-14, IN-15, OUT-4 | 15, 16, 5 | P2-TBDI1-15, P2-TBDI1-16, P2-TBRL1-5 | C2S1-15/P2-TBDI1-15, C2S1-16/P2-TBDI1-16, C2S6-5/P2-TBRL1-5 | P2-TBDI1-15/C2S1-15, P2-TBDI1-16/C2S1-16, P2-TBRL1-5/C2S6-5 | XV-40205B_DI_1, XV-40205B_DI_2, XV-40205B_DO_1 | JB-402 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
204 | XV-40205C | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S1, C2S6 | 1756-IB32, 1756-OB32 | IN-16, IN-17, OUT-5 | 19, 20, 6 | P2-TBDI1-17, P2-TBDI1-18, P2-TBRL1-6 | C2S1-19/P2-TBDI1-17, C2S1-20/P2-TBDI1-18, C2S6-6/P2-TBRL1-6 | P2-TBDI1-17/C2S1-19, P2-TBDI1-18/C2S1-20, P2-TBRL1-6/C2S6-6 | XV-40205C_DI_1, XV-40205C_DI_2, XV-40205C_DO_1 | JB-402 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
205 | XV-40205D | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S1, C2S6 | 1756-IB32, 1756-OB32 | IN-18, IN-19, OUT-6 | 21, 22, 7 | P2-TBDI1-19, P2-TBDI1-20, P2-TBRL1-7 | C2S1-21/P2-TBDI1-19, C2S1-22/P2-TBDI1-20, C2S6-7/P2-TBRL1-7 | P2-TBDI1-19/C2S1-21, P2-TBDI1-20/C2S1-22, P2-TBRL1-7/C2S6-7 | XV-40205D_DI_1, XV-40205D_DI_2, XV-40205D_DO_1 | JB-402 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
206 | XV-40205F | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S1, C2S6 | 1756-IB32, 1756-OB32 | IN-20, IN-21, OUT-7 | 23, 24, 8 | P2-TBDI1-21, P2-TBDI1-22, P2-TBRL1-8 | C2S1-23/P2-TBDI1-21, C2S1-24/P2-TBDI1-22, C2S6-8/P2-TBRL1-8 | P2-TBDI1-21/C2S1-23, P2-TBDI1-22/C2S1-24, P2-TBRL1-8/C2S6-8 | XV-40205F_DI_1, XV-40205F_DI_2, XV-40205F_DO_1 | JB-402 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
207 | XV-40222 | - | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S1, C2S6 | 1756-IB32, 1756-OB32 | IN-22, IN-23, OUT-8 | 25, 26, 9 | P2-TBDI1-23, P2-TBDI1-24, P2-TBRL1-9 | C2S1-25/P2-TBDI1-23, C2S1-26/P2-TBDI1-24, C2S6-9/P2-TBRL1-9 | P2-TBDI1-23/C2S1-25, P2-TBDI1-24/C2S1-26, P2-TBRL1-9/C2S6-9 | XV-40222_DI_1, XV-40222_DI_2, XV-40222_DO_1 | JB-402 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
208 | XV-60201 | - | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S3, C2S7 | 1756-IB32, 1756-OB32 | IN-16, IN-17, OUT-3 | 19, 20, 4 | P2-TBDI3-17, P2-TBDI3-18, P2-TBRL2-4 | C2S3-19/P2-TBDI3-17, C2S3-20/P2-TBDI3-18, C2S7-4/P2-TBRL2-4 | P2-TBDI3-17/C2S3-19, P2-TBDI3-18/C2S3-20, P2-TBRL2-4/C2S7-4 | XV-60201_DI_1, XV-60201_DI_2, XV-60201_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
209 | XV-60251 | - | 325-01-602-PD-01 | Liquid On/Off Valve for Drain Pipe (PIPE) | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S9 | 1756-OB32 | OUT-25 | 28 | P1-TBRL2-26 | C1S9-28/P1-TBRL2-26 | P1-TBRL2-26/C1S9-28 | XV-60251_DO_1 | JB-601 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
210 | XV-60214 | XV-60301 | 325-01-602-PD-03 | Steam feed to Spray dryer | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S2, C2S6 | 1756-IB32, 1756-OB32 | IN-19, IN-20, OUT-17 | 22, 23, 20 | P2-TBDI2-20, P2-TBDI2-21, P2-TBRL1-18 | C2S2-22/P2-TBDI2-20, C2S2-23/P2-TBDI2-21, C2S6-20/P2-TBRL1-18 | P2-TBDI2-20/C2S2-22, P2-TBDI2-21/C2S2-23, P2-TBRL1-18/C2S6-20 | XV-60214_DI_1, XV-60214_DI_2, XV-60214_DO_1 | JB-602 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
211 | XV-60202 | XV-61101 | 325-01-602-PD-11 | High Pressure Water On/Off Valve for Drain Pipe | Automatic on/off valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S7, C1S9 | 1756-IB32, 1756-OB32 | IN-13, IN-14, OUT-26 | 14, 15, 29 | P1-TBDI4-14, P1-TBDI4-15, P1-TBRL2-27 | C1S7-14/P1-TBDI4-14, C1S7-15/P1-TBDI4-15, C1S9-29/P1-TBRL2-27 | P1-TBDI4-14/C1S7-14, P1-TBDI4-15/C1S7-15, P1-TBRL2-27/C1S9-29 | XV-60202_DI_1, XV-60202_DI_2, XV-60202_DO_1 | JB-601 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
212 | XV-61301 | HV-61301 | 325-01-613-PD-01 | Product feed-out Packing silo | Automatic on/off valve | 24 VDC energized | PLC | On-Off | Ex d | - | 2 | - | - | - | C3 | C3S3, C3S5 | 1756-IB32, 1756-OB32 | IN-10, IN-11, OUT-8 | 11, 12, 9 | P3-TBDI3-11, P3-TBDI3-12, P3-TBRL2-9 | C3S3-11/P3-TBDI3-11, C3S3-12/P3-TBDI3-12, C3S5-9/P3-TBRL2-9 | P3-TBDI3-11/C3S3-11, P3-TBDI3-12/C3S3-12, P3-TBRL2-9/C3S5-9 | XV-61301_DI_1, XV-61301_DI_2, XV-61301_DO_1 | JB-618 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
213 | XV-61302 | - | 325-01-613-PD-02 | Dust collector feed vent | Automatic on/off valve | 24 VDC energized | PLC | On-Off | Ex d | 1 | 2 | - | - | - | C3 | C3S2, C3S4 | 1756-IB32, 1756-OB32 | IN-13, IN-14, OUT-29 | 14, 15, 32 | P3-TBDI2-14, P3-TBDI2-15, P3-TBRL1-30 | C3S2-14/P3-TBDI2-14, C3S2-15/P3-TBDI2-15, C3S4-32/P3-TBRL1-30 | P3-TBDI2-14/C3S2-14, P3-TBDI2-15/C3S2-15, P3-TBRL1-30/C3S4-32 | XV-61302_DI_1, XV-61302_DI_2, XV-61302_DO_1 | JB-612 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
214 | XV-61303 | - | 325-01-613-PD-02 | Dust collector feed from packer | Automatic on/off valve | 24 VDC energized | PLC | On-Off | Ex d | 1 | 2 | - | - | - | C3 | C3S2, C3S4 | 1756-IB32, 1756-OB32 | IN-15, IN-16, OUT-30 | 16, 19, 33 | P3-TBDI2-16, P3-TBDI2-17, P3-TBRL1-31 | C3S2-16/P3-TBDI2-16, C3S2-19/P3-TBDI2-17, C3S4-33/P3-TBRL1-31 | P3-TBDI2-16/C3S2-16, P3-TBDI2-17/C3S2-19, P3-TBRL1-31/C3S4-33 | XV-61303_DI_1, XV-61303_DI_2, XV-61303_DO_1 | JB-612 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
215 | DV-61301 | - | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61301 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | Ex d | 1 | 2 | - | - | - | C3 | C3S3, C3S5 | 1756-IB32, 1756-OB32 | IN-0, IN-1, OUT-0 | 1, 2, 1 | P3-TBDI3-1, P3-TBDI3-2, P3-TBRL2-1 | C3S3-1/P3-TBDI3-1, C3S3-2/P3-TBDI3-2, C3S5-1/P3-TBRL2-1 | P3-TBDI3-1/C3S3-1, P3-TBDI3-2/C3S3-2, P3-TBRL2-1/C3S5-1 | DV-61301_DI_1, DV-61301_DI_2, DV-61301_DO_1 | JB-618 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
216 | DV-61302 | - | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61302 | Automatic on/off valve | 24 VDC energized | PLC | On-Off | Ex d | 1 | 2 | - | - | - | C3 | C3S3, C3S5 | 1756-IB32, 1756-OB32 | IN-2, IN-3, OUT-1 | 3, 4, 2 | P3-TBDI3-3, P3-TBDI3-4, P3-TBRL2-2 | C3S3-3/P3-TBDI3-3, C3S3-4/P3-TBDI3-4, C3S5-2/P3-TBRL2-2 | P3-TBDI3-3/C3S3-3, P3-TBDI3-4/C3S3-4, P3-TBRL2-2/C3S5-2 | DV-61302_DI_1, DV-61302_DI_2, DV-61302_DO_1 | JB-618 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
217 | ZS-60201A | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-16 | 19 | P4-TBDI1-17 | C4S1-19/P4-TBDI1-17 | P4-TBDI1-17/C4S1-19 | ZS-60201A_DI_1 | IS-JB-608 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
218 | ZS-60201B | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-17 | 20 | P4-TBDI1-18 | C4S1-20/P4-TBDI1-18 | P4-TBDI1-18/C4S1-20 | ZS-60201B_DI_1 | IS-JB-608 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
219 | ZS-60201C | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-8 | 9 | P4-TBDI1-9 | C4S1-9/P4-TBDI1-9 | P4-TBDI1-9/C4S1-9 | ZS-60201C_DI_1 | IS-JB-603 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
220 | ZS-60201D | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-9 | 10 | P4-TBDI1-10 | C4S1-10/P4-TBDI1-10 | P4-TBDI1-10/C4S1-10 | ZS-60201D_DI_1 | IS-JB-603 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
221 | ZS-60201E | - | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-10 | 11 | P4-TBDI1-11 | C4S1-11/P4-TBDI1-11 | P4-TBDI1-11/C4S1-11 | ZS-60201E_DI_1 | IS-JB-603 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
222 | ZS-60229 | - | 325-01-602-PD-04 | Limit Switch for CY-60230 (Door Service) | Limit Switch | Switch PNP | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-11 | 12 | P4-TBDI1-12 | C4S1-12/P4-TBDI1-12 | P4-TBDI1-12/C4S1-12 | ZS-60229_DI_1 | IS-JB-603 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
223 | ZS-60230 | - | 325-01-602-PD-04 | Limit Switch for CY-60231 (Door Service) | Limit Switch | Switch PNP | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-12 | 13 | P4-TBDI1-13 | C4S1-13/P4-TBDI1-13 | P4-TBDI1-13/C4S1-13 | ZS-60230_DI_1 | IS-JB-603 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
224 | ZS-60231A | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Spectacle Inserted) | Limit Switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-13 | 14 | P4-TBDI1-14 | C4S1-14/P4-TBDI1-14 | P4-TBDI1-14/C4S1-14 | ZS-60231A_DI_1 | IS-JB-603 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
225 | ZS-60231B | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Blind Inserted) | Limit Switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-14 | 15 | P4-TBDI1-15 | C4S1-15/P4-TBDI1-15 | P4-TBDI1-15/C4S1-15 | ZS-60231B_DI_1 | IS-JB-603 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
226 | ZS-60231C | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Spool Inserted) | Limit Switch | Switch PNP | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-18 | 21 | P4-TBDI1-19 | C4S1-21/P4-TBDI1-19 | P4-TBDI1-19/C4S1-21 | ZS-60231C_DI_1 | IS-JB-608 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
227 | ZS-60231D | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Blind Inserted) | Limit Switch | Switch PNP | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-19 | 22 | P4-TBDI1-20 | C4S1-22/P4-TBDI1-20 | P4-TBDI1-20/C4S1-22 | ZS-60231D_DI_1 | IS-JB-608 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
228 | ZS-60231E | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Spool Inserted) | Limit Switch | Switch PNP | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-20 | 23 | P4-TBDI1-21 | C4S1-23/P4-TBDI1-21 | P4-TBDI1-21/C4S1-23 | ZS-60231E_DI_1 | IS-JB-608 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
229 | ZS-60231F | - | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Blind Inserted) | Limit Switch | Switch PNP | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-21 | 24 | P4-TBDI1-22 | C4S1-24/P4-TBDI1-22 | P4-TBDI1-22/C4S1-24 | ZS-60231F_DI_1 | IS-JB-608 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
230 | ZS-60240 | - | 325-01-602-PD-05 | Limit Switch for FA-60240 (Door Service) | Limit Switch | Switch PNP | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S1 | 1756-IB32 | IN-22 | 25 | P4-TBDI1-23 | C4S1-25/P4-TBDI1-23 | P4-TBDI1-23/C4S1-25 | ZS-60240_DI_1 | IS-JB-608 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
231 | ZS-61310 | - | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S3 | 1756-IB32 | IN-11 | 12 | P4-TBDI3-12 | C4S3-12/P4-TBDI3-12 | P4-TBDI3-12/C4S3-12 | ZS-61310_DI_1 | IS-JB-618 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
232 | ZS-61311 | - | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S3 | 1756-IB32 | IN-12 | 13 | P4-TBDI3-13 | C4S3-13/P4-TBDI3-13 | P4-TBDI3-13/C4S3-13 | ZS-61311_DI_1 | IS-JB-618 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
233 | ZS-61312 | - | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S2 | 1756-IB32 | IN-13 | 14 | P4-TBDI2-14 | C4S2-14/P4-TBDI2-14 | P4-TBDI2-14/C4S2-14 | ZS-61312_DI_1 | IS-JB-612 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
234 | ZS-61313 | - | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S2 | 1756-IB32 | IN-14 | 15 | P4-TBDI2-15 | C4S2-15/P4-TBDI2-15 | P4-TBDI2-15/C4S2-15 | ZS-61313_DI_1 | IS-JB-612 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
235 |  | - | - | Lototo-01 | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
236 |  | - | - | Lototo-02 | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
237 |  | - | - | Lototo-03 | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
238 |  | - | - | Lototo-04 | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
239 |  | - | - | Lototo-05 | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
240 |  | - | - | Lototo-06 | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
241 |  | - | - | Lototo-07 | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
242 |  | - | - | Lototo-08 | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
243 |  | - | - | Lototo-09 | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
244 |  | - | - | Lototo-10 | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
245 |  | - | - | Lototo-11 | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
246 |  | - | - | Lototo-12 | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
246 | ES-60201 | - | - | Emergency stop activated @ Spray Nozzle 7th Floor | E-Stop Swtich | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
246 | ES-60202 | - | - | Emergency stop activated @ Sight glass 6th Floor | E-Stop Swtich | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S6 | 1756-IB32 | IN-16 | 19 | P1-TBDI3-17 | C1S6-19/P1-TBDI3-17 | P1-TBDI3-17/C1S6-19 | ES-60202_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
246 | ES-60203 | - | - | Emergency stop activated @ Control Room | E-Stop Swtich | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
246 | ES-61301 | - | - | Emergency stop activated @ SC-61301,SC-61302 | E-Stop Swtich | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
247 | DEDERT SUPPLY EQUIPMENT | DEDERT SUPPLY EQUIPMENT | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
248 | FT-60207 | FT-60701 | 325-01-602-PD-07 | Instr. Air Flow Transmitter for Camera #4 (ACAM-21) | Flow Transmitter | 4 - 20 mA | PLC | - | - | - | - | - | 1 | - | C3 | C3S7 | 1756-IF16 | i RTN-0, IN-0 | 1, 2 | P3-TBAI2-1(B), P3-TBAI2-1(A) | C3S7-1/P3-TBAI2-1(B), C3S7-2/P3-TBAI2-1(A) | P3-TBAI2-1(B)/C3S7-1, P3-TBAI2-1(A)/C3S7-2 | FT-60207_AI_1, FT-60207_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
249 | PT-60207 | PT-60701 | 325-01-602-PD-07 | Instr. Air Pressure Transmitter for Camera #4 (ACAM-21) | Pressure Transmitter | 4 - 20 mA | PLC | - | - | - | - | - | 1 | - | C3 | C3S8 | 1756-IF16 | i RTN-3, IN-3 | 7, 8 | P3-TBAI3-4(B), P3-TBAI3-4(A) | C3S8-7/P3-TBAI3-4(B), C3S8-8/P3-TBAI3-4(A) | P3-TBAI3-4(B)/C3S8-7, P3-TBAI3-4(A)/C3S8-8 | PT-60207_AI_1, PT-60207_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
250 | XV-60240D | SV-60240D | 325-01-602-PD-05 | PA On/Off Valve for Bag House Tank Valve (BGHS-21) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S7, C1S9 | 1756-IB32, 1756-OB32 | IN-17, IN-18, IN-19, IN-20, OUT-24 | 20, 21, 22, 23, 27 | P1-TBDI4-18, P1-TBDI4-19, P1-TBDI4-20, P1-TBDI4-21, P1-TBRL2-25 | C1S7-20/P1-TBDI4-18, C1S7-21/P1-TBDI4-19, C1S7-22/P1-TBDI4-20... | P1-TBDI4-18/C1S7-20, P1-TBDI4-19/C1S7-21, P1-TBDI4-20/C1S7-22... | XV-60240D_DI_1, XV-60240D_DI_2, XV-60240D_DI_1, XV-60240D_DI_2, XV-60240D_DO_1 | JB-601 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
251 | SV-60207 | SV-60701 | 325-01-602-PD-07 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) | On/Off Valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C2 | C2S3, C2S7 | 1756-IB32, 1756-OB32 | IN-8, IN-9, OUT-0 | 9, 10, 1 | P2-TBDI3-9, P2-TBDI3-10, P2-TBRL2-1 | C2S3-9/P2-TBDI3-9, C2S3-10/P2-TBDI3-10, C2S7-1/P2-TBRL2-1 | P2-TBDI3-9/C2S3-9, P2-TBDI3-10/C2S3-10, P2-TBRL2-1/C2S7-1 | SV-60207_DI_1, SV-60207_DI_2, SV-60207_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
252 | SV-60201 | - | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) | On/Off Valve | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C1 | C1S6, C1S9 | 1756-IB32, 1756-OB32 | IN-19, IN-20, OUT-16 | 22, 23, 19 | P1-TBDI3-20, P1-TBDI3-21, P1-TBRL2-17 | C1S6-22/P1-TBDI3-20, C1S6-23/P1-TBDI3-21, C1S9-19/P1-TBRL2-17 | P1-TBDI3-20/C1S6-22, P1-TBDI3-21/C1S6-23, P1-TBRL2-17/C1S9-19 | SV-60201_DI_1, SV-60201_DI_2, SV-60201_DO_1 | JB-601 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
| SSL-60201 | - | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-21) | Low Speed Switch | Switch PNP | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
| ZS-60201 | - | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-21/ RV-60201) Casing Closed | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 4Cx1.0 (Open/Close Limit Switches) | SPARE_ALLOCATABLE
253 | SV-60202 | - | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) | On/Off Valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S6, C1S9 | 1756-IB32, 1756-OB32 | IN-21, IN-22, OUT-17 | 24, 25, 20 | P1-TBDI3-22, P1-TBDI3-23, P1-TBRL2-18 | C1S6-24/P1-TBDI3-22, C1S6-25/P1-TBDI3-23, C1S9-20/P1-TBRL2-18 | P1-TBDI3-22/C1S6-24, P1-TBDI3-23/C1S6-25, P1-TBRL2-18/C1S9-20 | SV-60202_DI_1, SV-60202_DI_2, SV-60202_DO_1 | JB-601 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
| SSL-60202 | - | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-22) | Low Speed Switch | Switch PNP | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
| ZS-60202 | - | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-22/ RV-60202) Casing Closed | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 4Cx1.0 (Open/Close Limit Switches) | SPARE_ALLOCATABLE
254 | SV-60203 | - | 325-01-602-PD-08 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) | On/Off Valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C1 | C1S6, C1S9 | 1756-IB32, 1756-OB32 | IN-23, IN-24, OUT-19 | 26, 27, 22 | P1-TBDI3-24, P1-TBDI3-25, P1-TBRL2-20 | C1S6-26/P1-TBDI3-24, C1S6-27/P1-TBDI3-25, C1S9-22/P1-TBRL2-20 | P1-TBDI3-24/C1S6-26, P1-TBDI3-25/C1S6-27, P1-TBRL2-20/C1S9-22 | SV-60203_DI_1, SV-60203_DI_2, SV-60203_DO_1 | JB-601 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
| SSL-60203 | - | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-23) | Low Speed Switch | Switch PNP | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
| ZS-60203 | - | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-23/ RV-60203) Casing Closed | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 4Cx1.0 (Open/Close Limit Switches) | SPARE_ALLOCATABLE
255 | SV-61304 | - | 325-01-613-PD-01 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) | On/Off Valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | C3 | C3S3, C3S5 | 1756-IB32, 1756-OB32 | IN-8, IN-9, OUT-5 | 9, 10, 6 | P3-TBDI3-9, P3-TBDI3-10, P3-TBRL2-6 | C3S3-9/P3-TBDI3-9, C3S3-10/P3-TBDI3-10, C3S5-6/P3-TBRL2-6 | P3-TBDI3-9/C3S3-9, P3-TBDI3-10/C3S3-10, P3-TBRL2-6/C3S5-6 | SV-61304_DI_1, SV-61304_DI_2, SV-61304_DO_1 | JB-618 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
| SSL-61304 | - | 325-01-613-PD-01 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-31) | Low Speed Switch | Switch PNP | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
| ZS-61304 | - | 325-01-613-PD-01 | Position - Rotary Valve (RVAL-31/ RV-61304) Casing Closed | Position switch | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 4Cx1.0 (Open/Close Limit Switches) | SPARE_ALLOCATABLE
256 | TT-60207 | TT-60701 | 325-01-602-PD-07 | Instr. Air Temperature Transmitter for Air Manifold - Camera #4 (ACAM-21) | Temperature Transmitter | 4 - 20 mA | PLC | - | - | - | - | - | 1 | - | C3 | C3S8 | 1756-IF16 | i RTN-9, IN-9 | 21, 22 | P3-TBAI3-10(B), P3-TBAI3-10(A) | C3S8-21/P3-TBAI3-10(B), C3S8-22/P3-TBAI3-10(A) | P3-TBAI3-10(B)/C3S8-21, P3-TBAI3-10(A)/C3S8-22 | TT-60207_AI_1, TT-60207_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
257 | XV-60261FA | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S3, C2S7 | 1756-IB32, 1756-OB32 | IN-24, IN-25, OUT-5 | 27, 28, 6 | P2-TBDI3-25, P2-TBDI3-26, P2-TBRL2-6 | C2S3-27/P2-TBDI3-25, C2S3-28/P2-TBDI3-26, C2S7-6/P2-TBRL2-6 | P2-TBDI3-25/C2S3-27, P2-TBDI3-26/C2S3-28, P2-TBRL2-6/C2S7-6 | XV-60261FA_DI_1, XV-60261FA_DI_2, XV-60261FA_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
258 | XV-60261FB | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S3, C2S7 | 1756-IB32, 1756-OB32 | IN-28, IN-29, OUT-6 | 31, 32, 7 | P2-TBDI3-29, P2-TBDI3-30, P2-TBRL2-7 | C2S3-31/P2-TBDI3-29, C2S3-32/P2-TBDI3-30, C2S7-7/P2-TBRL2-7 | P2-TBDI3-29/C2S3-31, P2-TBDI3-30/C2S3-32, P2-TBRL2-7/C2S7-7 | XV-60261FB_DI_1, XV-60261FB_DI_2, XV-60261FB_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
259 | XV-60261FC | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S7 | 1756-IB32, 1756-OB32 | IN-0, IN-1, OUT-7 | 1, 2, 8 | P2-TBDI4-1, P2-TBDI4-2, P2-TBRL2-8 | C2S4-1/P2-TBDI4-1, C2S4-2/P2-TBDI4-2, C2S7-8/P2-TBRL2-8 | P2-TBDI4-1/C2S4-1, P2-TBDI4-2/C2S4-2, P2-TBRL2-8/C2S7-8 | XV-60261FC_DI_1, XV-60261FC_DI_2, XV-60261FC_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
260 | XV-60261FD | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S7 | 1756-IB32, 1756-OB32 | IN-4, IN-5, OUT-8 | 5, 6, 9 | P2-TBDI4-5, P2-TBDI4-6, P2-TBRL2-9 | C2S4-5/P2-TBDI4-5, C2S4-6/P2-TBDI4-6, C2S7-9/P2-TBRL2-9 | P2-TBDI4-5/C2S4-5, P2-TBDI4-6/C2S4-6, P2-TBRL2-9/C2S7-9 | XV-60261FD_DI_1, XV-60261FD_DI_2, XV-60261FD_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
261 | XV-60261SA | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S7 | 1756-IB32, 1756-OB32 | IN-8, IN-9, OUT-9 | 9, 10, 10 | P2-TBDI4-9, P2-TBDI4-10, P2-TBRL2-10 | C2S4-9/P2-TBDI4-9, C2S4-10/P2-TBDI4-10, C2S7-10/P2-TBRL2-10 | P2-TBDI4-9/C2S4-9, P2-TBDI4-10/C2S4-10, P2-TBRL2-10/C2S7-10 | XV-60261SA_DI_1, XV-60261SA_DI_2, XV-60261SA_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
262 | XV-60261SB | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S7 | 1756-IB32, 1756-OB32 | IN-10, IN-11, OUT-10 | 11, 12, 11 | P2-TBDI4-11, P2-TBDI4-12, P2-TBRL2-11 | C2S4-11/P2-TBDI4-11, C2S4-12/P2-TBDI4-12, C2S7-11/P2-TBRL2-11 | P2-TBDI4-11/C2S4-11, P2-TBDI4-12/C2S4-12, P2-TBRL2-11/C2S7-11 | XV-60261SB_DI_1, XV-60261SB_DI_2, XV-60261SB_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
263 | XV-60261SC | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S7 | 1756-IB32, 1756-OB32 | IN-12, IN-13, OUT-11 | 13, 14, 12 | P2-TBDI4-13, P2-TBDI4-14, P2-TBRL2-12 | C2S4-13/P2-TBDI4-13, C2S4-14/P2-TBDI4-14, C2S7-12/P2-TBRL2-12 | P2-TBDI4-13/C2S4-13, P2-TBDI4-14/C2S4-14, P2-TBRL2-12/C2S7-12 | XV-60261SC_DI_1, XV-60261SC_DI_2, XV-60261SC_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
264 | XV-60261SD | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S7 | 1756-IB32, 1756-OB32 | IN-14, IN-15, OUT-12 | 15, 16, 13 | P2-TBDI4-15, P2-TBDI4-16, P2-TBRL2-13 | C2S4-15/P2-TBDI4-15, C2S4-16/P2-TBDI4-16, C2S7-13/P2-TBRL2-13 | P2-TBDI4-15/C2S4-15, P2-TBDI4-16/C2S4-16, P2-TBRL2-13/C2S7-13 | XV-60261SD_DI_1, XV-60261SD_DI_2, XV-60261SD_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
265 | XV-60262FE | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S7 | 1756-IB32, 1756-OB32 | IN-18, IN-19, OUT-14 | 21, 22, 15 | P2-TBDI4-19, P2-TBDI4-20, P2-TBRL2-15 | C2S4-21/P2-TBDI4-19, C2S4-22/P2-TBDI4-20, C2S7-15/P2-TBRL2-15 | P2-TBDI4-19/C2S4-21, P2-TBDI4-20/C2S4-22, P2-TBRL2-15/C2S7-15 | XV-60262FE_DI_1, XV-60262FE_DI_2, XV-60262FE_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
266 | XV-60262FF | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S7 | 1756-IB32, 1756-OB32 | IN-20, IN-21, OUT-15 | 23, 24, 16 | P2-TBDI4-21, P2-TBDI4-22, P2-TBRL2-16 | C2S4-23/P2-TBDI4-21, C2S4-24/P2-TBDI4-22, C2S7-16/P2-TBRL2-16 | P2-TBDI4-21/C2S4-23, P2-TBDI4-22/C2S4-24, P2-TBRL2-16/C2S7-16 | XV-60262FF_DI_1, XV-60262FF_DI_2, XV-60262FF_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
267 | XV-60262FG | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S7 | 1756-IB32, 1756-OB32 | IN-22, IN-23, OUT-16 | 25, 26, 19 | P2-TBDI4-23, P2-TBDI4-24, P2-TBRL2-17 | C2S4-25/P2-TBDI4-23, C2S4-26/P2-TBDI4-24, C2S7-19/P2-TBRL2-17 | P2-TBDI4-23/C2S4-25, P2-TBDI4-24/C2S4-26, P2-TBRL2-17/C2S7-19 | XV-60262FG_DI_1, XV-60262FG_DI_2, XV-60262FG_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
268 | XV-60262FH | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S7 | 1756-IB32, 1756-OB32 | IN-24, IN-25, OUT-17 | 27, 28, 20 | P2-TBDI4-25, P2-TBDI4-26, P2-TBRL2-18 | C2S4-27/P2-TBDI4-25, C2S4-28/P2-TBDI4-26, C2S7-20/P2-TBRL2-18 | P2-TBDI4-25/C2S4-27, P2-TBDI4-26/C2S4-28, P2-TBRL2-18/C2S7-20 | XV-60262FH_DI_1, XV-60262FH_DI_2, XV-60262FH_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
269 | XV-60262SE | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S7 | 1756-IB32, 1756-OB32 | IN-26, IN-27, OUT-18 | 29, 30, 21 | P2-TBDI4-27, P2-TBDI4-28, P2-TBRL2-19 | C2S4-29/P2-TBDI4-27, C2S4-30/P2-TBDI4-28, C2S7-21/P2-TBRL2-19 | P2-TBDI4-27/C2S4-29, P2-TBDI4-28/C2S4-30, P2-TBRL2-19/C2S7-21 | XV-60262SE_DI_1, XV-60262SE_DI_2, XV-60262SE_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
270 | XV-60262SF | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S7 | 1756-IB32, 1756-OB32 | IN-28, IN-29, OUT-19 | 31, 32, 22 | P2-TBDI4-29, P2-TBDI4-30, P2-TBRL2-20 | C2S4-31/P2-TBDI4-29, C2S4-32/P2-TBDI4-30, C2S7-22/P2-TBRL2-20 | P2-TBDI4-29/C2S4-31, P2-TBDI4-30/C2S4-32, P2-TBRL2-20/C2S7-22 | XV-60262SF_DI_1, XV-60262SF_DI_2, XV-60262SF_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
271 | XV-60262SG | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S7 | 1756-IB32, 1756-OB32 | IN-30, IN-31, OUT-20 | 33, 34, 23 | P2-TBDI4-31, P2-TBDI4-32, P2-TBRL2-21 | C2S4-33/P2-TBDI4-31, C2S4-34/P2-TBDI4-32, C2S7-23/P2-TBRL2-21 | P2-TBDI4-31/C2S4-33, P2-TBDI4-32/C2S4-34, P2-TBRL2-21/C2S7-23 | XV-60262SG_DI_1, XV-60262SG_DI_2, XV-60262SG_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
272 | XV-60262SH | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S5, C2S7 | 1756-IB32, 1756-OB32 | IN-0, IN-1, OUT-21 | 1, 2, 24 | P2-TBDI5-1, P2-TBDI5-2, P2-TBRL2-22 | C2S5-1/P2-TBDI5-1, C2S5-2/P2-TBDI5-2, C2S7-24/P2-TBRL2-22 | P2-TBDI5-1/C2S5-1, P2-TBDI5-2/C2S5-2, P2-TBRL2-22/C2S7-24 | XV-60262SH_DI_1, XV-60262SH_DI_2, XV-60262SH_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
273 | XV-60263FJ | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S5, C2S7 | 1756-IB32, 1756-OB32 | IN-4, IN-5, OUT-23 | 5, 6, 26 | P2-TBDI5-5, P2-TBDI5-6, P2-TBRL2-24 | C2S5-5/P2-TBDI5-5, C2S5-6/P2-TBDI5-6, C2S7-26/P2-TBRL2-24 | P2-TBDI5-5/C2S5-5, P2-TBDI5-6/C2S5-6, P2-TBRL2-24/C2S7-26 | XV-60263FJ_DI_1, XV-60263FJ_DI_2, XV-60263FJ_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
274 | XV-60263FK | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S5, C2S7 | 1756-IB32, 1756-OB32 | IN-6, IN-7, OUT-24 | 7, 8, 27 | P2-TBDI5-7, P2-TBDI5-8, P2-TBRL2-25 | C2S5-7/P2-TBDI5-7, C2S5-8/P2-TBDI5-8, C2S7-27/P2-TBRL2-25 | P2-TBDI5-7/C2S5-7, P2-TBDI5-8/C2S5-8, P2-TBRL2-25/C2S7-27 | XV-60263FK_DI_1, XV-60263FK_DI_2, XV-60263FK_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
275 | XV-60263FL | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S5, C2S7 | 1756-IB32, 1756-OB32 | IN-8, IN-9, OUT-25 | 9, 10, 28 | P2-TBDI5-9, P2-TBDI5-10, P2-TBRL2-26 | C2S5-9/P2-TBDI5-9, C2S5-10/P2-TBDI5-10, C2S7-28/P2-TBRL2-26 | P2-TBDI5-9/C2S5-9, P2-TBDI5-10/C2S5-10, P2-TBRL2-26/C2S7-28 | XV-60263FL_DI_1, XV-60263FL_DI_2, XV-60263FL_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
276 | XV-60263FM | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S5, C2S7 | 1756-IB32, 1756-OB32 | IN-10, IN-11, OUT-26 | 11, 12, 29 | P2-TBDI5-11, P2-TBDI5-12, P2-TBRL2-27 | C2S5-11/P2-TBDI5-11, C2S5-12/P2-TBDI5-12, C2S7-29/P2-TBRL2-27 | P2-TBDI5-11/C2S5-11, P2-TBDI5-12/C2S5-12, P2-TBRL2-27/C2S7-29 | XV-60263FM_DI_1, XV-60263FM_DI_2, XV-60263FM_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
277 | XV-60263SJ | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S5, C2S7 | 1756-IB32, 1756-OB32 | IN-12, IN-13, OUT-27 | 13, 14, 30 | P2-TBDI5-13, P2-TBDI5-14, P2-TBRL2-28 | C2S5-13/P2-TBDI5-13, C2S5-14/P2-TBDI5-14, C2S7-30/P2-TBRL2-28 | P2-TBDI5-13/C2S5-13, P2-TBDI5-14/C2S5-14, P2-TBRL2-28/C2S7-30 | XV-60263SJ_DI_1, XV-60263SJ_DI_2, XV-60263SJ_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
278 | XV-60263SK | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S5, C2S7 | 1756-IB32, 1756-OB32 | IN-14, IN-15, OUT-28 | 15, 16, 31 | P2-TBDI5-15, P2-TBDI5-16, P2-TBRL2-29 | C2S5-15/P2-TBDI5-15, C2S5-16/P2-TBDI5-16, C2S7-31/P2-TBRL2-29 | P2-TBDI5-15/C2S5-15, P2-TBDI5-16/C2S5-16, P2-TBRL2-29/C2S7-31 | XV-60263SK_DI_1, XV-60263SK_DI_2, XV-60263SK_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
279 | XV-60263SL | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S5, C2S7 | 1756-IB32, 1756-OB32 | IN-16, IN-17, OUT-29 | 19, 20, 32 | P2-TBDI5-17, P2-TBDI5-18, P2-TBRL2-30 | C2S5-19/P2-TBDI5-17, C2S5-20/P2-TBDI5-18, C2S7-32/P2-TBRL2-30 | P2-TBDI5-17/C2S5-19, P2-TBDI5-18/C2S5-20, P2-TBRL2-30/C2S7-32 | XV-60263SL_DI_1, XV-60263SL_DI_2, XV-60263SL_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
280 | XV-60263SM | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S5, C2S7 | 1756-IB32, 1756-OB32 | IN-18, IN-19, OUT-30 | 21, 22, 33 | P2-TBDI5-19, P2-TBDI5-20, P2-TBRL2-31 | C2S5-21/P2-TBDI5-19, C2S5-22/P2-TBDI5-20, C2S7-33/P2-TBRL2-31 | P2-TBDI5-19/C2S5-21, P2-TBDI5-20/C2S5-22, P2-TBRL2-31/C2S7-33 | XV-60263SM_DI_1, XV-60263SM_DI_2, XV-60263SM_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
281 | XV-60264FN | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S3, C2S8 | 1756-IB32, 1756-OB32 | IN-12, IN-13, OUT-1 | 13, 14, 2 | P2-TBDI3-13, P2-TBDI3-14, P2-TBRL3-2 | C2S3-13/P2-TBDI3-13, C2S3-14/P2-TBDI3-14, C2S8-2/P2-TBRL3-2 | P2-TBDI3-13/C2S3-13, P2-TBDI3-14/C2S3-14, P2-TBRL3-2/C2S8-2 | XV-60264FN_DI_1, XV-60264FN_DI_2, XV-60264FN_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
282 | XV-60264FP | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S3, C2S8 | 1756-IB32, 1756-OB32 | IN-14, IN-15, OUT-2 | 15, 16, 3 | P2-TBDI3-15, P2-TBDI3-16, P2-TBRL3-3 | C2S3-15/P2-TBDI3-15, C2S3-16/P2-TBDI3-16, C2S8-3/P2-TBRL3-3 | P2-TBDI3-15/C2S3-15, P2-TBDI3-16/C2S3-16, P2-TBRL3-3/C2S8-3 | XV-60264FP_DI_1, XV-60264FP_DI_2, XV-60264FP_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
283 | XV-60264FQ | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S3, C2S8 | 1756-IB32, 1756-OB32 | IN-18, IN-19, OUT-3 | 21, 22, 4 | P2-TBDI3-19, P2-TBDI3-20, P2-TBRL3-4 | C2S3-21/P2-TBDI3-19, C2S3-22/P2-TBDI3-20, C2S8-4/P2-TBRL3-4 | P2-TBDI3-19/C2S3-21, P2-TBDI3-20/C2S3-22, P2-TBRL3-4/C2S8-4 | XV-60264FQ_DI_1, XV-60264FQ_DI_2, XV-60264FQ_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
284 | XV-60264FR | - | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S3, C2S8 | 1756-IB32, 1756-OB32 | IN-22, IN-23, OUT-4 | 25, 26, 5 | P2-TBDI3-23, P2-TBDI3-24, P2-TBRL3-5 | C2S3-25/P2-TBDI3-23, C2S3-26/P2-TBDI3-24, C2S8-5/P2-TBRL3-5 | P2-TBDI3-23/C2S3-25, P2-TBDI3-24/C2S3-26, P2-TBRL3-5/C2S8-5 | XV-60264FR_DI_1, XV-60264FR_DI_2, XV-60264FR_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
285 | XV-60264SN | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S3, C2S8 | 1756-IB32, 1756-OB32 | IN-26, IN-27, OUT-5 | 29, 30, 6 | P2-TBDI3-27, P2-TBDI3-28, P2-TBRL3-6 | C2S3-29/P2-TBDI3-27, C2S3-30/P2-TBDI3-28, C2S8-6/P2-TBRL3-6 | P2-TBDI3-27/C2S3-29, P2-TBDI3-28/C2S3-30, P2-TBRL3-6/C2S8-6 | XV-60264SN_DI_1, XV-60264SN_DI_2, XV-60264SN_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
286 | XV-60264SP | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S3, C2S8 | 1756-IB32, 1756-OB32 | IN-30, IN-31, OUT-6 | 33, 34, 7 | P2-TBDI3-31, P2-TBDI3-32, P2-TBRL3-7 | C2S3-33/P2-TBDI3-31, C2S3-34/P2-TBDI3-32, C2S8-7/P2-TBRL3-7 | P2-TBDI3-31/C2S3-33, P2-TBDI3-32/C2S3-34, P2-TBRL3-7/C2S8-7 | XV-60264SP_DI_1, XV-60264SP_DI_2, XV-60264SP_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
287 | XV-60264SQ | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S8 | 1756-IB32, 1756-OB32 | IN-2, IN-3, OUT-7 | 3, 4, 8 | P2-TBDI4-3, P2-TBDI4-4, P2-TBRL3-8 | C2S4-3/P2-TBDI4-3, C2S4-4/P2-TBDI4-4, C2S8-8/P2-TBRL3-8 | P2-TBDI4-3/C2S4-3, P2-TBDI4-4/C2S4-4, P2-TBRL3-8/C2S8-8 | XV-60264SQ_DI_1, XV-60264SQ_DI_2, XV-60264SQ_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
288 | XV-60264SR | - | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S4, C2S8 | 1756-IB32, 1756-OB32 | IN-6, IN-7, OUT-8 | 7, 8, 9 | P2-TBDI4-7, P2-TBDI4-8, P2-TBRL3-9 | C2S4-7/P2-TBDI4-7, C2S4-8/P2-TBDI4-8, C2S8-9/P2-TBRL3-9 | P2-TBDI4-7/C2S4-7, P2-TBDI4-8/C2S4-8, P2-TBRL3-9/C2S8-9 | XV-60264SR_DI_1, XV-60264SR_DI_2, XV-60264SR_DO_1 | JB-607 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
289 | XV-60261DA | - | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11A | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | SPARE_ALLOCATABLE
290 | XV-60262DE | - | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11B | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | SPARE_ALLOCATABLE
291 | XV-60263DN | - | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11C | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | SPARE_ALLOCATABLE
292 | XV-60264DJ | - | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11D | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | SPARE_ALLOCATABLE
293 | XV-60241 | - | 325-01-602-PD-05 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | On/Off Valve | 24 VDC energized,Dry Contact | PLC | On-Off | - | 1 | 2 | - | - | - | C2 | C2S2, C2S6 | 1756-IB32, 1756-OB32 | IN-21, IN-22, OUT-18 | 24, 25, 21 | P2-TBDI2-22, P2-TBDI2-23, P2-TBRL1-19 | C2S2-24/P2-TBDI2-22, C2S2-25/P2-TBDI2-23, C2S6-21/P2-TBRL1-19 | P2-TBDI2-22/C2S2-24, P2-TBDI2-23/C2S2-25, P2-TBRL1-19/C2S6-21 | XV-60241_DI_1, XV-60241_DI_2, XV-60241_DO_1 | JB-602 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
294 | XV-60240 | - | 325-01-602-PD-08 | Powder On/Off Valve for Diverter Valve (DVTR-21) | On/Off Valve | 24 VDC energized | PLC | On-Off | - | 1 | 2 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | SPARE_ALLOCATABLE
295 | Machine Equipment Supply | Machine Equipment Supply | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
296 | PSE-61300 | - | 325-01-613-PD-01 | Explosion Vent PSE-61300 | Position switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S3 | 1756-IB32 | IN-6 | 7 | P4-TBDI3-7 | C4S3-7/P4-TBDI3-7 | P4-TBDI3-7/C4S3-7 | PSE-61300_DI_1 | IS-JB-618 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
297 | PSE-61301 | - | 325-01-613-PD-01 | Explosion Vent PSE-61301 | Position switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S3 | 1756-IB32 | IN-7 | 8 | P4-TBDI3-8 | C4S3-8/P4-TBDI3-8 | P4-TBDI3-8/C4S3-8 | PSE-61301_DI_1 | IS-JB-618 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
298 | ISV-61302 | - | 325-01-613-PD-01 | Explosion isolation flap valve ISV-61302 | Position switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | SPARE_ALLOCATABLE
299 | PSE-61302 | - | 325-01-613-PD-03 | Explosion Vent PSE-61302 | Position switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S2 | 1756-IB32 | IN-6 | 7 | P4-TBDI2-7 | C4S2-7/P4-TBDI2-7 | P4-TBDI2-7/C4S2-7 | PSE-61302_DI_1 | IS-JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
300 | PSE-61303 | - | 325-01-613-PD-05 | Explosion Vent PSE-61303 | Position switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S2 | 1756-IB32 | IN-7 | 8 | P4-TBDI2-8 | C4S2-8/P4-TBDI2-8 | P4-TBDI2-8/C4S2-8 | PSE-61303_DI_1 | IS-JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
301 | PSE-61304 | - | 325-01-613-PD-01 | Explosion Vent PSE-61304 | Position switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S3 | 1756-IB32 | IN-8 | 9 | P4-TBDI3-9 | C4S3-9/P4-TBDI3-9 | P4-TBDI3-9/C4S3-9 | PSE-61304_DI_1 | IS-JB-618 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
302 | ZS-61306 | PSV-61301A | 325-01-613-PD-01 | Position Brether Valve High Pressure PSV-61301 | Position switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S3 | 1756-IB32 | IN-9 | 10 | P4-TBDI3-10 | C4S3-10/P4-TBDI3-10 | P4-TBDI3-10/C4S3-10 | PSV-61301A_DI_1 | IS-JB-618 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
303 | ZS-61307 | PSV-61301B | 325-01-613-PD-01 | Position Brether Valve Vacuum Pressure PSV-61301 | Position switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S3 | 1756-IB32 | IN-10 | 11 | P4-TBDI3-11 | C4S3-11/P4-TBDI3-11 | P4-TBDI3-11/C4S3-11 | PSV-61301B_DI_1 | IS-JB-618 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_PLC
304 | ISV-61303 | - | 325-01-613-PD-03 | Explosion isolation flap valve ISV-61303 | Position switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S2 | 1756-IB32 | IN-0 | 1 | P4-TBDI2-1 | C4S2-1/P4-TBDI2-1 | P4-TBDI2-1/C4S2-1 | ISV-61303_DI_1 | IS-JB-612 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
305 | ISV-61304 | - | 325-01-613-PD-05 | Explosion isolation flap valve ISV-61304 | Position switch | Dry Contact | PLC | On-Off | Ex ic | - | 1 | - | - | - | C4 | C4S2 | 1756-IB32 | IN-1 | 2 | P4-TBDI2-2 | C4S2-2/P4-TBDI2-2 | P4-TBDI2-2/C4S2-2 | ISV-61304_DI_1 | IS-JB-612 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
306 | MCC ROOM | MCC ROOM | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
307 | AT-40201 | ATY-40101 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40201 |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | C4 | C4S1 | 1756-IB32 | IN-0 | 1 | P4-TBDI1-1 | C4S1-1/P4-TBDI1-1 | P4-TBDI1-1/C4S1-1 | AT-40201_DI_1 | IS-JB-603 | LiY-CY TP 2Px1.0 (Signal) + CVV 3Cx1.5 (24VDC Power) | MAPPED_PLC
308 | AT-40202 | ATY-40102 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40202 |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | C4 | C4S1 | 1756-IB32 | IN-1 | 2 | P4-TBDI1-2 | C4S1-2/P4-TBDI1-2 | P4-TBDI1-2/C4S1-2 | AT-40202_DI_1 | IS-JB-603 | LiY-CY TP 2Px1.0 (Signal) + CVV 3Cx1.5 (24VDC Power) | MAPPED_PLC
309 | AT-40203 | ATY-40201 | 325-01-402-PD-02 | Start / Stop Command for VSD AT-40203 |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | C4 | C4S1 | 1756-IB32 | IN-2 | 3 | P4-TBDI1-3 | C4S1-3/P4-TBDI1-3 | P4-TBDI1-3/C4S1-3 | AT-40203_DI_1 | IS-JB-603 | LiY-CY TP 2Px1.0 (Signal) + CVV 3Cx1.5 (24VDC Power) | MAPPED_PLC
310 | BF-60210 | BFY-60210 | 325-01-602-PD-03 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
311 | BF-60211 | BFY-60211 | 325-01-602-PD-03 | Start / Stop Command for VSD FANC-21 (Combustion Fan) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
312 | BF-60240 | BFY-60240 | 325-01-602-PD-05 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
313 | BF-60220 | BFY-60220 | 325-01-602-PD-04 | Start / Stop Command for VSD FANS-22 (Cooling Fan) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
314 | BF-60206 | BFY-60206 | 325-01-602-PD-08 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
315 | BF-61301 | BFY-61301 | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
316 | BF-61302 | BFY-61302 | 325-01-613-PD-05 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
317 | BF-61303 | BFY-61303 | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
318 | BLM-61302 | BLM-61302 | 325-01-613-PD-01 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | เปลี่ยนไปจ่ายเป็น Power Feeder | 24 VDC energized | PLC | On-Off | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
319 | PD-60202B | PCM-60205-B | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Oil Pump ) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
320 | PD-60202C | PCM-60205-C | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 1 ) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
321 | PD-60202D | PCM-60205-D | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 2 ) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
322 | PD-60202E | PCM-60205-E | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Main motor Fan ) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
323 | PC-40203 | PCY-40201 | 325-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
324 | PC-40201 | PCY-40101 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40201 |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
325 | PC-40202 | PCY-40102 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40202 |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
326 | PD-40204 | - | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40204 |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
327 | PD-40205 | - | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40205 |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
328 | PD-60202A | PCY-60205-A | 325-01-602-PD-01 | Start / Stop Command for VSD PUPD-11 (Positive Displacement Pump ) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
329 | PCY-60215 | PCY-60215 | 325-01-602-PD-03 | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
330 | BL-61301 | PVM-61301 | 325-01-613-PD-03 | Start / Stop Command for FVNR PV-61301 (Vacuum Cleaning Fan) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | C3 | C3S2, C3S4 | 1756-IB32, 1756-OB32 | IN-2, IN-3, OUT-16, OUT-17 | 3, 4, 19, 20 | P3-TBDI2-3, P3-TBDI2-4, P3-TBRL1-17, P3-TBRL1-18 | C3S2-3/P3-TBDI2-3, C3S2-4/P3-TBDI2-4, C3S4-19/P3-TBRL1-17... | P3-TBDI2-3/C3S2-3, P3-TBDI2-4/C3S2-4, P3-TBRL1-17/C3S4-19... | PVM-61301_DI_1, PVM-61301_DI_2, PVM-61301_DO_1, PVM-61301_DO_2 | JB-612 | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MAPPED_PLC
331 | RVM-60201 | RVM-60201 | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
332 | RVM-60202 | RVM-60202 | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
333 | RVM-60203 | RVM-60203 | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
334 | RVM-60204 | RVM-60204 | 325-01-602-PD-08 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
335 | RVM-61301 | RVM-61301 | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61301 |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
336 | RVM-61302 | RVM-61302 | 325-01-613-PD-03 | Start / Stop Command for FVNR RV-61302 |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
337 | RVM-61303 | RVM-61303 | 325-01-613-PD-05 | Start / Stop Command for FVNR RV-61303 |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
338 | RVM-61304 | RVM-61304 | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61304 |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
339 | RVM-61305 | RVM-61305 | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61305 |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
340 | SCM-61301 | SCM-61301 | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61301 (Sifter ) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
341 | SCM-61302 | SCM-61302 | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61302 (Sifter ) |  | 24 VDC energized | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
342 | B&B Packing | B&B Packing | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
343 | XA-61301A | - | 325-01-613-PD-02 | Request filter plant (Fugitive) | Request filter plant | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C3 | C3S2 | 1756-IB32 | IN-4 | 5 | P3-TBDI2-5 | C3S2-5/P3-TBDI2-5 | P3-TBDI2-5/C3S2-5 | XA-61301A_DI_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
344 | XA-61301B | - | 325-01-613-PD-02 | Request material transport | Request material transport | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C3 | C3S2 | 1756-IB32 | IN-5 | 6 | P3-TBDI2-6 | C3S2-6/P3-TBDI2-6 | P3-TBDI2-6/C3S2-6 | XA-61301B_DI_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
345 | XA-61301C | - | 325-01-613-PD-02 | Request belt plant | Request belt plant | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C3 | C3S2 | 1756-IB32 | IN-6 | 7 | P3-TBDI2-7 | C3S2-7/P3-TBDI2-7 | P3-TBDI2-7/C3S2-7 | XA-61301C_DI_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
346 | XA-61301D | - | 325-01-613-PD-02 | Machine in operation | Machine in operation | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C3 | C3S2 | 1756-IB32 | IN-7 | 8 | P3-TBDI2-8 | C3S2-8/P3-TBDI2-8 | P3-TBDI2-8/C3S2-8 | XA-61301D_DI_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
347 | XA-61301E | - | 325-01-613-PD-02 | General Fault | General Fault | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C3 | C3S2 | 1756-IB32 | IN-8 | 9 | P3-TBDI2-9 | C3S2-9/P3-TBDI2-9 | P3-TBDI2-9/C3S2-9 | XA-61301E_DI_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
348 | XA-61301F | - | 325-01-613-PD-02 | Machine is ready | Machine is ready | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C3 | C3S2 | 1756-IB32 | IN-9 | 10 | P3-TBDI2-10 | C3S2-10/P3-TBDI2-10 | P3-TBDI2-10/C3S2-10 | XA-61301F_DI_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
349 | XA-61301G | - | 325-01-613-PD-02 | Emergency stop activated | Emergency stop activated | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C3 | C3S2 | 1756-IB32 | IN-10 | 11 | P3-TBDI2-11 | C3S2-11/P3-TBDI2-11 | P3-TBDI2-11/C3S2-11 | XA-61301G_DI_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
350 | XA-61301H | - | 325-01-613-PD-02 | Silo minimum | Silo minimum | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C3 | C3S2 | 1756-IB32 | IN-11 | 12 | P3-TBDI2-12 | C3S2-12/P3-TBDI2-12 | P3-TBDI2-12/C3S2-12 | XA-61301H_DI_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
351 | XA-61301J | - | 325-01-613-PD-02 | Silo maximum | Silo maximum | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C3 | C3S2 | 1756-IB32 | IN-12 | 13 | P3-TBDI2-13 | C3S2-13/P3-TBDI2-13 | P3-TBDI2-13/C3S2-13 | XA-61301J_DI_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
352 | XS-61301A | - | 325-01-613-PD-02 | Filter plant in operation | Filter plant in operation | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C3 | C3S4 | 1756-OB32 | OUT-23 | 26 | P3-TBRL1-24 | C3S4-26/P3-TBRL1-24 | P3-TBRL1-24/C3S4-26 | XS-61301A_DO_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
353 | XS-61301B | - | 325-01-613-PD-02 | Material transport in operation | Material transport in operation | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C3 | C3S4 | 1756-OB32 | OUT-24 | 27 | P3-TBRL1-25 | C3S4-27/P3-TBRL1-25 | P3-TBRL1-25/C3S4-27 | XS-61301B_DO_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
354 | XS-61301C | - | 325-01-613-PD-02 | Belt plant in operation | Belt plant in operation | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C3 | C3S4 | 1756-OB32 | OUT-25 | 28 | P3-TBRL1-26 | C3S4-28/P3-TBRL1-26 | P3-TBRL1-26/C3S4-28 | XS-61301C_DO_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
355 | XS-61301D | - | 325-01-613-PD-02 | Sequence Stop | Sequence Stop | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C3 | C3S4 | 1756-OB32 | OUT-26 | 29 | P3-TBRL1-27 | C3S4-29/P3-TBRL1-27 | P3-TBRL1-27/C3S4-29 | XS-61301D_DO_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
356 | XS-61301E | - | 325-01-613-PD-02 | Status from Customer Emergency stop | Status from Customer Emergency stop | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C3 | C3S4 | 1756-OB32 | OUT-27 | 30 | P3-TBRL1-28 | C3S4-30/P3-TBRL1-28 | P3-TBRL1-28/C3S4-30 | XS-61301E_DO_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
357 | XS-61301F | - | 325-01-613-PD-02 | Operation Release | Operation Release | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C3 | C3S4 | 1756-OB32 | OUT-28 | 31 | P3-TBRL1-29 | C3S4-31/P3-TBRL1-29 | P3-TBRL1-29/C3S4-31 | XS-61301F_DO_1 | JB-612 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
358 |  | - | 325-01-613-PD-02 | Spare |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
359 |  | - | 325-01-613-PD-02 | Spare |  | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
360 |  | - | 325-01-613-PD-02 | Spare |  | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
361 |  | - | 325-01-613-PD-02 | Communication Signal |  | Communication Signal | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
362 | Boiler | Boiler | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
363 | XA-92201B | - | 325-01-922-PD-03 | Boiler common alarm |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
363 | XA-92201C | - | 325-01-922-PD-03 | Boiler Trip |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
363 | XA-92212B | - | 325-01-922-PD-03 | Burner Trip |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
363 | XL-92201B | - | 325-01-922-PD-03 | Boiler Operate |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
363 | XL-92201C | - | 325-01-922-PD-03 | Remote Setpoint Activated |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
363 | ZL-92201 | - | 325-01-922-PD-03 | Remote Setpoint Status |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
363 |  | - | 325-01-922-PD-03 | Communication Signal |  | Communication Signal | PLC | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
| Bin Vent Filter (FA-61301) | Bin Vent Filter (FA-61301) | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
363 | XA-FA-61301A | - | 325-01-613-PD-01 | Start / Stop Command for FA-61301 |  | Dry Contact | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
364 | XA-FA-61301B | - | 325-01-613-PD-01 | Compress air low (Spare) |  | Dry Contact | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
365 | XS-FA-61301 | - | 325-01-613-PD-01 | Alarm 1 |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
| Fugitive Dust Filter (FA-61310) | Fugitive Dust Filter (FA-61310) | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
363 | XA-FA-61310A | - | 325-01-613-PD-01 | Start / Stop Command for FA-61310 |  | Dry Contact | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
364 | XA-FA-61310B | - | 325-01-613-PD-01 | Compress air low (Spare) |  | Dry Contact | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
365 | XS-FA-61310 | - | 325-01-613-PD-01 | Alarm 1 |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
| Vacuum Cleaner Filter (FA-61311) | Vacuum Cleaner Filter (FA-61311) | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
363 | XA-FA-61311A | - | 325-01-613-PD-03 | Start / Stop Command for FA-61311 |  | Dry Contact | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
364 | XA-FA-61311B | - | 325-01-613-PD-03 | Compress air low (Spare) |  | Dry Contact | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
365 | XS-FA-61311 | - | 325-01-613-PD-03 | Alarm 1 |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
| Local Exhaust Ventilation Filter (FA-61312) | Local Exhaust Ventilation Filter (FA-61312) | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
363 | XA-FA-61312A | - | 325-01-613-PD-05 | Start / Stop Command for FA-61311 |  | Dry Contact | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
364 | XA-FA-61312B | - | 325-01-613-PD-05 | Compress air low (Spare) |  | Dry Contact | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
365 | XS-FA-61312 | - | 325-01-613-PD-05 | Alarm 1 |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
362 | Bag Filter Control Panel (FA-60240) | Bag Filter Control Panel (FA-60240) | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
363 | XS-60240A | - | 325-01-602-PD-05 | Start / Stop Command for BGHS-21 (Bag House Air Pulsing) |  | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
364 | XS-60240B | - | 325-01-602-PD-05 | Fan Command for BGHS-21 (Bag House Air Pulsing) |  | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C2 | C2S6 | 1756-OB32 | OUT-16 | 19 | P2-TBRL1-17 | C2S6-19/P2-TBRL1-17 | P2-TBRL1-17/C2S6-19 | XS-60240B_DO_1 | JB-602 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
365 | XA-60240A | - | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-11 | 12 | P2-TBDI2-12 | C2S2-12/P2-TBDI2-12 | P2-TBDI2-12/C2S2-12 | XA-60240A_DI_1 | JB-602 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
366 | XA-60240B | - | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-12 | 13 | P2-TBDI2-13 | C2S2-13/P2-TBDI2-13 | P2-TBDI2-13/C2S2-13 | XA-60240B_DI_1 | JB-602 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
367 | DPI-60240 | DPI-60240 | 325-01-602-PD-05 | Gas Pressure Differntial Pressure (Bag House Air Pulsing) |  | 4 - 20 mA | PLC | - | - | - | - | - | 1 | - | C1 | C1S11 | 1756-IF16 | i RTN-0, IN-0 | 1, 2 | P1-TBAI2-1(B), P1-TBAI2-1(A) | C1S11-1/P1-TBAI2-1(B), C1S11-2/P1-TBAI2-1(A) | P1-TBAI2-1(B)/C1S11-1, P1-TBAI2-1(A)/C1S11-2 | DPI-60240_AI_1, DPI-60240_AI_1 | JB-601 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
368 | HTRE-21 Heater Control Panel (TRACING) | HTRE-21 Heater Control Panel (TRACING) | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
369 | XS-60241A | - | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
370 | XA-60241A | - | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-13 | 14 | P2-TBDI2-14 | C2S2-14/P2-TBDI2-14 | P2-TBDI2-14/C2S2-14 | XA-60241A_DI_1 | JB-602 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
371 | XA-60241B | - | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-14 | 15 | P2-TBDI2-15 | C2S2-15/P2-TBDI2-15 | P2-TBDI2-15/C2S2-15 | XA-60241B_DI_1 | JB-602 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
372 | TSH-60241A | - | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | Heat Control Panel (HTRE-21) | 0 - 100 C | Ex d | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-5 | 6 | P2-TBDI2-6 | C2S2-6/P2-TBDI2-6 | P2-TBDI2-6/C2S2-6 | TSH-60241A_DI_1 | JB-602 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
373 | TSL-60241B | - | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | Heat Control Panel (HTRE-21) | 0 - 100 C | Ex d | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-8 | 9 | P2-TBDI2-9 | C2S2-9/P2-TBDI2-9 | P2-TBDI2-9/C2S2-9 | TSL-60241B_DI_1 | JB-602 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
374 | HTRE-22 Heater Control Panel (TRACING) | HTRE-22 Heater Control Panel (TRACING) | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
375 | XS-60242A | - | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
376 | XA-60242A | - | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-15 | 16 | P2-TBDI2-16 | C2S2-16/P2-TBDI2-16 | P2-TBDI2-16/C2S2-16 | XA-60242A_DI_1 | JB-602 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
377 | XA-60242B | - | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-16 | 19 | P2-TBDI2-17 | C2S2-19/P2-TBDI2-17 | P2-TBDI2-17/C2S2-19 | XA-60242B_DI_1 | JB-602 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
378 | TSH-60242A | - | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | Heat Control Panel (HTRE-22) | 0 - 100 C | Ex d | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-6 | 7 | P2-TBDI2-7 | C2S2-7/P2-TBDI2-7 | P2-TBDI2-7/C2S2-7 | TSH-60242A_DI_1 | JB-602 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
379 | TSL-60242B | - | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | Heat Control Panel (HTRE-22) | 0 - 100 C | Ex d | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-9 | 10 | P2-TBDI2-10 | C2S2-10/P2-TBDI2-10 | P2-TBDI2-10/C2S2-10 | TSL-60242B_DI_1 | JB-602 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
380 | HTRE-23 Heater Control Panel (TRACING) | HTRE-23 Heater Control Panel (TRACING) | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
381 | XS-60243A | - | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
382 | XA-60243A | - | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-17 | 20 | P2-TBDI2-18 | C2S2-20/P2-TBDI2-18 | P2-TBDI2-18/C2S2-20 | XA-60243A_DI_1 | JB-602 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
383 | XA-60243B | - | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-18 | 21 | P2-TBDI2-19 | C2S2-21/P2-TBDI2-19 | P2-TBDI2-19/C2S2-21 | XA-60243B_DI_1 | JB-602 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
384 | TSH-60243A | - | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | Heat Control Panel (HTRE-23) | 0 - 100 C | Ex d | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-7 | 8 | P2-TBDI2-8 | C2S2-8/P2-TBDI2-8 | P2-TBDI2-8/C2S2-8 | TSH-60243A_DI_1 | JB-602 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
385 | TSL-60243B | - | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | Dry Contact | Heat Control Panel (HTRE-23) | 0 - 100 C | Ex d | - | 1 | - | - | - | C2 | C2S2 | 1756-IB32 | IN-10 | 11 | P2-TBDI2-11 | C2S2-11/P2-TBDI2-11 | P2-TBDI2-11/C2S2-11 | TSL-60243B_DI_1 | JB-602 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
386 | Air Heater Burner Control Panel (PK-60210) | Air Heater Burner Control Panel (PK-60210) | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
387 | XA-FH-60210A | - | 325-01-602-PD-06 | BMS PANEL POWER ON for AHTR-21 |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S3 | 1756-IB32 | IN-0 | 1 | P2-TBDI3-1 | C2S3-1/P2-TBDI3-1 | P2-TBDI3-1/C2S3-1 | XA-FH-60210A_DI_1 | JB-607 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
388 | XA-FH-60210B | - | 325-01-602-PD-06 | BMS Burner High Fire Purge for AHTR-21 |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S3 | 1756-IB32 | IN-1 | 2 | P2-TBDI3-2 | C2S3-2/P2-TBDI3-2 | P2-TBDI3-2/C2S3-2 | XA-FH-60210B_DI_1 | JB-607 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
389 | XA-FH-60210C | - | 325-01-602-PD-06 | BMS Burner On for AHTR-21 |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S3 | 1756-IB32 | IN-2 | 3 | P2-TBDI3-3 | C2S3-3/P2-TBDI3-3 | P2-TBDI3-3/C2S3-3 | XA-FH-60210C_DI_1 | JB-607 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
390 | XA-FH-60210D | - | 325-01-602-PD-06 | BMS BMS Lockout for AHTR-21 |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S3 | 1756-IB32 | IN-3 | 4 | P2-TBDI3-4 | C2S3-4/P2-TBDI3-4 | P2-TBDI3-4/C2S3-4 | XA-FH-60210D_DI_1 | JB-607 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
391 | XA-FH-60210E | - | 325-01-602-PD-06 | BMS Remote Modet for AHTR-21 |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C2 | C2S3 | 1756-IB32 | IN-4 | 5 | P2-TBDI3-5 | C2S3-5/P2-TBDI3-5 | P2-TBDI3-5/C2S3-5 | XA-FH-60210E_DI_1 | JB-607 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
392 | XS-FH-60210A | - | 325-01-602-PD-06 | Burner Remote Start for AHTR-21 |  | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
393 | XS-FH-60210B | - | 325-01-602-PD-06 | Dryer Interlocks for AHTR-21 |  | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
394 | XS-FH-60210C | - | 325-01-602-PD-06 | Remote Reset for AHTR-21 |  | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C2 | C2S7 | 1756-OB32 | OUT-1 | 2 | P2-TBRL2-2 | C2S7-2/P2-TBRL2-2 | P2-TBRL2-2/C2S7-2 | XS-FH-60210C_DO_1 | JB-607 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
395 | XS-FH-60210D | - | 325-01-602-PD-06 | Spare |  | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | C2 | C2S7 | 1756-OB32 | OUT-2 | 3 | P2-TBRL2-3 | C2S7-3/P2-TBRL2-3 | P2-TBRL2-3/C2S7-3 | XS-FH-60210D_DO_1 | JB-607 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
396 | XS-FH-60210E | - | 325-01-602-PD-06 | Exhaust fan run status BF-60240 |  | Dry Contact | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
397 | XS-FH-60210F | - | 325-01-602-PD-06 | Supply fan run status BF-60210 |  | Dry Contact | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
398 | XS-FH-60210G | - | 325-01-602-PD-06 | Combusion fan run status BF-60211 |  | Dry Contact | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
399 | TI-FH-60210 | - | 325-01-602-PD-06 | Gas Burner Firing Rate Temp Signal |  | 4 - 20 mA | PLC | On-Off | - | - | - | - | 1 | - | C3 | C3S8 | 1756-IF16 | i RTN-6, IN-6 | 15, 16 | P3-TBAI3-7(B), P3-TBAI3-7(A) | C3S8-15/P3-TBAI3-7(B), C3S8-16/P3-TBAI3-7(A) | P3-TBAI3-7(B)/C3S8-15, P3-TBAI3-7(A)/C3S8-16 | TI-FH-60210_AI_1, TI-FH-60210_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
400 | UY-FH-60210A | - | 325-01-602-PD-06 | Comb fan VFD Speed Control |  | 4 - 20 mA | PLC | On-Off | - | - | - | - | 1 | - | C3 | C3S8 | 1756-IF16 | i RTN-10, IN-10 | 23, 24 | P3-TBAI3-11(B), P3-TBAI3-11(A) | C3S8-23/P3-TBAI3-11(B), C3S8-24/P3-TBAI3-11(A) | P3-TBAI3-11(B)/C3S8-23, P3-TBAI3-11(A)/C3S8-24 | UY-FH-60210A_AI_1, UY-FH-60210A_AI_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
401 | UY-FH-60210B | - | 325-01-602-PD-06 | Demand Signal |  | 4 - 20 mA | PLC | On-Off | - | - | - | 1 | - | - | C3 | C3S12 | 1756-OF8 | IOUT-4 | 4 | P3-TBAO1-5 | C3S12-4/P3-TBAO1-5 | P3-TBAO1-5/C3S12-4 | UY-FH-60210B_AO_1 | JB-607 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
402 | COM-FH-60210B | - | 325-01-602-PD-06 | Communication Signal |  | Modbus RTU | PLC | - | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
403 | TE-60212 | - | - | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Element | T/C Type K | AHTR Control Panel(HCP) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel(HCP) | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
404 | DPHL-60230 | - | - | Gas Pressure Differntial Switch Low for Exhaust Fan (FANE-21) | Pressure Differntial Switch Low | Dry Contact | AHTR Control Panel(HCP) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel(HCP) | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
405 | DPSL-60211 | - | - | Gas Pressure Differential Switch Low for Combustion Fan (FANC-21) | Pressure Differential Switch Low | Dry Contact | AHTR Control Panel(HCP) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel(HCP) | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
406 | FCV-60211B | - | - | Gas Flow Control Damper (Valve) for Burner Combustion Air Duct (DTCB-21) | Flow Control Damper (Valve) | Internal wiring | AHTR Control Panel(HCP) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel(HCP) | LiY-CY TP 2Px1.0 (Setpoint AO + Feedback AI) | PACKAGE_PANEL
407 | ZT-60211B | - | - | Gas Position Transmitter for Combustion Air Damper Actuator (DTCB-21) | Position Transmitter | Internal wiring | AHTR Control Panel(HCP) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel(HCP) | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
408 | ZSL-60211B | - | - | Gas Position Switch Low for Combustion Air Damper Actuator (DTCB-21) | Position Switch Low | Internal wiring | AHTR Control Panel(HCP) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel(HCP) | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
409 | ZSH-60211B | - | - | Gas Position Switch High for Combustion Air Damper Actuator (DTCB-21) | Position Switch High | Internal wiring | AHTR Control Panel(HCP) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel(HCP) | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
410 | VJ-01 (24VDC) | - | - | Valve train J-BOX | Control Box | Internal wiring | AHTR Control Panel(HCP) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel(HCP) | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
411 | VJ-01 (220VAC) | - | - | Valve train J-BOX | Control Box | Internal wiring | AHTR Control Panel(HCP) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel(HCP) | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
412 | UJ-01 (24VDC) | - | - | Valve train J-BOX | Control Box | Internal wiring | AHTR Control Panel(HCP) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel(HCP) | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
413 | UJ-01 (220VAC) | - | - | Valve train J-BOX | Control Box | Internal wiring | AHTR Control Panel(HCP) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel(HCP) | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
414 | PV-60210A | - | - | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
415 | PV-60210B | - | - | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
416 | DPT-60210 | - | - | Gas Pressure Differential Switch Low for Main Supply Air Fan (FANS-21) | Pressure Differential Switch Low | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
417 | DPSL-60210B | - | - | Gas Pressure Differential Switch Low for Air Heater (AHTR-21) | Pressure Differential Switch Low | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
418 | DPSH-60210C | - | - | Gas Pressure Differential Switch High for Air Heater (AHTR-21) | Pressure Differential Switch High | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
419 | BE-60210A | - | - | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
420 | BE-60210B | - | - | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
421 | IX-60210A | - | - | Gas Ignition Transformer for Air Heater (AHTR-21) | Ignition Transformer | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
422 | FCV-60210A | - | - | Gas Flow Control Valve for Air Heater Gas Train (GTRN-21) | Flow Control Valve | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | LiY-CY TP 2Px1.0 (Setpoint AO + Feedback AI) | PACKAGE_PANEL
423 | ZSL-60210A | - | - | Gas Position Switch Low for Air Heater Gas Train (GTRN-21) | Position Switch Low | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
424 | ZT-60210A | - | - | Gas Position Transmitter for Air Heater Gas Train (GTRN-21) | Position Transmitter | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
425 | PSH-60210 | - | - | Gas Pressure Switch High for Air Heater Gas Train (GTRN-21) | Pressure Switch High | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CVV 3Cx1.5 (24VDC Power + Switch Output) | PACKAGE_PANEL
426 | BV-60210B | - | - | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | PACKAGE_PANEL
427 | ZSO-60210B | - | - | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
428 | ZSC-60210B | - | - | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
429 | VV-60210 | - | - | Gas Venting Valve (main gas) for Air Heater Gas Train (GTRN-21) | Venting Valve (main gas) | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
430 | ZSO-60210C | - | - | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
431 | ZSC-60210C | - | - | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
432 | PSL-60210 | - | - | Gas Pressure Switch Low for Air Heater Gas Train (GTRN-21) | Pressure Switch Low | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CVV 3Cx1.5 (24VDC Power + Switch Output) | PACKAGE_PANEL
433 | BV-60210A | - | - | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | PACKAGE_PANEL
434 | ZSO-60210A | - | - | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
435 | ZSC-60210A | - | - | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | Internal wiring | AHTR Control Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AHTR Control Panel | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | PACKAGE_PANEL
436 | High Pressure Pump (PD-60202) | High Pressure Pump (PD-60202) | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
437 | XS-60202 | ES-60202 | 325-01-602-PD-01 | E-Stop for PUPD-11 (Positive Displacement Pump ) | E-Stop | Dry Contact | PLC | - | - | - | 1 | - | - | - | C1 | C1S6 | 1756-IB32 | IN-16 | 19 | P1-TBDI3-17 | C1S6-19/P1-TBDI3-17 | P1-TBDI3-17/C1S6-19 | ES-60202_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
438 | XA-60202 | - | 325-01-602-PD-01 | High Oil Pressure Alarm | Lamp | 24 VDC energized | PLC | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
439 | PT-60202 | PT-60205 | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter | 4 - 20 mA | PLC | - | - | - | - | - | 1 | - | C1 | C1S10 | 1756-IF16 | i RTN-10, IN-10 | 23, 24 | P1-TBAI1-11(B), P1-TBAI1-11(A) | C1S10-23/P1-TBAI1-11(B), C1S10-24/P1-TBAI1-11(A) | P1-TBAI1-11(B)/C1S10-23, P1-TBAI1-11(A)/C1S10-24 | PT-60202_AI_1, PT-60202_AI_1 | JB-401 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
440 | FS-60202 | FS-60205 | 325-01-602-PD-01 | Cooling Water Return Flow Switch for Positive Displacement Pump (PUPD-11) | Flow Switch | - | PLC | - | - | - | 1 | - | - | - | C1 | C1S6 | 1756-IB32 | IN-17 | 20 | P1-TBDI3-18 | C1S6-20/P1-TBDI3-18 | P1-TBDI3-18/C1S6-20 | FS-60205_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
441 | XS-60205 | - | 325-01-602-PD-01 | Start / Stop Command for PUPD-11 (Positive Displacement Pump ) | Start / Stop Command | - | PLC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | SPARE_ALLOCATABLE
442 | VS-60202 | VS-60205 | 325-01-602-PD-01 | Vibration Gear Box Vibration Switch for Switch Vibration for PUPD-11 (PUPD-11) | Vibration Switch | 4 - 20 mA | PLC | - | - | - | - | - | 1 | - | C1 | C1S6 | 1756-IB32 | IN-25 | 28 | P1-TBDI3-26 | C1S6-28/P1-TBDI3-26 | P1-TBDI3-26/C1S6-28 | VS-60205_DI_1 | JB-601 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_PLC
443 | XV-60202A | XV-60205A | 325-01-602-PD-01 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) | On/Off Valve | 24 VDC energized | PLC | - | - | 1 | - | - | - | - | C1 | C1S7, C1S9 | 1756-IB32, 1756-OB32 | IN-15, IN-16, OUT-27 | 16, 19, 30 | P1-TBDI4-16, P1-TBDI4-17, P1-TBRL2-28 | C1S7-16/P1-TBDI4-16, C1S7-19/P1-TBDI4-17, C1S9-30/P1-TBRL2-28 | P1-TBDI4-16/C1S7-16, P1-TBDI4-17/C1S7-19, P1-TBRL2-28/C1S9-30 | XV-60205A_DI_1, XV-60205A_DI_2, XV-60205A_DO_1 | JB-601 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
444 | PS-60202 | - | 325-01-602-PD-01 | Oil Pressure Switch for Positive Displacement Pump (PUPD-11) | Flow Switch | - | PLC | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 3Cx1.5 (24VDC Power + Switch Output) | SPARE_ALLOCATABLE
445 | TT-60202A | - | 325-01-602-PD-01 | Temperature for Positive Displacement Pump (PUPD-11) | TC / Temperature Transmitter | - | PLC | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | PLC | LiY-CY TP 1Px1.0 (Shielded Pair) | SPARE_ALLOCATABLE
446 | TT-60202B | - | 325-01-602-PD-01 | Temperature for Positive Displacement Pump (PUPD-11) | TC / Temperature Transmitter | - | PLC | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | - | PLC | LiY-CY TP 1Px1.0 (Shielded Pair) | SPARE_ALLOCATABLE
447 | YA-60205 | - | 325-01-602-PD-01 | Fault Command |  | - | PLC | - | - | - | - | - | - | - | C1 | C1S7 | 1756-IB32 | IN-21 | 24 | P1-TBDI4-22 | C1S7-24/P1-TBDI4-22 | P1-TBDI4-22/C1S7-24 | YA-60205_DI_1 | JB-601 | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MAPPED_PLC
448 | YI-60205 | - | 325-01-602-PD-01 | Run Command |  | - | PLC | - | - | - | - | - | - | - | C1 | C1S7 | 1756-IB32 | IN-22 | 25 | P1-TBDI4-23 | C1S7-25/P1-TBDI4-23 | P1-TBDI4-23/C1S7-25 | YI-60205_DI_1 | JB-601 | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MAPPED_PLC
449 | Suppression Panel | Suppression Panel | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
450 | PSH-61301 | - | 325-01-613-PD-01 | Gas and Powder Pressure Switch High for Storage Bin Cyclone Inlet Duct (####-##) | Pressure Switch High | - | Suppression Sys. Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Suppression Sys. Panel | CVV 3Cx1.5 (24VDC Power + Switch Output) | PACKAGE_PANEL
451 | PSH-60220 | - | 325-01-602-PD-04 | Gas Pressure Switch High for Spray Chamber (CHAM-21) | Pressure Switch High | - | Suppression Sys. Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Suppression Sys. Panel | CVV 3Cx1.5 (24VDC Power + Switch Output) | PACKAGE_PANEL
452 | PSH-60230 | - | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-21) | Pressure Switch High | - | Suppression Sys. Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Suppression Sys. Panel | CVV 3Cx1.5 (24VDC Power + Switch Output) | PACKAGE_PANEL
453 | PSH-60231 | - | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-22) | Pressure Switch High | - | Suppression Sys. Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Suppression Sys. Panel | CVV 3Cx1.5 (24VDC Power + Switch Output) | PACKAGE_PANEL
454 | PSH-60224 | - | 325-01-602-PD-05 | Gas and Powder Pressure Switch High for Bag House (BGHS-21) | Pressure Switch High | - | Suppression Sys. Panel | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Suppression Sys. Panel | CVV 3Cx1.5 (24VDC Power + Switch Output) | PACKAGE_PANEL
455 | XA-60202A | - | 325-01-602-PD-08 | General Alarm Emergency Stop Actuation for XSUP-5601 (Supression Panel) | General Alarm Emergency Stop Actuation | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S7 | 1756-IB32 | IN-0 | 1 | P1-TBDI4-1 | C1S7-1/P1-TBDI4-1 | P1-TBDI4-1/C1S7-1 | XA-60202A_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
456 | XA-60202B | - | 325-01-602-PD-08 | General Fault Controlled Stop for XSUP-5601 (Supression Panel) | General Fault Controlled Stop | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S7 | 1756-IB32 | IN-1 | 2 | P1-TBDI4-2 | C1S7-2/P1-TBDI4-2 | P1-TBDI4-2/C1S7-2 | XA-60202B_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
457 | XA-60202C | - | 325-01-602-PD-08 | General Armed Status Indicator for XSUP-5601 (Supression Panel) | General Armed Status Indicator | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S7 | 1756-IB32 | IN-2 | 3 | P1-TBDI4-3 | C1S7-3/P1-TBDI4-3 | P1-TBDI4-3/C1S7-3 | XA-60202C_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
458 | XA-60202D | - | 325-01-602-PD-08 | Power Fault Status Indicator for XSUP-5601 (Supression Panel) | Power Fault Status Indicator | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S7 | 1756-IB32 | IN-3 | 4 | P1-TBDI4-4 | C1S7-4/P1-TBDI4-4 | P1-TBDI4-4/C1S7-4 | XA-60202D_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
459 | XA-60202E | - | 325-01-602-PD-08 | Dryer CHAM-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | Dryer CHAM-21 Emergency Stop Actuation | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S7 | 1756-IB32 | IN-4 | 5 | P1-TBDI4-5 | C1S7-5/P1-TBDI4-5 | P1-TBDI4-5/C1S7-5 | XA-60202E_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
460 | XA-60202F | - | 325-01-602-PD-08 | CHAM-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CHAM-21 Controlled Stop Trouble (No Protection) | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S7 | 1756-IB32 | IN-5 | 6 | P1-TBDI4-6 | C1S7-6/P1-TBDI4-6 | P1-TBDI4-6/C1S7-6 | XA-60202F_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
461 | XA-60202G | - | 325-01-602-PD-08 | CYCL-21/22 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-21/22 Emergency Stop Actuation | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S7 | 1756-IB32 | IN-6 | 7 | P1-TBDI4-7 | C1S7-7/P1-TBDI4-7 | P1-TBDI4-7/C1S7-7 | XA-60202G_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
462 | XA-60202H | - | 325-01-602-PD-08 | CYCL-21/22 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-21/22 Controlled Stop Trouble (No Protection) | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S7 | 1756-IB32 | IN-7 | 8 | P1-TBDI4-8 | C1S7-8/P1-TBDI4-8 | P1-TBDI4-8/C1S7-8 | XA-60202H_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
463 | XA-60202J | - | 325-01-602-PD-08 | BGHS-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | BGHS-21 Emergency Stop Actuation | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S7 | 1756-IB32 | IN-9 | 10 | P1-TBDI4-10 | C1S7-10/P1-TBDI4-10 | P1-TBDI4-10/C1S7-10 | XA-60202J_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
464 | XA-60202K | - | 325-01-602-PD-08 | BGHS-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | BGHS-21 Controlled Stop Trouble (No Protection) | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S7 | 1756-IB32 | IN-10 | 11 | P1-TBDI4-11 | C1S7-11/P1-TBDI4-11 | P1-TBDI4-11/C1S7-11 | XA-60202K_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
465 | XA-60202L | - | 325-01-602-PD-08 | CYCL-31 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-31 Emergency Stop Actuation | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S7 | 1756-IB32 | IN-11 | 12 | P1-TBDI4-12 | C1S7-12/P1-TBDI4-12 | P1-TBDI4-12/C1S7-12 | XA-60202L_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
466 | XA-60202M | - | 325-01-602-PD-08 | CYCL-31 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-31 Controlled Stop Trouble (No Protection) | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S7 | 1756-IB32 | IN-12 | 13 | P1-TBDI4-13 | C1S7-13/P1-TBDI4-13 | P1-TBDI4-13/C1S7-13 | XA-60202M_DI_1 | JB-601 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
467 | Fire Deluge PK-60221 | Fire Deluge PK-60221 | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
468 | XA-60221A | XA-60261 | 325-01-602-PD-04 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Fire Deluge Fault (No Protection) | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C3 | C3S1 | 1756-IB32 | IN-18 | 21 | P3-TBDI1-19 | C3S1-21/P3-TBDI1-19 | P3-TBDI1-19/C3S1-21 | XA-60261_DI_1 | JB-606 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
469 | XA-60221B | XA-60262 | 325-01-602-PD-04 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Fire Deluge Alarm (Deluge Activated) | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | C3 | C3S1 | 1756-IB32 | IN-19 | 22 | P3-TBDI1-20 | C3S1-22/P3-TBDI1-20 | P3-TBDI1-20/C3S1-22 | XA-60262_DI_1 | JB-606 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_PLC
470 | XS-60221 | XS-60260 | 325-01-602-PD-04 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
139 | TSH-60230 | - | 325-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | Temperature Switch | Dry Contact | Fire Deluge Control Panel | 0 - 140 C | - | - | - | - | - | - | C2 | C2S2 | 1756-IB32 | IN-3 | 4 | P2-TBDI2-4 | C2S2-4/P2-TBDI2-4 | P2-TBDI2-4/C2S2-4 | TSH-60230_DI_1 | JB-602 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
471 | Fire Deluge PK-60222 | Fire Deluge PK-60222 | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
472 | XA-60222A | - | 325-01-602-PD-05 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Fire Deluge Fault (No Protection) | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
473 | XA-60222B | - | 325-01-602-PD-05 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Fire Deluge Alarm (Deluge Activated) | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
474 | XS-60222 | - | 325-01-602-PD-05 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command | 24 VDC energized | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
| XV-60240D | - | 325-01-602-PD-05 | Drain Valve |  | 24 VDC energized | PLC | On-Off | - | - | 1 | - | - | - | C1 | C1S7, C1S9 | 1756-IB32, 1756-OB32 | IN-17, IN-18, IN-19, IN-20, OUT-24 | 20, 21, 22, 23, 27 | P1-TBDI4-18, P1-TBDI4-19, P1-TBDI4-20, P1-TBDI4-21, P1-TBRL2-25 | C1S7-20/P1-TBDI4-18, C1S7-21/P1-TBDI4-19, C1S7-22/P1-TBDI4-20... | P1-TBDI4-18/C1S7-20, P1-TBDI4-19/C1S7-21, P1-TBDI4-20/C1S7-22... | XV-60240D_DI_1, XV-60240D_DI_2, XV-60240D_DI_1, XV-60240D_DI_2, XV-60240D_DO_1 | JB-601 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_PLC
140 | TSH-60240 | - | 325-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | Temperature Switch | Dry Contact | Fire Deluge Control Panel | 0 - 140 C | - | - | - | - | - | - | C2 | C2S2 | 1756-IB32 | IN-4 | 5 | P2-TBDI2-5 | C2S2-5/P2-TBDI2-5 | P2-TBDI2-5/C2S2-5 | TSH-60240_DI_1 | JB-602 | CVV 3Cx1.5 (24VDC Power + Switch Output) | MAPPED_PLC
475 | Keaser Air Blower | Keaser Air Blower | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
476 | XS-61302 | - | 325-01-613-PD-01 | Start / Stop Command for Bin Aerator Blower | Start / Stop Command | Dry Contact | PLC | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
477 | XA-61302A | - | 325-01-613-PD-01 | Operational / Running status |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
478 | XA-61302B | - | 325-01-613-PD-01 | Local / Remote status |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
479 | XA-61302C | - | 325-01-613-PD-01 | Fault / Trip condition |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
480 | XA-61302D | - | 325-01-613-PD-01 | Warning condition |  | Dry Contact | PLC | On-Off | - | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | PLC | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | SPARE_ALLOCATABLE
481 | REMOTE I-O Area-200 | REMOTE I-O Area-200 | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
482 | HV-20204 | HV-2022 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-7 | 8 | P5-TBDI1-8 | C5S1-8/P5-TBDI1-8 | P5-TBDI1-8/C5S1-8 | HV-20204_DI_1 | RIO-200 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_RIO200
483 | HV-20205 | HV-2024 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-8 | 9 | P5-TBDI1-9 | C5S1-9/P5-TBDI1-9 | P5-TBDI1-9/C5S1-9 | HV-20205_DI_1 | RIO-200 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_RIO200
484 | HV-20206 | HV-2026 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-9 | 10 | P5-TBDI1-10 | C5S1-10/P5-TBDI1-10 | P5-TBDI1-10/C5S1-10 | HV-20206_DI_1 | RIO-200 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_RIO200
485 | HV-20207 | HV-2030 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-10 | 11 | P5-TBDI1-11 | C5S1-11/P5-TBDI1-11 | P5-TBDI1-11/C5S1-11 | HV-20207_DI_1 | RIO-200 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_RIO200
486 | HV-20208 | HV-2032 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-11 | 12 | P5-TBDI1-12 | C5S1-12/P5-TBDI1-12 | P5-TBDI1-12/C5S1-12 | HV-20208_DI_1 | RIO-200 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_RIO200
487 | HV-20209 | HV-2035 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-12 | 13 | P5-TBDI1-13 | C5S1-13/P5-TBDI1-13 | P5-TBDI1-13/C5S1-13 | HV-20209_DI_1 | RIO-200 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_RIO200
488 | HV-20210 | HV-2038 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-13 | 14 | P5-TBDI1-14 | C5S1-14/P5-TBDI1-14 | P5-TBDI1-14/C5S1-14 | HV-20210_DI_1 | RIO-200 | CVV 4Cx1.0 (Open/Close Limit Switches) | MAPPED_RIO200
489 | XV-20201 | - | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 24 VDC energized | RIO-200 | On-Off | Ex d | 1 | 2 | - | - | - | C5 | C5S1, C5S3 | 1756-IB32, 1756-OB32 | IN-26, IN-27, OUT-1 | 29, 30, 2 | P5-TBDI1-27, P5-TBDI1-28, P5-TBRL1-2 | C5S1-29/P5-TBDI1-27, C5S1-30/P5-TBDI1-28, C5S3-2/P5-TBRL1-2 | P5-TBDI1-27/C5S1-29, P5-TBDI1-28/C5S1-30, P5-TBRL1-2/C5S3-2 | XV-20201_DI_1, XV-20201_DI_2, XV-20201_DO_1 | RIO-200 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_RIO200
490 | XV-20202 | - | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 24 VDC energized | RIO-200 | On-Off | Ex d | 1 | 2 | - | - | - | C5 | C5S1, C5S3 | 1756-IB32, 1756-OB32 | IN-28, IN-29, OUT-2 | 31, 32, 3 | P5-TBDI1-29, P5-TBDI1-30, P5-TBRL1-3 | C5S1-31/P5-TBDI1-29, C5S1-32/P5-TBDI1-30, C5S3-3/P5-TBRL1-3 | P5-TBDI1-29/C5S1-31, P5-TBDI1-30/C5S1-32, P5-TBRL1-3/C5S3-3 | XV-20202_DI_1, XV-20202_DI_2, XV-20202_DO_1 | RIO-200 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_RIO200
491 | XV-20203 | - | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 24 VDC energized | RIO-200 | On-Off | Ex d | 1 | 2 | - | - | - | C5 | C5S1, C5S3 | 1756-IB32, 1756-OB32 | IN-30, IN-31, OUT-3 | 33, 34, 4 | P5-TBDI1-31, P5-TBDI1-32, P5-TBRL1-4 | C5S1-33/P5-TBDI1-31, C5S1-34/P5-TBDI1-32, C5S3-4/P5-TBRL1-4 | P5-TBDI1-31/C5S1-33, P5-TBDI1-32/C5S1-34, P5-TBRL1-4/C5S3-4 | XV-20203_DI_1, XV-20203_DI_2, XV-20203_DO_1 | RIO-200 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_RIO200
492 | XV-20211 | - | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 24 VDC energized | RIO-200 | On-Off | Ex d | 1 | 2 | - | - | - | C5 | C5S2, C5S3 | 1756-IB32, 1756-OB32 | IN-0, IN-1, OUT-4 | 1, 2, 5 | P5-TBDI2-1, P5-TBDI2-2, P5-TBRL1-5 | C5S2-1/P5-TBDI2-1, C5S2-2/P5-TBDI2-2, C5S3-5/P5-TBRL1-5 | P5-TBDI2-1/C5S2-1, P5-TBDI2-2/C5S2-2, P5-TBRL1-5/C5S3-5 | XV-20211_DI_1, XV-20211_DI_2, XV-20211_DO_1 | RIO-200 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_RIO200
493 | XV-20212 | - | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 24 VDC energized | RIO-200 | On-Off | Ex d | 1 | 2 | - | - | - | C5 | C5S2, C5S3 | 1756-IB32, 1756-OB32 | IN-2, IN-3, OUT-5 | 3, 4, 6 | P5-TBDI2-3, P5-TBDI2-4, P5-TBRL1-6 | C5S2-3/P5-TBDI2-3, C5S2-4/P5-TBDI2-4, C5S3-6/P5-TBRL1-6 | P5-TBDI2-3/C5S2-3, P5-TBDI2-4/C5S2-4, P5-TBRL1-6/C5S3-6 | XV-20212_DI_1, XV-20212_DI_2, XV-20212_DO_1 | RIO-200 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_RIO200
494 | XV-20213 | - | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 24 VDC energized | RIO-200 | On-Off | Ex d | 1 | 2 | - | - | - | C5 | C5S2, C5S3 | 1756-IB32, 1756-OB32 | IN-4, IN-5, OUT-6 | 5, 6, 7 | P5-TBDI2-5, P5-TBDI2-6, P5-TBRL1-7 | C5S2-5/P5-TBDI2-5, C5S2-6/P5-TBDI2-6, C5S3-7/P5-TBRL1-7 | P5-TBDI2-5/C5S2-5, P5-TBDI2-6/C5S2-6, P5-TBRL1-7/C5S3-7 | XV-20213_DI_1, XV-20213_DI_2, XV-20213_DO_1 | RIO-200 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_RIO200
495 | LS-814201 | LS-81001 | 325-01-814-PD-01 | Level alarm low | Level switch | Dry Contact | RIO-200 | On-Off | Ex ic | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | RIO-200 | CVV 3Cx1.5 (24VDC Power + Switch Output) | RIO200_EXPANSION
496 | PC-20201 | PCM-2030 | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2030 |  | 24 VDC energized | RIO-200 | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | RIO-200 | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | RIO200_EXPANSION
497 | PCM-2031 | PCM-2031 | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2031 | ยกเลิก | 24 VDC energized | RIO-200 | On-Off | - | 2 | 2 | - | - | - | - | - | - | - | - | - | - | - | - | RIO-200 | CVV 7Cx1.5 Control Cable (MCC Start/Stop/Fault/Run) | RIO200_EXPANSION
498 | PC-814201 | PCY-81001 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81001 |  | 24 VDC energized | RIO-200 | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | RIO-200 | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | RIO200_EXPANSION
499 | PC-814202 | PCY-81002 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81002 |  | 24 VDC energized | RIO-200 | On-Off | - | - | - | - | - | 1 | - | - | - | - | - | - | - | - | - | RIO-200 | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | RIO200_EXPANSION
500 | LPG Station | LPG Station | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
501 | FT-913201 | FT-80301 | 325-01-913-PD-02 | Flow outlet LPG line | Coriolis Flow Transmitter | 4 - 20 mA,Pulse | RIO-200 | 0-1000kg/hr | Ex d | - | 1 | - | 2 | - | C5 | C5S1, C5S4 | 1756-IB32, 1756-IF16 | IN-1, i RTN-1, IN-1, i RTN-2, IN-2 | 2, 3, 4, 5, 6 | P5-TBDI1-2, P5-TBAI1-2(B), P5-TBAI1-2(A), P5-TBAI1-3(B), P5-TBAI1-3(A) | C5S1-2/P5-TBDI1-2, C5S4-3/P5-TBAI1-2(B), C5S4-4/P5-TBAI1-2(A)... | P5-TBDI1-2/C5S1-2, P5-TBAI1-2(B)/C5S4-3, P5-TBAI1-2(A)/C5S4-4... | FT-913201_DI_1, FT-913201_AI_1, FT-913201_AI_1, FT-913201_AI_2, FT-913201_AI_2 | RIO-200 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_RIO200
502 | LT-913201 | LT-80301 | 325-01-913-PD-01 | Level LPG in storage | Level transmitter | 4 - 20 mA | RIO-200 | - | Ex ia | - | - | - | 1 | - | C5 | C5S4 | 1756-IF16 | i RTN-5, IN-5 | 13, 14 | P5-TBAI1-6(B), P5-TBAI1-6(A) | C5S4-13/P5-TBAI1-6(B), C5S4-14/P5-TBAI1-6(A) | P5-TBAI1-6(B)/C5S4-13, P5-TBAI1-6(A)/C5S4-14 | LT-913201_AI_1, LT-913201_AI_1 | RIO-200 | LiY-CY(EB) 1Px1.0 (Blue) | MAPPED_RIO200
503 | PT-913201 | PT-80302 | 325-01-913-PD-02 | Pressure outlet LPG line | Pressure Transmitter | 4 - 20 mA | RIO-200 | 0 - 10 barg | Ex d | - | - | - | 1 | - | C5 | C5S4 | 1756-IF16 | i RTN-6, IN-6 | 15, 16 | P5-TBAI1-7(B), P5-TBAI1-7(A) | C5S4-15/P5-TBAI1-7(B), C5S4-16/P5-TBAI1-7(A) | P5-TBAI1-7(B)/C5S4-15, P5-TBAI1-7(A)/C5S4-16 | PT-913201_AI_1, PT-913201_AI_1 | RIO-200 | LiY-CY TP 1Px1.0 (Shielded Pair) | MAPPED_RIO200
504 | XV-913201 | - | 325-01-913-PD-02 | Outlet LPG line | Automatic on/off valve | 24 VDC energized | RIO-200 | On-Off | Ex d | 1 | 2 | - | - | - | C5 | C5S2, C5S3, C5S4 | 1756-IB32, 1756-IF16, 1756-OB32 | IN-6, IN-7, OUT-7, i RTN-8, IN-8 | 7, 8, 8, 19, 20 | P5-TBDI2-7, P5-TBDI2-8, P5-TBRL1-8, P5-TBAI1-9(B), P5-TBAI1-9(A) | C5S2-7/P5-TBDI2-7, C5S2-8/P5-TBDI2-8, C5S3-8/P5-TBRL1-8... | P5-TBDI2-7/C5S2-7, P5-TBDI2-8/C5S2-8, P5-TBRL1-8/C5S3-8... | XV-913201_DI_1, XV-913201_DI_1, XV-913201_DO_1, XV-913201_AI_1, XV-913201_AI_1 | RIO-200 | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | MAPPED_RIO200
505 | Gas Vaporizer 4 | Gas Vaporizer 4 | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
506 | XA-913201A | XA-80305A | 325-01-913-PD-02 | Gas Vaporizer 4 Run Status | Gas vaporizer Ready | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-14 | 15 | P5-TBDI1-15 | C5S1-15/P5-TBDI1-15 | P5-TBDI1-15/C5S1-15 | XA-80305A_DI_1 | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_RIO200
507 | XA-913201B | XA-80305B | 325-01-913-PD-02 | Gas Vaporizer 4 Alarm status | Gas vaporizer Run | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-15 | 16 | P5-TBDI1-16 | C5S1-16/P5-TBDI1-16 | P5-TBDI1-16/C5S1-16 | XA-80305B_DI_1 | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_RIO200
508 | XA-913201C | XA-80305C | 325-01-913-PD-02 | Gas Vaporizer 4 High Temp Shut-Down status | Gas vaporizer Failed | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-16 | 19 | P5-TBDI1-17 | C5S1-19/P5-TBDI1-17 | P5-TBDI1-17/C5S1-19 | XA-80305C_DI_1 | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_RIO200
509 | XA-913201D | XA-80305D | 325-01-913-PD-02 | Gas Vaporizer 4 Working Temp Shun-Off status | Gas vaporizer Overheated | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-17 | 20 | P5-TBDI1-18 | C5S1-20/P5-TBDI1-18 | P5-TBDI1-18/C5S1-20 | XA-80305D_DI_1 | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_RIO200
510 | XA-913201E | XA-80305E | 325-01-913-PD-02 | Gas Vaporizer 4 Low Water Shun-Off status | Gas vaporizer Excessive flow tripped | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-18 | 21 | P5-TBDI1-19 | C5S1-21/P5-TBDI1-19 | P5-TBDI1-19/C5S1-21 | XA-80305E_DI_1 | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_RIO200
512 | XS-913201A | XS-80305A | 325-01-913-PD-02 | Start Command for Gas Vaporizer 4 | Start Command | 24 VDC energized | RIO-200 | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | RIO200_EXPANSION
512 | XS-913201B | XS-80305B | 325-01-913-PD-02 | Stop Command for Gas Vaporizer 4 | Stop Command | 24 VDC energized | RIO-200 | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | RIO200_EXPANSION
513 | Gas Vaporizer 5 | Gas Vaporizer 5 | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAT 6 S/FTP Industrial Ethernet / Belden 3105A | MANUAL_LOCAL
514 | XA-913202A | XA-80306A | 325-01-913-PD-02 | Gas Vaporizer 5 Run Status | Gas vaporizer Ready | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-20 | 23 | P5-TBDI1-21 | C5S1-23/P5-TBDI1-21 | P5-TBDI1-21/C5S1-23 | XA-80306A_DI_1 | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_RIO200
515 | XA-913202B | XA-80306B | 325-01-913-PD-02 | Gas Vaporizer 5 Alarm status | Gas vaporizer Run | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-21 | 24 | P5-TBDI1-22 | C5S1-24/P5-TBDI1-22 | P5-TBDI1-22/C5S1-24 | XA-80306B_DI_1 | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_RIO200
516 | XA-913202C | XA-80306C | 325-01-913-PD-02 | Gas Vaporizer 5 High Temp Shut-Down status | Gas vaporizer Failed | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-22 | 25 | P5-TBDI1-23 | C5S1-25/P5-TBDI1-23 | P5-TBDI1-23/C5S1-25 | XA-80306C_DI_1 | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_RIO200
517 | XA-913202D | XA-80306D | 325-01-913-PD-02 | Gas Vaporizer 5 Working Temp Shun-Off status | Gas vaporizer Overheated | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-23 | 26 | P5-TBDI1-24 | C5S1-26/P5-TBDI1-24 | P5-TBDI1-24/C5S1-26 | XA-80306D_DI_1 | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_RIO200
518 | XA-913202E | XA-80306E | 325-01-913-PD-02 | Gas Vaporizer 5 Low Water Shun-Off status | Gas vaporizer Excessive flow tripped | Dry Contact | RIO-200 | On-Off | - | - | 1 | - | - | - | C5 | C5S1 | 1756-IB32 | IN-24 | 27 | P5-TBDI1-25 | C5S1-27/P5-TBDI1-25 | P5-TBDI1-25/C5S1-27 | XA-80306E_DI_1 | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | MAPPED_RIO200
519 | XS-913202A | XS-80306A | 325-01-913-PD-02 | Start Command for Gas Vaporizer 5 | Start Command | 24 VDC energized | RIO-200 | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | RIO200_EXPANSION
520 | XS-913202B | XS-80306B | 325-01-913-PD-02 | Stop Command for Gas Vaporizer 5 | Stop Command | 24 VDC energized | RIO-200 | On-Off | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | RIO-200 | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | RIO200_EXPANSION

## 02_PLC_Channel_IO_Mapping
KALASIN ENGINEERING ¦ CONTROLLOGIX 1756 POINT-BY-POINT PLC I/O CHANNEL MAPPING
1,466 Physical Terminal Channels across 5 Chassis (C1S0 - C5S4) with Marshaling Blocks, Field Wire Marks & Instrument Master Data
Seq No. | Chassis | Slot Tag | Module Catalog | Signal Family | Terminal Pin | Channel / Terminal Description | Marshaling Terminal (Px-TB) | Wire Mark (PLC Side) | Wire Mark (Terminal Side) | Destination Area | PLC Tag Name | Instrument Tag | Instrument Description | Instrument Name / Type | P&ID No. | Signal Type | Calibrated Range | Manufacturer | Model Series | Suggested Field Cable | Channel Status | Engineering Remark
1 | C1 | C1S0 | 1756-L950TPSXT | CPU (Controller) | RJ45-1 | Embedded 1Gbps EtherNet/IP Port (SCADA / Enterprise Network) | ETH-CORE-01 | C1S0-ETH1/SW-CORE-01 | SW-CORE-01/C1S0-ETH1 | CA1 (Main Control Room) | CPU_Embedded_ETH | PLC-01 | Main Process Controller EtherNet/IP Uplink Port | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
2 | C1 | C1S0 | 1756-L950TPSXT | CPU (Controller) | USB-1 | USB 2.0 Type-B Programming Port (Maintenance / Diagnostics) | USB-CONSOLE | C1S0-USB/CONSOLE | CONSOLE/C1S0-USB | CA1 (Main Control Room) | CPU_USB_Console | USB-PGM | Engineering Workstation Maintenance Access Port | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
3 | C1 | C1S0 | 1756-L950TPSXT | CPU (Controller) | SD-1 | 1784-SD2 Industrial SD Memory Card Slot (Firmware & Program Backup) | SD-SLOT | C1S0-SD/INTERNAL | INTERNAL/C1S0-SD | CA1 (Main Control Room) | CPU_SD_Card | 1784-SD2 | Non-volatile System Image & User Program Storage | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
4 | C1 | C1S0 | 1756-L950TPSXT | CPU (Controller) | ESM-1 | Capacitor Energy Storage Module (Maintenance-free, Battery-free) | ESM-CAP | C1S0-ESM/INTERNAL | INTERNAL/C1S0-ESM | CA1 (Main Control Room) | CPU_ESM_Module | 1756-ESMCAP | Energy Storage Module for Power Loss Data Retention | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
5 | C1 | C1S0 | 1756-L950TPSXT | CPU (Controller) | DISP-1 | 4-Character Alphanumeric Diagnostic Display & Status LEDs (RUN, FORCE, SD, OK) | DIAG-DISP | C1S0-DISP/DIAG | DIAG/C1S0-DISP | CA1 (Main Control Room) | CPU_Status_Display | DIAG-LED | System Controller Status & Fault Diagnostic Indicators | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
6 | C1 | C1S1 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | ETH-DLR-P1 | C1S1-/- | -/C1S1- | CA1 | C1S1_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
7 | C1 | C1S1 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C1S1-P2/ETH | ETH/C1S1-P2 | CA1 | C1S1_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
8 | C1 | C1S1 | 1756-EN4TR | COMM (EtherNet/IP) | USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C1S1-USB/CONSOLE | CONSOLE/C1S1-USB | CA1 | C1S1_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
9 | C1 | C1S1 | 1756-EN4TR | COMM (EtherNet/IP) | DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C1S1-DISP/DIAG | DIAG/C1S1-DISP | CA1 | C1S1_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
10 | C1 | C1S2 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | ETH-DLR-P1 | C1S2-/- | -/C1S2- | CA1 | C1S2_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
11 | C1 | C1S2 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C1S2-P2/ETH | ETH/C1S2-P2 | CA1 | C1S2_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
12 | C1 | C1S2 | 1756-EN4TR | COMM (EtherNet/IP) | USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C1S2-USB/CONSOLE | CONSOLE/C1S2-USB | CA1 | C1S2_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
13 | C1 | C1S2 | 1756-EN4TR | COMM (EtherNet/IP) | DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C1S2-DISP/DIAG | DIAG/C1S2-DISP | CA1 | C1S2_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
14 | C1 | C1S3 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | ETH-DLR-P1 | C1S3-/- | -/C1S3- | CA1 | C1S3_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
15 | C1 | C1S3 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C1S3-P2/ETH | ETH/C1S3-P2 | CA1 | C1S3_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
16 | C1 | C1S3 | 1756-EN4TR | COMM (EtherNet/IP) | USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C1S3-USB/CONSOLE | CONSOLE/C1S3-USB | CA1 | C1S3_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
17 | C1 | C1S3 | 1756-EN4TR | COMM (EtherNet/IP) | DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C1S3-DISP/DIAG | DIAG/C1S3-DISP | CA1 | C1S3_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
18 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P1-TBDI1-1 | C1S4-1/P1-TBDI1-1 | P1-TBDI1-1/C1S4-1 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
19 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P1-TBDI1-2 | C1S4-2/P1-TBDI1-2 | P1-TBDI1-2/C1S4-2 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
20 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P1-TBDI1-3 | C1S4-3/P1-TBDI1-3 | P1-TBDI1-3/C1S4-3 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
21 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P1-TBDI1-4 | C1S4-4/P1-TBDI1-4 | P1-TBDI1-4/C1S4-4 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
22 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P1-TBDI1-5 | C1S4-5/P1-TBDI1-5 | P1-TBDI1-5/C1S4-5 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
23 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P1-TBDI1-6 | C1S4-6/P1-TBDI1-6 | P1-TBDI1-6/C1S4-6 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
24 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P1-TBDI1-7 | C1S4-7/P1-TBDI1-7 | P1-TBDI1-7/C1S4-7 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
25 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P1-TBDI1-8 | C1S4-8/P1-TBDI1-8 | P1-TBDI1-8/C1S4-8 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
26 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P1-TBDI1-9 | C1S4-9/P1-TBDI1-9 | P1-TBDI1-9/C1S4-9 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
27 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P1-TBDI1-10 | C1S4-10/P1-TBDI1-10 | P1-TBDI1-10/C1S4-10 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
28 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P1-TBDI1-11 | C1S4-11/P1-TBDI1-11 | P1-TBDI1-11/C1S4-11 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
29 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P1-TBDI1-12 | C1S4-12/P1-TBDI1-12 | P1-TBDI1-12/C1S4-12 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
30 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P1-TBDI1-13 | C1S4-13/P1-TBDI1-13 | P1-TBDI1-13/C1S4-13 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
31 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P1-TBDI1-14 | C1S4-14/P1-TBDI1-14 | P1-TBDI1-14/C1S4-14 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
32 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P1-TBDI1-15 | C1S4-15/P1-TBDI1-15 | P1-TBDI1-15/C1S4-15 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
33 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P1-TBDI1-16 | C1S4-16/P1-TBDI1-16 | P1-TBDI1-16/C1S4-16 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
34 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
35 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
36 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P1-TBDI1-17 | C1S4-19/P1-TBDI1-17 | P1-TBDI1-17/C1S4-19 | JB-401 | FSL-40201_DI_1 | FSL-40201 | Flow Switch | Flow Switch | 325-01-402-PD-01 | Dry Contact |  | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Jet Cooker
37 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P1-TBDI1-18 | C1S4-20/P1-TBDI1-18 | P1-TBDI1-18/C1S4-20 | JB-401 | FSL-40202_DI_1 | FSL-40202 | Flow Switch | Flow Switch | 325-01-402-PD-01 | Dry Contact |  | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Jet Cooker
38 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P1-TBDI1-19 | C1S4-21/P1-TBDI1-19 | P1-TBDI1-19/C1S4-21 | JB-401 | FT-40201_DI_1 | FT-40201 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-15 m³/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
39 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P1-TBDI1-20 | C1S4-22/P1-TBDI1-20 | P1-TBDI1-20/C1S4-22 | JB-401 | FT-40202_DI_1 | FT-40202 | Magnetic Flow Transmitter | Magnetic Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0 to 8,000 m³/hr | Endress+Hauser | Promag W 400 / 50W (Electromagnetic Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
40 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P1-TBDI1-21 | C1S4-23/P1-TBDI1-21 | P1-TBDI1-21/C1S4-23 | JB-401 | HV-40201_DI_1 | HV-40201 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-402-PD-01 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | -
41 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P1-TBDI1-22 | C1S4-24/P1-TBDI1-22 | P1-TBDI1-22/C1S4-24 | JB-401 | HV-40202_DI_1 | HV-40202 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-402-PD-01 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | -
42 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P1-TBDI1-23 | C1S4-25/P1-TBDI1-23 | P1-TBDI1-23/C1S4-25 | JB-401 | HV-40203_DI_1 | HV-40203 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-402-PD-01 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | -
43 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P1-TBDI1-24 | C1S4-26/P1-TBDI1-24 | P1-TBDI1-24/C1S4-26 | JB-401 | HV-40204_DI_1 | HV-40204 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-402-PD-01 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | -
44 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P1-TBDI1-25 | C1S4-27/P1-TBDI1-25 | P1-TBDI1-25/C1S4-27 | JB-401 | HV-40205_DI_1 | HV-40205 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-402-PD-01 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | -
45 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P1-TBDI1-26 | C1S4-28/P1-TBDI1-26 | P1-TBDI1-26/C1S4-28 | JB-401 | HV-40206_DI_1 | HV-40206 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-402-PD-01 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | -
46 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P1-TBDI1-27 | C1S4-29/P1-TBDI1-27 | P1-TBDI1-27/C1S4-29 | JB-401 | XV-40201A_DI_1 | XV-40201A | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
47 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P1-TBDI1-28 | C1S4-30/P1-TBDI1-28 | P1-TBDI1-28/C1S4-30 | JB-401 | XV-40201A_DI_2 | XV-40201A | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
48 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P1-TBDI1-29 | C1S4-31/P1-TBDI1-29 | P1-TBDI1-29/C1S4-31 | JB-401 | XV-40201B_DI_1 | XV-40201B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
49 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P1-TBDI1-30 | C1S4-32/P1-TBDI1-30 | P1-TBDI1-30/C1S4-32 | JB-401 | XV-40201B_DI_2 | XV-40201B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
50 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P1-TBDI1-31 | C1S4-33/P1-TBDI1-31 | P1-TBDI1-31/C1S4-33 | JB-401 | XV-40201C_DI_1 | XV-40201C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
51 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P1-TBDI1-32 | C1S4-34/P1-TBDI1-32 | P1-TBDI1-32/C1S4-34 | JB-401 | XV-40201C_DI_2 | XV-40201C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
52 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
53 | C1 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
54 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P1-TBDI2-1 | C1S5-1/P1-TBDI2-1 | P1-TBDI2-1/C1S5-1 | JB-401 | XV-40201D_DI_1 | XV-40201D | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
55 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P1-TBDI2-2 | C1S5-2/P1-TBDI2-2 | P1-TBDI2-2/C1S5-2 | JB-401 | XV-40201D_DI_2 | XV-40201D | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
56 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P1-TBDI2-3 | C1S5-3/P1-TBDI2-3 | P1-TBDI2-3/C1S5-3 | JB-401 | XV-40201E_DI_1 | XV-40201E | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
57 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P1-TBDI2-4 | C1S5-4/P1-TBDI2-4 | P1-TBDI2-4/C1S5-4 | JB-401 | XV-40201E_DI_2 | XV-40201E | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
58 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P1-TBDI2-5 | C1S5-5/P1-TBDI2-5 | P1-TBDI2-5/C1S5-5 | JB-401 | XV-40201F_DI_1 | XV-40201F | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
59 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P1-TBDI2-6 | C1S5-6/P1-TBDI2-6 | P1-TBDI2-6/C1S5-6 | JB-401 | XV-40201F_DI_2 | XV-40201F | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
60 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P1-TBDI2-7 | C1S5-7/P1-TBDI2-7 | P1-TBDI2-7/C1S5-7 | JB-401 | XV-40201G_DI_1 | XV-40201G | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
61 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P1-TBDI2-8 | C1S5-8/P1-TBDI2-8 | P1-TBDI2-8/C1S5-8 | JB-401 | XV-40201G_DI_2 | XV-40201G | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
62 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P1-TBDI2-9 | C1S5-9/P1-TBDI2-9 | P1-TBDI2-9/C1S5-9 | JB-401 | XV-40201H_DI_1 | XV-40201H | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
63 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P1-TBDI2-10 | C1S5-10/P1-TBDI2-10 | P1-TBDI2-10/C1S5-10 | JB-401 | XV-40201H_DI_2 | XV-40201H | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
64 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P1-TBDI2-11 | C1S5-11/P1-TBDI2-11 | P1-TBDI2-11/C1S5-11 | JB-401 | XV-40202A_DI_2 | XV-40202A | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
65 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P1-TBDI2-12 | C1S5-12/P1-TBDI2-12 | P1-TBDI2-12/C1S5-12 | JB-401 | XV-40202B_DI_1 | XV-40202B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
66 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P1-TBDI2-13 | C1S5-13/P1-TBDI2-13 | P1-TBDI2-13/C1S5-13 | JB-401 | XV-40202B_DI_2 | XV-40202B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
67 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P1-TBDI2-14 | C1S5-14/P1-TBDI2-14 | P1-TBDI2-14/C1S5-14 | JB-401 | XV-40202C_DI_1 | XV-40202C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
68 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P1-TBDI2-15 | C1S5-15/P1-TBDI2-15 | P1-TBDI2-15/C1S5-15 | JB-401 | XV-40202C_DI_2 | XV-40202C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
69 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P1-TBDI2-16 | C1S5-16/P1-TBDI2-16 | P1-TBDI2-16/C1S5-16 | JB-401 | XV-40202D_DI_1 | XV-40202D | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
70 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
71 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
72 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P1-TBDI2-17 | C1S5-19/P1-TBDI2-17 | P1-TBDI2-17/C1S5-19 | JB-401 | XV-40202D_DI_2 | XV-40202D | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
73 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P1-TBDI2-18 | C1S5-20/P1-TBDI2-18 | P1-TBDI2-18/C1S5-20 | JB-401 | XV-40202E_DI_1 | XV-40202E | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
74 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P1-TBDI2-19 | C1S5-21/P1-TBDI2-19 | P1-TBDI2-19/C1S5-21 | JB-401 | XV-40202A_DI_1 | XV-40202A | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
75 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P1-TBDI2-20 | C1S5-22/P1-TBDI2-20 | P1-TBDI2-20/C1S5-22 | JB-401 | XV-40202E_DI_2 | XV-40202E | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
76 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P1-TBDI2-21 | C1S5-23/P1-TBDI2-21 | P1-TBDI2-21/C1S5-23 | JB-401 | XV-40202F_DI_1 | XV-40202F | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
77 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P1-TBDI2-22 | C1S5-24/P1-TBDI2-22 | P1-TBDI2-22/C1S5-24 | JB-401 | XV-40202F_DI_2 | XV-40202F | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
78 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P1-TBDI2-23 | C1S5-25/P1-TBDI2-23 | P1-TBDI2-23/C1S5-25 | JB-401 | XV-40202G_DI_1 | XV-40202G | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
79 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P1-TBDI2-24 | C1S5-26/P1-TBDI2-24 | P1-TBDI2-24/C1S5-26 | JB-401 | XV-40202G_DI_2 | XV-40202G | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
80 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P1-TBDI2-25 | C1S5-27/P1-TBDI2-25 | P1-TBDI2-25/C1S5-27 | JB-401 | XV-40202H_DI_1 | XV-40202H | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
81 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P1-TBDI2-26 | C1S5-28/P1-TBDI2-26 | P1-TBDI2-26/C1S5-28 | JB-401 | XV-40202H_DI_2 | XV-40202H | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
82 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P1-TBDI2-27 | C1S5-29/P1-TBDI2-27 | P1-TBDI2-27/C1S5-29 | JB-401 | XV-40203B_DI_1 | XV-40203B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
83 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P1-TBDI2-28 | C1S5-30/P1-TBDI2-28 | P1-TBDI2-28/C1S5-30 | JB-401 | XV-40203B_DI_2 | XV-40203B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
84 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P1-TBDI2-29 | C1S5-31/P1-TBDI2-29 | P1-TBDI2-29/C1S5-31 | JB-401 | XV-40203C_DI_1 | XV-40203C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
85 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P1-TBDI2-30 | C1S5-32/P1-TBDI2-30 | P1-TBDI2-30/C1S5-32 | JB-401 | XV-40203C_DI_2 | XV-40203C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
86 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P1-TBDI2-31 | C1S5-33/P1-TBDI2-31 | P1-TBDI2-31/C1S5-33 | JB-401 | XV-40203D_DI_1 | XV-40203D | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
87 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P1-TBDI2-32 | C1S5-34/P1-TBDI2-32 | P1-TBDI2-32/C1S5-34 | JB-401 | XV-40203D_DI_2 | XV-40203D | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
88 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
89 | C1 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
90 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P1-TBDI3-1 | C1S6-1/P1-TBDI3-1 | P1-TBDI3-1/C1S6-1 | JB-401 | XV-40203E_DI_1 | XV-40203E | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
91 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P1-TBDI3-2 | C1S6-2/P1-TBDI3-2 | P1-TBDI3-2/C1S6-2 | JB-401 | XV-40203E_DI_2 | XV-40203E | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
92 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P1-TBDI3-3 | C1S6-3/P1-TBDI3-3 | P1-TBDI3-3/C1S6-3 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
93 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P1-TBDI3-4 | C1S6-4/P1-TBDI3-4 | P1-TBDI3-4/C1S6-4 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
94 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P1-TBDI3-5 | C1S6-5/P1-TBDI3-5 | P1-TBDI3-5/C1S6-5 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
95 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P1-TBDI3-6 | C1S6-6/P1-TBDI3-6 | P1-TBDI3-6/C1S6-6 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
96 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P1-TBDI3-7 | C1S6-7/P1-TBDI3-7 | P1-TBDI3-7/C1S6-7 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
97 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P1-TBDI3-8 | C1S6-8/P1-TBDI3-8 | P1-TBDI3-8/C1S6-8 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
98 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P1-TBDI3-9 | C1S6-9/P1-TBDI3-9 | P1-TBDI3-9/C1S6-9 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
99 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P1-TBDI3-10 | C1S6-10/P1-TBDI3-10 | P1-TBDI3-10/C1S6-10 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
100 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P1-TBDI3-11 | C1S6-11/P1-TBDI3-11 | P1-TBDI3-11/C1S6-11 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
101 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P1-TBDI3-12 | C1S6-12/P1-TBDI3-12 | P1-TBDI3-12/C1S6-12 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
102 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P1-TBDI3-13 | C1S6-13/P1-TBDI3-13 | P1-TBDI3-13/C1S6-13 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
103 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P1-TBDI3-14 | C1S6-14/P1-TBDI3-14 | P1-TBDI3-14/C1S6-14 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
104 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P1-TBDI3-15 | C1S6-15/P1-TBDI3-15 | P1-TBDI3-15/C1S6-15 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
105 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P1-TBDI3-16 | C1S6-16/P1-TBDI3-16 | P1-TBDI3-16/C1S6-16 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
106 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
107 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
108 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P1-TBDI3-17 | C1S6-19/P1-TBDI3-17 | P1-TBDI3-17/C1S6-19 | JB-601 | ES-60202_DI_1 | ES-60202 | Process Instrument | E-Stop | 325-01-602-PD-01 | Dry Contact |  | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
109 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P1-TBDI3-18 | C1S6-20/P1-TBDI3-18 | P1-TBDI3-18/C1S6-20 | JB-601 | FS-60205_DI_1 | FS-60205 | Flow Switch | Flow Switch | 325-01-602-PD-01 |  |  | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
110 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P1-TBDI3-19 | C1S6-21/P1-TBDI3-19 | P1-TBDI3-19/C1S6-21 | JB-601 | LSL-60201_DI_1 | LSL-60201 | Process Instrument | Level switch | 325-01-602-PD-11 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | -
111 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P1-TBDI3-20 | C1S6-22/P1-TBDI3-20 | P1-TBDI3-20/C1S6-22 | JB-601 | SV-60201_DI_1 | SV-60201 | Process Instrument | On/Off Valve | 325-01-602-PD-08 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
112 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P1-TBDI3-21 | C1S6-23/P1-TBDI3-21 | P1-TBDI3-21/C1S6-23 | JB-601 | SV-60201_DI_2 | SV-60201 | Process Instrument | On/Off Valve | 325-01-602-PD-08 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
113 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P1-TBDI3-22 | C1S6-24/P1-TBDI3-22 | P1-TBDI3-22/C1S6-24 | JB-601 | SV-60202_DI_1 | SV-60202 | Process Instrument | On/Off Valve | 325-01-602-PD-08 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
114 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P1-TBDI3-23 | C1S6-25/P1-TBDI3-23 | P1-TBDI3-23/C1S6-25 | JB-601 | SV-60202_DI_2 | SV-60202 | Process Instrument | On/Off Valve | 325-01-602-PD-08 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
115 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P1-TBDI3-24 | C1S6-26/P1-TBDI3-24 | P1-TBDI3-24/C1S6-26 | JB-601 | SV-60203_DI_1 | SV-60203 | Process Instrument | On/Off Valve | 325-01-602-PD-08 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
116 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P1-TBDI3-25 | C1S6-27/P1-TBDI3-25 | P1-TBDI3-25/C1S6-27 | JB-601 | SV-60203_DI_2 | SV-60203 | Process Instrument | On/Off Valve | 325-01-602-PD-08 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
117 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P1-TBDI3-26 | C1S6-28/P1-TBDI3-26 | P1-TBDI3-26/C1S6-28 | JB-601 | VS-60205_DI_1 | VS-60205 | Vibration Switch | Vibration Switch | 325-01-602-PD-01 | 4 - 20 mA |  | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE
118 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P1-TBDI3-27 | C1S6-29/P1-TBDI3-27 | P1-TBDI3-27/C1S6-29 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
119 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P1-TBDI3-28 | C1S6-30/P1-TBDI3-28 | P1-TBDI3-28/C1S6-30 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
120 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P1-TBDI3-29 | C1S6-31/P1-TBDI3-29 | P1-TBDI3-29/C1S6-31 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
121 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P1-TBDI3-30 | C1S6-32/P1-TBDI3-30 | P1-TBDI3-30/C1S6-32 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
122 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P1-TBDI3-31 | C1S6-33/P1-TBDI3-31 | P1-TBDI3-31/C1S6-33 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
123 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P1-TBDI3-32 | C1S6-34/P1-TBDI3-32 | P1-TBDI3-32/C1S6-34 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
124 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
125 | C1 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
126 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P1-TBDI4-1 | C1S7-1/P1-TBDI4-1 | P1-TBDI4-1/C1S7-1 | JB-601 | XA-60202A_DI_1 | XA-60202A | Process Instrument | General Alarm Emergency Stop Actuation | 325-01-602-PD-08 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
127 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P1-TBDI4-2 | C1S7-2/P1-TBDI4-2 | P1-TBDI4-2/C1S7-2 | JB-601 | XA-60202B_DI_1 | XA-60202B | Process Instrument | General Fault Controlled Stop | 325-01-602-PD-08 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
128 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P1-TBDI4-3 | C1S7-3/P1-TBDI4-3 | P1-TBDI4-3/C1S7-3 | JB-601 | XA-60202C_DI_1 | XA-60202C | Process Instrument | General Armed Status Indicator | 325-01-602-PD-08 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
129 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P1-TBDI4-4 | C1S7-4/P1-TBDI4-4 | P1-TBDI4-4/C1S7-4 | JB-601 | XA-60202D_DI_1 | XA-60202D | Process Instrument | Power Fault Status Indicator | 325-01-602-PD-08 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
130 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P1-TBDI4-5 | C1S7-5/P1-TBDI4-5 | P1-TBDI4-5/C1S7-5 | JB-601 | XA-60202E_DI_1 | XA-60202E | Process Instrument | Dryer CHAM-21 Emergency Stop Actuation | 325-01-602-PD-08 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
131 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P1-TBDI4-6 | C1S7-6/P1-TBDI4-6 | P1-TBDI4-6/C1S7-6 | JB-601 | XA-60202F_DI_1 | XA-60202F | Process Instrument | CHAM-21 Controlled Stop Trouble (No Protection) | 325-01-602-PD-08 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
132 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P1-TBDI4-7 | C1S7-7/P1-TBDI4-7 | P1-TBDI4-7/C1S7-7 | JB-601 | XA-60202G_DI_1 | XA-60202G | Process Instrument | CYCL-21/22 Emergency Stop Actuation | 325-01-602-PD-08 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
133 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P1-TBDI4-8 | C1S7-8/P1-TBDI4-8 | P1-TBDI4-8/C1S7-8 | JB-601 | XA-60202H_DI_1 | XA-60202H | Process Instrument | CYCL-21/22 Controlled Stop Trouble (No Protection) | 325-01-602-PD-08 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
134 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P1-TBDI4-9 | C1S7-9/P1-TBDI4-9 | P1-TBDI4-9/C1S7-9 | JB-601 | XA-60202I_DI_1 | XA-60202I | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
135 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P1-TBDI4-10 | C1S7-10/P1-TBDI4-10 | P1-TBDI4-10/C1S7-10 | JB-601 | XA-60202J_DI_1 | XA-60202J | Process Instrument | BGHS-21 Emergency Stop Actuation | 325-01-602-PD-08 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
136 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P1-TBDI4-11 | C1S7-11/P1-TBDI4-11 | P1-TBDI4-11/C1S7-11 | JB-601 | XA-60202K_DI_1 | XA-60202K | Process Instrument | BGHS-21 Controlled Stop Trouble (No Protection) | 325-01-602-PD-08 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
137 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P1-TBDI4-12 | C1S7-12/P1-TBDI4-12 | P1-TBDI4-12/C1S7-12 | JB-601 | XA-60202L_DI_1 | XA-60202L | Process Instrument | CYCL-31 Emergency Stop Actuation | 325-01-602-PD-08 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
138 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P1-TBDI4-13 | C1S7-13/P1-TBDI4-13 | P1-TBDI4-13/C1S7-13 | JB-601 | XA-60202M_DI_1 | XA-60202M | Process Instrument | CYCL-31 Controlled Stop Trouble (No Protection) | 325-01-602-PD-08 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
139 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P1-TBDI4-14 | C1S7-14/P1-TBDI4-14 | P1-TBDI4-14/C1S7-14 | JB-601 | XV-60202_DI_1 | XV-60202 | Control Valve Position Feedback | Automatic on/off valve | 325-01-602-PD-11 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
140 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P1-TBDI4-15 | C1S7-15/P1-TBDI4-15 | P1-TBDI4-15/C1S7-15 | JB-601 | XV-60202_DI_2 | XV-60202 | Control Valve Position Feedback | Automatic on/off valve | 325-01-602-PD-11 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
141 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P1-TBDI4-16 | C1S7-16/P1-TBDI4-16 | P1-TBDI4-16/C1S7-16 | JB-601 | XV-60205A_DI_1 | XV-60205A | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-01 | 24 VDC energized |  | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
142 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
143 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
144 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P1-TBDI4-17 | C1S7-19/P1-TBDI4-17 | P1-TBDI4-17/C1S7-19 | JB-601 | XV-60205A_DI_2 | XV-60205A | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-01 | 24 VDC energized |  | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
145 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P1-TBDI4-18 | C1S7-20/P1-TBDI4-18 | P1-TBDI4-18/C1S7-20 | JB-601 | XV-60240D_DI_1 | XV-60240D | Control Valve Position Feedback |  | 325-01-602-PD-05 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | ส่งcommand เปิดวาวล์เข้า PLC ก่อน
146 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P1-TBDI4-19 | C1S7-21/P1-TBDI4-19 | P1-TBDI4-19/C1S7-21 | JB-601 | XV-60240D_DI_2 | XV-60240D | Control Valve Position Feedback |  | 325-01-602-PD-05 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | ส่งcommand เปิดวาวล์เข้า PLC ก่อน
147 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P1-TBDI4-20 | C1S7-22/P1-TBDI4-20 | P1-TBDI4-20/C1S7-22 | JB-601 | XV-60240D_DI_1 | XV-60240D | Control Valve Position Feedback |  | 325-01-602-PD-05 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | ส่งcommand เปิดวาวล์เข้า PLC ก่อน
148 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P1-TBDI4-21 | C1S7-23/P1-TBDI4-21 | P1-TBDI4-21/C1S7-23 | JB-601 | XV-60240D_DI_2 | XV-60240D | Control Valve Position Feedback |  | 325-01-602-PD-05 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | ส่งcommand เปิดวาวล์เข้า PLC ก่อน
149 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P1-TBDI4-22 | C1S7-24/P1-TBDI4-22 | P1-TBDI4-22/C1S7-24 | JB-601 | YA-60205_DI_1 | YA-60205 | Process Instrument |  | 325-01-602-PD-01 |  |  | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
150 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P1-TBDI4-23 | C1S7-25/P1-TBDI4-23 | P1-TBDI4-23/C1S7-25 | JB-601 | YI-60205_DI_1 | YI-60205 | Process Instrument |  | 325-01-602-PD-01 |  |  | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
151 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P1-TBDI4-24 | C1S7-26/P1-TBDI4-24 | P1-TBDI4-24/C1S7-26 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
152 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P1-TBDI4-25 | C1S7-27/P1-TBDI4-25 | P1-TBDI4-25/C1S7-27 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
153 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P1-TBDI4-26 | C1S7-28/P1-TBDI4-26 | P1-TBDI4-26/C1S7-28 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
154 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P1-TBDI4-27 | C1S7-29/P1-TBDI4-27 | P1-TBDI4-27/C1S7-29 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
155 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P1-TBDI4-28 | C1S7-30/P1-TBDI4-28 | P1-TBDI4-28/C1S7-30 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
156 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P1-TBDI4-29 | C1S7-31/P1-TBDI4-29 | P1-TBDI4-29/C1S7-31 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
157 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P1-TBDI4-30 | C1S7-32/P1-TBDI4-30 | P1-TBDI4-30/C1S7-32 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
158 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P1-TBDI4-31 | C1S7-33/P1-TBDI4-31 | P1-TBDI4-31/C1S7-33 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
159 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P1-TBDI4-32 | C1S7-34/P1-TBDI4-32 | P1-TBDI4-32/C1S7-34 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
160 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
161 | C1 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
162 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 1 | OUT-0 | P1-TBRL1-1 | C1S8-1/P1-TBRL1-1 | P1-TBRL1-1/C1S8-1 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
163 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 2 | OUT-1 | P1-TBRL1-2 | C1S8-2/P1-TBRL1-2 | P1-TBRL1-2/C1S8-2 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
164 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 3 | OUT-2 | P1-TBRL1-3 | C1S8-3/P1-TBRL1-3 | P1-TBRL1-3/C1S8-3 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
165 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 4 | OUT-3 | P1-TBRL1-4 | C1S8-4/P1-TBRL1-4 | P1-TBRL1-4/C1S8-4 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
166 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 5 | OUT-4 | P1-TBRL1-5 | C1S8-5/P1-TBRL1-5 | P1-TBRL1-5/C1S8-5 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
167 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 6 | OUT-5 | P1-TBRL1-6 | C1S8-6/P1-TBRL1-6 | P1-TBRL1-6/C1S8-6 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
168 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 7 | OUT-6 | P1-TBRL1-7 | C1S8-7/P1-TBRL1-7 | P1-TBRL1-7/C1S8-7 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
169 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 8 | OUT-7 | P1-TBRL1-8 | C1S8-8/P1-TBRL1-8 | P1-TBRL1-8/C1S8-8 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
170 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 9 | OUT-8 | P1-TBRL1-9 | C1S8-9/P1-TBRL1-9 | P1-TBRL1-9/C1S8-9 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
171 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 10 | OUT-9 | P1-TBRL1-10 | C1S8-10/P1-TBRL1-10 | P1-TBRL1-10/C1S8-10 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
172 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 11 | OUT-10 | P1-TBRL1-11 | C1S8-11/P1-TBRL1-11 | P1-TBRL1-11/C1S8-11 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
173 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 12 | OUT-11 | P1-TBRL1-12 | C1S8-12/P1-TBRL1-12 | P1-TBRL1-12/C1S8-12 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
174 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 13 | OUT-12 | P1-TBRL1-13 | C1S8-13/P1-TBRL1-13 | P1-TBRL1-13/C1S8-13 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
175 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 14 | OUT-13 | P1-TBRL1-14 | C1S8-14/P1-TBRL1-14 | P1-TBRL1-14/C1S8-14 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
176 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 15 | OUT-14 | P1-TBRL1-15 | C1S8-15/P1-TBRL1-15 | P1-TBRL1-15/C1S8-15 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
177 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 16 | OUT-15 | P1-TBRL1-16 | C1S8-16/P1-TBRL1-16 | P1-TBRL1-16/C1S8-16 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
178 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 17 | RTN OUT-0 | P1-TBRL1-17 | C1S8-17/P1-TBRL1-17 | P1-TBRL1-17/C1S8-17 | CA1 | Spare_DO_17 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
179 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 18 | DC-0(+) | +24VDC | +24VDC | +24VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
180 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 19 | OUT-16 | P1-TBRL1-17 | C1S8-19/P1-TBRL1-17 | P1-TBRL1-17/C1S8-19 | JB-401 | XV-40202E_DO_1 | XV-40202E | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
181 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 20 | OUT-17 | P1-TBRL1-18 | C1S8-20/P1-TBRL1-18 | P1-TBRL1-18/C1S8-20 | JB-401 | XV-40202F_DO_1 | XV-40202F | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
182 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 21 | OUT-18 | P1-TBRL1-19 | C1S8-21/P1-TBRL1-19 | P1-TBRL1-19/C1S8-21 | JB-401 | XV-40202G_DO_1 | XV-40202G | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
183 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 22 | OUT-19 | P1-TBRL1-20 | C1S8-22/P1-TBRL1-20 | P1-TBRL1-20/C1S8-22 | JB-401 | XV-40202H_DO_1 | XV-40202H | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
184 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 23 | OUT-20 | P1-TBRL1-21 | C1S8-23/P1-TBRL1-21 | P1-TBRL1-21/C1S8-23 | JB-401 | XV-40203B_DO_1 | XV-40203B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
185 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 24 | OUT-21 | P1-TBRL1-22 | C1S8-24/P1-TBRL1-22 | P1-TBRL1-22/C1S8-24 | JB-401 | XV-40203C_DO_1 | XV-40203C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
186 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 25 | OUT-22 | P1-TBRL1-23 | C1S8-25/P1-TBRL1-23 | P1-TBRL1-23/C1S8-25 | JB-401 | XV-40203D_DO_1 | XV-40203D | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
187 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 26 | OUT-23 | P1-TBRL1-24 | C1S8-26/P1-TBRL1-24 | P1-TBRL1-24/C1S8-26 | JB-401 | XV-40203E_DO_1 | XV-40203E | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
188 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 27 | OUT-24 | P1-TBRL1-25 | C1S8-27/P1-TBRL1-25 | P1-TBRL1-25/C1S8-27 | JB-401 | SV-40201_DO_1 | SV-40201 | Process Instrument | Solenoid valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
189 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 28 | OUT-25 | P1-TBRL1-26 | C1S8-28/P1-TBRL1-26 | P1-TBRL1-26/C1S8-28 | JB-401 | SV-40202_DO_1 | SV-40202 | Process Instrument | Solenoid valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
190 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 29 | OUT-26 | P1-TBRL1-27 | C1S8-29/P1-TBRL1-27 | P1-TBRL1-27/C1S8-29 | JB-401 | SV-40203_DO_1 | SV-40203 | Process Instrument | Solenoid valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
191 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 30 | OUT-27 | P1-TBRL1-28 | C1S8-30/P1-TBRL1-28 | P1-TBRL1-28/C1S8-30 | JB-401 | SV-40204_DO_1 | SV-40204 | Process Instrument | Solenoid valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
192 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 31 | OUT-28 | P1-TBRL1-29 | C1S8-31/P1-TBRL1-29 | P1-TBRL1-29/C1S8-31 | JB-401 | XV-40201A_DO_1 | XV-40201A | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
193 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 32 | OUT-29 | P1-TBRL1-30 | C1S8-32/P1-TBRL1-30 | P1-TBRL1-30/C1S8-32 | JB-401 | XV-40201B_DO_1 | XV-40201B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
194 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 33 | OUT-30 | P1-TBRL1-31 | C1S8-33/P1-TBRL1-31 | P1-TBRL1-31/C1S8-33 | JB-401 | XV-40201C_DO_1 | XV-40201C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
195 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 34 | OUT-31 | P1-TBRL1-32 | C1S8-34/P1-TBRL1-32 | P1-TBRL1-32/C1S8-34 | JB-401 | XV-40201D_DO_1 | XV-40201D | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
196 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 35 | RTN OUT-1 | P1-TBRL1-35 | C1S8-35/P1-TBRL1-35 | P1-TBRL1-35/C1S8-35 | CA1 | Spare_DO_35 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
197 | C1 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 36 | DC-1(+) | +24VDC | +24VDC | +24VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
198 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 1 | OUT-0 | P1-TBRL2-1 | C1S9-1/P1-TBRL2-1 | P1-TBRL2-1/C1S9-1 | JB-401 | XV-40201E_DO_1 | XV-40201E | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
199 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 2 | OUT-1 | P1-TBRL2-2 | C1S9-2/P1-TBRL2-2 | P1-TBRL2-2/C1S9-2 | JB-401 | XV-40201F_DO_1 | XV-40201F | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
200 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 3 | OUT-2 | P1-TBRL2-3 | C1S9-3/P1-TBRL2-3 | P1-TBRL2-3/C1S9-3 | JB-401 | XV-40201G_DO_1 | XV-40201G | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
201 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 4 | OUT-3 | P1-TBRL2-4 | C1S9-4/P1-TBRL2-4 | P1-TBRL2-4/C1S9-4 | JB-401 | XV-40201H_DO_1 | XV-40201H | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
202 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 5 | OUT-4 | P1-TBRL2-5 | C1S9-5/P1-TBRL2-5 | P1-TBRL2-5/C1S9-5 | JB-401 | XV-40202A_DO_1 | XV-40202A | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
203 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 6 | OUT-5 | P1-TBRL2-6 | C1S9-6/P1-TBRL2-6 | P1-TBRL2-6/C1S9-6 | JB-401 | XV-40202B_DO_1 | XV-40202B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
204 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 7 | OUT-6 | P1-TBRL2-7 | C1S9-7/P1-TBRL2-7 | P1-TBRL2-7/C1S9-7 | JB-401 | XV-40202C_DO_1 | XV-40202C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
205 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 8 | OUT-7 | P1-TBRL2-8 | C1S9-8/P1-TBRL2-8 | P1-TBRL2-8/C1S9-8 | JB-401 | XV-40202D_DO_1 | XV-40202D | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
206 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 9 | OUT-8 | P1-TBRL2-9 | C1S9-9/P1-TBRL2-9 | P1-TBRL2-9/C1S9-9 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
207 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 10 | OUT-9 | P1-TBRL2-10 | C1S9-10/P1-TBRL2-10 | P1-TBRL2-10/C1S9-10 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
208 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 11 | OUT-10 | P1-TBRL2-11 | C1S9-11/P1-TBRL2-11 | P1-TBRL2-11/C1S9-11 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
209 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 12 | OUT-11 | P1-TBRL2-12 | C1S9-12/P1-TBRL2-12 | P1-TBRL2-12/C1S9-12 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
210 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 13 | OUT-12 | P1-TBRL2-13 | C1S9-13/P1-TBRL2-13 | P1-TBRL2-13/C1S9-13 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
211 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 14 | OUT-13 | P1-TBRL2-14 | C1S9-14/P1-TBRL2-14 | P1-TBRL2-14/C1S9-14 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
212 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 15 | OUT-14 | P1-TBRL2-15 | C1S9-15/P1-TBRL2-15 | P1-TBRL2-15/C1S9-15 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
213 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 16 | OUT-15 | P1-TBRL2-16 | C1S9-16/P1-TBRL2-16 | P1-TBRL2-16/C1S9-16 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
214 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 17 | RTN OUT-0 | P1-TBRL2-17 | C1S9-17/P1-TBRL2-17 | P1-TBRL2-17/C1S9-17 | JB-401 | Spare_DO_17 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
215 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 18 | DC-0(+) | +24VDC | +24VDC | +24VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
216 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 19 | OUT-16 | P1-TBRL2-17 | C1S9-19/P1-TBRL2-17 | P1-TBRL2-17/C1S9-19 | JB-601 | SV-60201_DO_1 | SV-60201 | Process Instrument | On/Off Valve | 325-01-602-PD-08 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
217 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 20 | OUT-17 | P1-TBRL2-18 | C1S9-20/P1-TBRL2-18 | P1-TBRL2-18/C1S9-20 | JB-601 | SV-60202_DO_1 | SV-60202 | Process Instrument | On/Off Valve | 325-01-602-PD-08 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
218 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 21 | OUT-18 | P1-TBRL2-19 | C1S9-21/P1-TBRL2-19 | P1-TBRL2-19/C1S9-21 | JB-601 | SV-60230_DO_1 | SV-60230 | Process Instrument | Solenoid valve | 325-01-602-PD-04 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
219 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 22 | OUT-19 | P1-TBRL2-20 | C1S9-22/P1-TBRL2-20 | P1-TBRL2-20/C1S9-22 | JB-601 | SV-60203_DO_1 | SV-60203 | Process Instrument | On/Off Valve | 325-01-602-PD-08 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
220 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 23 | OUT-20 | P1-TBRL2-21 | C1S9-23/P1-TBRL2-21 | P1-TBRL2-21/C1S9-23 | JB-601 | SV-60240A_DO_1 | SV-60240A | Process Instrument | Solenoid valve | 325-01-602-PD-05 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
221 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 24 | OUT-21 | P1-TBRL2-22 | C1S9-24/P1-TBRL2-22 | P1-TBRL2-22/C1S9-24 | JB-601 | SV-60231_DO_1 | SV-60231 | Process Instrument | Solenoid valve | 325-01-602-PD-04 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
222 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 25 | OUT-22 | P1-TBRL2-23 | C1S9-25/P1-TBRL2-23 | P1-TBRL2-23/C1S9-25 | JB-601 | SV-60240B_DO_1 | SV-60240B | Process Instrument | Solenoid valve | 325-01-602-PD-05 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
223 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 26 | OUT-23 | P1-TBRL2-24 | C1S9-26/P1-TBRL2-24 | P1-TBRL2-24/C1S9-26 | JB-601 | SV-60240C_DO_1 | SV-60240C | Process Instrument | Solenoid valve | 325-01-602-PD-05 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
224 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 27 | OUT-24 | P1-TBRL2-25 | C1S9-27/P1-TBRL2-25 | P1-TBRL2-25/C1S9-27 | JB-601 | XV-60240D_DO_1 | XV-60240D | Control Valve Position Feedback |  | 325-01-602-PD-05 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | ส่งcommand เปิดวาวล์เข้า PLC ก่อน
225 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 28 | OUT-25 | P1-TBRL2-26 | C1S9-28/P1-TBRL2-26 | P1-TBRL2-26/C1S9-28 | JB-601 | XV-60251_DO_1 | XV-60251 | Control Valve Position Feedback | Automatic on/off valve | 325-01-602-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
226 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 29 | OUT-26 | P1-TBRL2-27 | C1S9-29/P1-TBRL2-27 | P1-TBRL2-27/C1S9-29 | JB-601 | XV-60202_DO_1 | XV-60202 | Control Valve Position Feedback | Automatic on/off valve | 325-01-602-PD-11 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
227 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 30 | OUT-27 | P1-TBRL2-28 | C1S9-30/P1-TBRL2-28 | P1-TBRL2-28/C1S9-30 | JB-601 | XV-60205A_DO_1 | XV-60205A | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-01 | 24 VDC energized |  | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
228 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 31 | OUT-28 | P1-TBRL2-29 | C1S9-31/P1-TBRL2-29 | P1-TBRL2-29/C1S9-31 | JB-601 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
229 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 32 | OUT-29 | P1-TBRL2-30 | C1S9-32/P1-TBRL2-30 | P1-TBRL2-30/C1S9-32 | JB-601 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
230 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 33 | OUT-30 | P1-TBRL2-31 | C1S9-33/P1-TBRL2-31 | P1-TBRL2-31/C1S9-33 | JB-601 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
231 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 34 | OUT-31 | P1-TBRL2-32 | C1S9-34/P1-TBRL2-32 | P1-TBRL2-32/C1S9-34 | JB-601 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
232 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 35 | RTN OUT-1 | P1-TBRL2-35 | C1S9-35/P1-TBRL2-35 | P1-TBRL2-35/C1S9-35 | JB-401 | Spare_DO_35 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
233 | C1 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 36 | DC-1(+) | +24VDC | +24VDC | +24VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
234 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1 | i RTN-0 | P1-TBAI1-1(B) | C1S10-1/P1-TBAI1-1(B) | P1-TBAI1-1(B)/C1S10-1 | JB-401 | FT-40201_AI_1 | FT-40201 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-15 m³/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
235 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 2 | IN-0 | P1-TBAI1-1(A) | C1S10-2/P1-TBAI1-1(A) | P1-TBAI1-1(A)/C1S10-2 | JB-401 | FT-40201_AI_1 | FT-40201 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-15 m³/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
236 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 3 | i RTN-1 | P1-TBAI1-2(B) | C1S10-3/P1-TBAI1-2(B) | P1-TBAI1-2(B)/C1S10-3 | JB-401 | FT-40201_AI_2 | FT-40201 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-15 m³/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
237 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 4 | IN-1 | P1-TBAI1-2(A) | C1S10-4/P1-TBAI1-2(A) | P1-TBAI1-2(A)/C1S10-4 | JB-401 | FT-40201_AI_2 | FT-40201 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-15 m³/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
238 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 5 | i RTN-2 | P1-TBAI1-3(B) | C1S10-5/P1-TBAI1-3(B) | P1-TBAI1-3(B)/C1S10-5 | JB-401 | FT-40202_AI_1 | FT-40202 | Magnetic Flow Transmitter | Magnetic Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0 to 8,000 m³/hr | Endress+Hauser | Promag W 400 / 50W (Electromagnetic Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
239 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 6 | IN-2 | P1-TBAI1-3(A) | C1S10-6/P1-TBAI1-3(A) | P1-TBAI1-3(A)/C1S10-6 | JB-401 | FT-40202_AI_1 | FT-40202 | Magnetic Flow Transmitter | Magnetic Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0 to 8,000 m³/hr | Endress+Hauser | Promag W 400 / 50W (Electromagnetic Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
240 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 7 | i RTN-3 | P1-TBAI1-4(B) | C1S10-7/P1-TBAI1-4(B) | P1-TBAI1-4(B)/C1S10-7 | JB-401 | LT-40203_AI_1 | LT-40203 | Level Transmitter | Level transmitter | 325-01-402-PD-02 | 4 - 20 mA | 0 - 10 m. | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
241 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 8 | IN-3 | P1-TBAI1-4(A) | C1S10-8/P1-TBAI1-4(A) | P1-TBAI1-4(A)/C1S10-8 | JB-401 | LT-40203_AI_1 | LT-40203 | Level Transmitter | Level transmitter | 325-01-402-PD-02 | 4 - 20 mA | 0 - 10 m. | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
242 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 9 | RTN | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
243 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 10 | RTN | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
244 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 11 | i RTN-4 | P1-TBAI1-5(B) | C1S10-11/P1-TBAI1-5(B) | P1-TBAI1-5(B)/C1S10-11 | JB-401 | LT-40201_AI_1 | LT-40201 | Level Transmitter | Level transmitter | 325-01-402-PD-02 | 4 - 20 mA | 0 - 10 m. | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
245 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 12 | IN-4 | P1-TBAI1-5(A) | C1S10-12/P1-TBAI1-5(A) | P1-TBAI1-5(A)/C1S10-12 | JB-401 | LT-40201_AI_1 | LT-40201 | Level Transmitter | Level transmitter | 325-01-402-PD-02 | 4 - 20 mA | 0 - 10 m. | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
246 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 13 | i RTN-5 | P1-TBAI1-6(B) | C1S10-13/P1-TBAI1-6(B) | P1-TBAI1-6(B)/C1S10-13 | JB-401 | LT-40202_AI_1 | LT-40202 | Level Transmitter | Level transmitter | 325-01-402-PD-01 | 4 - 20 mA | 0 - 10 m. | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
247 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 14 | IN-5 | P1-TBAI1-6(A) | C1S10-14/P1-TBAI1-6(A) | P1-TBAI1-6(A)/C1S10-14 | JB-401 | LT-40202_AI_1 | LT-40202 | Level Transmitter | Level transmitter | 325-01-402-PD-01 | 4 - 20 mA | 0 - 10 m. | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
248 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 15 | i RTN-6 | P1-TBAI1-7(B) | C1S10-15/P1-TBAI1-7(B) | P1-TBAI1-7(B)/C1S10-15 | JB-401 | pHT-40201_AI_1 | pHT-40201 | PH Transmitter | pH Analyzer | 325-01-402-PD-01 | 4 - 20 mA | 0-14 | Mettler Toledo | M300G2 + InPro3250i (pH System) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
249 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IN-6 | P1-TBAI1-7(A) | C1S10-16/P1-TBAI1-7(A) | P1-TBAI1-7(A)/C1S10-16 | JB-401 | pHT-40201_AI_1 | pHT-40201 | PH Transmitter | pH Analyzer | 325-01-402-PD-01 | 4 - 20 mA | 0-14 | Mettler Toledo | M300G2 + InPro3250i (pH System) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
250 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 17 | i RTN-7 | P1-TBAI1-8(B) | C1S10-17/P1-TBAI1-8(B) | P1-TBAI1-8(B)/C1S10-17 | JB-401 | pHT-40202_AI_1 | pHT-40202 | PH Transmitter | pH Analyzer | 325-01-402-PD-01 | 4 - 20 mA | 0-14 | Mettler Toledo | M300G2 + InPro3250i (pH System) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
251 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 18 | IN-7 | P1-TBAI1-8(A) | C1S10-18/P1-TBAI1-8(A) | P1-TBAI1-8(A)/C1S10-18 | JB-401 | pHT-40202_AI_1 | pHT-40202 | PH Transmitter | pH Analyzer | 325-01-402-PD-01 | 4 - 20 mA | 0-14 | Mettler Toledo | M300G2 + InPro3250i (pH System) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
252 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 19 | i RTN-8 | P1-TBAI1-9(B) | C1S10-19/P1-TBAI1-9(B) | P1-TBAI1-9(B)/C1S10-19 | JB-401 | PT-40201_AI_1 | PT-40201 | Pressure Transmitter | Pressure Transmitter | 325-01-402-PD-02 | 4 - 20 mA | -100 to 500 mBar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
253 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 20 | IN-8 | P1-TBAI1-9(A) | C1S10-20/P1-TBAI1-9(A) | P1-TBAI1-9(A)/C1S10-20 | JB-401 | PT-40201_AI_1 | PT-40201 | Pressure Transmitter | Pressure Transmitter | 325-01-402-PD-02 | 4 - 20 mA | -100 to 500 mBar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
254 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 21 | i RTN-9 | P1-TBAI1-10(B) | C1S10-21/P1-TBAI1-10(B) | P1-TBAI1-10(B)/C1S10-21 | JB-401 | PT-40202_AI_1 | PT-40202 | Pressure Transmitter | Pressure Transmitter | 325-01-402-PD-02 | 4 - 20 mA | 0 - 10'barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
255 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 22 | IN-9 | P1-TBAI1-10(A) | C1S10-22/P1-TBAI1-10(A) | P1-TBAI1-10(A)/C1S10-22 | JB-401 | PT-40202_AI_1 | PT-40202 | Pressure Transmitter | Pressure Transmitter | 325-01-402-PD-02 | 4 - 20 mA | 0 - 10'barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
256 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 23 | i RTN-10 | P1-TBAI1-11(B) | C1S10-23/P1-TBAI1-11(B) | P1-TBAI1-11(B)/C1S10-23 | JB-401 | PT-60202_AI_1 | PT-60202 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-01 | 4 - 20 mA |  | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE
257 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 24 | IN-10 | P1-TBAI1-11(A) | C1S10-24/P1-TBAI1-11(A) | P1-TBAI1-11(A)/C1S10-24 | JB-401 | PT-60202_AI_1 | PT-60202 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-01 | 4 - 20 mA |  | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE
258 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 25 | i RTN-11 | P1-TBAI1-12(B) | C1S10-25/P1-TBAI1-12(B) | P1-TBAI1-12(B)/C1S10-25 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
259 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 26 | IN-11 | P1-TBAI1-12(A) | C1S10-26/P1-TBAI1-12(A) | P1-TBAI1-12(A)/C1S10-26 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
260 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 27 | RTN | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
261 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 28 | RTN | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
262 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 29 | i RTN-12 | P1-TBAI1-13(B) | C1S10-29/P1-TBAI1-13(B) | P1-TBAI1-13(B)/C1S10-29 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
263 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 30 | IN-12 | P1-TBAI1-13(A) | C1S10-30/P1-TBAI1-13(A) | P1-TBAI1-13(A)/C1S10-30 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
264 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 31 | i RTN-13 | P1-TBAI1-14(B) | C1S10-31/P1-TBAI1-14(B) | P1-TBAI1-14(B)/C1S10-31 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
265 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 32 | IN-13 | P1-TBAI1-14(A) | C1S10-32/P1-TBAI1-14(A) | P1-TBAI1-14(A)/C1S10-32 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
266 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 33 | i RTN-14 | P1-TBAI1-15(B) | C1S10-33/P1-TBAI1-15(B) | P1-TBAI1-15(B)/C1S10-33 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
267 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 34 | IN-14 | P1-TBAI1-15(A) | C1S10-34/P1-TBAI1-15(A) | P1-TBAI1-15(A)/C1S10-34 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
268 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 35 | i RTN-15 | P1-TBAI1-16(B) | C1S10-35/P1-TBAI1-16(B) | P1-TBAI1-16(B)/C1S10-35 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
269 | C1 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 36 | IN-15 | P1-TBAI1-16(A) | C1S10-36/P1-TBAI1-16(A) | P1-TBAI1-16(A)/C1S10-36 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
270 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1 | i RTN-0 | P1-TBAI2-1(B) | C1S11-1/P1-TBAI2-1(B) | P1-TBAI2-1(B)/C1S11-1 | JB-601 | DPI-60240_AI_1 | DPI-60240 | Process Instrument |  | 325-01-602-PD-05 | 4 - 20 mA |  | Ashcroft | Model 1132 Diff. Pressure Gauge | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
271 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 2 | IN-0 | P1-TBAI2-1(A) | C1S11-2/P1-TBAI2-1(A) | P1-TBAI2-1(A)/C1S11-2 | JB-601 | DPI-60240_AI_1 | DPI-60240 | Process Instrument |  | 325-01-602-PD-05 | 4 - 20 mA |  | Ashcroft | Model 1132 Diff. Pressure Gauge | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
272 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 3 | i RTN-1 | P1-TBAI2-2(B) | C1S11-3/P1-TBAI2-2(B) | P1-TBAI2-2(B)/C1S11-3 | JB-601 | DPT-60202_AI_1 | DPT-60202 | Differential Pressure Transmitte | Differential Pressure Transmitter | 325-01-602-PD-08 | 4 - 20 mA | -100 to 500 mBar | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
273 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 4 | IN-1 | P1-TBAI2-2(A) | C1S11-4/P1-TBAI2-2(A) | P1-TBAI2-2(A)/C1S11-4 | JB-601 | DPT-60202_AI_1 | DPT-60202 | Differential Pressure Transmitte | Differential Pressure Transmitter | 325-01-602-PD-08 | 4 - 20 mA | -100 to 500 mBar | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
274 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 5 | i RTN-2 | P1-TBAI2-3(B) | C1S11-5/P1-TBAI2-3(B) | P1-TBAI2-3(B)/C1S11-5 | JB-601 | FT-60201_AI_1 | FT-60201 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-08 | 4 - 20 mA | 70000 m3/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
275 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 6 | IN-2 | P1-TBAI2-3(A) | C1S11-6/P1-TBAI2-3(A) | P1-TBAI2-3(A)/C1S11-6 | JB-601 | FT-60201_AI_1 | FT-60201 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-08 | 4 - 20 mA | 70000 m3/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
276 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 7 | i RTN-3 | P1-TBAI2-4(B) | C1S11-7/P1-TBAI2-4(B) | P1-TBAI2-4(B)/C1S11-7 | JB-601 | FT-60204_AI_1 | FT-60204 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-10 | 4 - 20 mA | 0 - 1000 m3/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
277 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 8 | IN-3 | P1-TBAI2-4(A) | C1S11-8/P1-TBAI2-4(A) | P1-TBAI2-4(A)/C1S11-8 | JB-601 | FT-60204_AI_1 | FT-60204 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-10 | 4 - 20 mA | 0 - 1000 m3/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
278 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 9 | RTN | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
279 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 10 | RTN | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
280 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 11 | i RTN-4 | P1-TBAI2-5(B) | C1S11-11/P1-TBAI2-5(B) | P1-TBAI2-5(B)/C1S11-11 | JB-601 | FT-61307_AI_1 | FT-61307 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-613-PD-04 | 4 - 20 mA | 0 - 1000 m3/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
281 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 12 | IN-4 | P1-TBAI2-5(A) | C1S11-12/P1-TBAI2-5(A) | P1-TBAI2-5(A)/C1S11-12 | JB-601 | FT-61307_AI_1 | FT-61307 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-613-PD-04 | 4 - 20 mA | 0 - 1000 m3/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
282 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 13 | i RTN-5 | P1-TBAI2-6(B) | C1S11-13/P1-TBAI2-6(B) | P1-TBAI2-6(B)/C1S11-13 | JB-601 | PT-60203_AI_1 | PT-60203 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-08 | 4 - 20 mA | 0 - 0.1 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
283 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 14 | IN-5 | P1-TBAI2-6(A) | C1S11-14/P1-TBAI2-6(A) | P1-TBAI2-6(A)/C1S11-14 | JB-601 | PT-60203_AI_1 | PT-60203 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-08 | 4 - 20 mA | 0 - 0.1 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
284 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 15 | i RTN-6 | P1-TBAI2-7(B) | C1S11-15/P1-TBAI2-7(B) | P1-TBAI2-7(B)/C1S11-15 | JB-601 | PT-60204_AI_1 | PT-60204 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-10 | 4 - 20 mA | 0 - 10 barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
285 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IN-6 | P1-TBAI2-7(A) | C1S11-16/P1-TBAI2-7(A) | P1-TBAI2-7(A)/C1S11-16 | JB-601 | PT-60204_AI_1 | PT-60204 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-10 | 4 - 20 mA | 0 - 10 barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
286 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 17 | i RTN-7 | P1-TBAI2-8(B) | C1S11-17/P1-TBAI2-8(B) | P1-TBAI2-8(B)/C1S11-17 | JB-601 | PT-60205_AI_1 | PT-60205 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-01 | 4 - 20 mA |  | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE
287 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 18 | IN-7 | P1-TBAI2-8(A) | C1S11-18/P1-TBAI2-8(A) | P1-TBAI2-8(A)/C1S11-18 | JB-601 | PT-60205_AI_1 | PT-60205 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-01 | 4 - 20 mA |  | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE
288 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 19 | i RTN-8 | P1-TBAI2-9(B) | C1S11-19/P1-TBAI2-9(B) | P1-TBAI2-9(B)/C1S11-19 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
289 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 20 | IN-8 | P1-TBAI2-9(A) | C1S11-20/P1-TBAI2-9(A) | P1-TBAI2-9(A)/C1S11-20 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
290 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 21 | i RTN-9 | P1-TBAI2-10(B) | C1S11-21/P1-TBAI2-10(B) | P1-TBAI2-10(B)/C1S11-21 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
291 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 22 | IN-9 | P1-TBAI2-10(A) | C1S11-22/P1-TBAI2-10(A) | P1-TBAI2-10(A)/C1S11-22 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
292 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 23 | i RTN-10 | P1-TBAI2-11(B) | C1S11-23/P1-TBAI2-11(B) | P1-TBAI2-11(B)/C1S11-23 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
293 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 24 | IN-10 | P1-TBAI2-11(A) | C1S11-24/P1-TBAI2-11(A) | P1-TBAI2-11(A)/C1S11-24 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
294 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 25 | i RTN-11 | P1-TBAI2-12(B) | C1S11-25/P1-TBAI2-12(B) | P1-TBAI2-12(B)/C1S11-25 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
295 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 26 | IN-11 | P1-TBAI2-12(A) | C1S11-26/P1-TBAI2-12(A) | P1-TBAI2-12(A)/C1S11-26 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
296 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 27 | RTN | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
297 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 28 | RTN | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
298 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 29 | i RTN-12 | P1-TBAI2-13(B) | C1S11-29/P1-TBAI2-13(B) | P1-TBAI2-13(B)/C1S11-29 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
299 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 30 | IN-12 | P1-TBAI2-13(A) | C1S11-30/P1-TBAI2-13(A) | P1-TBAI2-13(A)/C1S11-30 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
300 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 31 | i RTN-13 | P1-TBAI2-14(B) | C1S11-31/P1-TBAI2-14(B) | P1-TBAI2-14(B)/C1S11-31 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
301 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 32 | IN-13 | P1-TBAI2-14(A) | C1S11-32/P1-TBAI2-14(A) | P1-TBAI2-14(A)/C1S11-32 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
302 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 33 | i RTN-14 | P1-TBAI2-15(B) | C1S11-33/P1-TBAI2-15(B) | P1-TBAI2-15(B)/C1S11-33 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
303 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 34 | IN-14 | P1-TBAI2-15(A) | C1S11-34/P1-TBAI2-15(A) | P1-TBAI2-15(A)/C1S11-34 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
304 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 35 | i RTN-15 | P1-TBAI2-16(B) | C1S11-35/P1-TBAI2-16(B) | P1-TBAI2-16(B)/C1S11-35 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
305 | C1 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 36 | IN-15 | P1-TBAI2-16(A) | C1S11-36/P1-TBAI2-16(A) | P1-TBAI2-16(A)/C1S11-36 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
306 | C1 | C1S12 | 1756-N2 | EMPTY (Reserve Position) | - | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | - | - | - | - | - | - | - | EMPTY | -
307 | C2 | C2S0 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | -16(A) | C2S0-36/-16(A) | -16(A)/C2S0-36 | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C2S0_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
308 | C2 | C2S0 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C2S0-P2/ETH | ETH/C2S0-P2 | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C2S0_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
309 | C2 | C2S0 | 1756-EN4TR | COMM (EtherNet/IP) | USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C2S0-USB/CONSOLE | CONSOLE/C2S0-USB | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C2S0_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
310 | C2 | C2S0 | 1756-EN4TR | COMM (EtherNet/IP) | DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C2S0-DISP/DIAG | DIAG/C2S0-DISP | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C2S0_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
311 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P2-TBDI1-1 | C2S1-1/P2-TBDI1-1 | P2-TBDI1-1/C2S1-1 | JB-402 | FS-40204_DI_1 | FS-40204 | Flow Switch | Flow Switch | 325-01-402-PD-01 | Dry Contact |  | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Jet Cooker
312 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P2-TBDI1-2 | C2S1-2/P2-TBDI1-2 | P2-TBDI1-2/C2S1-2 | JB-402 | FS-40205_DI_1 | FS-40205 | Flow Switch | Flow Switch | 325-01-402-PD-02 | Dry Contact |  | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Jet Cooker
313 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P2-TBDI1-3 | C2S1-3/P2-TBDI1-3 | P2-TBDI1-3/C2S1-3 | JB-402 | FT-40221_DI_1 | FT-40221 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-6 m³/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
314 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P2-TBDI1-4 | C2S1-4/P2-TBDI1-4 | P2-TBDI1-4/C2S1-4 | JB-402 | FT-40222_DI_1 | FT-40222 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-850 kg/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
315 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P2-TBDI1-5 | C2S1-5/P2-TBDI1-5 | P2-TBDI1-5/C2S1-5 | JB-402 | HV-40207_DI_1 | HV-40207 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-402-PD-01 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Jet Cooker
316 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P2-TBDI1-6 | C2S1-6/P2-TBDI1-6 | P2-TBDI1-6/C2S1-6 | JB-402 | HV-40208_DI_1 | HV-40208 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-402-PD-01 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Jet Cooker
317 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P2-TBDI1-7 | C2S1-7/P2-TBDI1-7 | P2-TBDI1-7/C2S1-7 | JB-402 | XV-40203F_DI_1 | XV-40203F | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
318 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P2-TBDI1-8 | C2S1-8/P2-TBDI1-8 | P2-TBDI1-8/C2S1-8 | JB-402 | XV-40203F_DI_2 | XV-40203F | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
319 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P2-TBDI1-9 | C2S1-9/P2-TBDI1-9 | P2-TBDI1-9/C2S1-9 | JB-402 | XV-40204B_DI_1 | XV-40204B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
320 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P2-TBDI1-10 | C2S1-10/P2-TBDI1-10 | P2-TBDI1-10/C2S1-10 | JB-402 | XV-40204B_DI_2 | XV-40204B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
321 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P2-TBDI1-11 | C2S1-11/P2-TBDI1-11 | P2-TBDI1-11/C2S1-11 | JB-402 | XV-40204C_DI_1 | XV-40204C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
322 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P2-TBDI1-12 | C2S1-12/P2-TBDI1-12 | P2-TBDI1-12/C2S1-12 | JB-402 | XV-40204C_DI_2 | XV-40204C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
323 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P2-TBDI1-13 | C2S1-13/P2-TBDI1-13 | P2-TBDI1-13/C2S1-13 | JB-402 | XV-40205A_DI_1 | XV-40205A | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
324 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P2-TBDI1-14 | C2S1-14/P2-TBDI1-14 | P2-TBDI1-14/C2S1-14 | JB-402 | XV-40205A_DI_2 | XV-40205A | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
325 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P2-TBDI1-15 | C2S1-15/P2-TBDI1-15 | P2-TBDI1-15/C2S1-15 | JB-402 | XV-40205B_DI_1 | XV-40205B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
326 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P2-TBDI1-16 | C2S1-16/P2-TBDI1-16 | P2-TBDI1-16/C2S1-16 | JB-402 | XV-40205B_DI_2 | XV-40205B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
327 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
328 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
329 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P2-TBDI1-17 | C2S1-19/P2-TBDI1-17 | P2-TBDI1-17/C2S1-19 | JB-402 | XV-40205C_DI_1 | XV-40205C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
330 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P2-TBDI1-18 | C2S1-20/P2-TBDI1-18 | P2-TBDI1-18/C2S1-20 | JB-402 | XV-40205C_DI_2 | XV-40205C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
331 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P2-TBDI1-19 | C2S1-21/P2-TBDI1-19 | P2-TBDI1-19/C2S1-21 | JB-402 | XV-40205D_DI_1 | XV-40205D | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
332 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P2-TBDI1-20 | C2S1-22/P2-TBDI1-20 | P2-TBDI1-20/C2S1-22 | JB-402 | XV-40205D_DI_2 | XV-40205D | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
333 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P2-TBDI1-21 | C2S1-23/P2-TBDI1-21 | P2-TBDI1-21/C2S1-23 | JB-402 | XV-40205F_DI_1 | XV-40205F | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
334 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P2-TBDI1-22 | C2S1-24/P2-TBDI1-22 | P2-TBDI1-22/C2S1-24 | JB-402 | XV-40205F_DI_2 | XV-40205F | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
335 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P2-TBDI1-23 | C2S1-25/P2-TBDI1-23 | P2-TBDI1-23/C2S1-25 | JB-402 | XV-40222_DI_1 | XV-40222 | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
336 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P2-TBDI1-24 | C2S1-26/P2-TBDI1-24 | P2-TBDI1-24/C2S1-26 | JB-402 | XV-40222_DI_2 | XV-40222 | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
337 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P2-TBDI1-25 | C2S1-27/P2-TBDI1-25 | P2-TBDI1-25/C2S1-27 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
338 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P2-TBDI1-26 | C2S1-28/P2-TBDI1-26 | P2-TBDI1-26/C2S1-28 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
339 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P2-TBDI1-27 | C2S1-29/P2-TBDI1-27 | P2-TBDI1-27/C2S1-29 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
340 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P2-TBDI1-28 | C2S1-30/P2-TBDI1-28 | P2-TBDI1-28/C2S1-30 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
341 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P2-TBDI1-29 | C2S1-31/P2-TBDI1-29 | P2-TBDI1-29/C2S1-31 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
342 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P2-TBDI1-30 | C2S1-32/P2-TBDI1-30 | P2-TBDI1-30/C2S1-32 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
343 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P2-TBDI1-31 | C2S1-33/P2-TBDI1-31 | P2-TBDI1-31/C2S1-33 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
344 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P2-TBDI1-32 | C2S1-34/P2-TBDI1-32 | P2-TBDI1-32/C2S1-34 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
345 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
346 | C2 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
347 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P2-TBDI2-1 | C2S2-1/P2-TBDI2-1 | P2-TBDI2-1/C2S2-1 | JB-602 | FT-60202_DI_1 | FT-60202 | Flow Transmitter | Vortex Flow Transmitter | 325-01-602-PD-09 | 4 - 20 mA | 0 - 2000 kg/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
348 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P2-TBDI2-2 | C2S2-2/P2-TBDI2-2 | P2-TBDI2-2/C2S2-2 | JB-602 | LSH-60251_DI_1 | LSH-60251 | Process Instrument | Level switch | 325-01-602-PD-04 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | -
349 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P2-TBDI2-3 | C2S2-3/P2-TBDI2-3 | P2-TBDI2-3/C2S2-3 | JB-602 | PSL-60220_DI_1 | PSL-60220 | Process Instrument | Pressure switch | 325-01-602-PD-04 | Dry Contact | -0.01 mbar | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | -
350 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P2-TBDI2-4 | C2S2-4/P2-TBDI2-4 | P2-TBDI2-4/C2S2-4 | JB-602 | TSH-60230_DI_1 | TSH-60230 | Process Instrument | Temperature Switch | 325-01-602-PD-04 | Dry Contact | 0 - 140 C | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Switch มี 2 contact เข้า PLC กับ Fire Deluge
351 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P2-TBDI2-5 | C2S2-5/P2-TBDI2-5 | P2-TBDI2-5/C2S2-5 | JB-602 | TSH-60240_DI_1 | TSH-60240 | Process Instrument | Temperature Switch | 325-01-602-PD-05 | Dry Contact | 0 - 140 C | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Switch มี 2 contact เข้า PLC กับ Fire Deluge
352 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P2-TBDI2-6 | C2S2-6/P2-TBDI2-6 | P2-TBDI2-6/C2S2-6 | JB-602 | TSH-60241A_DI_1 | TSH-60241A | Process Instrument | Temperature Switch | 325-01-602-PD-05 | Dry Contact | 0 - 100 C | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Waiting
353 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P2-TBDI2-7 | C2S2-7/P2-TBDI2-7 | P2-TBDI2-7/C2S2-7 | JB-602 | TSH-60242A_DI_1 | TSH-60242A | Process Instrument | Temperature Switch | 325-01-602-PD-05 | Dry Contact | 0 - 100 C | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Waiting
354 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P2-TBDI2-8 | C2S2-8/P2-TBDI2-8 | P2-TBDI2-8/C2S2-8 | JB-602 | TSH-60243A_DI_1 | TSH-60243A | Process Instrument | Temperature Switch | 325-01-602-PD-05 | Dry Contact | 0 - 100 C | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Waiting
355 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P2-TBDI2-9 | C2S2-9/P2-TBDI2-9 | P2-TBDI2-9/C2S2-9 | JB-602 | TSL-60241B_DI_1 | TSL-60241B | Process Instrument | Temperature Switch | 325-01-602-PD-05 | Dry Contact | 0 - 100 C | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Waiting
356 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P2-TBDI2-10 | C2S2-10/P2-TBDI2-10 | P2-TBDI2-10/C2S2-10 | JB-602 | TSL-60242B_DI_1 | TSL-60242B | Process Instrument | Temperature Switch | 325-01-602-PD-05 | Dry Contact | 0 - 100 C | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Waiting
357 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P2-TBDI2-11 | C2S2-11/P2-TBDI2-11 | P2-TBDI2-11/C2S2-11 | JB-602 | TSL-60243B_DI_1 | TSL-60243B | Process Instrument | Temperature Switch | 325-01-602-PD-05 | Dry Contact | 0 - 100 C | Endress+Hauser | Thermophant TTR35 (Temperature Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Waiting
358 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P2-TBDI2-12 | C2S2-12/P2-TBDI2-12 | P2-TBDI2-12/C2S2-12 | JB-602 | XA-60240A_DI_1 | XA-60240A | Process Instrument |  | 325-01-602-PD-05 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
359 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P2-TBDI2-13 | C2S2-13/P2-TBDI2-13 | P2-TBDI2-13/C2S2-13 | JB-602 | XA-60240B_DI_1 | XA-60240B | Process Instrument |  | 325-01-602-PD-05 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
360 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P2-TBDI2-14 | C2S2-14/P2-TBDI2-14 | P2-TBDI2-14/C2S2-14 | JB-602 | XA-60241A_DI_1 | XA-60241A | Process Instrument |  | 325-01-602-PD-05 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Waiting
361 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P2-TBDI2-15 | C2S2-15/P2-TBDI2-15 | P2-TBDI2-15/C2S2-15 | JB-602 | XA-60241B_DI_1 | XA-60241B | Process Instrument |  | 325-01-602-PD-05 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Waiting
362 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P2-TBDI2-16 | C2S2-16/P2-TBDI2-16 | P2-TBDI2-16/C2S2-16 | JB-602 | XA-60242A_DI_1 | XA-60242A | Process Instrument |  | 325-01-602-PD-05 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Waiting
363 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
364 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
365 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P2-TBDI2-17 | C2S2-19/P2-TBDI2-17 | P2-TBDI2-17/C2S2-19 | JB-602 | XA-60242B_DI_1 | XA-60242B | Process Instrument |  | 325-01-602-PD-05 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Waiting
366 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P2-TBDI2-18 | C2S2-20/P2-TBDI2-18 | P2-TBDI2-18/C2S2-20 | JB-602 | XA-60243A_DI_1 | XA-60243A | Process Instrument |  | 325-01-602-PD-05 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Waiting
367 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P2-TBDI2-19 | C2S2-21/P2-TBDI2-19 | P2-TBDI2-19/C2S2-21 | JB-602 | XA-60243B_DI_1 | XA-60243B | Process Instrument |  | 325-01-602-PD-05 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Waiting
368 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P2-TBDI2-20 | C2S2-22/P2-TBDI2-20 | P2-TBDI2-20/C2S2-22 | JB-602 | XV-60214_DI_1 | XV-60214 | Control Valve Position Feedback | Automatic on/off valve | 325-01-602-PD-03 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
369 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P2-TBDI2-21 | C2S2-23/P2-TBDI2-21 | P2-TBDI2-21/C2S2-23 | JB-602 | XV-60214_DI_2 | XV-60214 | Control Valve Position Feedback | Automatic on/off valve | 325-01-602-PD-03 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
370 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P2-TBDI2-22 | C2S2-24/P2-TBDI2-22 | P2-TBDI2-22/C2S2-24 | JB-602 | XV-60241_DI_1 | XV-60241 | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-05 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
371 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P2-TBDI2-23 | C2S2-25/P2-TBDI2-23 | P2-TBDI2-23/C2S2-25 | JB-602 | XV-60241_DI_2 | XV-60241 | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-05 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
372 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P2-TBDI2-24 | C2S2-26/P2-TBDI2-24 | P2-TBDI2-24/C2S2-26 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
373 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P2-TBDI2-25 | C2S2-27/P2-TBDI2-25 | P2-TBDI2-25/C2S2-27 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
374 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P2-TBDI2-26 | C2S2-28/P2-TBDI2-26 | P2-TBDI2-26/C2S2-28 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
375 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P2-TBDI2-27 | C2S2-29/P2-TBDI2-27 | P2-TBDI2-27/C2S2-29 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
376 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P2-TBDI2-28 | C2S2-30/P2-TBDI2-28 | P2-TBDI2-28/C2S2-30 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
377 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P2-TBDI2-29 | C2S2-31/P2-TBDI2-29 | P2-TBDI2-29/C2S2-31 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
378 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P2-TBDI2-30 | C2S2-32/P2-TBDI2-30 | P2-TBDI2-30/C2S2-32 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
379 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P2-TBDI2-31 | C2S2-33/P2-TBDI2-31 | P2-TBDI2-31/C2S2-33 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
380 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P2-TBDI2-32 | C2S2-34/P2-TBDI2-32 | P2-TBDI2-32/C2S2-34 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
381 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
382 | C2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
383 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P2-TBDI3-1 | C2S3-1/P2-TBDI3-1 | P2-TBDI3-1/C2S3-1 | JB-607 | XA-FH-60210A_DI_1 | XA-FH-60210A | Process Instrument |  | 325-01-602-PD-06 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
384 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P2-TBDI3-2 | C2S3-2/P2-TBDI3-2 | P2-TBDI3-2/C2S3-2 | JB-607 | XA-FH-60210B_DI_1 | XA-FH-60210B | Process Instrument |  | 325-01-602-PD-06 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
385 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P2-TBDI3-3 | C2S3-3/P2-TBDI3-3 | P2-TBDI3-3/C2S3-3 | JB-607 | XA-FH-60210C_DI_1 | XA-FH-60210C | Process Instrument |  | 325-01-602-PD-06 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
386 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P2-TBDI3-4 | C2S3-4/P2-TBDI3-4 | P2-TBDI3-4/C2S3-4 | JB-607 | XA-FH-60210D_DI_1 | XA-FH-60210D | Process Instrument |  | 325-01-602-PD-06 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
387 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P2-TBDI3-5 | C2S3-5/P2-TBDI3-5 | P2-TBDI3-5/C2S3-5 | JB-607 | XA-FH-60210E_DI_1 | XA-FH-60210E | Process Instrument |  | 325-01-602-PD-06 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
388 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P2-TBDI3-6 | C2S3-6/P2-TBDI3-6 | P2-TBDI3-6/C2S3-6 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
389 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P2-TBDI3-7 | C2S3-7/P2-TBDI3-7 | P2-TBDI3-7/C2S3-7 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
390 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P2-TBDI3-8 | C2S3-8/P2-TBDI3-8 | P2-TBDI3-8/C2S3-8 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
391 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P2-TBDI3-9 | C2S3-9/P2-TBDI3-9 | P2-TBDI3-9/C2S3-9 | JB-607 | SV-60207_DI_1 | SV-60207 | Process Instrument | On/Off Valve | 325-01-602-PD-07 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
392 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P2-TBDI3-10 | C2S3-10/P2-TBDI3-10 | P2-TBDI3-10/C2S3-10 | JB-607 | SV-60207_DI_2 | SV-60207 | Process Instrument | On/Off Valve | 325-01-602-PD-07 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
393 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P2-TBDI3-11 | C2S3-11/P2-TBDI3-11 | P2-TBDI3-11/C2S3-11 | JB-607 | XV-60264_DI_1 | XV-60264 | Control Valve Position Feedback | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
394 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P2-TBDI3-12 | C2S3-12/P2-TBDI3-12 | P2-TBDI3-12/C2S3-12 | JB-607 | XV-60264_DI_2 | XV-60264 | Control Valve Position Feedback | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
395 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P2-TBDI3-13 | C2S3-13/P2-TBDI3-13 | P2-TBDI3-13/C2S3-13 | JB-607 | XV-60264FN_DI_1 | XV-60264FN | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
396 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P2-TBDI3-14 | C2S3-14/P2-TBDI3-14 | P2-TBDI3-14/C2S3-14 | JB-607 | XV-60264FN_DI_2 | XV-60264FN | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
397 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P2-TBDI3-15 | C2S3-15/P2-TBDI3-15 | P2-TBDI3-15/C2S3-15 | JB-607 | XV-60264FP_DI_1 | XV-60264FP | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
398 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P2-TBDI3-16 | C2S3-16/P2-TBDI3-16 | P2-TBDI3-16/C2S3-16 | JB-607 | XV-60264FP_DI_2 | XV-60264FP | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
399 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
400 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
401 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P2-TBDI3-17 | C2S3-19/P2-TBDI3-17 | P2-TBDI3-17/C2S3-19 | JB-607 | XV-60201_DI_1 | XV-60201 | Control Valve Position Feedback | Automatic on/off valve | 325-01-602-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
402 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P2-TBDI3-18 | C2S3-20/P2-TBDI3-18 | P2-TBDI3-18/C2S3-20 | JB-607 | XV-60201_DI_2 | XV-60201 | Control Valve Position Feedback | Automatic on/off valve | 325-01-602-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
403 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P2-TBDI3-19 | C2S3-21/P2-TBDI3-19 | P2-TBDI3-19/C2S3-21 | JB-607 | XV-60264FQ_DI_1 | XV-60264FQ | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
404 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P2-TBDI3-20 | C2S3-22/P2-TBDI3-20 | P2-TBDI3-20/C2S3-22 | JB-607 | XV-60264FQ_DI_2 | XV-60264FQ | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
405 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P2-TBDI3-21 | C2S3-23/P2-TBDI3-21 | P2-TBDI3-21/C2S3-23 | JB-607 | XV-60261_DI_1 | XV-60261 | Control Valve Position Feedback | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
406 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P2-TBDI3-22 | C2S3-24/P2-TBDI3-22 | P2-TBDI3-22/C2S3-24 | JB-607 | XV-60261_DI_2 | XV-60261 | Control Valve Position Feedback | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
407 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P2-TBDI3-23 | C2S3-25/P2-TBDI3-23 | P2-TBDI3-23/C2S3-25 | JB-607 | XV-60264FR_DI_1 | XV-60264FR | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
408 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P2-TBDI3-24 | C2S3-26/P2-TBDI3-24 | P2-TBDI3-24/C2S3-26 | JB-607 | XV-60264FR_DI_2 | XV-60264FR | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
409 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P2-TBDI3-25 | C2S3-27/P2-TBDI3-25 | P2-TBDI3-25/C2S3-27 | JB-607 | XV-60261FA_DI_1 | XV-60261FA | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
410 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P2-TBDI3-26 | C2S3-28/P2-TBDI3-26 | P2-TBDI3-26/C2S3-28 | JB-607 | XV-60261FA_DI_2 | XV-60261FA | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
411 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P2-TBDI3-27 | C2S3-29/P2-TBDI3-27 | P2-TBDI3-27/C2S3-29 | JB-607 | XV-60264SN_DI_1 | XV-60264SN | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
412 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P2-TBDI3-28 | C2S3-30/P2-TBDI3-28 | P2-TBDI3-28/C2S3-30 | JB-607 | XV-60264SN_DI_2 | XV-60264SN | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
413 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P2-TBDI3-29 | C2S3-31/P2-TBDI3-29 | P2-TBDI3-29/C2S3-31 | JB-607 | XV-60261FB_DI_1 | XV-60261FB | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
414 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P2-TBDI3-30 | C2S3-32/P2-TBDI3-30 | P2-TBDI3-30/C2S3-32 | JB-607 | XV-60261FB_DI_2 | XV-60261FB | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
415 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P2-TBDI3-31 | C2S3-33/P2-TBDI3-31 | P2-TBDI3-31/C2S3-33 | JB-607 | XV-60264SP_DI_1 | XV-60264SP | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
416 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P2-TBDI3-32 | C2S3-34/P2-TBDI3-32 | P2-TBDI3-32/C2S3-34 | JB-607 | XV-60264SP_DI_2 | XV-60264SP | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
417 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
418 | C2 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
419 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P2-TBDI4-1 | C2S4-1/P2-TBDI4-1 | P2-TBDI4-1/C2S4-1 | JB-607 | XV-60261FC_DI_1 | XV-60261FC | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
420 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P2-TBDI4-2 | C2S4-2/P2-TBDI4-2 | P2-TBDI4-2/C2S4-2 | JB-607 | XV-60261FC_DI_2 | XV-60261FC | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
421 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P2-TBDI4-3 | C2S4-3/P2-TBDI4-3 | P2-TBDI4-3/C2S4-3 | JB-607 | XV-60264SQ_DI_1 | XV-60264SQ | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
422 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P2-TBDI4-4 | C2S4-4/P2-TBDI4-4 | P2-TBDI4-4/C2S4-4 | JB-607 | XV-60264SQ_DI_2 | XV-60264SQ | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
423 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P2-TBDI4-5 | C2S4-5/P2-TBDI4-5 | P2-TBDI4-5/C2S4-5 | JB-607 | XV-60261FD_DI_1 | XV-60261FD | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
424 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P2-TBDI4-6 | C2S4-6/P2-TBDI4-6 | P2-TBDI4-6/C2S4-6 | JB-607 | XV-60261FD_DI_2 | XV-60261FD | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
425 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P2-TBDI4-7 | C2S4-7/P2-TBDI4-7 | P2-TBDI4-7/C2S4-7 | JB-607 | XV-60264SR_DI_1 | XV-60264SR | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
426 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P2-TBDI4-8 | C2S4-8/P2-TBDI4-8 | P2-TBDI4-8/C2S4-8 | JB-607 | XV-60264SR_DI_2 | XV-60264SR | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
427 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P2-TBDI4-9 | C2S4-9/P2-TBDI4-9 | P2-TBDI4-9/C2S4-9 | JB-607 | XV-60261SA_DI_1 | XV-60261SA | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
428 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P2-TBDI4-10 | C2S4-10/P2-TBDI4-10 | P2-TBDI4-10/C2S4-10 | JB-607 | XV-60261SA_DI_2 | XV-60261SA | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
429 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P2-TBDI4-11 | C2S4-11/P2-TBDI4-11 | P2-TBDI4-11/C2S4-11 | JB-607 | XV-60261SB_DI_1 | XV-60261SB | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
430 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P2-TBDI4-12 | C2S4-12/P2-TBDI4-12 | P2-TBDI4-12/C2S4-12 | JB-607 | XV-60261SB_DI_2 | XV-60261SB | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
431 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P2-TBDI4-13 | C2S4-13/P2-TBDI4-13 | P2-TBDI4-13/C2S4-13 | JB-607 | XV-60261SC_DI_1 | XV-60261SC | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
432 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P2-TBDI4-14 | C2S4-14/P2-TBDI4-14 | P2-TBDI4-14/C2S4-14 | JB-607 | XV-60261SC_DI_2 | XV-60261SC | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
433 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P2-TBDI4-15 | C2S4-15/P2-TBDI4-15 | P2-TBDI4-15/C2S4-15 | JB-607 | XV-60261SD_DI_1 | XV-60261SD | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
434 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P2-TBDI4-16 | C2S4-16/P2-TBDI4-16 | P2-TBDI4-16/C2S4-16 | JB-607 | XV-60261SD_DI_2 | XV-60261SD | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
435 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
436 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
437 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P2-TBDI4-17 | C2S4-19/P2-TBDI4-17 | P2-TBDI4-17/C2S4-19 | JB-607 | XV-60262_DI_1 | XV-60262 | Control Valve Position Feedback | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
438 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P2-TBDI4-18 | C2S4-20/P2-TBDI4-18 | P2-TBDI4-18/C2S4-20 | JB-607 | XV-60262_DI_2 | XV-60262 | Control Valve Position Feedback | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
439 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P2-TBDI4-19 | C2S4-21/P2-TBDI4-19 | P2-TBDI4-19/C2S4-21 | JB-607 | XV-60262FE_DI_1 | XV-60262FE | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
440 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P2-TBDI4-20 | C2S4-22/P2-TBDI4-20 | P2-TBDI4-20/C2S4-22 | JB-607 | XV-60262FE_DI_2 | XV-60262FE | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
441 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P2-TBDI4-21 | C2S4-23/P2-TBDI4-21 | P2-TBDI4-21/C2S4-23 | JB-607 | XV-60262FF_DI_1 | XV-60262FF | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
442 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P2-TBDI4-22 | C2S4-24/P2-TBDI4-22 | P2-TBDI4-22/C2S4-24 | JB-607 | XV-60262FF_DI_2 | XV-60262FF | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
443 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P2-TBDI4-23 | C2S4-25/P2-TBDI4-23 | P2-TBDI4-23/C2S4-25 | JB-607 | XV-60262FG_DI_1 | XV-60262FG | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
444 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P2-TBDI4-24 | C2S4-26/P2-TBDI4-24 | P2-TBDI4-24/C2S4-26 | JB-607 | XV-60262FG_DI_2 | XV-60262FG | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
445 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P2-TBDI4-25 | C2S4-27/P2-TBDI4-25 | P2-TBDI4-25/C2S4-27 | JB-607 | XV-60262FH_DI_1 | XV-60262FH | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
446 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P2-TBDI4-26 | C2S4-28/P2-TBDI4-26 | P2-TBDI4-26/C2S4-28 | JB-607 | XV-60262FH_DI_2 | XV-60262FH | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
447 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P2-TBDI4-27 | C2S4-29/P2-TBDI4-27 | P2-TBDI4-27/C2S4-29 | JB-607 | XV-60262SE_DI_1 | XV-60262SE | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
448 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P2-TBDI4-28 | C2S4-30/P2-TBDI4-28 | P2-TBDI4-28/C2S4-30 | JB-607 | XV-60262SE_DI_2 | XV-60262SE | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
449 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P2-TBDI4-29 | C2S4-31/P2-TBDI4-29 | P2-TBDI4-29/C2S4-31 | JB-607 | XV-60262SF_DI_1 | XV-60262SF | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
450 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P2-TBDI4-30 | C2S4-32/P2-TBDI4-30 | P2-TBDI4-30/C2S4-32 | JB-607 | XV-60262SF_DI_2 | XV-60262SF | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
451 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P2-TBDI4-31 | C2S4-33/P2-TBDI4-31 | P2-TBDI4-31/C2S4-33 | JB-607 | XV-60262SG_DI_1 | XV-60262SG | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
452 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P2-TBDI4-32 | C2S4-34/P2-TBDI4-32 | P2-TBDI4-32/C2S4-34 | JB-607 | XV-60262SG_DI_2 | XV-60262SG | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
453 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
454 | C2 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
455 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P2-TBDI5-1 | C2S5-1/P2-TBDI5-1 | P2-TBDI5-1/C2S5-1 | JB-607 | XV-60262SH_DI_1 | XV-60262SH | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
456 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P2-TBDI5-2 | C2S5-2/P2-TBDI5-2 | P2-TBDI5-2/C2S5-2 | JB-607 | XV-60262SH_DI_2 | XV-60262SH | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
457 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P2-TBDI5-3 | C2S5-3/P2-TBDI5-3 | P2-TBDI5-3/C2S5-3 | JB-607 | XV-60263_DI_1 | XV-60263 | Control Valve Position Feedback | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
458 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P2-TBDI5-4 | C2S5-4/P2-TBDI5-4 | P2-TBDI5-4/C2S5-4 | JB-607 | XV-60263_DI_2 | XV-60263 | Control Valve Position Feedback | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
459 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P2-TBDI5-5 | C2S5-5/P2-TBDI5-5 | P2-TBDI5-5/C2S5-5 | JB-607 | XV-60263FJ_DI_1 | XV-60263FJ | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
460 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P2-TBDI5-6 | C2S5-6/P2-TBDI5-6 | P2-TBDI5-6/C2S5-6 | JB-607 | XV-60263FJ_DI_2 | XV-60263FJ | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
461 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P2-TBDI5-7 | C2S5-7/P2-TBDI5-7 | P2-TBDI5-7/C2S5-7 | JB-607 | XV-60263FK_DI_1 | XV-60263FK | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
462 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P2-TBDI5-8 | C2S5-8/P2-TBDI5-8 | P2-TBDI5-8/C2S5-8 | JB-607 | XV-60263FK_DI_2 | XV-60263FK | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
463 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P2-TBDI5-9 | C2S5-9/P2-TBDI5-9 | P2-TBDI5-9/C2S5-9 | JB-607 | XV-60263FL_DI_1 | XV-60263FL | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
464 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P2-TBDI5-10 | C2S5-10/P2-TBDI5-10 | P2-TBDI5-10/C2S5-10 | JB-607 | XV-60263FL_DI_2 | XV-60263FL | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
465 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P2-TBDI5-11 | C2S5-11/P2-TBDI5-11 | P2-TBDI5-11/C2S5-11 | JB-607 | XV-60263FM_DI_1 | XV-60263FM | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
466 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P2-TBDI5-12 | C2S5-12/P2-TBDI5-12 | P2-TBDI5-12/C2S5-12 | JB-607 | XV-60263FM_DI_2 | XV-60263FM | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
467 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P2-TBDI5-13 | C2S5-13/P2-TBDI5-13 | P2-TBDI5-13/C2S5-13 | JB-607 | XV-60263SJ_DI_1 | XV-60263SJ | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
468 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P2-TBDI5-14 | C2S5-14/P2-TBDI5-14 | P2-TBDI5-14/C2S5-14 | JB-607 | XV-60263SJ_DI_2 | XV-60263SJ | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
469 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P2-TBDI5-15 | C2S5-15/P2-TBDI5-15 | P2-TBDI5-15/C2S5-15 | JB-607 | XV-60263SK_DI_1 | XV-60263SK | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
470 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P2-TBDI5-16 | C2S5-16/P2-TBDI5-16 | P2-TBDI5-16/C2S5-16 | JB-607 | XV-60263SK_DI_2 | XV-60263SK | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
471 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
472 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
473 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P2-TBDI5-17 | C2S5-19/P2-TBDI5-17 | P2-TBDI5-17/C2S5-19 | JB-607 | XV-60263SL_DI_1 | XV-60263SL | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
474 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P2-TBDI5-18 | C2S5-20/P2-TBDI5-18 | P2-TBDI5-18/C2S5-20 | JB-607 | XV-60263SL_DI_2 | XV-60263SL | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
475 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P2-TBDI5-19 | C2S5-21/P2-TBDI5-19 | P2-TBDI5-19/C2S5-21 | JB-607 | XV-60263SM_DI_1 | XV-60263SM | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
476 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P2-TBDI5-20 | C2S5-22/P2-TBDI5-20 | P2-TBDI5-20/C2S5-22 | JB-607 | XV-60263SM_DI_2 | XV-60263SM | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
477 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P2-TBDI5-21 | C2S5-23/P2-TBDI5-21 | P2-TBDI5-21/C2S5-23 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
478 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P2-TBDI5-22 | C2S5-24/P2-TBDI5-22 | P2-TBDI5-22/C2S5-24 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
479 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P2-TBDI5-23 | C2S5-25/P2-TBDI5-23 | P2-TBDI5-23/C2S5-25 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
480 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P2-TBDI5-24 | C2S5-26/P2-TBDI5-24 | P2-TBDI5-24/C2S5-26 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
481 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P2-TBDI5-25 | C2S5-27/P2-TBDI5-25 | P2-TBDI5-25/C2S5-27 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
482 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P2-TBDI5-26 | C2S5-28/P2-TBDI5-26 | P2-TBDI5-26/C2S5-28 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
483 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P2-TBDI5-27 | C2S5-29/P2-TBDI5-27 | P2-TBDI5-27/C2S5-29 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
484 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P2-TBDI5-28 | C2S5-30/P2-TBDI5-28 | P2-TBDI5-28/C2S5-30 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
485 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P2-TBDI5-29 | C2S5-31/P2-TBDI5-29 | P2-TBDI5-29/C2S5-31 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
486 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P2-TBDI5-30 | C2S5-32/P2-TBDI5-30 | P2-TBDI5-30/C2S5-32 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
487 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P2-TBDI5-31 | C2S5-33/P2-TBDI5-31 | P2-TBDI5-31/C2S5-33 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
488 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P2-TBDI5-32 | C2S5-34/P2-TBDI5-32 | P2-TBDI5-32/C2S5-34 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
489 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
490 | C2 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
491 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 1 | OUT-0 | P2-TBRL1-1 | C2S6-1/P2-TBRL1-1 | P2-TBRL1-1/C2S6-1 | JB-402 | XV-40203F_DO_1 | XV-40203F | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
492 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 2 | OUT-1 | P2-TBRL1-2 | C2S6-2/P2-TBRL1-2 | P2-TBRL1-2/C2S6-2 | JB-402 | XV-40204B_DO_1 | XV-40204B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
493 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 3 | OUT-2 | P2-TBRL1-3 | C2S6-3/P2-TBRL1-3 | P2-TBRL1-3/C2S6-3 | JB-402 | XV-40204C_DO_1 | XV-40204C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
494 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 4 | OUT-3 | P2-TBRL1-4 | C2S6-4/P2-TBRL1-4 | P2-TBRL1-4/C2S6-4 | JB-402 | XV-40205A_DO_1 | XV-40205A | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
495 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 5 | OUT-4 | P2-TBRL1-5 | C2S6-5/P2-TBRL1-5 | P2-TBRL1-5/C2S6-5 | JB-402 | XV-40205B_DO_1 | XV-40205B | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
496 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 6 | OUT-5 | P2-TBRL1-6 | C2S6-6/P2-TBRL1-6 | P2-TBRL1-6/C2S6-6 | JB-402 | XV-40205C_DO_1 | XV-40205C | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
497 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 7 | OUT-6 | P2-TBRL1-7 | C2S6-7/P2-TBRL1-7 | P2-TBRL1-7/C2S6-7 | JB-402 | XV-40205D_DO_1 | XV-40205D | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
498 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 8 | OUT-7 | P2-TBRL1-8 | C2S6-8/P2-TBRL1-8 | P2-TBRL1-8/C2S6-8 | JB-402 | XV-40205F_DO_1 | XV-40205F | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
499 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 9 | OUT-8 | P2-TBRL1-9 | C2S6-9/P2-TBRL1-9 | P2-TBRL1-9/C2S6-9 | JB-402 | XV-40222_DO_1 | XV-40222 | Control Valve Position Feedback | Automatic on/off valve | 325-01-402-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Jet Cooker
500 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 10 | OUT-9 | P2-TBRL1-10 | C2S6-10/P2-TBRL1-10 | P2-TBRL1-10/C2S6-10 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
501 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 11 | OUT-10 | P2-TBRL1-11 | C2S6-11/P2-TBRL1-11 | P2-TBRL1-11/C2S6-11 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
502 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 12 | OUT-11 | P2-TBRL1-12 | C2S6-12/P2-TBRL1-12 | P2-TBRL1-12/C2S6-12 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
503 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 13 | OUT-12 | P2-TBRL1-13 | C2S6-13/P2-TBRL1-13 | P2-TBRL1-13/C2S6-13 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
504 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 14 | OUT-13 | P2-TBRL1-14 | C2S6-14/P2-TBRL1-14 | P2-TBRL1-14/C2S6-14 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
505 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 15 | OUT-14 | P2-TBRL1-15 | C2S6-15/P2-TBRL1-15 | P2-TBRL1-15/C2S6-15 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
506 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 16 | OUT-15 | P2-TBRL1-16 | C2S6-16/P2-TBRL1-16 | P2-TBRL1-16/C2S6-16 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
507 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 17 | RTN OUT-0 | P2-TBRL1-17 | C2S6-17/P2-TBRL1-17 | P2-TBRL1-17/C2S6-17 | JB-402 | Spare_DO_17 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
508 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 18 | DC-0(+) | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
509 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 19 | OUT-16 | P2-TBRL1-17 | C2S6-19/P2-TBRL1-17 | P2-TBRL1-17/C2S6-19 | JB-602 | XS-60240B_DO_1 | XS-60240B | Process Instrument |  | 325-01-602-PD-05 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
510 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 20 | OUT-17 | P2-TBRL1-18 | C2S6-20/P2-TBRL1-18 | P2-TBRL1-18/C2S6-20 | JB-602 | XV-60214_DO_1 | XV-60214 | Control Valve Position Feedback | Automatic on/off valve | 325-01-602-PD-03 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
511 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 21 | OUT-18 | P2-TBRL1-19 | C2S6-21/P2-TBRL1-19 | P2-TBRL1-19/C2S6-21 | JB-602 | XV-60241_DO_1 | XV-60241 | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-05 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
512 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 22 | OUT-19 | P2-TBRL1-20 | C2S6-22/P2-TBRL1-20 | P2-TBRL1-20/C2S6-22 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
513 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 23 | OUT-20 | P2-TBRL1-21 | C2S6-23/P2-TBRL1-21 | P2-TBRL1-21/C2S6-23 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
514 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 24 | OUT-21 | P2-TBRL1-22 | C2S6-24/P2-TBRL1-22 | P2-TBRL1-22/C2S6-24 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
515 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 25 | OUT-22 | P2-TBRL1-23 | C2S6-25/P2-TBRL1-23 | P2-TBRL1-23/C2S6-25 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
516 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 26 | OUT-23 | P2-TBRL1-24 | C2S6-26/P2-TBRL1-24 | P2-TBRL1-24/C2S6-26 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
517 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 27 | OUT-24 | P2-TBRL1-25 | C2S6-27/P2-TBRL1-25 | P2-TBRL1-25/C2S6-27 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
518 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 28 | OUT-25 | P2-TBRL1-26 | C2S6-28/P2-TBRL1-26 | P2-TBRL1-26/C2S6-28 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
519 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 29 | OUT-26 | P2-TBRL1-27 | C2S6-29/P2-TBRL1-27 | P2-TBRL1-27/C2S6-29 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
520 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 30 | OUT-27 | P2-TBRL1-28 | C2S6-30/P2-TBRL1-28 | P2-TBRL1-28/C2S6-30 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
521 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 31 | OUT-28 | P2-TBRL1-29 | C2S6-31/P2-TBRL1-29 | P2-TBRL1-29/C2S6-31 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
522 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 32 | OUT-29 | P2-TBRL1-30 | C2S6-32/P2-TBRL1-30 | P2-TBRL1-30/C2S6-32 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
523 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 33 | OUT-30 | P2-TBRL1-31 | C2S6-33/P2-TBRL1-31 | P2-TBRL1-31/C2S6-33 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
524 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 34 | OUT-31 | P2-TBRL1-32 | C2S6-34/P2-TBRL1-32 | P2-TBRL1-32/C2S6-34 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
525 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 35 | RTN OUT-1 | P2-TBRL1-35 | C2S6-35/P2-TBRL1-35 | P2-TBRL1-35/C2S6-35 | JB-402 | Spare_DO_35 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
526 | C2 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 36 | DC-1(+) | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
527 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 1 | OUT-0 | P2-TBRL2-1 | C2S7-1/P2-TBRL2-1 | P2-TBRL2-1/C2S7-1 | JB-607 | SV-60207_DO_1 | SV-60207 | Process Instrument | On/Off Valve | 325-01-602-PD-07 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
528 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 2 | OUT-1 | P2-TBRL2-2 | C2S7-2/P2-TBRL2-2 | P2-TBRL2-2/C2S7-2 | JB-607 | XS-FH-60210C_DO_1 | XS-FH-60210C | Process Instrument |  | 325-01-602-PD-06 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
529 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 3 | OUT-2 | P2-TBRL2-3 | C2S7-3/P2-TBRL2-3 | P2-TBRL2-3/C2S7-3 | JB-607 | XS-FH-60210D_DO_1 | XS-FH-60210D | Process Instrument |  | 325-01-602-PD-06 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
530 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 4 | OUT-3 | P2-TBRL2-4 | C2S7-4/P2-TBRL2-4 | P2-TBRL2-4/C2S7-4 | JB-607 | XV-60201_DO_1 | XV-60201 | Control Valve Position Feedback | Automatic on/off valve | 325-01-602-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
531 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 5 | OUT-4 | P2-TBRL2-5 | C2S7-5/P2-TBRL2-5 | P2-TBRL2-5/C2S7-5 | JB-607 | XV-60261_DO_1 | XV-60261 | Control Valve Position Feedback | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
532 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 6 | OUT-5 | P2-TBRL2-6 | C2S7-6/P2-TBRL2-6 | P2-TBRL2-6/C2S7-6 | JB-607 | XV-60261FA_DO_1 | XV-60261FA | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
533 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 7 | OUT-6 | P2-TBRL2-7 | C2S7-7/P2-TBRL2-7 | P2-TBRL2-7/C2S7-7 | JB-607 | XV-60261FB_DO_1 | XV-60261FB | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
534 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 8 | OUT-7 | P2-TBRL2-8 | C2S7-8/P2-TBRL2-8 | P2-TBRL2-8/C2S7-8 | JB-607 | XV-60261FC_DO_1 | XV-60261FC | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
535 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 9 | OUT-8 | P2-TBRL2-9 | C2S7-9/P2-TBRL2-9 | P2-TBRL2-9/C2S7-9 | JB-607 | XV-60261FD_DO_1 | XV-60261FD | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
536 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 10 | OUT-9 | P2-TBRL2-10 | C2S7-10/P2-TBRL2-10 | P2-TBRL2-10/C2S7-10 | JB-607 | XV-60261SA_DO_1 | XV-60261SA | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
537 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 11 | OUT-10 | P2-TBRL2-11 | C2S7-11/P2-TBRL2-11 | P2-TBRL2-11/C2S7-11 | JB-607 | XV-60261SB_DO_1 | XV-60261SB | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
538 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 12 | OUT-11 | P2-TBRL2-12 | C2S7-12/P2-TBRL2-12 | P2-TBRL2-12/C2S7-12 | JB-607 | XV-60261SC_DO_1 | XV-60261SC | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
539 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 13 | OUT-12 | P2-TBRL2-13 | C2S7-13/P2-TBRL2-13 | P2-TBRL2-13/C2S7-13 | JB-607 | XV-60261SD_DO_1 | XV-60261SD | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
540 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 14 | OUT-13 | P2-TBRL2-14 | C2S7-14/P2-TBRL2-14 | P2-TBRL2-14/C2S7-14 | JB-607 | XV-60262_DO_1 | XV-60262 | Control Valve Position Feedback | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
541 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 15 | OUT-14 | P2-TBRL2-15 | C2S7-15/P2-TBRL2-15 | P2-TBRL2-15/C2S7-15 | JB-607 | XV-60262FE_DO_1 | XV-60262FE | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
542 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 16 | OUT-15 | P2-TBRL2-16 | C2S7-16/P2-TBRL2-16 | P2-TBRL2-16/C2S7-16 | JB-607 | XV-60262FF_DO_1 | XV-60262FF | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
543 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 17 | RTN OUT-0 | P2-TBRL2-17 | C2S7-17/P2-TBRL2-17 | P2-TBRL2-17/C2S7-17 | JB-607 | Spare_DO_17 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
544 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 18 | DC-0(+) | +24VDC | +24VDC | +24VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
545 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 19 | OUT-16 | P2-TBRL2-17 | C2S7-19/P2-TBRL2-17 | P2-TBRL2-17/C2S7-19 | JB-607 | XV-60262FG_DO_1 | XV-60262FG | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
546 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 20 | OUT-17 | P2-TBRL2-18 | C2S7-20/P2-TBRL2-18 | P2-TBRL2-18/C2S7-20 | JB-607 | XV-60262FH_DO_1 | XV-60262FH | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
547 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 21 | OUT-18 | P2-TBRL2-19 | C2S7-21/P2-TBRL2-19 | P2-TBRL2-19/C2S7-21 | JB-607 | XV-60262SE_DO_1 | XV-60262SE | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
548 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 22 | OUT-19 | P2-TBRL2-20 | C2S7-22/P2-TBRL2-20 | P2-TBRL2-20/C2S7-22 | JB-607 | XV-60262SF_DO_1 | XV-60262SF | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
549 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 23 | OUT-20 | P2-TBRL2-21 | C2S7-23/P2-TBRL2-21 | P2-TBRL2-21/C2S7-23 | JB-607 | XV-60262SG_DO_1 | XV-60262SG | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
550 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 24 | OUT-21 | P2-TBRL2-22 | C2S7-24/P2-TBRL2-22 | P2-TBRL2-22/C2S7-24 | JB-607 | XV-60262SH_DO_1 | XV-60262SH | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
551 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 25 | OUT-22 | P2-TBRL2-23 | C2S7-25/P2-TBRL2-23 | P2-TBRL2-23/C2S7-25 | JB-607 | XV-60263_DO_1 | XV-60263 | Control Valve Position Feedback | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
552 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 26 | OUT-23 | P2-TBRL2-24 | C2S7-26/P2-TBRL2-24 | P2-TBRL2-24/C2S7-26 | JB-607 | XV-60263FJ_DO_1 | XV-60263FJ | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
553 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 27 | OUT-24 | P2-TBRL2-25 | C2S7-27/P2-TBRL2-25 | P2-TBRL2-25/C2S7-27 | JB-607 | XV-60263FK_DO_1 | XV-60263FK | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
554 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 28 | OUT-25 | P2-TBRL2-26 | C2S7-28/P2-TBRL2-26 | P2-TBRL2-26/C2S7-28 | JB-607 | XV-60263FL_DO_1 | XV-60263FL | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
555 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 29 | OUT-26 | P2-TBRL2-27 | C2S7-29/P2-TBRL2-27 | P2-TBRL2-27/C2S7-29 | JB-607 | XV-60263FM_DO_1 | XV-60263FM | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
556 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 30 | OUT-27 | P2-TBRL2-28 | C2S7-30/P2-TBRL2-28 | P2-TBRL2-28/C2S7-30 | JB-607 | XV-60263SJ_DO_1 | XV-60263SJ | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
557 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 31 | OUT-28 | P2-TBRL2-29 | C2S7-31/P2-TBRL2-29 | P2-TBRL2-29/C2S7-31 | JB-607 | XV-60263SK_DO_1 | XV-60263SK | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
558 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 32 | OUT-29 | P2-TBRL2-30 | C2S7-32/P2-TBRL2-30 | P2-TBRL2-30/C2S7-32 | JB-607 | XV-60263SL_DO_1 | XV-60263SL | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
559 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 33 | OUT-30 | P2-TBRL2-31 | C2S7-33/P2-TBRL2-31 | P2-TBRL2-31/C2S7-33 | JB-607 | XV-60263SM_DO_1 | XV-60263SM | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
560 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 34 | OUT-31 | P2-TBRL2-32 | C2S7-34/P2-TBRL2-32 | P2-TBRL2-32/C2S7-34 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
561 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 35 | RTN OUT-1 | P2-TBRL2-35 | C2S7-35/P2-TBRL2-35 | P2-TBRL2-35/C2S7-35 | JB-607 | Spare_DO_35 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
562 | C2 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 36 | DC-1(+) | +24VDC | +24VDC | +24VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
563 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 1 | OUT-0 | P2-TBRL3-1 | C2S8-1/P2-TBRL3-1 | P2-TBRL3-1/C2S8-1 | JB-607 | XV-60264_DO_1 | XV-60264 | Control Valve Position Feedback | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
564 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 2 | OUT-1 | P2-TBRL3-2 | C2S8-2/P2-TBRL3-2 | P2-TBRL3-2/C2S8-2 | JB-607 | XV-60264FN_DO_1 | XV-60264FN | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
565 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 3 | OUT-2 | P2-TBRL3-3 | C2S8-3/P2-TBRL3-3 | P2-TBRL3-3/C2S8-3 | JB-607 | XV-60264FP_DO_1 | XV-60264FP | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
566 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 4 | OUT-3 | P2-TBRL3-4 | C2S8-4/P2-TBRL3-4 | P2-TBRL3-4/C2S8-4 | JB-607 | XV-60264FQ_DO_1 | XV-60264FQ | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
567 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 5 | OUT-4 | P2-TBRL3-5 | C2S8-5/P2-TBRL3-5 | P2-TBRL3-5/C2S8-5 | JB-607 | XV-60264FR_DO_1 | XV-60264FR | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
568 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 6 | OUT-5 | P2-TBRL3-6 | C2S8-6/P2-TBRL3-6 | P2-TBRL3-6/C2S8-6 | JB-607 | XV-60264SN_DO_1 | XV-60264SN | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
569 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 7 | OUT-6 | P2-TBRL3-7 | C2S8-7/P2-TBRL3-7 | P2-TBRL3-7/C2S8-7 | JB-607 | XV-60264SP_DO_1 | XV-60264SP | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
570 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 8 | OUT-7 | P2-TBRL3-8 | C2S8-8/P2-TBRL3-8 | P2-TBRL3-8/C2S8-8 | JB-607 | XV-60264SQ_DO_1 | XV-60264SQ | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
571 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 9 | OUT-8 | P2-TBRL3-9 | C2S8-9/P2-TBRL3-9 | P2-TBRL3-9/C2S8-9 | JB-607 | XV-60264SR_DO_1 | XV-60264SR | Control Valve Position Feedback | On/Off Valve | 325-01-602-PD-02 | 24 VDC energized,Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
572 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 10 | OUT-9 | P2-TBRL3-10 | C2S8-10/P2-TBRL3-10 | P2-TBRL3-10/C2S8-10 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
573 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 11 | OUT-10 | P2-TBRL3-11 | C2S8-11/P2-TBRL3-11 | P2-TBRL3-11/C2S8-11 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
574 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 12 | OUT-11 | P2-TBRL3-12 | C2S8-12/P2-TBRL3-12 | P2-TBRL3-12/C2S8-12 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
575 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 13 | OUT-12 | P2-TBRL3-13 | C2S8-13/P2-TBRL3-13 | P2-TBRL3-13/C2S8-13 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
576 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 14 | OUT-13 | P2-TBRL3-14 | C2S8-14/P2-TBRL3-14 | P2-TBRL3-14/C2S8-14 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
577 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 15 | OUT-14 | P2-TBRL3-15 | C2S8-15/P2-TBRL3-15 | P2-TBRL3-15/C2S8-15 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
578 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 16 | OUT-15 | P2-TBRL3-16 | C2S8-16/P2-TBRL3-16 | P2-TBRL3-16/C2S8-16 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
579 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 17 | RTN OUT-0 | P2-TBRL3-17 | C2S8-17/P2-TBRL3-17 | P2-TBRL3-17/C2S8-17 | JB-607 | Spare_DO_17 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
580 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 18 | DC-0(+) | +24VDC | +24VDC | +24VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
581 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 19 | OUT-16 | P2-TBRL3-17 | C2S8-19/P2-TBRL3-17 | P2-TBRL3-17/C2S8-19 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
582 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 20 | OUT-17 | P2-TBRL3-18 | C2S8-20/P2-TBRL3-18 | P2-TBRL3-18/C2S8-20 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
583 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 21 | OUT-18 | P2-TBRL3-19 | C2S8-21/P2-TBRL3-19 | P2-TBRL3-19/C2S8-21 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
584 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 22 | OUT-19 | P2-TBRL3-20 | C2S8-22/P2-TBRL3-20 | P2-TBRL3-20/C2S8-22 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
585 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 23 | OUT-20 | P2-TBRL3-21 | C2S8-23/P2-TBRL3-21 | P2-TBRL3-21/C2S8-23 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
586 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 24 | OUT-21 | P2-TBRL3-22 | C2S8-24/P2-TBRL3-22 | P2-TBRL3-22/C2S8-24 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
587 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 25 | OUT-22 | P2-TBRL3-23 | C2S8-25/P2-TBRL3-23 | P2-TBRL3-23/C2S8-25 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
588 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 26 | OUT-23 | P2-TBRL3-24 | C2S8-26/P2-TBRL3-24 | P2-TBRL3-24/C2S8-26 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
589 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 27 | OUT-24 | P2-TBRL3-25 | C2S8-27/P2-TBRL3-25 | P2-TBRL3-25/C2S8-27 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
590 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 28 | OUT-25 | P2-TBRL3-26 | C2S8-28/P2-TBRL3-26 | P2-TBRL3-26/C2S8-28 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
591 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 29 | OUT-26 | P2-TBRL3-27 | C2S8-29/P2-TBRL3-27 | P2-TBRL3-27/C2S8-29 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
592 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 30 | OUT-27 | P2-TBRL3-28 | C2S8-30/P2-TBRL3-28 | P2-TBRL3-28/C2S8-30 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
593 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 31 | OUT-28 | P2-TBRL3-29 | C2S8-31/P2-TBRL3-29 | P2-TBRL3-29/C2S8-31 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
594 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 32 | OUT-29 | P2-TBRL3-30 | C2S8-32/P2-TBRL3-30 | P2-TBRL3-30/C2S8-32 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
595 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 33 | OUT-30 | P2-TBRL3-31 | C2S8-33/P2-TBRL3-31 | P2-TBRL3-31/C2S8-33 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
596 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 34 | OUT-31 | P2-TBRL3-32 | C2S8-34/P2-TBRL3-32 | P2-TBRL3-32/C2S8-34 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
597 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 35 | RTN OUT-1 | P2-TBRL3-35 | C2S8-35/P2-TBRL3-35 | P2-TBRL3-35/C2S8-35 | JB-607 | Spare_DO_35 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
598 | C2 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 36 | DC-1(+) | +24VDC | +24VDC | +24VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
599 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1 | i RTN-0 | P2-TBAI1-1(B) | C2S9-1/P2-TBAI1-1(B) | P2-TBAI1-1(B)/C2S9-1 | JB-402 | FT-40221_AI_1 | FT-40221 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-6 m³/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
600 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 2 | IN-0 | P2-TBAI1-1(A) | C2S9-2/P2-TBAI1-1(A) | P2-TBAI1-1(A)/C2S9-2 | JB-402 | FT-40221_AI_1 | FT-40221 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-6 m³/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
601 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 3 | i RTN-1 | P2-TBAI1-2(B) | C2S9-3/P2-TBAI1-2(B) | P2-TBAI1-2(B)/C2S9-3 | JB-402 | FT-40221_AI_2 | FT-40221 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-6 m³/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
602 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 4 | IN-1 | P2-TBAI1-2(A) | C2S9-4/P2-TBAI1-2(A) | P2-TBAI1-2(A)/C2S9-4 | JB-402 | FT-40221_AI_2 | FT-40221 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-6 m³/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
603 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 5 | i RTN-2 | P2-TBAI1-3(B) | C2S9-5/P2-TBAI1-3(B) | P2-TBAI1-3(B)/C2S9-5 | JB-402 | FT-40222_AI_1 | FT-40222 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-850 kg/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
604 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 6 | IN-2 | P2-TBAI1-3(A) | C2S9-6/P2-TBAI1-3(A) | P2-TBAI1-3(A)/C2S9-6 | JB-402 | FT-40222_AI_1 | FT-40222 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-850 kg/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
605 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 7 | i RTN-3 | P2-TBAI1-4(B) | C2S9-7/P2-TBAI1-4(B) | P2-TBAI1-4(B)/C2S9-7 | JB-402 | FT-40222_AI_2 | FT-40222 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-850 kg/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
606 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 8 | IN-3 | P2-TBAI1-4(A) | C2S9-8/P2-TBAI1-4(A) | P2-TBAI1-4(A)/C2S9-8 | JB-402 | FT-40222_AI_2 | FT-40222 | Coriolis Flow Transmitter | Coriolis Flow Transmitter | 325-01-402-PD-02 | 4 - 20 mA,Pulse | 0-850 kg/hr | Endress+Hauser | Promass F 300 / 83F (Coriolis Mass Flow) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
607 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 9 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
608 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 10 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
609 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 11 | i RTN-4 | P2-TBAI1-5(B) | C2S9-11/P2-TBAI1-5(B) | P2-TBAI1-5(B)/C2S9-11 | JB-402 | PT-40222_AI_1 | PT-40222 | Pressure Transmitter | Pressure Transmitter | 325-01-402-PD-02 | 4 - 20 mA | 0 - 12'barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
610 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 12 | IN-4 | P2-TBAI1-5(A) | C2S9-12/P2-TBAI1-5(A) | P2-TBAI1-5(A)/C2S9-12 | JB-402 | PT-40222_AI_1 | PT-40222 | Pressure Transmitter | Pressure Transmitter | 325-01-402-PD-02 | 4 - 20 mA | 0 - 12'barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
611 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 13 | i RTN-5 | P2-TBAI1-6(B) | C2S9-13/P2-TBAI1-6(B) | P2-TBAI1-6(B)/C2S9-13 | JB-402 | TT-40221_AI_1 | TT-40221 | Temperature Transmitter | Temperature Transmitter | 325-01-402-PD-02 | 4 - 20 mA | 0 - 120 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
612 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 14 | IN-5 | P2-TBAI1-6(A) | C2S9-14/P2-TBAI1-6(A) | P2-TBAI1-6(A)/C2S9-14 | JB-402 | TT-40221_AI_1 | TT-40221 | Temperature Transmitter | Temperature Transmitter | 325-01-402-PD-02 | 4 - 20 mA | 0 - 120 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
613 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 15 | i RTN-6 | P2-TBAI1-7(B) | C2S9-15/P2-TBAI1-7(B) | P2-TBAI1-7(B)/C2S9-15 | JB-402 | TT-40222_AI_1 | TT-40222 | Temperature Transmitter | Temperature Transmitter | 325-01-402-PD-02 | 4 - 20 mA | 0 - 200 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
614 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IN-6 | P2-TBAI1-7(A) | C2S9-16/P2-TBAI1-7(A) | P2-TBAI1-7(A)/C2S9-16 | JB-402 | TT-40222_AI_1 | TT-40222 | Temperature Transmitter | Temperature Transmitter | 325-01-402-PD-02 | 4 - 20 mA | 0 - 200 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Jet Cooker
615 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 17 | i RTN-7 | P2-TBAI1-8(B) | C2S9-17/P2-TBAI1-8(B) | P2-TBAI1-8(B)/C2S9-17 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
616 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 18 | IN-7 | P2-TBAI1-8(A) | C2S9-18/P2-TBAI1-8(A) | P2-TBAI1-8(A)/C2S9-18 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
617 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 19 | i RTN-8 | P2-TBAI1-9(B) | C2S9-19/P2-TBAI1-9(B) | P2-TBAI1-9(B)/C2S9-19 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
618 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 20 | IN-8 | P2-TBAI1-9(A) | C2S9-20/P2-TBAI1-9(A) | P2-TBAI1-9(A)/C2S9-20 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
619 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 21 | i RTN-9 | P2-TBAI1-10(B) | C2S9-21/P2-TBAI1-10(B) | P2-TBAI1-10(B)/C2S9-21 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
620 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 22 | IN-9 | P2-TBAI1-10(A) | C2S9-22/P2-TBAI1-10(A) | P2-TBAI1-10(A)/C2S9-22 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
621 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 23 | i RTN-10 | P2-TBAI1-11(B) | C2S9-23/P2-TBAI1-11(B) | P2-TBAI1-11(B)/C2S9-23 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
622 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 24 | IN-10 | P2-TBAI1-11(A) | C2S9-24/P2-TBAI1-11(A) | P2-TBAI1-11(A)/C2S9-24 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
623 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 25 | i RTN-11 | P2-TBAI1-12(B) | C2S9-25/P2-TBAI1-12(B) | P2-TBAI1-12(B)/C2S9-25 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
624 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 26 | IN-11 | P2-TBAI1-12(A) | C2S9-26/P2-TBAI1-12(A) | P2-TBAI1-12(A)/C2S9-26 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
625 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 27 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
626 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 28 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
627 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 29 | i RTN-12 | P2-TBAI1-13(B) | C2S9-29/P2-TBAI1-13(B) | P2-TBAI1-13(B)/C2S9-29 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
628 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 30 | IN-12 | P2-TBAI1-13(A) | C2S9-30/P2-TBAI1-13(A) | P2-TBAI1-13(A)/C2S9-30 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
629 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 31 | i RTN-13 | P2-TBAI1-14(B) | C2S9-31/P2-TBAI1-14(B) | P2-TBAI1-14(B)/C2S9-31 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
630 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 32 | IN-13 | P2-TBAI1-14(A) | C2S9-32/P2-TBAI1-14(A) | P2-TBAI1-14(A)/C2S9-32 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
631 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 33 | i RTN-14 | P2-TBAI1-15(B) | C2S9-33/P2-TBAI1-15(B) | P2-TBAI1-15(B)/C2S9-33 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
632 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 34 | IN-14 | P2-TBAI1-15(A) | C2S9-34/P2-TBAI1-15(A) | P2-TBAI1-15(A)/C2S9-34 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
633 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 35 | i RTN-15 | P2-TBAI1-16(B) | C2S9-35/P2-TBAI1-16(B) | P2-TBAI1-16(B)/C2S9-35 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
634 | C2 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 36 | IN-15 | P2-TBAI1-16(A) | C2S9-36/P2-TBAI1-16(A) | P2-TBAI1-16(A)/C2S9-36 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
635 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1 | i RTN-0 | P2-TBAI2-1(B) | C2S10-1/P2-TBAI2-1(B) | P2-TBAI2-1(B)/C2S10-1 | JB-602 | AT-60241_AI_1 | AT-60241 | Dust Analyzer Transmitter | Dust Analyzer Transmitter | 325-01-602-PD-05 | 4 - 20 mA | 5000 mg | ENVEA / PCME | PCME QAL 991 (Dust Analyzer) | LiY-CY TP 2Px1.0 (Signal) + CVV 3Cx1.5 (24VDC Power) | ACTIVE | -
636 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 2 | IN-0 | P2-TBAI2-1(A) | C2S10-2/P2-TBAI2-1(A) | P2-TBAI2-1(A)/C2S10-2 | JB-602 | AT-60241_AI_1 | AT-60241 | Dust Analyzer Transmitter | Dust Analyzer Transmitter | 325-01-602-PD-05 | 4 - 20 mA | 5000 mg | ENVEA / PCME | PCME QAL 991 (Dust Analyzer) | LiY-CY TP 2Px1.0 (Signal) + CVV 3Cx1.5 (24VDC Power) | ACTIVE | -
637 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 3 | i RTN-1 | P2-TBAI2-2(B) | C2S10-3/P2-TBAI2-2(B) | P2-TBAI2-2(B)/C2S10-3 | JB-602 | DPT-60203_AI_1 | DPT-60203 | Differential Pressure Transmitte | Differential Pressure Transmitter | 325-01-602-PD-03 | 4 - 20 mA | -100 to 500 mBar | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
638 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 4 | IN-1 | P2-TBAI2-2(A) | C2S10-4/P2-TBAI2-2(A) | P2-TBAI2-2(A)/C2S10-4 | JB-602 | DPT-60203_AI_1 | DPT-60203 | Differential Pressure Transmitte | Differential Pressure Transmitter | 325-01-602-PD-03 | 4 - 20 mA | -100 to 500 mBar | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
639 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 5 | i RTN-2 | P2-TBAI2-3(B) | C2S10-5/P2-TBAI2-3(B) | P2-TBAI2-3(B)/C2S10-5 | JB-602 | FT-60202_AI_1 | FT-60202 | Flow Transmitter | Vortex Flow Transmitter | 325-01-602-PD-09 | 4 - 20 mA | 0 - 2000 kg/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
640 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 6 | IN-2 | P2-TBAI2-3(A) | C2S10-6/P2-TBAI2-3(A) | P2-TBAI2-3(A)/C2S10-6 | JB-602 | FT-60202_AI_1 | FT-60202 | Flow Transmitter | Vortex Flow Transmitter | 325-01-602-PD-09 | 4 - 20 mA | 0 - 2000 kg/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
641 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 7 | i RTN-3 | P2-TBAI2-4(B) | C2S10-7/P2-TBAI2-4(B) | P2-TBAI2-4(B)/C2S10-7 | JB-602 | PT-60210_AI_1 | PT-60210 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 0.1 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
642 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 8 | IN-3 | P2-TBAI2-4(A) | C2S10-8/P2-TBAI2-4(A) | P2-TBAI2-4(A)/C2S10-8 | JB-602 | PT-60210_AI_1 | PT-60210 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 0.1 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
643 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 9 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
644 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 10 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
645 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 11 | i RTN-4 | P2-TBAI2-5(B) | C2S10-11/P2-TBAI2-5(B) | P2-TBAI2-5(B)/C2S10-11 | JB-602 | PT-60215_AI_1 | PT-60215 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 6 bar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
646 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 12 | IN-4 | P2-TBAI2-5(A) | C2S10-12/P2-TBAI2-5(A) | P2-TBAI2-5(A)/C2S10-12 | JB-602 | PT-60215_AI_1 | PT-60215 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 6 bar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
647 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 13 | i RTN-5 | P2-TBAI2-6(B) | C2S10-13/P2-TBAI2-6(B) | P2-TBAI2-6(B)/C2S10-13 | JB-602 | PT-60216_AI_1 | PT-60216 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 100 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
648 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 14 | IN-5 | P2-TBAI2-6(A) | C2S10-14/P2-TBAI2-6(A) | P2-TBAI2-6(A)/C2S10-14 | JB-602 | PT-60216_AI_1 | PT-60216 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 100 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
649 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 15 | i RTN-6 | P2-TBAI2-7(B) | C2S10-15/P2-TBAI2-7(B) | P2-TBAI2-7(B)/C2S10-15 | JB-602 | PT-60240_AI_1 | PT-60240 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-05 | 4 - 20 mA | -100 to 200 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
650 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IN-6 | P2-TBAI2-7(A) | C2S10-16/P2-TBAI2-7(A) | P2-TBAI2-7(A)/C2S10-16 | JB-602 | PT-60240_AI_1 | PT-60240 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-05 | 4 - 20 mA | -100 to 200 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
651 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 17 | i RTN-7 | P2-TBAI2-8(B) | C2S10-17/P2-TBAI2-8(B) | P2-TBAI2-8(B)/C2S10-17 | JB-602 | PT-60241_AI_1 | PT-60241 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-05 | 4 - 20 mA | 0 - 0.1 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
652 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 18 | IN-7 | P2-TBAI2-8(A) | C2S10-18/P2-TBAI2-8(A) | P2-TBAI2-8(A)/C2S10-18 | JB-602 | PT-60241_AI_1 | PT-60241 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-05 | 4 - 20 mA | 0 - 0.1 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
653 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 19 | i RTN-8 | P2-TBAI2-9(B) | C2S10-19/P2-TBAI2-9(B) | P2-TBAI2-9(B)/C2S10-19 | JB-602 | TT-60210_AI_1 | TT-60210 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
654 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 20 | IN-8 | P2-TBAI2-9(A) | C2S10-20/P2-TBAI2-9(A) | P2-TBAI2-9(A)/C2S10-20 | JB-602 | TT-60210_AI_1 | TT-60210 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
655 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 21 | i RTN-9 | P2-TBAI2-10(B) | C2S10-21/P2-TBAI2-10(B) | P2-TBAI2-10(B)/C2S10-21 | JB-602 | TT-60210A_AI_1 | TT-60210A | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 100 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
656 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 22 | IN-9 | P2-TBAI2-10(A) | C2S10-22/P2-TBAI2-10(A) | P2-TBAI2-10(A)/C2S10-22 | JB-602 | TT-60210A_AI_1 | TT-60210A | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 100 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
657 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 23 | i RTN-10 | P2-TBAI2-11(B) | C2S10-23/P2-TBAI2-11(B) | P2-TBAI2-11(B)/C2S10-23 | JB-602 | TT-60210B_AI_1 | TT-60210B | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 100 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
658 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 24 | IN-10 | P2-TBAI2-11(A) | C2S10-24/P2-TBAI2-11(A) | P2-TBAI2-11(A)/C2S10-24 | JB-602 | TT-60210B_AI_1 | TT-60210B | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 100 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
659 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 25 | i RTN-11 | P2-TBAI2-12(B) | C2S10-25/P2-TBAI2-12(B) | P2-TBAI2-12(B)/C2S10-25 | JB-602 | TT-60211_AI_1 | TT-60211 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
660 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 26 | IN-11 | P2-TBAI2-12(A) | C2S10-26/P2-TBAI2-12(A) | P2-TBAI2-12(A)/C2S10-26 | JB-602 | TT-60211_AI_1 | TT-60211 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
661 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 27 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
662 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 28 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
663 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 29 | i RTN-12 | P2-TBAI2-13(B) | C2S10-29/P2-TBAI2-13(B) | P2-TBAI2-13(B)/C2S10-29 | JB-602 | TT-60212A_AI_1 | TT-60212A | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 100 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
664 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 30 | IN-12 | P2-TBAI2-13(A) | C2S10-30/P2-TBAI2-13(A) | P2-TBAI2-13(A)/C2S10-30 | JB-602 | TT-60212A_AI_1 | TT-60212A | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 100 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
665 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 31 | i RTN-13 | P2-TBAI2-14(B) | C2S10-31/P2-TBAI2-14(B) | P2-TBAI2-14(B)/C2S10-31 | JB-602 | TT-60212B_AI_1 | TT-60212B | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 100 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
666 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 32 | IN-13 | P2-TBAI2-14(A) | C2S10-32/P2-TBAI2-14(A) | P2-TBAI2-14(A)/C2S10-32 | JB-602 | TT-60212B_AI_1 | TT-60212B | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 100 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
667 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 33 | i RTN-14 | P2-TBAI2-15(B) | C2S10-33/P2-TBAI2-15(B) | P2-TBAI2-15(B)/C2S10-33 | JB-602 | TT-60214_AI_1 | TT-60214 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | -10 to 250°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
668 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 34 | IN-14 | P2-TBAI2-15(A) | C2S10-34/P2-TBAI2-15(A) | P2-TBAI2-15(A)/C2S10-34 | JB-602 | TT-60214_AI_1 | TT-60214 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | -10 to 250°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
669 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 35 | i RTN-15 | P2-TBAI2-16(B) | C2S10-35/P2-TBAI2-16(B) | P2-TBAI2-16(B)/C2S10-35 | JB-602 | TT-60215A_AI_1 | TT-60215A | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | -10 to 150°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
670 | C2 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 36 | IN-15 | P2-TBAI2-16(A) | C2S10-36/P2-TBAI2-16(A) | P2-TBAI2-16(A)/C2S10-36 | JB-602 | TT-60215A_AI_1 | TT-60215A | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | -10 to 150°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
671 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1 | i RTN-0 | P2-TBAI3-1(B) | C2S11-1/P2-TBAI3-1(B) | P2-TBAI3-1(B)/C2S11-1 | CA1 | Spare_AI_1 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
672 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 2 | IN-0 | P2-TBAI3-1(A) | C2S11-2/P2-TBAI3-1(A) | P2-TBAI3-1(A)/C2S11-2 | CA1 | Spare_AI_1 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
673 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 3 | i RTN-1 | P2-TBAI3-2(B) | C2S11-3/P2-TBAI3-2(B) | P2-TBAI3-2(B)/C2S11-3 | CA1 | Spare_AI_2 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
674 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 4 | IN-1 | P2-TBAI3-2(A) | C2S11-4/P2-TBAI3-2(A) | P2-TBAI3-2(A)/C2S11-4 | CA1 | Spare_AI_2 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
675 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 5 | i RTN-2 | P2-TBAI3-3(B) | C2S11-5/P2-TBAI3-3(B) | P2-TBAI3-3(B)/C2S11-5 | CA1 | Spare_AI_3 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
676 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 6 | IN-2 | P2-TBAI3-3(A) | C2S11-6/P2-TBAI3-3(A) | P2-TBAI3-3(A)/C2S11-6 | CA1 | Spare_AI_3 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
677 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 7 | i RTN-3 | P2-TBAI3-4(B) | C2S11-7/P2-TBAI3-4(B) | P2-TBAI3-4(B)/C2S11-7 | CA1 | Spare_AI_4 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
678 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 8 | IN-3 | P2-TBAI3-4(A) | C2S11-8/P2-TBAI3-4(A) | P2-TBAI3-4(A)/C2S11-8 | CA1 | Spare_AI_4 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
679 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 9 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
680 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 10 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
681 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 11 | i RTN-4 | P2-TBAI3-5(B) | C2S11-11/P2-TBAI3-5(B) | P2-TBAI3-5(B)/C2S11-11 | CA1 | Spare_AI_5 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
682 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 12 | IN-4 | P2-TBAI3-5(A) | C2S11-12/P2-TBAI3-5(A) | P2-TBAI3-5(A)/C2S11-12 | CA1 | Spare_AI_5 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
683 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 13 | i RTN-5 | P2-TBAI3-6(B) | C2S11-13/P2-TBAI3-6(B) | P2-TBAI3-6(B)/C2S11-13 | CA1 | Spare_AI_6 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
684 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 14 | IN-5 | P2-TBAI3-6(A) | C2S11-14/P2-TBAI3-6(A) | P2-TBAI3-6(A)/C2S11-14 | CA1 | Spare_AI_6 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
685 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 15 | i RTN-6 | P2-TBAI3-7(B) | C2S11-15/P2-TBAI3-7(B) | P2-TBAI3-7(B)/C2S11-15 | CA1 | Spare_AI_7 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
686 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IN-6 | P2-TBAI3-7(A) | C2S11-16/P2-TBAI3-7(A) | P2-TBAI3-7(A)/C2S11-16 | CA1 | Spare_AI_7 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
687 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 17 | i RTN-7 | P2-TBAI3-8(B) | C2S11-17/P2-TBAI3-8(B) | P2-TBAI3-8(B)/C2S11-17 | CA1 | Spare_AI_8 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
688 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 18 | IN-7 | P2-TBAI3-8(A) | C2S11-18/P2-TBAI3-8(A) | P2-TBAI3-8(A)/C2S11-18 | CA1 | Spare_AI_8 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
689 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 19 | i RTN-8 | P2-TBAI3-9(B) | C2S11-19/P2-TBAI3-9(B) | P2-TBAI3-9(B)/C2S11-19 | CA1 | Spare_AI_9 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
690 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 20 | IN-8 | P2-TBAI3-9(A) | C2S11-20/P2-TBAI3-9(A) | P2-TBAI3-9(A)/C2S11-20 | CA1 | Spare_AI_9 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
691 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 21 | i RTN-9 | P2-TBAI3-10(B) | C2S11-21/P2-TBAI3-10(B) | P2-TBAI3-10(B)/C2S11-21 | CA1 | Spare_AI_10 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
692 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 22 | IN-9 | P2-TBAI3-10(A) | C2S11-22/P2-TBAI3-10(A) | P2-TBAI3-10(A)/C2S11-22 | CA1 | Spare_AI_10 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
693 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 23 | i RTN-10 | P2-TBAI3-11(B) | C2S11-23/P2-TBAI3-11(B) | P2-TBAI3-11(B)/C2S11-23 | CA1 | Spare_AI_11 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
694 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 24 | IN-10 | P2-TBAI3-11(A) | C2S11-24/P2-TBAI3-11(A) | P2-TBAI3-11(A)/C2S11-24 | CA1 | Spare_AI_11 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
695 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 25 | i RTN-11 | P2-TBAI3-12(B) | C2S11-25/P2-TBAI3-12(B) | P2-TBAI3-12(B)/C2S11-25 | CA1 | Spare_AI_12 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
696 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 26 | IN-11 | P2-TBAI3-12(A) | C2S11-26/P2-TBAI3-12(A) | P2-TBAI3-12(A)/C2S11-26 | CA1 | Spare_AI_12 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
697 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 27 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
698 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 28 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
699 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 29 | i RTN-12 | P2-TBAI3-13(B) | C2S11-29/P2-TBAI3-13(B) | P2-TBAI3-13(B)/C2S11-29 | CA1 | Spare_AI_13 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
700 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 30 | IN-12 | P2-TBAI3-13(A) | C2S11-30/P2-TBAI3-13(A) | P2-TBAI3-13(A)/C2S11-30 | CA1 | Spare_AI_13 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
701 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 31 | i RTN-13 | P2-TBAI3-14(B) | C2S11-31/P2-TBAI3-14(B) | P2-TBAI3-14(B)/C2S11-31 | CA1 | Spare_AI_14 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
702 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 32 | IN-13 | P2-TBAI3-14(A) | C2S11-32/P2-TBAI3-14(A) | P2-TBAI3-14(A)/C2S11-32 | CA1 | Spare_AI_14 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
703 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 33 | i RTN-14 | P2-TBAI3-15(B) | C2S11-33/P2-TBAI3-15(B) | P2-TBAI3-15(B)/C2S11-33 | CA1 | Spare_AI_15 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
704 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 34 | IN-14 | P2-TBAI3-15(A) | C2S11-34/P2-TBAI3-15(A) | P2-TBAI3-15(A)/C2S11-34 | CA1 | Spare_AI_15 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
705 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 35 | i RTN-15 | P2-TBAI3-16(B) | C2S11-35/P2-TBAI3-16(B) | P2-TBAI3-16(B)/C2S11-35 | CA1 | Spare_AI_16 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
706 | C2 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 36 | IN-15 | P2-TBAI3-16(A) | C2S11-36/P2-TBAI3-16(A) | P2-TBAI3-16(A)/C2S11-36 | CA1 | Spare_AI_16 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
707 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1 | i RTN-0 | P2-TBAI4-1(B) | C2S12-1/P2-TBAI4-1(B) | P2-TBAI4-1(B)/C2S12-1 | CA1 | Spare_AI_1 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
708 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 2 | IN-0 | P2-TBAI4-1(A) | C2S12-2/P2-TBAI4-1(A) | P2-TBAI4-1(A)/C2S12-2 | CA1 | Spare_AI_1 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
709 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 3 | i RTN-1 | P2-TBAI4-2(B) | C2S12-3/P2-TBAI4-2(B) | P2-TBAI4-2(B)/C2S12-3 | CA1 | Spare_AI_2 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
710 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 4 | IN-1 | P2-TBAI4-2(A) | C2S12-4/P2-TBAI4-2(A) | P2-TBAI4-2(A)/C2S12-4 | CA1 | Spare_AI_2 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
711 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 5 | i RTN-2 | P2-TBAI4-3(B) | C2S12-5/P2-TBAI4-3(B) | P2-TBAI4-3(B)/C2S12-5 | CA1 | Spare_AI_3 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
712 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 6 | IN-2 | P2-TBAI4-3(A) | C2S12-6/P2-TBAI4-3(A) | P2-TBAI4-3(A)/C2S12-6 | CA1 | Spare_AI_3 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
713 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 7 | i RTN-3 | P2-TBAI4-4(B) | C2S12-7/P2-TBAI4-4(B) | P2-TBAI4-4(B)/C2S12-7 | CA1 | Spare_AI_4 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
714 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 8 | IN-3 | P2-TBAI4-4(A) | C2S12-8/P2-TBAI4-4(A) | P2-TBAI4-4(A)/C2S12-8 | CA1 | Spare_AI_4 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
715 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 9 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
716 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 10 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
717 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 11 | i RTN-4 | P2-TBAI4-5(B) | C2S12-11/P2-TBAI4-5(B) | P2-TBAI4-5(B)/C2S12-11 | CA1 | Spare_AI_5 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
718 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 12 | IN-4 | P2-TBAI4-5(A) | C2S12-12/P2-TBAI4-5(A) | P2-TBAI4-5(A)/C2S12-12 | CA1 | Spare_AI_5 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
719 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 13 | i RTN-5 | P2-TBAI4-6(B) | C2S12-13/P2-TBAI4-6(B) | P2-TBAI4-6(B)/C2S12-13 | CA1 | Spare_AI_6 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
720 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 14 | IN-5 | P2-TBAI4-6(A) | C2S12-14/P2-TBAI4-6(A) | P2-TBAI4-6(A)/C2S12-14 | CA1 | Spare_AI_6 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
721 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 15 | i RTN-6 | P2-TBAI4-7(B) | C2S12-15/P2-TBAI4-7(B) | P2-TBAI4-7(B)/C2S12-15 | CA1 | Spare_AI_7 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
722 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IN-6 | P2-TBAI4-7(A) | C2S12-16/P2-TBAI4-7(A) | P2-TBAI4-7(A)/C2S12-16 | CA1 | Spare_AI_7 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
723 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 17 | i RTN-7 | P2-TBAI4-8(B) | C2S12-17/P2-TBAI4-8(B) | P2-TBAI4-8(B)/C2S12-17 | CA1 | Spare_AI_8 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
724 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 18 | IN-7 | P2-TBAI4-8(A) | C2S12-18/P2-TBAI4-8(A) | P2-TBAI4-8(A)/C2S12-18 | CA1 | Spare_AI_8 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
725 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 19 | i RTN-8 | P2-TBAI4-9(B) | C2S12-19/P2-TBAI4-9(B) | P2-TBAI4-9(B)/C2S12-19 | CA1 | Spare_AI_9 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
726 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 20 | IN-8 | P2-TBAI4-9(A) | C2S12-20/P2-TBAI4-9(A) | P2-TBAI4-9(A)/C2S12-20 | CA1 | Spare_AI_9 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
727 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 21 | i RTN-9 | P2-TBAI4-10(B) | C2S12-21/P2-TBAI4-10(B) | P2-TBAI4-10(B)/C2S12-21 | CA1 | Spare_AI_10 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
728 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 22 | IN-9 | P2-TBAI4-10(A) | C2S12-22/P2-TBAI4-10(A) | P2-TBAI4-10(A)/C2S12-22 | CA1 | Spare_AI_10 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
729 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 23 | i RTN-10 | P2-TBAI4-11(B) | C2S12-23/P2-TBAI4-11(B) | P2-TBAI4-11(B)/C2S12-23 | CA1 | Spare_AI_11 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
730 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 24 | IN-10 | P2-TBAI4-11(A) | C2S12-24/P2-TBAI4-11(A) | P2-TBAI4-11(A)/C2S12-24 | CA1 | Spare_AI_11 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
731 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 25 | i RTN-11 | P2-TBAI4-12(B) | C2S12-25/P2-TBAI4-12(B) | P2-TBAI4-12(B)/C2S12-25 | CA1 | Spare_AI_12 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
732 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 26 | IN-11 | P2-TBAI4-12(A) | C2S12-26/P2-TBAI4-12(A) | P2-TBAI4-12(A)/C2S12-26 | CA1 | Spare_AI_12 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
733 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 27 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
734 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 28 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
735 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 29 | i RTN-12 | P2-TBAI4-13(B) | C2S12-29/P2-TBAI4-13(B) | P2-TBAI4-13(B)/C2S12-29 | CA1 | Spare_AI_13 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
736 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 30 | IN-12 | P2-TBAI4-13(A) | C2S12-30/P2-TBAI4-13(A) | P2-TBAI4-13(A)/C2S12-30 | CA1 | Spare_AI_13 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
737 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 31 | i RTN-13 | P2-TBAI4-14(B) | C2S12-31/P2-TBAI4-14(B) | P2-TBAI4-14(B)/C2S12-31 | CA1 | Spare_AI_14 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
738 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 32 | IN-13 | P2-TBAI4-14(A) | C2S12-32/P2-TBAI4-14(A) | P2-TBAI4-14(A)/C2S12-32 | CA1 | Spare_AI_14 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
739 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 33 | i RTN-14 | P2-TBAI4-15(B) | C2S12-33/P2-TBAI4-15(B) | P2-TBAI4-15(B)/C2S12-33 | CA1 | Spare_AI_15 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
740 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 34 | IN-14 | P2-TBAI4-15(A) | C2S12-34/P2-TBAI4-15(A) | P2-TBAI4-15(A)/C2S12-34 | CA1 | Spare_AI_15 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
741 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 35 | i RTN-15 | P2-TBAI4-16(B) | C2S12-35/P2-TBAI4-16(B) | P2-TBAI4-16(B)/C2S12-35 | CA1 | Spare_AI_16 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
742 | C2 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 36 | IN-15 | P2-TBAI4-16(A) | C2S12-36/P2-TBAI4-16(A) | P2-TBAI4-16(A)/C2S12-36 | CA1 | Spare_AI_16 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
743 | C3 | C3S0 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | ETH-DLR-P1 | C3S0-/- | -/C3S0- | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C3S0_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
744 | C3 | C3S0 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C3S0-P2/ETH | ETH/C3S0-P2 | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C3S0_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
745 | C3 | C3S0 | 1756-EN4TR | COMM (EtherNet/IP) | USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C3S0-USB/CONSOLE | CONSOLE/C3S0-USB | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C3S0_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
746 | C3 | C3S0 | 1756-EN4TR | COMM (EtherNet/IP) | DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C3S0-DISP/DIAG | DIAG/C3S0-DISP | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C3S0_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
747 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P3-TBDI1-1 | C3S1-1/P3-TBDI1-1 | P3-TBDI1-1/C3S1-1 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
748 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P3-TBDI1-2 | C3S1-2/P3-TBDI1-2 | P3-TBDI1-2/C3S1-2 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
749 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P3-TBDI1-3 | C3S1-3/P3-TBDI1-3 | P3-TBDI1-3/C3S1-3 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
750 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P3-TBDI1-4 | C3S1-4/P3-TBDI1-4 | P3-TBDI1-4/C3S1-4 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
751 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P3-TBDI1-5 | C3S1-5/P3-TBDI1-5 | P3-TBDI1-5/C3S1-5 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
752 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P3-TBDI1-6 | C3S1-6/P3-TBDI1-6 | P3-TBDI1-6/C3S1-6 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
753 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P3-TBDI1-7 | C3S1-7/P3-TBDI1-7 | P3-TBDI1-7/C3S1-7 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
754 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P3-TBDI1-8 | C3S1-8/P3-TBDI1-8 | P3-TBDI1-8/C3S1-8 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
755 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P3-TBDI1-9 | C3S1-9/P3-TBDI1-9 | P3-TBDI1-9/C3S1-9 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
756 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P3-TBDI1-10 | C3S1-10/P3-TBDI1-10 | P3-TBDI1-10/C3S1-10 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
757 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P3-TBDI1-11 | C3S1-11/P3-TBDI1-11 | P3-TBDI1-11/C3S1-11 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
758 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P3-TBDI1-12 | C3S1-12/P3-TBDI1-12 | P3-TBDI1-12/C3S1-12 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
759 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P3-TBDI1-13 | C3S1-13/P3-TBDI1-13 | P3-TBDI1-13/C3S1-13 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
760 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P3-TBDI1-14 | C3S1-14/P3-TBDI1-14 | P3-TBDI1-14/C3S1-14 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
761 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P3-TBDI1-15 | C3S1-15/P3-TBDI1-15 | P3-TBDI1-15/C3S1-15 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
762 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P3-TBDI1-16 | C3S1-16/P3-TBDI1-16 | P3-TBDI1-16/C3S1-16 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
763 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-606 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
764 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-606 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
765 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P3-TBDI1-17 | C3S1-19/P3-TBDI1-17 | P3-TBDI1-17/C3S1-19 | JB-606 | FT-60203_DI_1 | FT-60203 | Flow Transmitter | Vortex Flow Transmitter | 325-01-602-PD-09 | 4 - 20 mA | 0 - 7000 kg/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
766 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P3-TBDI1-18 | C3S1-20/P3-TBDI1-18 | P3-TBDI1-18/C3S1-20 | JB-606 | LSH-60250_DI_1 | LSH-60250 | Process Instrument | Level switch | 325-01-602-PD-05 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | -
767 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P3-TBDI1-19 | C3S1-21/P3-TBDI1-19 | P3-TBDI1-19/C3S1-21 | JB-606 | XA-60261_DI_1 | XA-60261 | Process Instrument | Fire Deluge Fault (No Protection) | 325-01-602-PD-04 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
768 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P3-TBDI1-20 | C3S1-22/P3-TBDI1-20 | P3-TBDI1-20/C3S1-22 | JB-606 | XA-60262_DI_1 | XA-60262 | Process Instrument | Fire Deluge Alarm (Deluge Activated) | 325-01-602-PD-04 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
769 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P3-TBDI1-21 | C3S1-23/P3-TBDI1-21 | P3-TBDI1-21/C3S1-23 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
770 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P3-TBDI1-22 | C3S1-24/P3-TBDI1-22 | P3-TBDI1-22/C3S1-24 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
771 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P3-TBDI1-23 | C3S1-25/P3-TBDI1-23 | P3-TBDI1-23/C3S1-25 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
772 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P3-TBDI1-24 | C3S1-26/P3-TBDI1-24 | P3-TBDI1-24/C3S1-26 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
773 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P3-TBDI1-25 | C3S1-27/P3-TBDI1-25 | P3-TBDI1-25/C3S1-27 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
774 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P3-TBDI1-26 | C3S1-28/P3-TBDI1-26 | P3-TBDI1-26/C3S1-28 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
775 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P3-TBDI1-27 | C3S1-29/P3-TBDI1-27 | P3-TBDI1-27/C3S1-29 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
776 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P3-TBDI1-28 | C3S1-30/P3-TBDI1-28 | P3-TBDI1-28/C3S1-30 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
777 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P3-TBDI1-29 | C3S1-31/P3-TBDI1-29 | P3-TBDI1-29/C3S1-31 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
778 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P3-TBDI1-30 | C3S1-32/P3-TBDI1-30 | P3-TBDI1-30/C3S1-32 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
779 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P3-TBDI1-31 | C3S1-33/P3-TBDI1-31 | P3-TBDI1-31/C3S1-33 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
780 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P3-TBDI1-32 | C3S1-34/P3-TBDI1-32 | P3-TBDI1-32/C3S1-34 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
781 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | JB-606 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
782 | C3 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | JB-606 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
783 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P3-TBDI2-1 | C3S2-1/P3-TBDI2-1 | P3-TBDI2-1/C3S2-1 | JB-612 | PSL-61305_DI_1 | PSL-61305 | Process Instrument | Pressure switch | 325-01-613-PD-03 | Dry Contact |  | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | -
784 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P3-TBDI2-2 | C3S2-2/P3-TBDI2-2 | P3-TBDI2-2/C3S2-2 | JB-612 | PSL-61306_DI_1 | PSL-61306 | Process Instrument | Pressure switch | 325-01-613-PD-05 | Dry Contact |  | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | -
785 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P3-TBDI2-3 | C3S2-3/P3-TBDI2-3 | P3-TBDI2-3/C3S2-3 | JB-612 | PVM-61301_DI_1 | PVM-61301 | Process Instrument |  | 325-01-613-PD-03 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
786 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P3-TBDI2-4 | C3S2-4/P3-TBDI2-4 | P3-TBDI2-4/C3S2-4 | JB-612 | PVM-61301_DI_2 | PVM-61301 | Process Instrument |  | 325-01-613-PD-03 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
787 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P3-TBDI2-5 | C3S2-5/P3-TBDI2-5 | P3-TBDI2-5/C3S2-5 | JB-612 | XA-61301A_DI_1 | XA-61301A | Process Instrument | Request filter plant | 325-01-613-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
788 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P3-TBDI2-6 | C3S2-6/P3-TBDI2-6 | P3-TBDI2-6/C3S2-6 | JB-612 | XA-61301B_DI_1 | XA-61301B | Process Instrument | Request material transport | 325-01-613-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
789 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P3-TBDI2-7 | C3S2-7/P3-TBDI2-7 | P3-TBDI2-7/C3S2-7 | JB-612 | XA-61301C_DI_1 | XA-61301C | Process Instrument | Request belt plant | 325-01-613-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
790 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P3-TBDI2-8 | C3S2-8/P3-TBDI2-8 | P3-TBDI2-8/C3S2-8 | JB-612 | XA-61301D_DI_1 | XA-61301D | Process Instrument | Machine in operation | 325-01-613-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
791 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P3-TBDI2-9 | C3S2-9/P3-TBDI2-9 | P3-TBDI2-9/C3S2-9 | JB-612 | XA-61301E_DI_1 | XA-61301E | Process Instrument | General Fault | 325-01-613-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
792 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P3-TBDI2-10 | C3S2-10/P3-TBDI2-10 | P3-TBDI2-10/C3S2-10 | JB-612 | XA-61301F_DI_1 | XA-61301F | Process Instrument | Machine is ready | 325-01-613-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
793 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P3-TBDI2-11 | C3S2-11/P3-TBDI2-11 | P3-TBDI2-11/C3S2-11 | JB-612 | XA-61301G_DI_1 | XA-61301G | Process Instrument | Emergency stop activated | 325-01-613-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
794 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P3-TBDI2-12 | C3S2-12/P3-TBDI2-12 | P3-TBDI2-12/C3S2-12 | JB-612 | XA-61301H_DI_1 | XA-61301H | Process Instrument | Silo minimum | 325-01-613-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
795 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P3-TBDI2-13 | C3S2-13/P3-TBDI2-13 | P3-TBDI2-13/C3S2-13 | JB-612 | XA-61301J_DI_1 | XA-61301J | Process Instrument | Silo maximum | 325-01-613-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
796 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P3-TBDI2-14 | C3S2-14/P3-TBDI2-14 | P3-TBDI2-14/C3S2-14 | JB-612 | XV-61302_DI_1 | XV-61302 | Control Valve Position Feedback | Automatic on/off valve | 325-01-613-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
797 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P3-TBDI2-15 | C3S2-15/P3-TBDI2-15 | P3-TBDI2-15/C3S2-15 | JB-612 | XV-61302_DI_2 | XV-61302 | Control Valve Position Feedback | Automatic on/off valve | 325-01-613-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
798 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P3-TBDI2-16 | C3S2-16/P3-TBDI2-16 | P3-TBDI2-16/C3S2-16 | JB-612 | XV-61303_DI_1 | XV-61303 | Control Valve Position Feedback | Automatic on/off valve | 325-01-613-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
799 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
800 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
801 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P3-TBDI2-17 | C3S2-19/P3-TBDI2-17 | P3-TBDI2-17/C3S2-19 | JB-612 | XV-61303_DI_2 | XV-61303 | Control Valve Position Feedback | Automatic on/off valve | 325-01-613-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
802 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P3-TBDI2-18 | C3S2-20/P3-TBDI2-18 | P3-TBDI2-18/C3S2-20 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
803 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P3-TBDI2-19 | C3S2-21/P3-TBDI2-19 | P3-TBDI2-19/C3S2-21 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
804 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P3-TBDI2-20 | C3S2-22/P3-TBDI2-20 | P3-TBDI2-20/C3S2-22 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
805 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P3-TBDI2-21 | C3S2-23/P3-TBDI2-21 | P3-TBDI2-21/C3S2-23 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
806 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P3-TBDI2-22 | C3S2-24/P3-TBDI2-22 | P3-TBDI2-22/C3S2-24 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
807 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P3-TBDI2-23 | C3S2-25/P3-TBDI2-23 | P3-TBDI2-23/C3S2-25 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
808 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P3-TBDI2-24 | C3S2-26/P3-TBDI2-24 | P3-TBDI2-24/C3S2-26 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
809 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P3-TBDI2-25 | C3S2-27/P3-TBDI2-25 | P3-TBDI2-25/C3S2-27 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
810 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P3-TBDI2-26 | C3S2-28/P3-TBDI2-26 | P3-TBDI2-26/C3S2-28 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
811 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P3-TBDI2-27 | C3S2-29/P3-TBDI2-27 | P3-TBDI2-27/C3S2-29 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
812 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P3-TBDI2-28 | C3S2-30/P3-TBDI2-28 | P3-TBDI2-28/C3S2-30 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
813 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P3-TBDI2-29 | C3S2-31/P3-TBDI2-29 | P3-TBDI2-29/C3S2-31 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
814 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P3-TBDI2-30 | C3S2-32/P3-TBDI2-30 | P3-TBDI2-30/C3S2-32 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
815 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P3-TBDI2-31 | C3S2-33/P3-TBDI2-31 | P3-TBDI2-31/C3S2-33 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
816 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P3-TBDI2-32 | C3S2-34/P3-TBDI2-32 | P3-TBDI2-32/C3S2-34 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
817 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
818 | C3 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
819 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P3-TBDI3-1 | C3S3-1/P3-TBDI3-1 | P3-TBDI3-1/C3S3-1 | JB-618 | DV-61301_DI_1 | DV-61301 | Process Instrument | Automatic on/off valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
820 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P3-TBDI3-2 | C3S3-2/P3-TBDI3-2 | P3-TBDI3-2/C3S3-2 | JB-618 | DV-61301_DI_2 | DV-61301 | Process Instrument | Automatic on/off valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
821 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P3-TBDI3-3 | C3S3-3/P3-TBDI3-3 | P3-TBDI3-3/C3S3-3 | JB-618 | DV-61302_DI_1 | DV-61302 | Process Instrument | Automatic on/off valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
822 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P3-TBDI3-4 | C3S3-4/P3-TBDI3-4 | P3-TBDI3-4/C3S3-4 | JB-618 | DV-61302_DI_2 | DV-61302 | Process Instrument | Automatic on/off valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
823 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P3-TBDI3-5 | C3S3-5/P3-TBDI3-5 | P3-TBDI3-5/C3S3-5 | JB-618 | LS-61303_DI_1 | LS-61303 | Process Instrument | Level switch | 325-01-613-PD-01 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Safety Barriers
824 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P3-TBDI3-6 | C3S3-6/P3-TBDI3-6 | P3-TBDI3-6/C3S3-6 | JB-618 | PSL-61301_DI_1 | PSL-61301 | Process Instrument | Pressure switch | 325-01-613-PD-01 | Dry Contact | 0.3-0.7barg | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | -
825 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P3-TBDI3-7 | C3S3-7/P3-TBDI3-7 | P3-TBDI3-7/C3S3-7 | JB-618 | PSL-61302_DI_1 | PSL-61302 | Process Instrument | Pressure switch | 325-01-613-PD-01 | Dry Contact | 40 mbarg | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | -
826 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P3-TBDI3-8 | C3S3-8/P3-TBDI3-8 | P3-TBDI3-8/C3S3-8 | JB-618 | PSL-61311_DI_1 | PSL-61311 | Process Instrument | Pressure switch | 325-01-613-PD-04 | Dry Contact |  | Endress+Hauser | Ceraphant PTC31B (Pressure Switch) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | -
827 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P3-TBDI3-9 | C3S3-9/P3-TBDI3-9 | P3-TBDI3-9/C3S3-9 | JB-618 | SV-61304_DI_1 | SV-61304 | Process Instrument | On/Off Valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
828 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P3-TBDI3-10 | C3S3-10/P3-TBDI3-10 | P3-TBDI3-10/C3S3-10 | JB-618 | SV-61304_DI_2 | SV-61304 | Process Instrument | On/Off Valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
829 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P3-TBDI3-11 | C3S3-11/P3-TBDI3-11 | P3-TBDI3-11/C3S3-11 | JB-618 | XV-61301_DI_1 | XV-61301 | Control Valve Position Feedback | Automatic on/off valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
830 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P3-TBDI3-12 | C3S3-12/P3-TBDI3-12 | P3-TBDI3-12/C3S3-12 | JB-618 | XV-61301_DI_2 | XV-61301 | Control Valve Position Feedback | Automatic on/off valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
831 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P3-TBDI3-13 | C3S3-13/P3-TBDI3-13 | P3-TBDI3-13/C3S3-13 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
832 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P3-TBDI3-14 | C3S3-14/P3-TBDI3-14 | P3-TBDI3-14/C3S3-14 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
833 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P3-TBDI3-15 | C3S3-15/P3-TBDI3-15 | P3-TBDI3-15/C3S3-15 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
834 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P3-TBDI3-16 | C3S3-16/P3-TBDI3-16 | P3-TBDI3-16/C3S3-16 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
835 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
836 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
837 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P3-TBDI3-17 | C3S3-19/P3-TBDI3-17 | P3-TBDI3-17/C3S3-19 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
838 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P3-TBDI3-18 | C3S3-20/P3-TBDI3-18 | P3-TBDI3-18/C3S3-20 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
839 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P3-TBDI3-19 | C3S3-21/P3-TBDI3-19 | P3-TBDI3-19/C3S3-21 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
840 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P3-TBDI3-20 | C3S3-22/P3-TBDI3-20 | P3-TBDI3-20/C3S3-22 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
841 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P3-TBDI3-21 | C3S3-23/P3-TBDI3-21 | P3-TBDI3-21/C3S3-23 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
842 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P3-TBDI3-22 | C3S3-24/P3-TBDI3-22 | P3-TBDI3-22/C3S3-24 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
843 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P3-TBDI3-23 | C3S3-25/P3-TBDI3-23 | P3-TBDI3-23/C3S3-25 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
844 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P3-TBDI3-24 | C3S3-26/P3-TBDI3-24 | P3-TBDI3-24/C3S3-26 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
845 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P3-TBDI3-25 | C3S3-27/P3-TBDI3-25 | P3-TBDI3-25/C3S3-27 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
846 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P3-TBDI3-26 | C3S3-28/P3-TBDI3-26 | P3-TBDI3-26/C3S3-28 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
847 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P3-TBDI3-27 | C3S3-29/P3-TBDI3-27 | P3-TBDI3-27/C3S3-29 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
848 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P3-TBDI3-28 | C3S3-30/P3-TBDI3-28 | P3-TBDI3-28/C3S3-30 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
849 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P3-TBDI3-29 | C3S3-31/P3-TBDI3-29 | P3-TBDI3-29/C3S3-31 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
850 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P3-TBDI3-30 | C3S3-32/P3-TBDI3-30 | P3-TBDI3-30/C3S3-32 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
851 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P3-TBDI3-31 | C3S3-33/P3-TBDI3-31 | P3-TBDI3-31/C3S3-33 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
852 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P3-TBDI3-32 | C3S3-34/P3-TBDI3-32 | P3-TBDI3-32/C3S3-34 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
853 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
854 | C3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
855 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 1 | OUT-0 | P3-TBRL1-1 | C3S4-1/P3-TBRL1-1 | P3-TBRL1-1/C3S4-1 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
856 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 2 | OUT-1 | P3-TBRL1-2 | C3S4-2/P3-TBRL1-2 | P3-TBRL1-2/C3S4-2 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
857 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 3 | OUT-2 | P3-TBRL1-3 | C3S4-3/P3-TBRL1-3 | P3-TBRL1-3/C3S4-3 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
858 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 4 | OUT-3 | P3-TBRL1-4 | C3S4-4/P3-TBRL1-4 | P3-TBRL1-4/C3S4-4 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
859 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 5 | OUT-4 | P3-TBRL1-5 | C3S4-5/P3-TBRL1-5 | P3-TBRL1-5/C3S4-5 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
860 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 6 | OUT-5 | P3-TBRL1-6 | C3S4-6/P3-TBRL1-6 | P3-TBRL1-6/C3S4-6 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
861 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 7 | OUT-6 | P3-TBRL1-7 | C3S4-7/P3-TBRL1-7 | P3-TBRL1-7/C3S4-7 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
862 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 8 | OUT-7 | P3-TBRL1-8 | C3S4-8/P3-TBRL1-8 | P3-TBRL1-8/C3S4-8 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
863 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 9 | OUT-8 | P3-TBRL1-9 | C3S4-9/P3-TBRL1-9 | P3-TBRL1-9/C3S4-9 | JB-606 | SV-60220_DO_1 | SV-60220 | Process Instrument | Solenoid valve | 325-01-602-PD-04 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
864 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 10 | OUT-9 | P3-TBRL1-10 | C3S4-10/P3-TBRL1-10 | P3-TBRL1-10/C3S4-10 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
865 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 11 | OUT-10 | P3-TBRL1-11 | C3S4-11/P3-TBRL1-11 | P3-TBRL1-11/C3S4-11 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
866 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 12 | OUT-11 | P3-TBRL1-12 | C3S4-12/P3-TBRL1-12 | P3-TBRL1-12/C3S4-12 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
867 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 13 | OUT-12 | P3-TBRL1-13 | C3S4-13/P3-TBRL1-13 | P3-TBRL1-13/C3S4-13 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
868 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 14 | OUT-13 | P3-TBRL1-14 | C3S4-14/P3-TBRL1-14 | P3-TBRL1-14/C3S4-14 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
869 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 15 | OUT-14 | P3-TBRL1-15 | C3S4-15/P3-TBRL1-15 | P3-TBRL1-15/C3S4-15 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
870 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 16 | OUT-15 | P3-TBRL1-16 | C3S4-16/P3-TBRL1-16 | P3-TBRL1-16/C3S4-16 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
871 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 17 | RTN OUT-0 | P3-TBRL1-17 | C3S4-17/P3-TBRL1-17 | P3-TBRL1-17/C3S4-17 | JB-606 | Spare_DO_17 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
872 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 18 | DC-0(+) | +24VDC | +24VDC | +24VDC | JB-606 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
873 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 19 | OUT-16 | P3-TBRL1-17 | C3S4-19/P3-TBRL1-17 | P3-TBRL1-17/C3S4-19 | JB-612 | PVM-61301_DO_1 | PVM-61301 | Process Instrument |  | 325-01-613-PD-03 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
874 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 20 | OUT-17 | P3-TBRL1-18 | C3S4-20/P3-TBRL1-18 | P3-TBRL1-18/C3S4-20 | JB-612 | PVM-61301_DO_2 | PVM-61301 | Process Instrument |  | 325-01-613-PD-03 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE
875 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 21 | OUT-18 | P3-TBRL1-19 | C3S4-21/P3-TBRL1-19 | P3-TBRL1-19/C3S4-21 | JB-612 | SV-61307_DO_1 | SV-61307 | Process Instrument | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
876 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 22 | OUT-19 | P3-TBRL1-20 | C3S4-22/P3-TBRL1-20 | P3-TBRL1-20/C3S4-22 | JB-612 | SV-61308_DO_1 | SV-61308 | Process Instrument | Solenoid valve | 325-01-613-PD-03 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
877 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 23 | OUT-20 | P3-TBRL1-21 | C3S4-23/P3-TBRL1-21 | P3-TBRL1-21/C3S4-23 | JB-612 | SV-61309_DO_1 | SV-61309 | Process Instrument | Solenoid valve | 325-01-613-PD-03 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
878 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 24 | OUT-21 | P3-TBRL1-22 | C3S4-24/P3-TBRL1-22 | P3-TBRL1-22/C3S4-24 | JB-612 | SV-61310_DO_1 | SV-61310 | Process Instrument | Solenoid valve | 325-01-613-PD-05 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
879 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 25 | OUT-22 | P3-TBRL1-23 | C3S4-25/P3-TBRL1-23 | P3-TBRL1-23/C3S4-25 | JB-612 | SV-61311_DO_1 | SV-61311 | Process Instrument | Solenoid valve | 325-01-613-PD-05 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
880 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 26 | OUT-23 | P3-TBRL1-24 | C3S4-26/P3-TBRL1-24 | P3-TBRL1-24/C3S4-26 | JB-612 | XS-61301A_DO_1 | XS-61301A | Process Instrument | Filter plant in operation | 325-01-613-PD-02 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
881 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 27 | OUT-24 | P3-TBRL1-25 | C3S4-27/P3-TBRL1-25 | P3-TBRL1-25/C3S4-27 | JB-612 | XS-61301B_DO_1 | XS-61301B | Process Instrument | Material transport in operation | 325-01-613-PD-02 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
882 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 28 | OUT-25 | P3-TBRL1-26 | C3S4-28/P3-TBRL1-26 | P3-TBRL1-26/C3S4-28 | JB-612 | XS-61301C_DO_1 | XS-61301C | Process Instrument | Belt plant in operation | 325-01-613-PD-02 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
883 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 29 | OUT-26 | P3-TBRL1-27 | C3S4-29/P3-TBRL1-27 | P3-TBRL1-27/C3S4-29 | JB-612 | XS-61301D_DO_1 | XS-61301D | Process Instrument | Sequence Stop | 325-01-613-PD-02 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
884 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 30 | OUT-27 | P3-TBRL1-28 | C3S4-30/P3-TBRL1-28 | P3-TBRL1-28/C3S4-30 | JB-612 | XS-61301E_DO_1 | XS-61301E | Process Instrument | Status from Customer Emergency stop | 325-01-613-PD-02 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
885 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 31 | OUT-28 | P3-TBRL1-29 | C3S4-31/P3-TBRL1-29 | P3-TBRL1-29/C3S4-31 | JB-612 | XS-61301F_DO_1 | XS-61301F | Process Instrument | Operation Release | 325-01-613-PD-02 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
886 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 32 | OUT-29 | P3-TBRL1-30 | C3S4-32/P3-TBRL1-30 | P3-TBRL1-30/C3S4-32 | JB-612 | XV-61302_DO_1 | XV-61302 | Control Valve Position Feedback | Automatic on/off valve | 325-01-613-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
887 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 33 | OUT-30 | P3-TBRL1-31 | C3S4-33/P3-TBRL1-31 | P3-TBRL1-31/C3S4-33 | JB-612 | XV-61303_DO_1 | XV-61303 | Control Valve Position Feedback | Automatic on/off valve | 325-01-613-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
888 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 34 | OUT-31 | P3-TBRL1-32 | C3S4-34/P3-TBRL1-32 | P3-TBRL1-32/C3S4-34 | JB-612 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
889 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 35 | RTN OUT-1 | P3-TBRL1-35 | C3S4-35/P3-TBRL1-35 | P3-TBRL1-35/C3S4-35 | JB-606 | Spare_DO_35 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
890 | C3 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 36 | DC-1(+) | +24VDC | +24VDC | +24VDC | JB-606 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
891 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 1 | OUT-0 | P3-TBRL2-1 | C3S5-1/P3-TBRL2-1 | P3-TBRL2-1/C3S5-1 | JB-618 | DV-61301_DO_1 | DV-61301 | Process Instrument | Automatic on/off valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
892 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 2 | OUT-1 | P3-TBRL2-2 | C3S5-2/P3-TBRL2-2 | P3-TBRL2-2/C3S5-2 | JB-618 | DV-61302_DO_1 | DV-61302 | Process Instrument | Automatic on/off valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
893 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 3 | OUT-2 | P3-TBRL2-3 | C3S5-3/P3-TBRL2-3 | P3-TBRL2-3/C3S5-3 | JB-618 | SV-61301_DO_1 | SV-61301 | Process Instrument | Solenoid valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
894 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 4 | OUT-3 | P3-TBRL2-4 | C3S5-4/P3-TBRL2-4 | P3-TBRL2-4/C3S5-4 | JB-618 | SV-61302_DO_1 | SV-61302 | Process Instrument | Solenoid valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
895 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 5 | OUT-4 | P3-TBRL2-5 | C3S5-5/P3-TBRL2-5 | P3-TBRL2-5/C3S5-5 | JB-618 | SV-61303_DO_1 | SV-61303 | Process Instrument | Solenoid valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
896 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 6 | OUT-5 | P3-TBRL2-6 | C3S5-6/P3-TBRL2-6 | P3-TBRL2-6/C3S5-6 | JB-618 | SV-61304_DO_1 | SV-61304 | Process Instrument | On/Off Valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE
897 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 7 | OUT-6 | P3-TBRL2-7 | C3S5-7/P3-TBRL2-7 | P3-TBRL2-7/C3S5-7 | JB-618 | SV-61305_DO_1 | SV-61305 | Process Instrument | Solenoid valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
898 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 8 | OUT-7 | P3-TBRL2-8 | C3S5-8/P3-TBRL2-8 | P3-TBRL2-8/C3S5-8 | JB-618 | SV-61306_DO_1 | SV-61306 | Process Instrument | Solenoid valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
899 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 9 | OUT-8 | P3-TBRL2-9 | C3S5-9/P3-TBRL2-9 | P3-TBRL2-9/C3S5-9 | JB-618 | XV-61301_DO_1 | XV-61301 | Control Valve Position Feedback | Automatic on/off valve | 325-01-613-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
900 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 10 | OUT-9 | P3-TBRL2-10 | C3S5-10/P3-TBRL2-10 | P3-TBRL2-10/C3S5-10 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
901 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 11 | OUT-10 | P3-TBRL2-11 | C3S5-11/P3-TBRL2-11 | P3-TBRL2-11/C3S5-11 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
902 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 12 | OUT-11 | P3-TBRL2-12 | C3S5-12/P3-TBRL2-12 | P3-TBRL2-12/C3S5-12 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
903 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 13 | OUT-12 | P3-TBRL2-13 | C3S5-13/P3-TBRL2-13 | P3-TBRL2-13/C3S5-13 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
904 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 14 | OUT-13 | P3-TBRL2-14 | C3S5-14/P3-TBRL2-14 | P3-TBRL2-14/C3S5-14 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
905 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 15 | OUT-14 | P3-TBRL2-15 | C3S5-15/P3-TBRL2-15 | P3-TBRL2-15/C3S5-15 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
906 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 16 | OUT-15 | P3-TBRL2-16 | C3S5-16/P3-TBRL2-16 | P3-TBRL2-16/C3S5-16 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
907 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 17 | RTN OUT-0 | P3-TBRL2-17 | C3S5-17/P3-TBRL2-17 | P3-TBRL2-17/C3S5-17 | JB-618 | Spare_DO_17 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
908 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 18 | DC-0(+) | +24VDC | +24VDC | +24VDC | JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
909 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 19 | OUT-16 | P3-TBRL2-17 | C3S5-19/P3-TBRL2-17 | P3-TBRL2-17/C3S5-19 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
910 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 20 | OUT-17 | P3-TBRL2-18 | C3S5-20/P3-TBRL2-18 | P3-TBRL2-18/C3S5-20 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
911 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 21 | OUT-18 | P3-TBRL2-19 | C3S5-21/P3-TBRL2-19 | P3-TBRL2-19/C3S5-21 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
912 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 22 | OUT-19 | P3-TBRL2-20 | C3S5-22/P3-TBRL2-20 | P3-TBRL2-20/C3S5-22 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
913 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 23 | OUT-20 | P3-TBRL2-21 | C3S5-23/P3-TBRL2-21 | P3-TBRL2-21/C3S5-23 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
914 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 24 | OUT-21 | P3-TBRL2-22 | C3S5-24/P3-TBRL2-22 | P3-TBRL2-22/C3S5-24 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
915 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 25 | OUT-22 | P3-TBRL2-23 | C3S5-25/P3-TBRL2-23 | P3-TBRL2-23/C3S5-25 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
916 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 26 | OUT-23 | P3-TBRL2-24 | C3S5-26/P3-TBRL2-24 | P3-TBRL2-24/C3S5-26 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
917 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 27 | OUT-24 | P3-TBRL2-25 | C3S5-27/P3-TBRL2-25 | P3-TBRL2-25/C3S5-27 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
918 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 28 | OUT-25 | P3-TBRL2-26 | C3S5-28/P3-TBRL2-26 | P3-TBRL2-26/C3S5-28 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
919 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 29 | OUT-26 | P3-TBRL2-27 | C3S5-29/P3-TBRL2-27 | P3-TBRL2-27/C3S5-29 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
920 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 30 | OUT-27 | P3-TBRL2-28 | C3S5-30/P3-TBRL2-28 | P3-TBRL2-28/C3S5-30 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
921 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 31 | OUT-28 | P3-TBRL2-29 | C3S5-31/P3-TBRL2-29 | P3-TBRL2-29/C3S5-31 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
922 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 32 | OUT-29 | P3-TBRL2-30 | C3S5-32/P3-TBRL2-30 | P3-TBRL2-30/C3S5-32 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
923 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 33 | OUT-30 | P3-TBRL2-31 | C3S5-33/P3-TBRL2-31 | P3-TBRL2-31/C3S5-33 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
924 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 34 | OUT-31 | P3-TBRL2-32 | C3S5-34/P3-TBRL2-32 | P3-TBRL2-32/C3S5-34 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
925 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 35 | RTN OUT-1 | P3-TBRL2-35 | C3S5-35/P3-TBRL2-35 | P3-TBRL2-35/C3S5-35 | JB-618 | Spare_DO_35 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
926 | C3 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 36 | DC-1(+) | +24VDC | +24VDC | +24VDC | JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
927 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1 | i RTN-0 | P3-TBAI1-1(B) | C3S6-1/P3-TBAI1-1(B) | P3-TBAI1-1(B)/C3S6-1 | JB-602 | TT-60215B_AI_1 | TT-60215B | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | -10 to 150°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
928 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 2 | IN-0 | P3-TBAI1-1(A) | C3S6-2/P3-TBAI1-1(A) | P3-TBAI1-1(A)/C3S6-2 | JB-602 | TT-60215B_AI_1 | TT-60215B | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | -10 to 150°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
929 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 3 | i RTN-1 | P3-TBAI1-2(B) | C3S6-3/P3-TBAI1-2(B) | P3-TBAI1-2(B)/C3S6-3 | JB-602 | TT-60216_AI_1 | TT-60216 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 200'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
930 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 4 | IN-1 | P3-TBAI1-2(A) | C3S6-4/P3-TBAI1-2(A) | P3-TBAI1-2(A)/C3S6-4 | JB-602 | TT-60216_AI_1 | TT-60216 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 0 - 200'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
931 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 5 | i RTN-2 | P3-TBAI1-3(B) | C3S6-5/P3-TBAI1-3(B) | P3-TBAI1-3(B)/C3S6-5 | JB-602 | TT-60240_AI_1 | TT-60240 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-05 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
932 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 6 | IN-2 | P3-TBAI1-3(A) | C3S6-6/P3-TBAI1-3(A) | P3-TBAI1-3(A)/C3S6-6 | JB-602 | TT-60240_AI_1 | TT-60240 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-05 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
933 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 7 | i RTN-3 | P3-TBAI1-4(B) | C3S6-7/P3-TBAI1-4(B) | P3-TBAI1-4(B)/C3S6-7 | JB-602 | TT-60241A_AI_1 | TT-60241A | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-05 | 4 - 20 mA | 0 - 100 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
934 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 8 | IN-3 | P3-TBAI1-4(A) | C3S6-8/P3-TBAI1-4(A) | P3-TBAI1-4(A)/C3S6-8 | JB-602 | TT-60241A_AI_1 | TT-60241A | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-05 | 4 - 20 mA | 0 - 100 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
935 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 9 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
936 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 10 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
937 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 11 | i RTN-4 | P3-TBAI1-5(B) | C3S6-11/P3-TBAI1-5(B) | P3-TBAI1-5(B)/C3S6-11 | JB-602 | TT-60241B_AI_1 | TT-60241B | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-05 | 4 - 20 mA | 0 - 100 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
938 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 12 | IN-4 | P3-TBAI1-5(A) | C3S6-12/P3-TBAI1-5(A) | P3-TBAI1-5(A)/C3S6-12 | JB-602 | TT-60241B_AI_1 | TT-60241B | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-05 | 4 - 20 mA | 0 - 100 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
939 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 13 | i RTN-5 | P3-TBAI1-6(B) | C3S6-13/P3-TBAI1-6(B) | P3-TBAI1-6(B)/C3S6-13 | JB-602 | VT-60210A_AI_1 | VT-60210A | Vibration Transmitter | Vibration Transmitter | 325-01-602-PD-03 | 4 - 20 mA | mm/sec | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
940 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 14 | IN-5 | P3-TBAI1-6(A) | C3S6-14/P3-TBAI1-6(A) | P3-TBAI1-6(A)/C3S6-14 | JB-602 | VT-60210A_AI_1 | VT-60210A | Vibration Transmitter | Vibration Transmitter | 325-01-602-PD-03 | 4 - 20 mA | mm/sec | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
941 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 15 | i RTN-6 | P3-TBAI1-7(B) | C3S6-15/P3-TBAI1-7(B) | P3-TBAI1-7(B)/C3S6-15 | JB-602 | VT-60210B_AI_1 | VT-60210B | Vibration Transmitter | Vibration Transmitter | 325-01-602-PD-03 | 4 - 20 mA | mm/sec | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
942 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IN-6 | P3-TBAI1-7(A) | C3S6-16/P3-TBAI1-7(A) | P3-TBAI1-7(A)/C3S6-16 | JB-602 | VT-60210B_AI_1 | VT-60210B | Vibration Transmitter | Vibration Transmitter | 325-01-602-PD-03 | 4 - 20 mA | mm/sec | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
943 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 17 | i RTN-7 | P3-TBAI1-8(B) | C3S6-17/P3-TBAI1-8(B) | P3-TBAI1-8(B)/C3S6-17 | JB-602 | VT-60241A_AI_1 | VT-60241A | Vibration Transmitter | Vibration Transmitter | 325-01-602-PD-05 | 4 - 20 mA | mm/sec | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
944 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 18 | IN-7 | P3-TBAI1-8(A) | C3S6-18/P3-TBAI1-8(A) | P3-TBAI1-8(A)/C3S6-18 | JB-602 | VT-60241A_AI_1 | VT-60241A | Vibration Transmitter | Vibration Transmitter | 325-01-602-PD-05 | 4 - 20 mA | mm/sec | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
945 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 19 | i RTN-8 | P3-TBAI1-9(B) | C3S6-19/P3-TBAI1-9(B) | P3-TBAI1-9(B)/C3S6-19 | JB-602 | VT-60241B_AI_1 | VT-60241B | Vibration Transmitter | Vibration Transmitter | 325-01-602-PD-05 | 4 - 20 mA | mm/sec | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
946 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 20 | IN-8 | P3-TBAI1-9(A) | C3S6-20/P3-TBAI1-9(A) | P3-TBAI1-9(A)/C3S6-20 | JB-602 | VT-60241B_AI_1 | VT-60241B | Vibration Transmitter | Vibration Transmitter | 325-01-602-PD-05 | 4 - 20 mA | mm/sec | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
947 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 21 | i RTN-9 | P3-TBAI1-10(B) | C3S6-21/P3-TBAI1-10(B) | P3-TBAI1-10(B)/C3S6-21 | JB-602 | FT-60210_AI_1 | FT-60210 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 126000 m3/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
948 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 22 | IN-9 | P3-TBAI1-10(A) | C3S6-22/P3-TBAI1-10(A) | P3-TBAI1-10(A)/C3S6-22 | JB-602 | FT-60210_AI_1 | FT-60210 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 126000 m3/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
949 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 23 | i RTN-10 | P3-TBAI1-11(B) | C3S6-23/P3-TBAI1-11(B) | P3-TBAI1-11(B)/C3S6-23 | JB-602 | FT-60211_AI_1 | FT-60211 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 126000 m3/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
950 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 24 | IN-10 | P3-TBAI1-11(A) | C3S6-24/P3-TBAI1-11(A) | P3-TBAI1-11(A)/C3S6-24 | JB-602 | FT-60211_AI_1 | FT-60211 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 126000 m3/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
951 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 25 | i RTN-11 | P3-TBAI1-12(B) | C3S6-25/P3-TBAI1-12(B) | P3-TBAI1-12(B)/C3S6-25 | JB-602 | FT-60210_AI_2 | FT-60210 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 126000 m3/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
952 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 26 | IN-11 | P3-TBAI1-12(A) | C3S6-26/P3-TBAI1-12(A) | P3-TBAI1-12(A)/C3S6-26 | JB-602 | FT-60210_AI_2 | FT-60210 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 126000 m3/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
953 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 27 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
954 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 28 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
955 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 29 | i RTN-12 | P3-TBAI1-13(B) | C3S6-29/P3-TBAI1-13(B) | P3-TBAI1-13(B)/C3S6-29 | JB-602 | FT-60211_AI_2 | FT-60211 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 126000 m3/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
956 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 30 | IN-12 | P3-TBAI1-13(A) | C3S6-30/P3-TBAI1-13(A) | P3-TBAI1-13(A)/C3S6-30 | JB-602 | FT-60211_AI_2 | FT-60211 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-03 | 4 - 20 mA | 126000 m3/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
957 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 31 | i RTN-13 | P3-TBAI1-14(B) | C3S6-31/P3-TBAI1-14(B) | P3-TBAI1-14(B)/C3S6-31 | JB-602 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
958 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 32 | IN-13 | P3-TBAI1-14(A) | C3S6-32/P3-TBAI1-14(A) | P3-TBAI1-14(A)/C3S6-32 | JB-602 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
959 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 33 | i RTN-14 | P3-TBAI1-15(B) | C3S6-33/P3-TBAI1-15(B) | P3-TBAI1-15(B)/C3S6-33 | JB-606 | DPT-60201_AI_1 | DPT-60201 | Differential Pressure Transmitte | Differential Pressure Transmitter | 325-01-602-PD-09 | 4 - 20 mA | 0-1 barg | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
960 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 34 | IN-14 | P3-TBAI1-15(A) | C3S6-34/P3-TBAI1-15(A) | P3-TBAI1-15(A)/C3S6-34 | JB-606 | DPT-60201_AI_1 | DPT-60201 | Differential Pressure Transmitte | Differential Pressure Transmitter | 325-01-602-PD-09 | 4 - 20 mA | 0-1 barg | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
961 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 35 | i RTN-15 | P3-TBAI1-16(B) | C3S6-35/P3-TBAI1-16(B) | P3-TBAI1-16(B)/C3S6-35 | JB-606 | FT-60203_AI_1 | FT-60203 | Flow Transmitter | Vortex Flow Transmitter | 325-01-602-PD-09 | 4 - 20 mA | 0 - 7000 kg/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
962 | C3 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 36 | IN-15 | P3-TBAI1-16(A) | C3S6-36/P3-TBAI1-16(A) | P3-TBAI1-16(A)/C3S6-36 | JB-606 | FT-60203_AI_1 | FT-60203 | Flow Transmitter | Vortex Flow Transmitter | 325-01-602-PD-09 | 4 - 20 mA | 0 - 7000 kg/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
963 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1 | i RTN-0 | P3-TBAI2-1(B) | C3S7-1/P3-TBAI2-1(B) | P3-TBAI2-1(B)/C3S7-1 | JB-607 | FT-60207_AI_1 | FT-60207 | Flow Transmitter | Flow Transmitter | 325-01-602-PD-07 | 4 - 20 mA |  | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE
964 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 2 | IN-0 | P3-TBAI2-1(A) | C3S7-2/P3-TBAI2-1(A) | P3-TBAI2-1(A)/C3S7-2 | JB-607 | FT-60207_AI_1 | FT-60207 | Flow Transmitter | Flow Transmitter | 325-01-602-PD-07 | 4 - 20 mA |  | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE
965 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 3 | i RTN-1 | P3-TBAI2-2(B) | C3S7-3/P3-TBAI2-2(B) | P3-TBAI2-2(B)/C3S7-3 | JB-607 | FT-60221_AI_1 | FT-60221 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 2500 m3/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
966 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 4 | IN-1 | P3-TBAI2-2(A) | C3S7-4/P3-TBAI2-2(A) | P3-TBAI2-2(A)/C3S7-4 | JB-607 | FT-60221_AI_1 | FT-60221 | Flow Transmitter | Thermal Mass Flow Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 2500 m3/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
967 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 5 | i RTN-2 | P3-TBAI2-3(B) | C3S7-5/P3-TBAI2-3(B) | P3-TBAI2-3(B)/C3S7-5 | JB-607 | FT-60261FA_AI_1 | FT-60261FA | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
968 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 6 | IN-2 | P3-TBAI2-3(A) | C3S7-6/P3-TBAI2-3(A) | P3-TBAI2-3(A)/C3S7-6 | JB-607 | FT-60261FA_AI_1 | FT-60261FA | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
969 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 7 | i RTN-3 | P3-TBAI2-4(B) | C3S7-7/P3-TBAI2-4(B) | P3-TBAI2-4(B)/C3S7-7 | JB-607 | FT-60261FB_AI_1 | FT-60261FB | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
970 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 8 | IN-3 | P3-TBAI2-4(A) | C3S7-8/P3-TBAI2-4(A) | P3-TBAI2-4(A)/C3S7-8 | JB-607 | FT-60261FB_AI_1 | FT-60261FB | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
971 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 9 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
972 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 10 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
973 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 11 | i RTN-4 | P3-TBAI2-5(B) | C3S7-11/P3-TBAI2-5(B) | P3-TBAI2-5(B)/C3S7-11 | JB-607 | FT-60261FC_AI_1 | FT-60261FC | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
974 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 12 | IN-4 | P3-TBAI2-5(A) | C3S7-12/P3-TBAI2-5(A) | P3-TBAI2-5(A)/C3S7-12 | JB-607 | FT-60261FC_AI_1 | FT-60261FC | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
975 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 13 | i RTN-5 | P3-TBAI2-6(B) | C3S7-13/P3-TBAI2-6(B) | P3-TBAI2-6(B)/C3S7-13 | JB-607 | FT-60261FD_AI_1 | FT-60261FD | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
976 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 14 | IN-5 | P3-TBAI2-6(A) | C3S7-14/P3-TBAI2-6(A) | P3-TBAI2-6(A)/C3S7-14 | JB-607 | FT-60261FD_AI_1 | FT-60261FD | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
977 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 15 | i RTN-6 | P3-TBAI2-7(B) | C3S7-15/P3-TBAI2-7(B) | P3-TBAI2-7(B)/C3S7-15 | JB-607 | FT-60262FE_AI_1 | FT-60262FE | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
978 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IN-6 | P3-TBAI2-7(A) | C3S7-16/P3-TBAI2-7(A) | P3-TBAI2-7(A)/C3S7-16 | JB-607 | FT-60262FE_AI_1 | FT-60262FE | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
979 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 17 | i RTN-7 | P3-TBAI2-8(B) | C3S7-17/P3-TBAI2-8(B) | P3-TBAI2-8(B)/C3S7-17 | JB-607 | FT-60262FF_AI_1 | FT-60262FF | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
980 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 18 | IN-7 | P3-TBAI2-8(A) | C3S7-18/P3-TBAI2-8(A) | P3-TBAI2-8(A)/C3S7-18 | JB-607 | FT-60262FF_AI_1 | FT-60262FF | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
981 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 19 | i RTN-8 | P3-TBAI2-9(B) | C3S7-19/P3-TBAI2-9(B) | P3-TBAI2-9(B)/C3S7-19 | JB-607 | FT-60262FG_AI_1 | FT-60262FG | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
982 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 20 | IN-8 | P3-TBAI2-9(A) | C3S7-20/P3-TBAI2-9(A) | P3-TBAI2-9(A)/C3S7-20 | JB-607 | FT-60262FG_AI_1 | FT-60262FG | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
983 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 21 | i RTN-9 | P3-TBAI2-10(B) | C3S7-21/P3-TBAI2-10(B) | P3-TBAI2-10(B)/C3S7-21 | JB-607 | FT-60262FH_AI_1 | FT-60262FH | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
984 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 22 | IN-9 | P3-TBAI2-10(A) | C3S7-22/P3-TBAI2-10(A) | P3-TBAI2-10(A)/C3S7-22 | JB-607 | FT-60262FH_AI_1 | FT-60262FH | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
985 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 23 | i RTN-10 | P3-TBAI2-11(B) | C3S7-23/P3-TBAI2-11(B) | P3-TBAI2-11(B)/C3S7-23 | JB-607 | FT-60263FJ_AI_1 | FT-60263FJ | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
986 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 24 | IN-10 | P3-TBAI2-11(A) | C3S7-24/P3-TBAI2-11(A) | P3-TBAI2-11(A)/C3S7-24 | JB-607 | FT-60263FJ_AI_1 | FT-60263FJ | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
987 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 25 | i RTN-11 | P3-TBAI2-12(B) | C3S7-25/P3-TBAI2-12(B) | P3-TBAI2-12(B)/C3S7-25 | JB-607 | FT-60263FK_AI_1 | FT-60263FK | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
988 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 26 | IN-11 | P3-TBAI2-12(A) | C3S7-26/P3-TBAI2-12(A) | P3-TBAI2-12(A)/C3S7-26 | JB-607 | FT-60263FK_AI_1 | FT-60263FK | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
989 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 27 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
990 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 28 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
991 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 29 | i RTN-12 | P3-TBAI2-13(B) | C3S7-29/P3-TBAI2-13(B) | P3-TBAI2-13(B)/C3S7-29 | JB-607 | FT-60263FL_AI_1 | FT-60263FL | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
992 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 30 | IN-12 | P3-TBAI2-13(A) | C3S7-30/P3-TBAI2-13(A) | P3-TBAI2-13(A)/C3S7-30 | JB-607 | FT-60263FL_AI_1 | FT-60263FL | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
993 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 31 | i RTN-13 | P3-TBAI2-14(B) | C3S7-31/P3-TBAI2-14(B) | P3-TBAI2-14(B)/C3S7-31 | JB-607 | FT-60263FM_AI_1 | FT-60263FM | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
994 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 32 | IN-13 | P3-TBAI2-14(A) | C3S7-32/P3-TBAI2-14(A) | P3-TBAI2-14(A)/C3S7-32 | JB-607 | FT-60263FM_AI_1 | FT-60263FM | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
995 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 33 | i RTN-14 | P3-TBAI2-15(B) | C3S7-33/P3-TBAI2-15(B) | P3-TBAI2-15(B)/C3S7-33 | JB-607 | FT-60264FN_AI_1 | FT-60264FN | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
996 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 34 | IN-14 | P3-TBAI2-15(A) | C3S7-34/P3-TBAI2-15(A) | P3-TBAI2-15(A)/C3S7-34 | JB-607 | FT-60264FN_AI_1 | FT-60264FN | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
997 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 35 | i RTN-15 | P3-TBAI2-16(B) | C3S7-35/P3-TBAI2-16(B) | P3-TBAI2-16(B)/C3S7-35 | JB-607 | FT-60264FP_AI_1 | FT-60264FP | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
998 | C3 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 36 | IN-15 | P3-TBAI2-16(A) | C3S7-36/P3-TBAI2-16(A) | P3-TBAI2-16(A)/C3S7-36 | JB-607 | FT-60264FP_AI_1 | FT-60264FP | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
999 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1 | i RTN-0 | P3-TBAI3-1(B) | C3S8-1/P3-TBAI3-1(B) | P3-TBAI3-1(B)/C3S8-1 | JB-607 | FT-60264FQ_AI_1 | FT-60264FQ | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1000 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 2 | IN-0 | P3-TBAI3-1(A) | C3S8-2/P3-TBAI3-1(A) | P3-TBAI3-1(A)/C3S8-2 | JB-607 | FT-60264FQ_AI_1 | FT-60264FQ | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1001 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 3 | i RTN-1 | P3-TBAI3-2(B) | C3S8-3/P3-TBAI3-2(B) | P3-TBAI3-2(B)/C3S8-3 | JB-607 | FT-60264FR_AI_1 | FT-60264FR | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1002 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 4 | IN-1 | P3-TBAI3-2(A) | C3S8-4/P3-TBAI3-2(A) | P3-TBAI3-2(A)/C3S8-4 | JB-607 | FT-60264FR_AI_1 | FT-60264FR | Flow Transmitter | Ultrasonic Flow Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 to 100 l/h | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1003 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 5 | i RTN-2 | P3-TBAI3-3(B) | C3S8-5/P3-TBAI3-3(B) | P3-TBAI3-3(B)/C3S8-5 | JB-607 | PT-60201_AI_1 | PT-60201 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 - 20 bar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1004 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 6 | IN-2 | P3-TBAI3-3(A) | C3S8-6/P3-TBAI3-3(A) | P3-TBAI3-3(A)/C3S8-6 | JB-607 | PT-60201_AI_1 | PT-60201 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 - 20 bar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1005 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 7 | i RTN-3 | P3-TBAI3-4(B) | C3S8-7/P3-TBAI3-4(B) | P3-TBAI3-4(B)/C3S8-7 | JB-607 | PT-60207_AI_1 | PT-60207 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-07 | 4 - 20 mA |  | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE
1006 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 8 | IN-3 | P3-TBAI3-4(A) | C3S8-8/P3-TBAI3-4(A) | P3-TBAI3-4(A)/C3S8-8 | JB-607 | PT-60207_AI_1 | PT-60207 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-07 | 4 - 20 mA |  | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE
1007 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 9 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1008 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 10 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1009 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 11 | i RTN-4 | P3-TBAI3-5(B) | C3S8-11/P3-TBAI3-5(B) | P3-TBAI3-5(B)/C3S8-11 | JB-607 | PT-60221_AI_1 | PT-60221 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 0.1 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1010 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 12 | IN-4 | P3-TBAI3-5(A) | C3S8-12/P3-TBAI3-5(A) | P3-TBAI3-5(A)/C3S8-12 | JB-607 | PT-60221_AI_1 | PT-60221 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 0.1 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1011 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 13 | i RTN-5 | P3-TBAI3-6(B) | C3S8-13/P3-TBAI3-6(B) | P3-TBAI3-6(B)/C3S8-13 | JB-607 | PT-60221_AI_1 | PT-60221 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 0.1 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1012 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 14 | IN-5 | P3-TBAI3-6(A) | C3S8-14/P3-TBAI3-6(A) | P3-TBAI3-6(A)/C3S8-14 | JB-607 | PT-60221_AI_1 | PT-60221 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 0.1 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1013 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 15 | i RTN-6 | P3-TBAI3-7(B) | C3S8-15/P3-TBAI3-7(B) | P3-TBAI3-7(B)/C3S8-15 | JB-607 | TI-FH-60210_AI_1 | TI-FH-60210 | Temperature Indicator / Sensor |  | 325-01-602-PD-06 | 4 - 20 mA | On-Off | Ashcroft | Model FI Bimetal Dial Thermometer | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1014 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IN-6 | P3-TBAI3-7(A) | C3S8-16/P3-TBAI3-7(A) | P3-TBAI3-7(A)/C3S8-16 | JB-607 | TI-FH-60210_AI_1 | TI-FH-60210 | Temperature Indicator / Sensor |  | 325-01-602-PD-06 | 4 - 20 mA | On-Off | Ashcroft | Model FI Bimetal Dial Thermometer | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1015 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 17 | i RTN-7 | P3-TBAI3-8(B) | C3S8-17/P3-TBAI3-8(B) | P3-TBAI3-8(B)/C3S8-17 | JB-607 | TT-60201_AI_1 | TT-60201 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 - 300 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1016 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 18 | IN-7 | P3-TBAI3-8(A) | C3S8-18/P3-TBAI3-8(A) | P3-TBAI3-8(A)/C3S8-18 | JB-607 | TT-60201_AI_1 | TT-60201 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-02 | 4 - 20 mA | 0 - 300 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1017 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 19 | i RTN-8 | P3-TBAI3-9(B) | C3S8-19/P3-TBAI3-9(B) | P3-TBAI3-9(B)/C3S8-19 | JB-607 | TT-60202_AI_1 | TT-60202 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-07 | 4 - 20 mA | 0 - 40 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1018 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 20 | IN-8 | P3-TBAI3-9(A) | C3S8-20/P3-TBAI3-9(A) | P3-TBAI3-9(A)/C3S8-20 | JB-607 | TT-60202_AI_1 | TT-60202 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-07 | 4 - 20 mA | 0 - 40 C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1019 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 21 | i RTN-9 | P3-TBAI3-10(B) | C3S8-21/P3-TBAI3-10(B) | P3-TBAI3-10(B)/C3S8-21 | JB-607 | TT-60207_AI_1 | TT-60207 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-07 | 4 - 20 mA |  | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE
1020 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 22 | IN-9 | P3-TBAI3-10(A) | C3S8-22/P3-TBAI3-10(A) | P3-TBAI3-10(A)/C3S8-22 | JB-607 | TT-60207_AI_1 | TT-60207 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-07 | 4 - 20 mA |  | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE
1021 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 23 | i RTN-10 | P3-TBAI3-11(B) | C3S8-23/P3-TBAI3-11(B) | P3-TBAI3-11(B)/C3S8-23 | JB-607 | UY-FH-60210A_AI_1 | UY-FH-60210A | I/P Converter Control Valve |  | 325-01-602-PD-06 | 4 - 20 mA | On-Off | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1022 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 24 | IN-10 | P3-TBAI3-11(A) | C3S8-24/P3-TBAI3-11(A) | P3-TBAI3-11(A)/C3S8-24 | JB-607 | UY-FH-60210A_AI_1 | UY-FH-60210A | I/P Converter Control Valve |  | 325-01-602-PD-06 | 4 - 20 mA | On-Off | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1023 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 25 | i RTN-11 | P3-TBAI3-12(B) | C3S8-25/P3-TBAI3-12(B) | P3-TBAI3-12(B)/C3S8-25 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1024 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 26 | IN-11 | P3-TBAI3-12(A) | C3S8-26/P3-TBAI3-12(A) | P3-TBAI3-12(A)/C3S8-26 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1025 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 27 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1026 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 28 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1027 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 29 | i RTN-12 | P3-TBAI3-13(B) | C3S8-29/P3-TBAI3-13(B) | P3-TBAI3-13(B)/C3S8-29 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1028 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 30 | IN-12 | P3-TBAI3-13(A) | C3S8-30/P3-TBAI3-13(A) | P3-TBAI3-13(A)/C3S8-30 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1029 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 31 | i RTN-13 | P3-TBAI3-14(B) | C3S8-31/P3-TBAI3-14(B) | P3-TBAI3-14(B)/C3S8-31 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1030 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 32 | IN-13 | P3-TBAI3-14(A) | C3S8-32/P3-TBAI3-14(A) | P3-TBAI3-14(A)/C3S8-32 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1031 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 33 | i RTN-14 | P3-TBAI3-15(B) | C3S8-33/P3-TBAI3-15(B) | P3-TBAI3-15(B)/C3S8-33 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1032 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 34 | IN-14 | P3-TBAI3-15(A) | C3S8-34/P3-TBAI3-15(A) | P3-TBAI3-15(A)/C3S8-34 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1033 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 35 | i RTN-15 | P3-TBAI3-16(B) | C3S8-35/P3-TBAI3-16(B) | P3-TBAI3-16(B)/C3S8-35 | JB-608 | TT-60245_AI_1 | TT-60245 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-05 | 4 - 20 mA | -10 to 150°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1034 | C3 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 36 | IN-15 | P3-TBAI3-16(A) | C3S8-36/P3-TBAI3-16(A) | P3-TBAI3-16(A)/C3S8-36 | JB-608 | TT-60245_AI_1 | TT-60245 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-05 | 4 - 20 mA | -10 to 150°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1035 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1 | i RTN-0 | P3-TBAI4-1(B) | C3S9-1/P3-TBAI4-1(B) | P3-TBAI4-1(B)/C3S9-1 | JB-618 | PT-61303_AI_1 | PT-61303 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA | -100 to 200 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1036 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 2 | IN-0 | P3-TBAI4-1(A) | C3S9-2/P3-TBAI4-1(A) | P3-TBAI4-1(A)/C3S9-2 | JB-618 | PT-61303_AI_1 | PT-61303 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA | -100 to 200 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1037 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 3 | i RTN-1 | P3-TBAI4-2(B) | C3S9-3/P3-TBAI4-2(B) | P3-TBAI4-2(B)/C3S9-3 | JB-618 | PT-61306_AI_1 | PT-61306 | Pressure Transmitter | Process Field Device | - | 4-20mA Analog | - | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1038 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 4 | IN-1 | P3-TBAI4-2(A) | C3S9-4/P3-TBAI4-2(A) | P3-TBAI4-2(A)/C3S9-4 | JB-618 | PT-61306_AI_1 | PT-61306 | Pressure Transmitter | Process Field Device | - | 4-20mA Analog | - | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1039 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 5 | i RTN-2 | P3-TBAI4-3(B) | C3S9-5/P3-TBAI4-3(B) | P3-TBAI4-3(B)/C3S9-5 | JB-618 | TT-61303_AI_1 | TT-61303 | Temperature Transmitter | Process Field Device | - | 4-20mA Analog | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1040 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 6 | IN-2 | P3-TBAI4-3(A) | C3S9-6/P3-TBAI4-3(A) | P3-TBAI4-3(A)/C3S9-6 | JB-618 | TT-61303_AI_1 | TT-61303 | Temperature Transmitter | Process Field Device | - | 4-20mA Analog | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1041 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 7 | i RTN-3 | P3-TBAI4-4(B) | C3S9-7/P3-TBAI4-4(B) | P3-TBAI4-4(B)/C3S9-7 | JB-618 | TT-61304_AI_1 | TT-61304 | Temperature Transmitter | Process Field Device | - | 4-20mA Analog | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1042 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 8 | IN-3 | P3-TBAI4-4(A) | C3S9-8/P3-TBAI4-4(A) | P3-TBAI4-4(A)/C3S9-8 | JB-618 | TT-61304_AI_1 | TT-61304 | Temperature Transmitter | Process Field Device | - | 4-20mA Analog | - | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1043 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 9 | RTN | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1044 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 10 | RTN | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1045 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 11 | i RTN-4 | P3-TBAI4-5(B) | C3S9-11/P3-TBAI4-5(B) | P3-TBAI4-5(B)/C3S9-11 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1046 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 12 | IN-4 | P3-TBAI4-5(A) | C3S9-12/P3-TBAI4-5(A) | P3-TBAI4-5(A)/C3S9-12 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1047 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 13 | i RTN-5 | P3-TBAI4-6(B) | C3S9-13/P3-TBAI4-6(B) | P3-TBAI4-6(B)/C3S9-13 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1048 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 14 | IN-5 | P3-TBAI4-6(A) | C3S9-14/P3-TBAI4-6(A) | P3-TBAI4-6(A)/C3S9-14 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1049 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 15 | i RTN-6 | P3-TBAI4-7(B) | C3S9-15/P3-TBAI4-7(B) | P3-TBAI4-7(B)/C3S9-15 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1050 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IN-6 | P3-TBAI4-7(A) | C3S9-16/P3-TBAI4-7(A) | P3-TBAI4-7(A)/C3S9-16 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1051 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 17 | i RTN-7 | P3-TBAI4-8(B) | C3S9-17/P3-TBAI4-8(B) | P3-TBAI4-8(B)/C3S9-17 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1052 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 18 | IN-7 | P3-TBAI4-8(A) | C3S9-18/P3-TBAI4-8(A) | P3-TBAI4-8(A)/C3S9-18 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1053 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 19 | i RTN-8 | P3-TBAI4-9(B) | C3S9-19/P3-TBAI4-9(B) | P3-TBAI4-9(B)/C3S9-19 | JB-612 | PT-61302_AI_1 | PT-61302 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-03 | 4 - 20 mA | -100 - 100 mbarg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1054 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 20 | IN-8 | P3-TBAI4-9(A) | C3S9-20/P3-TBAI4-9(A) | P3-TBAI4-9(A)/C3S9-20 | JB-612 | PT-61302_AI_1 | PT-61302 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-03 | 4 - 20 mA | -100 - 100 mbarg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1055 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 21 | i RTN-9 | P3-TBAI4-10(B) | C3S9-21/P3-TBAI4-10(B) | P3-TBAI4-10(B)/C3S9-21 | JB-612 | PT-61309_AI_1 | PT-61309 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-04 | 4 - 20 mA | 0 - 10 barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1056 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 22 | IN-9 | P3-TBAI4-10(A) | C3S9-22/P3-TBAI4-10(A) | P3-TBAI4-10(A)/C3S9-22 | JB-612 | PT-61309_AI_1 | PT-61309 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-04 | 4 - 20 mA | 0 - 10 barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1057 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 23 | i RTN-10 | P3-TBAI4-11(B) | C3S9-23/P3-TBAI4-11(B) | P3-TBAI4-11(B)/C3S9-23 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1058 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 24 | IN-10 | P3-TBAI4-11(A) | C3S9-24/P3-TBAI4-11(A) | P3-TBAI4-11(A)/C3S9-24 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1059 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 25 | i RTN-11 | P3-TBAI4-12(B) | C3S9-25/P3-TBAI4-12(B) | P3-TBAI4-12(B)/C3S9-25 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1060 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 26 | IN-11 | P3-TBAI4-12(A) | C3S9-26/P3-TBAI4-12(A) | P3-TBAI4-12(A)/C3S9-26 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1061 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 27 | RTN | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1062 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 28 | RTN | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1063 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 29 | i RTN-12 | P3-TBAI4-13(B) | C3S9-29/P3-TBAI4-13(B) | P3-TBAI4-13(B)/C3S9-29 | JB-612 | PT-61302_AI_1 | PT-61302 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-03 | 4 - 20 mA | -100 - 100 mbarg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1064 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 30 | IN-12 | P3-TBAI4-13(A) | C3S9-30/P3-TBAI4-13(A) | P3-TBAI4-13(A)/C3S9-30 | JB-612 | PT-61302_AI_1 | PT-61302 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-03 | 4 - 20 mA | -100 - 100 mbarg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1065 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 31 | i RTN-13 | P3-TBAI4-14(B) | C3S9-31/P3-TBAI4-14(B) | P3-TBAI4-14(B)/C3S9-31 | JB-612 | PT-61309_AI_1 | PT-61309 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-04 | 4 - 20 mA | 0 - 10 barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1066 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 32 | IN-13 | P3-TBAI4-14(A) | C3S9-32/P3-TBAI4-14(A) | P3-TBAI4-14(A)/C3S9-32 | JB-612 | PT-61309_AI_1 | PT-61309 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-04 | 4 - 20 mA | 0 - 10 barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1067 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 33 | i RTN-14 | P3-TBAI4-15(B) | C3S9-33/P3-TBAI4-15(B) | P3-TBAI4-15(B)/C3S9-33 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1068 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 34 | IN-14 | P3-TBAI4-15(A) | C3S9-34/P3-TBAI4-15(A) | P3-TBAI4-15(A)/C3S9-34 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1069 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 35 | i RTN-15 | P3-TBAI4-16(B) | C3S9-35/P3-TBAI4-16(B) | P3-TBAI4-16(B)/C3S9-35 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1070 | C3 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 36 | IN-15 | P3-TBAI4-16(A) | C3S9-36/P3-TBAI4-16(A) | P3-TBAI4-16(A)/C3S9-36 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1071 | C3 | C3S10 | 1756-N2 | EMPTY (Reserve Position) | - | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | - | - | - | - | - | - | - | EMPTY | -
1072 | C3 | C3S11 | 1756-N2 | EMPTY (Reserve Position) | - | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | - | - | - | - | - | - | - | EMPTY | -
1073 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 1 | VOUT-0 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1074 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 2 | VOUT-4 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1075 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 3 | IOUT-0 | P3-TBAO1-1 | C3S12-3/P3-TBAO1-1 | P3-TBAO1-1/C3S12-3 | JB-402 | TCV-40222_AO_1 | TCV-40222 | Temperature Control Valve | Automatic Control valve | 325-01-402-PD-02 | 4 - 20 mA | 0 - 100% | Samson | Type 3241 Globe Valve + Trovis 3730-1 | LiY-CY TP 2Px1.0 (Setpoint AO + Feedback AI) | ACTIVE | Jet Cooker
1076 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 4 | IOUT-4 | P3-TBAO1-5 | C3S12-4/P3-TBAO1-5 | P3-TBAO1-5/C3S12-4 | JB-607 | UY-FH-60210B_AO_1 | UY-FH-60210B | I/P Converter Control Valve |  | 325-01-602-PD-06 | 4 - 20 mA | On-Off | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1077 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 5 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1078 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 6 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1079 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 7 | VOUT-1 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1080 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 8 | VOUT-5 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1081 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 9 | IOUT-1 | P3-TBAO1-2 | C3S12-9/P3-TBAO1-2 | P3-TBAO1-2/C3S12-9 | JB-602 | TV-60202_AO_1 | TV-60202 | Temperature Control Valve | Process Field Device | - | 4-20mA Analog | - | Samson | Type 3241 Globe Valve + Trovis 3730-1 | LiY-CY TP 2Px1.0 (Setpoint AO + Feedback AI) | ACTIVE | -
1082 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 10 | IOUT-5 | P3-TBAO1-6 | C3S12-10/P3-TBAO1-6 | P3-TBAO1-6/C3S12-10 | JB-607 | Spare_AO_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1083 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 11 | VOUT-2 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1084 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 12 | VOUT-6 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1085 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 13 | IOUT-2 | P3-TBAO1-3 | C3S12-13/P3-TBAO1-3 | P3-TBAO1-3/C3S12-13 | JB-602 | TV-60214_AO_1 | TV-60214 | Temperature Control Valve | Automatic Control valve | 325-01-602-PD-03 | 4 - 20 mA | 0 - 100% | Samson | Type 3241 Globe Valve + Trovis 3730-1 | LiY-CY TP 2Px1.0 (Setpoint AO + Feedback AI) | ACTIVE | -
1086 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 14 | IOUT-6 | P3-TBAO1-7 | C3S12-14/P3-TBAO1-7 | P3-TBAO1-7/C3S12-14 | JB-607 | Spare_AO_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1087 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 15 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1088 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 16 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1089 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 17 | VOUT-3 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1090 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 18 | VOUT-7 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1091 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 19 | IOUT-3 | P3-TBAO1-4 | C3S12-19/P3-TBAO1-4 | P3-TBAO1-4/C3S12-19 | JB-607 | PV-60201_AO_1 | PV-60201 | Pressure Control Valve | Automatic Control valve | 325-01-602-PD-02 | 4 - 20 mA | 0 - 100% | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1092 | C3 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 20 | IOUT-7 | P3-TBAO1-8 | C3S12-20/P3-TBAO1-8 | P3-TBAO1-8/C3S12-20 | JB-607 | Spare_AO_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1093 | C4 | C4S0 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | ETH-DLR-P1 | C4S0-/- | -/C4S0- | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C4S0_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1094 | C4 | C4S0 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C4S0-P2/ETH | ETH/C4S0-P2 | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C4S0_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1095 | C4 | C4S0 | 1756-EN4TR | COMM (EtherNet/IP) | USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C4S0-USB/CONSOLE | CONSOLE/C4S0-USB | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C4S0_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1096 | C4 | C4S0 | 1756-EN4TR | COMM (EtherNet/IP) | DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C4S0-DISP/DIAG | DIAG/C4S0-DISP | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C4S0_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1097 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P4-TBDI1-1 | C4S1-1/P4-TBDI1-1 | P4-TBDI1-1/C4S1-1 | IS-JB-603 | AT-40201_DI_1 | AT-40201 | Process Instrument |  | 325-01-402-PD-01 | 24 VDC energized | On-Off | ENVEA / PCME | PCME QAL 991 (Dust Analyzer) | LiY-CY TP 2Px1.0 (Signal) + CVV 3Cx1.5 (24VDC Power) | ACTIVE
1098 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P4-TBDI1-2 | C4S1-2/P4-TBDI1-2 | P4-TBDI1-2/C4S1-2 | IS-JB-603 | AT-40202_DI_1 | AT-40202 | Process Instrument |  | 325-01-402-PD-01 | 24 VDC energized | On-Off | ENVEA / PCME | PCME QAL 991 (Dust Analyzer) | LiY-CY TP 2Px1.0 (Signal) + CVV 3Cx1.5 (24VDC Power) | ACTIVE
1099 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P4-TBDI1-3 | C4S1-3/P4-TBDI1-3 | P4-TBDI1-3/C4S1-3 | IS-JB-603 | AT-40203_DI_1 | AT-40203 | Process Instrument |  | 325-01-402-PD-02 | 24 VDC energized | On-Off | ENVEA / PCME | PCME QAL 991 (Dust Analyzer) | LiY-CY TP 2Px1.0 (Signal) + CVV 3Cx1.5 (24VDC Power) | ACTIVE
1100 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P4-TBDI1-4 | C4S1-4/P4-TBDI1-4 | P4-TBDI1-4/C4S1-4 | IS-JB-603 | LSH-60230_DI_1 | LSH-60230 | Process Instrument | Level switch | 325-01-602-PD-04 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Safety Barriers
1101 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P4-TBDI1-5 | C4S1-5/P4-TBDI1-5 | P4-TBDI1-5/C4S1-5 | IS-JB-603 | LSH-60231_DI_1 | LSH-60231 | Process Instrument | Level switch | 325-01-602-PD-04 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Safety Barriers
1102 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P4-TBDI1-6 | C4S1-6/P4-TBDI1-6 | P4-TBDI1-6/C4S1-6 | IS-JB-603 | LSH-60240_DI_1 | LSH-60240 | Process Instrument | Level switch | 325-01-602-PD-05 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Safety Barriers
1103 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P4-TBDI1-7 | C4S1-7/P4-TBDI1-7 | P4-TBDI1-7/C4S1-7 | IS-JB-603 | PD-60202_DI_1 | PD-60202 | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1104 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P4-TBDI1-8 | C4S1-8/P4-TBDI1-8 | P4-TBDI1-8/C4S1-8 | IS-JB-603 | RV-60204_DI_1 | RV-60204 | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1105 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P4-TBDI1-9 | C4S1-9/P4-TBDI1-9 | P4-TBDI1-9/C4S1-9 | IS-JB-603 | ZS-60201C_DI_1 | ZS-60201C | Process Instrument | Limit Switch | 325-01-602-PD-04 | Dry Contact | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1106 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P4-TBDI1-10 | C4S1-10/P4-TBDI1-10 | P4-TBDI1-10/C4S1-10 | IS-JB-603 | ZS-60201D_DI_1 | ZS-60201D | Process Instrument | Limit Switch | 325-01-602-PD-04 | Dry Contact | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1107 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P4-TBDI1-11 | C4S1-11/P4-TBDI1-11 | P4-TBDI1-11/C4S1-11 | IS-JB-603 | ZS-60201E_DI_1 | ZS-60201E | Process Instrument | Limit Switch | 325-01-602-PD-04 | Dry Contact | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1108 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P4-TBDI1-12 | C4S1-12/P4-TBDI1-12 | P4-TBDI1-12/C4S1-12 | IS-JB-603 | ZS-60229_DI_1 | ZS-60229 | Process Instrument | Limit Switch | 325-01-602-PD-04 | Switch PNP | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1109 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P4-TBDI1-13 | C4S1-13/P4-TBDI1-13 | P4-TBDI1-13/C4S1-13 | IS-JB-603 | ZS-60230_DI_1 | ZS-60230 | Process Instrument | Limit Switch | 325-01-602-PD-04 | Switch PNP | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1110 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P4-TBDI1-14 | C4S1-14/P4-TBDI1-14 | P4-TBDI1-14/C4S1-14 | IS-JB-603 | ZS-60231A_DI_1 | ZS-60231A | Process Instrument | Limit Switch | 325-01-602-PD-05 | Dry Contact | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1111 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P4-TBDI1-15 | C4S1-15/P4-TBDI1-15 | P4-TBDI1-15/C4S1-15 | IS-JB-603 | ZS-60231B_DI_1 | ZS-60231B | Process Instrument | Limit Switch | 325-01-602-PD-05 | Dry Contact | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1112 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P4-TBDI1-16 | C4S1-16/P4-TBDI1-16 | P4-TBDI1-16/C4S1-16 | IS-JB-603 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1113 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1114 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1115 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P4-TBDI1-17 | C4S1-19/P4-TBDI1-17 | P4-TBDI1-17/C4S1-19 | IS-JB-608 | ZS-60201A_DI_1 | ZS-60201A | Process Instrument | Limit Switch | 325-01-602-PD-04 | Dry Contact | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1116 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P4-TBDI1-18 | C4S1-20/P4-TBDI1-18 | P4-TBDI1-18/C4S1-20 | IS-JB-608 | ZS-60201B_DI_1 | ZS-60201B | Process Instrument | Limit Switch | 325-01-602-PD-04 | Dry Contact | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1117 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P4-TBDI1-19 | C4S1-21/P4-TBDI1-19 | P4-TBDI1-19/C4S1-21 | IS-JB-608 | ZS-60231C_DI_1 | ZS-60231C | Process Instrument | Limit Switch | 325-01-602-PD-05 | Switch PNP | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1118 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P4-TBDI1-20 | C4S1-22/P4-TBDI1-20 | P4-TBDI1-20/C4S1-22 | IS-JB-608 | ZS-60231D_DI_1 | ZS-60231D | Process Instrument | Limit Switch | 325-01-602-PD-05 | Switch PNP | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1119 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P4-TBDI1-21 | C4S1-23/P4-TBDI1-21 | P4-TBDI1-21/C4S1-23 | IS-JB-608 | ZS-60231E_DI_1 | ZS-60231E | Process Instrument | Limit Switch | 325-01-602-PD-05 | Switch PNP | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1120 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P4-TBDI1-22 | C4S1-24/P4-TBDI1-22 | P4-TBDI1-22/C4S1-24 | IS-JB-608 | ZS-60231F_DI_1 | ZS-60231F | Process Instrument | Limit Switch | 325-01-602-PD-05 | Switch PNP | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1121 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P4-TBDI1-23 | C4S1-25/P4-TBDI1-23 | P4-TBDI1-23/C4S1-25 | IS-JB-608 | ZS-60240_DI_1 | ZS-60240 | Process Instrument | Limit Switch | 325-01-602-PD-05 | Switch PNP | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1122 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P4-TBDI1-24 | C4S1-26/P4-TBDI1-24 | P4-TBDI1-24/C4S1-26 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1123 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P4-TBDI1-25 | C4S1-27/P4-TBDI1-25 | P4-TBDI1-25/C4S1-27 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1124 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P4-TBDI1-26 | C4S1-28/P4-TBDI1-26 | P4-TBDI1-26/C4S1-28 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1125 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P4-TBDI1-27 | C4S1-29/P4-TBDI1-27 | P4-TBDI1-27/C4S1-29 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1126 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P4-TBDI1-28 | C4S1-30/P4-TBDI1-28 | P4-TBDI1-28/C4S1-30 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1127 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P4-TBDI1-29 | C4S1-31/P4-TBDI1-29 | P4-TBDI1-29/C4S1-31 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1128 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P4-TBDI1-30 | C4S1-32/P4-TBDI1-30 | P4-TBDI1-30/C4S1-32 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1129 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P4-TBDI1-31 | C4S1-33/P4-TBDI1-31 | P4-TBDI1-31/C4S1-33 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1130 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P4-TBDI1-32 | C4S1-34/P4-TBDI1-32 | P4-TBDI1-32/C4S1-34 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1131 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1132 | C4 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1133 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P4-TBDI2-1 | C4S2-1/P4-TBDI2-1 | P4-TBDI2-1/C4S2-1 | IS-JB-612 | ISV-61303_DI_1 | ISV-61303 | Process Instrument | Position switch | 325-01-613-PD-03 | Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Safety Barriers
1134 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P4-TBDI2-2 | C4S2-2/P4-TBDI2-2 | P4-TBDI2-2/C4S2-2 | IS-JB-612 | ISV-61304_DI_1 | ISV-61304 | Process Instrument | Position switch | 325-01-613-PD-05 | Dry Contact | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | Safety Barriers
1135 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P4-TBDI2-3 | C4S2-3/P4-TBDI2-3 | P4-TBDI2-3/C4S2-3 | IS-JB-612 | LSH-61304_DI_1 | LSH-61304 | Process Instrument | Level switch | 325-01-613-PD-03 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Safety Barriers
1136 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P4-TBDI2-4 | C4S2-4/P4-TBDI2-4 | P4-TBDI2-4/C4S2-4 | IS-JB-612 | LSH-61305_DI_1 | LSH-61305 | Process Instrument | Level switch | 325-01-613-PD-05 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Safety Barriers
1137 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P4-TBDI2-5 | C4S2-5/P4-TBDI2-5 | P4-TBDI2-5/C4S2-5 | IS-JB-612 | LSH-61307_DI_1 | LSH-61307 | Process Instrument | Level switch | 325-01-613-PD-01 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Safety Barriers
1138 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P4-TBDI2-6 | C4S2-6/P4-TBDI2-6 | P4-TBDI2-6/C4S2-6 | IS-JB-612 | LSH-61312_DI_1 | LSH-61312 | Process Instrument | Level switch | 325-01-613-PD-05 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Safety Barriers
1139 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P4-TBDI2-7 | C4S2-7/P4-TBDI2-7 | P4-TBDI2-7/C4S2-7 | IS-JB-612 | PSE-61302_DI_1 | PSE-61302 | Process Instrument | Position switch | 325-01-613-PD-03 | Dry Contact | On-Off | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Safety Barriers
1140 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P4-TBDI2-8 | C4S2-8/P4-TBDI2-8 | P4-TBDI2-8/C4S2-8 | IS-JB-612 | PSE-61303_DI_1 | PSE-61303 | Process Instrument | Position switch | 325-01-613-PD-05 | Dry Contact | On-Off | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Safety Barriers
1141 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P4-TBDI2-9 | C4S2-9/P4-TBDI2-9 | P4-TBDI2-9/C4S2-9 | IS-JB-612 | RV-61301_DI_1 | RV-61301 | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1142 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P4-TBDI2-10 | C4S2-10/P4-TBDI2-10 | P4-TBDI2-10/C4S2-10 | IS-JB-612 | RV-61304_DI_1 | RV-61304 | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1143 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P4-TBDI2-11 | C4S2-11/P4-TBDI2-11 | P4-TBDI2-11/C4S2-11 | IS-JB-612 | RV-61305_DI_1 | RV-61305 | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1144 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P4-TBDI2-12 | C4S2-12/P4-TBDI2-12 | P4-TBDI2-12/C4S2-12 | IS-JB-612 | SC-61301_DI_1 | SC-61301 | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1145 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P4-TBDI2-13 | C4S2-13/P4-TBDI2-13 | P4-TBDI2-13/C4S2-13 | IS-JB-612 | SC-61302_DI_1 | SC-61302 | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1146 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P4-TBDI2-14 | C4S2-14/P4-TBDI2-14 | P4-TBDI2-14/C4S2-14 | IS-JB-612 | ZS-61312_DI_1 | ZS-61312 | Process Instrument | Limit Switch | 325-01-613-PD-01 | Dry Contact | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1147 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P4-TBDI2-15 | C4S2-15/P4-TBDI2-15 | P4-TBDI2-15/C4S2-15 | IS-JB-612 | ZS-61313_DI_1 | ZS-61313 | Process Instrument | Limit Switch | 325-01-613-PD-01 | Dry Contact | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1148 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P4-TBDI2-16 | C4S2-16/P4-TBDI2-16 | P4-TBDI2-16/C4S2-16 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1149 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1150 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1151 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P4-TBDI2-17 | C4S2-19/P4-TBDI2-17 | P4-TBDI2-17/C4S2-19 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1152 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P4-TBDI2-18 | C4S2-20/P4-TBDI2-18 | P4-TBDI2-18/C4S2-20 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1153 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P4-TBDI2-19 | C4S2-21/P4-TBDI2-19 | P4-TBDI2-19/C4S2-21 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1154 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P4-TBDI2-20 | C4S2-22/P4-TBDI2-20 | P4-TBDI2-20/C4S2-22 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1155 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P4-TBDI2-21 | C4S2-23/P4-TBDI2-21 | P4-TBDI2-21/C4S2-23 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1156 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P4-TBDI2-22 | C4S2-24/P4-TBDI2-22 | P4-TBDI2-22/C4S2-24 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1157 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P4-TBDI2-23 | C4S2-25/P4-TBDI2-23 | P4-TBDI2-23/C4S2-25 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1158 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P4-TBDI2-24 | C4S2-26/P4-TBDI2-24 | P4-TBDI2-24/C4S2-26 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1159 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P4-TBDI2-25 | C4S2-27/P4-TBDI2-25 | P4-TBDI2-25/C4S2-27 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1160 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P4-TBDI2-26 | C4S2-28/P4-TBDI2-26 | P4-TBDI2-26/C4S2-28 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1161 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P4-TBDI2-27 | C4S2-29/P4-TBDI2-27 | P4-TBDI2-27/C4S2-29 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1162 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P4-TBDI2-28 | C4S2-30/P4-TBDI2-28 | P4-TBDI2-28/C4S2-30 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1163 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P4-TBDI2-29 | C4S2-31/P4-TBDI2-29 | P4-TBDI2-29/C4S2-31 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1164 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P4-TBDI2-30 | C4S2-32/P4-TBDI2-30 | P4-TBDI2-30/C4S2-32 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1165 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P4-TBDI2-31 | C4S2-33/P4-TBDI2-31 | P4-TBDI2-31/C4S2-33 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1166 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P4-TBDI2-32 | C4S2-34/P4-TBDI2-32 | P4-TBDI2-32/C4S2-34 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1167 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1168 | C4 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1169 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P4-TBDI3-1 | C4S3-1/P4-TBDI3-1 | P4-TBDI3-1/C4S3-1 | IS-JB-618 | ISV-61301_DI_1 | ISV-61301 | Process Instrument | Process Field Device | - | 24VDC Discrete | - | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1170 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P4-TBDI3-2 | C4S3-2/P4-TBDI3-2 | P4-TBDI3-2/C4S3-2 | IS-JB-618 | LSH-61301_DI_1 | LSH-61301 | Process Instrument | Level switch | 325-01-613-PD-01 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Safety Barriers
1171 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P4-TBDI3-3 | C4S3-3/P4-TBDI3-3 | P4-TBDI3-3/C4S3-3 | IS-JB-618 | LSH-61303_DI_1 | LSH-61303 | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | -
1172 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P4-TBDI3-4 | C4S3-4/P4-TBDI3-4 | P4-TBDI3-4/C4S3-4 | IS-JB-618 | LSH-61306_DI_1 | LSH-61306 | Process Instrument | Level switch | 325-01-613-PD-01 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Safety Barriers
1173 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P4-TBDI3-5 | C4S3-5/P4-TBDI3-5 | P4-TBDI3-5/C4S3-5 | IS-JB-618 | LSH-61308_DI_1 | LSH-61308 | Process Instrument | Level switch | 325-01-613-PD-01 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Safety Barriers
1174 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P4-TBDI3-6 | C4S3-6/P4-TBDI3-6 | P4-TBDI3-6/C4S3-6 | IS-JB-618 | LSL-61302_DI_1 | LSL-61302 | Process Instrument | Level switch | 325-01-613-PD-01 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Safety Barriers
1175 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P4-TBDI3-7 | C4S3-7/P4-TBDI3-7 | P4-TBDI3-7/C4S3-7 | IS-JB-618 | PSE-61300_DI_1 | PSE-61300 | Process Instrument | Position switch | 325-01-613-PD-01 | Dry Contact | On-Off | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Safety Barriers
1176 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P4-TBDI3-8 | C4S3-8/P4-TBDI3-8 | P4-TBDI3-8/C4S3-8 | IS-JB-618 | PSE-61301_DI_1 | PSE-61301 | Process Instrument | Position switch | 325-01-613-PD-01 | Dry Contact | On-Off | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Safety Barriers
1177 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P4-TBDI3-9 | C4S3-9/P4-TBDI3-9 | P4-TBDI3-9/C4S3-9 | IS-JB-618 | PSE-61304_DI_1 | PSE-61304 | Process Instrument | Position switch | 325-01-613-PD-01 | Dry Contact | On-Off | BS&B / Fike | Burst-Alert Sensor / Rupture Disk Monitor | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Safety Barriers
1178 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P4-TBDI3-10 | C4S3-10/P4-TBDI3-10 | P4-TBDI3-10/C4S3-10 | IS-JB-618 | PSV-61301A_DI_1 | PSV-61301A | Process Instrument | Position switch | 325-01-613-PD-01 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Safety Barriers
1179 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P4-TBDI3-11 | C4S3-11/P4-TBDI3-11 | P4-TBDI3-11/C4S3-11 | IS-JB-618 | PSV-61301B_DI_1 | PSV-61301B | Process Instrument | Position switch | 325-01-613-PD-01 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | Safety Barriers
1180 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P4-TBDI3-12 | C4S3-12/P4-TBDI3-12 | P4-TBDI3-12/C4S3-12 | IS-JB-618 | ZS-61310_DI_1 | ZS-61310 | Process Instrument | Limit Switch | 325-01-613-PD-01 | Dry Contact | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1181 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P4-TBDI3-13 | C4S3-13/P4-TBDI3-13 | P4-TBDI3-13/C4S3-13 | IS-JB-618 | ZS-61311_DI_1 | ZS-61311 | Process Instrument | Limit Switch | 325-01-613-PD-01 | Dry Contact | On-Off | APL-HKC | APL-210N / APL-510N Valve Monitor | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | Safety Barriers
1182 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P4-TBDI3-14 | C4S3-14/P4-TBDI3-14 | P4-TBDI3-14/C4S3-14 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1183 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P4-TBDI3-15 | C4S3-15/P4-TBDI3-15 | P4-TBDI3-15/C4S3-15 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1184 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P4-TBDI3-16 | C4S3-16/P4-TBDI3-16 | P4-TBDI3-16/C4S3-16 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1185 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | IS-JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1186 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | IS-JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1187 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P4-TBDI3-17 | C4S3-19/P4-TBDI3-17 | P4-TBDI3-17/C4S3-19 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1188 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P4-TBDI3-18 | C4S3-20/P4-TBDI3-18 | P4-TBDI3-18/C4S3-20 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1189 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P4-TBDI3-19 | C4S3-21/P4-TBDI3-19 | P4-TBDI3-19/C4S3-21 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1190 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P4-TBDI3-20 | C4S3-22/P4-TBDI3-20 | P4-TBDI3-20/C4S3-22 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1191 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P4-TBDI3-21 | C4S3-23/P4-TBDI3-21 | P4-TBDI3-21/C4S3-23 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1192 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P4-TBDI3-22 | C4S3-24/P4-TBDI3-22 | P4-TBDI3-22/C4S3-24 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1193 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P4-TBDI3-23 | C4S3-25/P4-TBDI3-23 | P4-TBDI3-23/C4S3-25 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1194 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P4-TBDI3-24 | C4S3-26/P4-TBDI3-24 | P4-TBDI3-24/C4S3-26 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1195 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P4-TBDI3-25 | C4S3-27/P4-TBDI3-25 | P4-TBDI3-25/C4S3-27 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1196 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P4-TBDI3-26 | C4S3-28/P4-TBDI3-26 | P4-TBDI3-26/C4S3-28 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1197 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P4-TBDI3-27 | C4S3-29/P4-TBDI3-27 | P4-TBDI3-27/C4S3-29 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1198 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P4-TBDI3-28 | C4S3-30/P4-TBDI3-28 | P4-TBDI3-28/C4S3-30 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1199 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P4-TBDI3-29 | C4S3-31/P4-TBDI3-29 | P4-TBDI3-29/C4S3-31 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1200 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P4-TBDI3-30 | C4S3-32/P4-TBDI3-30 | P4-TBDI3-30/C4S3-32 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1201 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P4-TBDI3-31 | C4S3-33/P4-TBDI3-31 | P4-TBDI3-31/C4S3-33 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1202 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P4-TBDI3-32 | C4S3-34/P4-TBDI3-32 | P4-TBDI3-32/C4S3-34 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1203 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | IS-JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1204 | C4 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | IS-JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1205 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 1 | OUT-0 | P4-TBRL1-1 | C4S4-1/P4-TBRL1-1 | P4-TBRL1-1/C4S4-1 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1206 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 2 | OUT-1 | P4-TBRL1-2 | C4S4-2/P4-TBRL1-2 | P4-TBRL1-2/C4S4-2 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1207 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 3 | OUT-2 | P4-TBRL1-3 | C4S4-3/P4-TBRL1-3 | P4-TBRL1-3/C4S4-3 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1208 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 4 | OUT-3 | P4-TBRL1-4 | C4S4-4/P4-TBRL1-4 | P4-TBRL1-4/C4S4-4 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1209 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 5 | OUT-4 | P4-TBRL1-5 | C4S4-5/P4-TBRL1-5 | P4-TBRL1-5/C4S4-5 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1210 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 6 | OUT-5 | P4-TBRL1-6 | C4S4-6/P4-TBRL1-6 | P4-TBRL1-6/C4S4-6 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1211 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 7 | OUT-6 | P4-TBRL1-7 | C4S4-7/P4-TBRL1-7 | P4-TBRL1-7/C4S4-7 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1212 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 8 | OUT-7 | P4-TBRL1-8 | C4S4-8/P4-TBRL1-8 | P4-TBRL1-8/C4S4-8 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1213 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 9 | OUT-8 | P4-TBRL1-9 | C4S4-9/P4-TBRL1-9 | P4-TBRL1-9/C4S4-9 | IS-JB-608 | XA-60201_DO_1 | XA-60201 | Process Instrument | Gas detector | 325-01-402-PD-03 | 4 - 20 mA | 0-10%LEL | Industrial Process Equipment | Standard Process Field Device | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1214 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 10 | OUT-9 | P4-TBRL1-10 | C4S4-10/P4-TBRL1-10 | P4-TBRL1-10/C4S4-10 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1215 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 11 | OUT-10 | P4-TBRL1-11 | C4S4-11/P4-TBRL1-11 | P4-TBRL1-11/C4S4-11 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1216 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 12 | OUT-11 | P4-TBRL1-12 | C4S4-12/P4-TBRL1-12 | P4-TBRL1-12/C4S4-12 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1217 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 13 | OUT-12 | P4-TBRL1-13 | C4S4-13/P4-TBRL1-13 | P4-TBRL1-13/C4S4-13 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1218 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 14 | OUT-13 | P4-TBRL1-14 | C4S4-14/P4-TBRL1-14 | P4-TBRL1-14/C4S4-14 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1219 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 15 | OUT-14 | P4-TBRL1-15 | C4S4-15/P4-TBRL1-15 | P4-TBRL1-15/C4S4-15 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1220 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 16 | OUT-15 | P4-TBRL1-16 | C4S4-16/P4-TBRL1-16 | P4-TBRL1-16/C4S4-16 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1221 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 17 | RTN OUT-0 | P4-TBRL1-17 | C4S4-17/P4-TBRL1-17 | P4-TBRL1-17/C4S4-17 | IS-JB-608 | Spare_DO_17 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1222 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 18 | DC-0(+) | +24VDC | +24VDC | +24VDC | IS-JB-608 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1223 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 19 | OUT-16 | P4-TBRL1-17 | C4S4-19/P4-TBRL1-17 | P4-TBRL1-17/C4S4-19 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1224 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 20 | OUT-17 | P4-TBRL1-18 | C4S4-20/P4-TBRL1-18 | P4-TBRL1-18/C4S4-20 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1225 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 21 | OUT-18 | P4-TBRL1-19 | C4S4-21/P4-TBRL1-19 | P4-TBRL1-19/C4S4-21 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1226 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 22 | OUT-19 | P4-TBRL1-20 | C4S4-22/P4-TBRL1-20 | P4-TBRL1-20/C4S4-22 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1227 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 23 | OUT-20 | P4-TBRL1-21 | C4S4-23/P4-TBRL1-21 | P4-TBRL1-21/C4S4-23 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1228 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 24 | OUT-21 | P4-TBRL1-22 | C4S4-24/P4-TBRL1-22 | P4-TBRL1-22/C4S4-24 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1229 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 25 | OUT-22 | P4-TBRL1-23 | C4S4-25/P4-TBRL1-23 | P4-TBRL1-23/C4S4-25 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1230 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 26 | OUT-23 | P4-TBRL1-24 | C4S4-26/P4-TBRL1-24 | P4-TBRL1-24/C4S4-26 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1231 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 27 | OUT-24 | P4-TBRL1-25 | C4S4-27/P4-TBRL1-25 | P4-TBRL1-25/C4S4-27 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1232 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 28 | OUT-25 | P4-TBRL1-26 | C4S4-28/P4-TBRL1-26 | P4-TBRL1-26/C4S4-28 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1233 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 29 | OUT-26 | P4-TBRL1-27 | C4S4-29/P4-TBRL1-27 | P4-TBRL1-27/C4S4-29 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1234 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 30 | OUT-27 | P4-TBRL1-28 | C4S4-30/P4-TBRL1-28 | P4-TBRL1-28/C4S4-30 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1235 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 31 | OUT-28 | P4-TBRL1-29 | C4S4-31/P4-TBRL1-29 | P4-TBRL1-29/C4S4-31 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1236 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 32 | OUT-29 | P4-TBRL1-30 | C4S4-32/P4-TBRL1-30 | P4-TBRL1-30/C4S4-32 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1237 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 33 | OUT-30 | P4-TBRL1-31 | C4S4-33/P4-TBRL1-31 | P4-TBRL1-31/C4S4-33 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1238 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 34 | OUT-31 | P4-TBRL1-32 | C4S4-34/P4-TBRL1-32 | P4-TBRL1-32/C4S4-34 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1239 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 35 | RTN OUT-1 | P4-TBRL1-35 | C4S4-35/P4-TBRL1-35 | P4-TBRL1-35/C4S4-35 | IS-JB-608 | Spare_DO_35 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1240 | C4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 36 | DC-1(+) | +24VDC | +24VDC | +24VDC | IS-JB-608 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1241 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1 | i RTN-0 | P4-TBAI1-1(B) | C4S5-1/P4-TBAI1-1(B) | P4-TBAI1-1(B)/C4S5-1 | IS-JB-603 | PT-60230_AI_1 | PT-60230 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 0.1 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1242 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 2 | IN-0 | P4-TBAI1-1(A) | C4S5-2/P4-TBAI1-1(A) | P4-TBAI1-1(A)/C4S5-2 | IS-JB-603 | PT-60230_AI_1 | PT-60230 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 0.1 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1243 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 3 | i RTN-1 | P4-TBAI1-2(B) | C4S5-3/P4-TBAI1-2(B) | P4-TBAI1-2(B)/C4S5-3 | IS-JB-603 | PT-60231_AI_1 | PT-60231 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-04 | 4 - 20 mA | -100 to 200 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1244 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 4 | IN-1 | P4-TBAI1-2(A) | C4S5-4/P4-TBAI1-2(A) | P4-TBAI1-2(A)/C4S5-4 | IS-JB-603 | PT-60231_AI_1 | PT-60231 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-04 | 4 - 20 mA | -100 to 200 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1245 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 5 | i RTN-2 | P4-TBAI1-3(B) | C4S5-5/P4-TBAI1-3(B) | P4-TBAI1-3(B)/C4S5-5 | IS-JB-603 | TT-60224_AI_1 | TT-60224 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1246 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 6 | IN-2 | P4-TBAI1-3(A) | C4S5-6/P4-TBAI1-3(A) | P4-TBAI1-3(A)/C4S5-6 | IS-JB-603 | TT-60224_AI_1 | TT-60224 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1247 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 7 | i RTN-3 | P4-TBAI1-4(B) | C4S5-7/P4-TBAI1-4(B) | P4-TBAI1-4(B)/C4S5-7 | IS-JB-603 | TT-60225_AI_1 | TT-60225 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1248 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 8 | IN-3 | P4-TBAI1-4(A) | C4S5-8/P4-TBAI1-4(A) | P4-TBAI1-4(A)/C4S5-8 | IS-JB-603 | TT-60225_AI_1 | TT-60225 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1249 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 9 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1250 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 10 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1251 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 11 | i RTN-4 | P4-TBAI1-5(B) | C4S5-11/P4-TBAI1-5(B) | P4-TBAI1-5(B)/C4S5-11 | IS-JB-603 | TT-60226_AI_1 | TT-60226 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1252 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 12 | IN-4 | P4-TBAI1-5(A) | C4S5-12/P4-TBAI1-5(A) | P4-TBAI1-5(A)/C4S5-12 | IS-JB-603 | TT-60226_AI_1 | TT-60226 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1253 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 13 | i RTN-5 | P4-TBAI1-6(B) | C4S5-13/P4-TBAI1-6(B) | P4-TBAI1-6(B)/C4S5-13 | IS-JB-603 | TT-60227_AI_1 | TT-60227 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1254 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 14 | IN-5 | P4-TBAI1-6(A) | C4S5-14/P4-TBAI1-6(A) | P4-TBAI1-6(A)/C4S5-14 | IS-JB-603 | TT-60227_AI_1 | TT-60227 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1255 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 15 | i RTN-6 | P4-TBAI1-7(B) | C4S5-15/P4-TBAI1-7(B) | P4-TBAI1-7(B)/C4S5-15 | IS-JB-603 | TT-60230_AI_1 | TT-60230 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1256 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IN-6 | P4-TBAI1-7(A) | C4S5-16/P4-TBAI1-7(A) | P4-TBAI1-7(A)/C4S5-16 | IS-JB-603 | TT-60230_AI_1 | TT-60230 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1257 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 17 | i RTN-7 | P4-TBAI1-8(B) | C4S5-17/P4-TBAI1-8(B) | P4-TBAI1-8(B)/C4S5-17 | IS-JB-603 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1258 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 18 | IN-7 | P4-TBAI1-8(A) | C4S5-18/P4-TBAI1-8(A) | P4-TBAI1-8(A)/C4S5-18 | IS-JB-603 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1259 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 19 | i RTN-8 | P4-TBAI1-9(B) | C4S5-19/P4-TBAI1-9(B) | P4-TBAI1-9(B)/C4S5-19 | IS-JB-608 | PT-60220_AI_1 | PT-60220 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-04 | 4 - 20 mA | -100 - 100 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1260 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 20 | IN-8 | P4-TBAI1-9(A) | C4S5-20/P4-TBAI1-9(A) | P4-TBAI1-9(A)/C4S5-20 | IS-JB-608 | PT-60220_AI_1 | PT-60220 | Pressure Transmitter | Pressure Transmitter | 325-01-602-PD-04 | 4 - 20 mA | -100 - 100 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1261 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 21 | i RTN-9 | P4-TBAI1-10(B) | C4S5-21/P4-TBAI1-10(B) | P4-TBAI1-10(B)/C4S5-21 | IS-JB-608 | TT-60220_AI_1 | TT-60220 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1262 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 22 | IN-9 | P4-TBAI1-10(A) | C4S5-22/P4-TBAI1-10(A) | P4-TBAI1-10(A)/C4S5-22 | IS-JB-608 | TT-60220_AI_1 | TT-60220 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1263 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 23 | i RTN-10 | P4-TBAI1-11(B) | C4S5-23/P4-TBAI1-11(B) | P4-TBAI1-11(B)/C4S5-23 | IS-JB-608 | TT-60221_AI_1 | TT-60221 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1264 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 24 | IN-10 | P4-TBAI1-11(A) | C4S5-24/P4-TBAI1-11(A) | P4-TBAI1-11(A)/C4S5-24 | IS-JB-608 | TT-60221_AI_1 | TT-60221 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1265 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 25 | i RTN-11 | P4-TBAI1-12(B) | C4S5-25/P4-TBAI1-12(B) | P4-TBAI1-12(B)/C4S5-25 | IS-JB-608 | TT-60222_AI_1 | TT-60222 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1266 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 26 | IN-11 | P4-TBAI1-12(A) | C4S5-26/P4-TBAI1-12(A) | P4-TBAI1-12(A)/C4S5-26 | IS-JB-608 | TT-60222_AI_1 | TT-60222 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1267 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 27 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1268 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 28 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1269 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 29 | i RTN-12 | P4-TBAI1-13(B) | C4S5-29/P4-TBAI1-13(B) | P4-TBAI1-13(B)/C4S5-29 | IS-JB-608 | TT-60223_AI_1 | TT-60223 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1270 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 30 | IN-12 | P4-TBAI1-13(A) | C4S5-30/P4-TBAI1-13(A) | P4-TBAI1-13(A)/C4S5-30 | IS-JB-608 | TT-60223_AI_1 | TT-60223 | Temperature Transmitter | Temperature Transmitter | 325-01-602-PD-04 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1271 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 31 | i RTN-13 | P4-TBAI1-14(B) | C4S5-31/P4-TBAI1-14(B) | P4-TBAI1-14(B)/C4S5-31 | IS-JB-608 | XT-60201_AI_1 | XT-60201 | Speed / Position Transmitter | Gas detector | 325-01-402-PD-03 | 4 - 20 mA | 0-10%LEL | Industrial Process Equipment | Standard Process Field Device | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1272 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 32 | IN-13 | P4-TBAI1-14(A) | C4S5-32/P4-TBAI1-14(A) | P4-TBAI1-14(A)/C4S5-32 | IS-JB-608 | XT-60201_AI_1 | XT-60201 | Speed / Position Transmitter | Gas detector | 325-01-402-PD-03 | 4 - 20 mA | 0-10%LEL | Industrial Process Equipment | Standard Process Field Device | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1273 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 33 | i RTN-14 | P4-TBAI1-15(B) | C4S5-33/P4-TBAI1-15(B) | P4-TBAI1-15(B)/C4S5-33 | IS-JB-608 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1274 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 34 | IN-14 | P4-TBAI1-15(A) | C4S5-34/P4-TBAI1-15(A) | P4-TBAI1-15(A)/C4S5-34 | IS-JB-608 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1275 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 35 | i RTN-15 | P4-TBAI1-16(B) | C4S5-35/P4-TBAI1-16(B) | P4-TBAI1-16(B)/C4S5-35 | IS-JB-608 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1276 | C4 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 36 | IN-15 | P4-TBAI1-16(A) | C4S5-36/P4-TBAI1-16(A) | P4-TBAI1-16(A)/C4S5-36 | IS-JB-608 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1277 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1 | i RTN-0 | P4-TBAI2-1(B) | C4S6-1/P4-TBAI2-1(B) | P4-TBAI2-1(B)/C4S6-1 | IS-JB-612 | DPT-61310_AI_1 | DPT-61310 | Differential Pressure Transmitte | Differential Pressure Transmitter | 325-01-613-PD-03 | 4 - 20 mA |  | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Safety Barriers
1278 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 2 | IN-0 | P4-TBAI2-1(A) | C4S6-2/P4-TBAI2-1(A) | P4-TBAI2-1(A)/C4S6-2 | IS-JB-612 | DPT-61310_AI_1 | DPT-61310 | Differential Pressure Transmitte | Differential Pressure Transmitter | 325-01-613-PD-03 | 4 - 20 mA |  | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Safety Barriers
1279 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 3 | i RTN-1 | P4-TBAI2-2(B) | C4S6-3/P4-TBAI2-2(B) | P4-TBAI2-2(B)/C4S6-3 | IS-JB-612 | DPT-61312_AI_1 | DPT-61312 | Differential Pressure Transmitter | Differential Pressure Transmitter | 325-01-613-PD-05 | 4 - 20 mA |  | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Safety Barriers
1280 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 4 | IN-1 | P4-TBAI2-2(A) | C4S6-4/P4-TBAI2-2(A) | P4-TBAI2-2(A)/C4S6-4 | IS-JB-612 | DPT-61312_AI_1 | DPT-61312 | Differential Pressure Transmitter | Differential Pressure Transmitter | 325-01-613-PD-05 | 4 - 20 mA |  | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Safety Barriers
1281 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 5 | i RTN-2 | P4-TBAI2-3(B) | C4S6-5/P4-TBAI2-3(B) | P4-TBAI2-3(B)/C4S6-5 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1282 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 6 | IN-2 | P4-TBAI2-3(A) | C4S6-6/P4-TBAI2-3(A) | P4-TBAI2-3(A)/C4S6-6 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1283 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 7 | i RTN-3 | P4-TBAI2-4(B) | C4S6-7/P4-TBAI2-4(B) | P4-TBAI2-4(B)/C4S6-7 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1284 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 8 | IN-3 | P4-TBAI2-4(A) | C4S6-8/P4-TBAI2-4(A) | P4-TBAI2-4(A)/C4S6-8 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1285 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 9 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1286 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 10 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1287 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 11 | i RTN-4 | P4-TBAI2-5(B) | C4S6-11/P4-TBAI2-5(B) | P4-TBAI2-5(B)/C4S6-11 | IS-JB-618 | DPT-61301_AI_1 | DPT-61301 | Differential Pressure Transmitte | Differential Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA |  | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Safety Barriers
1288 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 12 | IN-4 | P4-TBAI2-5(A) | C4S6-12/P4-TBAI2-5(A) | P4-TBAI2-5(A)/C4S6-12 | IS-JB-618 | DPT-61301_AI_1 | DPT-61301 | Differential Pressure Transmitte | Differential Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA |  | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Safety Barriers
1289 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 13 | i RTN-5 | P4-TBAI2-6(B) | C4S6-13/P4-TBAI2-6(B) | P4-TBAI2-6(B)/C4S6-13 | IS-JB-618 | DPT-61302_AI_1 | DPT-61302 | Differential Pressure Transmitte | Differential Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA |  | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Safety Barriers
1290 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 14 | IN-5 | P4-TBAI2-6(A) | C4S6-14/P4-TBAI2-6(A) | P4-TBAI2-6(A)/C4S6-14 | IS-JB-618 | DPT-61302_AI_1 | DPT-61302 | Differential Pressure Transmitte | Differential Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA |  | Endress+Hauser | Deltabar PMD55B (Diff. Pressure) | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | Safety Barriers
1291 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 15 | i RTN-6 | P4-TBAI2-7(B) | C4S6-15/P4-TBAI2-7(B) | P4-TBAI2-7(B)/C4S6-15 | IS-JB-618 | LT-61301_AI_1 | LT-61301 | Level Transmitter | Level transmitter | 325-01-613-PD-01 | 4 - 20 mA |  | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1292 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IN-6 | P4-TBAI2-7(A) | C4S6-16/P4-TBAI2-7(A) | P4-TBAI2-7(A)/C4S6-16 | IS-JB-618 | LT-61301_AI_1 | LT-61301 | Level Transmitter | Level transmitter | 325-01-613-PD-01 | 4 - 20 mA |  | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1293 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 17 | i RTN-7 | P4-TBAI2-8(B) | C4S6-17/P4-TBAI2-8(B) | P4-TBAI2-8(B)/C4S6-17 | IS-JB-618 | PT-61301_AI_1 | PT-61301 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA | 0 - 1 barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1294 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 18 | IN-7 | P4-TBAI2-8(A) | C4S6-18/P4-TBAI2-8(A) | P4-TBAI2-8(A)/C4S6-18 | IS-JB-618 | PT-61301_AI_1 | PT-61301 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA | 0 - 1 barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1295 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 19 | i RTN-8 | P4-TBAI2-9(B) | C4S6-19/P4-TBAI2-9(B) | P4-TBAI2-9(B)/C4S6-19 | IS-JB-618 | PT-61303_AI_1 | PT-61303 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA | -100 to 200 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1296 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 20 | IN-8 | P4-TBAI2-9(A) | C4S6-20/P4-TBAI2-9(A) | P4-TBAI2-9(A)/C4S6-20 | IS-JB-618 | PT-61303_AI_1 | PT-61303 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA | -100 to 200 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1297 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 21 | i RTN-9 | P4-TBAI2-10(B) | C4S6-21/P4-TBAI2-10(B) | P4-TBAI2-10(B)/C4S6-21 | IS-JB-618 | PT-61304_AI_1 | PT-61304 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA | -100 to 200 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1298 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 22 | IN-9 | P4-TBAI2-10(A) | C4S6-22/P4-TBAI2-10(A) | P4-TBAI2-10(A)/C4S6-22 | IS-JB-618 | PT-61304_AI_1 | PT-61304 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA | -100 to 200 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1299 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 23 | i RTN-10 | P4-TBAI2-11(B) | C4S6-23/P4-TBAI2-11(B) | P4-TBAI2-11(B)/C4S6-23 | IS-JB-618 | PT-61305_AI_1 | PT-61305 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA | -100 to 200 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1300 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 24 | IN-10 | P4-TBAI2-11(A) | C4S6-24/P4-TBAI2-11(A) | P4-TBAI2-11(A)/C4S6-24 | IS-JB-618 | PT-61305_AI_1 | PT-61305 | Pressure Transmitter | Pressure Transmitter | 325-01-613-PD-01 | 4 - 20 mA | -100 to 200 mbar | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1301 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 25 | i RTN-11 | P4-TBAI2-12(B) | C4S6-25/P4-TBAI2-12(B) | P4-TBAI2-12(B)/C4S6-25 | IS-JB-618 | TT-61301_AI_1 | TT-61301 | Temperature Transmitter | Temperature Transmitter | 325-01-613-PD-01 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1302 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 26 | IN-11 | P4-TBAI2-12(A) | C4S6-26/P4-TBAI2-12(A) | P4-TBAI2-12(A)/C4S6-26 | IS-JB-618 | TT-61301_AI_1 | TT-61301 | Temperature Transmitter | Temperature Transmitter | 325-01-613-PD-01 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1303 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 27 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1304 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 28 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1305 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 29 | i RTN-12 | P4-TBAI2-13(B) | C4S6-29/P4-TBAI2-13(B) | P4-TBAI2-13(B)/C4S6-29 | IS-JB-618 | TT-61302_AI_1 | TT-61302 | Temperature Transmitter | Temperature Transmitter | 325-01-613-PD-01 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1306 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 30 | IN-12 | P4-TBAI2-13(A) | C4S6-30/P4-TBAI2-13(A) | P4-TBAI2-13(A)/C4S6-30 | IS-JB-618 | TT-61302_AI_1 | TT-61302 | Temperature Transmitter | Temperature Transmitter | 325-01-613-PD-01 | 4 - 20 mA | 0 - 400'°C | Endress+Hauser | iTEMP TMT71 / TM411 (Pt100 RTD) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1307 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 31 | i RTN-13 | P4-TBAI2-14(B) | C4S6-31/P4-TBAI2-14(B) | P4-TBAI2-14(B)/C4S6-31 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1308 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 32 | IN-13 | P4-TBAI2-14(A) | C4S6-32/P4-TBAI2-14(A) | P4-TBAI2-14(A)/C4S6-32 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1309 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 33 | i RTN-14 | P4-TBAI2-15(B) | C4S6-33/P4-TBAI2-15(B) | P4-TBAI2-15(B)/C4S6-33 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1310 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 34 | IN-14 | P4-TBAI2-15(A) | C4S6-34/P4-TBAI2-15(A) | P4-TBAI2-15(A)/C4S6-34 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1311 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 35 | i RTN-15 | P4-TBAI2-16(B) | C4S6-35/P4-TBAI2-16(B) | P4-TBAI2-16(B)/C4S6-35 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1312 | C4 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 36 | IN-15 | P4-TBAI2-16(A) | C4S6-36/P4-TBAI2-16(A) | P4-TBAI2-16(A)/C4S6-36 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1313 | C4 | C4S7 | 1756-N2 | EMPTY (Reserve Position) | - | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | - | - | - | - | - | - | - | EMPTY | -
1314 | C4 | C4S8 | 1756-N2 | EMPTY (Reserve Position) | - | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | - | - | - | - | - | - | - | EMPTY | -
1315 | C4 | C4S9 | 1756-N2 | EMPTY (Reserve Position) | - | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | - | - | - | - | - | - | - | EMPTY | -
1316 | C4 | C4S10 | 1756-N2 | EMPTY (Reserve Position) | - | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | - | - | - | - | - | - | - | EMPTY | -
1317 | C4 | C4S11 | 1756-N2 | EMPTY (Reserve Position) | - | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | - | - | - | - | - | - | - | EMPTY | -
1318 | C4 | C4S12 | 1756-N2 | EMPTY (Reserve Position) | - | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | - | - | - | - | - | - | - | EMPTY | -
1319 | C5 | C5S0 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | ETH-DLR-P1 | C5S0-/- | -/C5S0- | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C5S0_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1320 | C5 | C5S0 | 1756-EN4TR | COMM (EtherNet/IP) | RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C5S0-P2/ETH | ETH/C5S0-P2 | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C5S0_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1321 | C5 | C5S0 | 1756-EN4TR | COMM (EtherNet/IP) | USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C5S0-USB/CONSOLE | CONSOLE/C5S0-USB | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C5S0_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1322 | C5 | C5S0 | 1756-EN4TR | COMM (EtherNet/IP) | DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C5S0-DISP/DIAG | DIAG/C5S0-DISP | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C5S0_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | Process Field Device | - | - | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1323 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P5-TBDI1-1 | C5S1-1/P5-TBDI1-1 | P5-TBDI1-1/C5S1-1 | RIO-200 | FS-20201_DI_1 | FS-20201 | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1324 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P5-TBDI1-2 | C5S1-2/P5-TBDI1-2 | P5-TBDI1-2/C5S1-2 | RIO-200 | FT-913201_DI_1 | FT-913201 | Flow Transmitter | Coriolis Flow Transmitter | 325-01-913-PD-02 | 4 - 20 mA,Pulse | 0-1000kg/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1325 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P5-TBDI1-3 | C5S1-3/P5-TBDI1-3 | P5-TBDI1-3/C5S1-3 | RIO-200 | FT-936201_DI_1 | FT-936201 | Flow Transmitter | Magnetic Flow Transmitter | 325-01-930-PD-01 | 4 - 20 mA,Pulse | 0-1000kg/m³ | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1326 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P5-TBDI1-4 | C5S1-4/P5-TBDI1-4 | P5-TBDI1-4/C5S1-4 | RIO-200 | FT-936202_DI_1 | FT-936202 | Flow Transmitter | Magnetic Flow Transmitter | 325-01-930-PD-02 | 4 - 20 mA,Pulse | 0 - 20 m3/ hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1327 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P5-TBDI1-5 | C5S1-5/P5-TBDI1-5 | P5-TBDI1-5/C5S1-5 | RIO-200 | LSL-814201_DI_1 | LSL-814201 | Process Instrument |  | 325-01-814-PD-01 | Dry Contact |  | Endress+Hauser | Liquiphant FTL51B (Vibrating Fork Liquids) | CVV 3Cx1.5 (24VDC Power + Switch Output) | ACTIVE | Safety Barriers
1328 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P5-TBDI1-6 | C5S1-6/P5-TBDI1-6 | P5-TBDI1-6/C5S1-6 | RIO-200 | PK-913201_DI_1 | PK-913201 | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1329 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P5-TBDI1-7 | C5S1-7/P5-TBDI1-7 | P5-TBDI1-7/C5S1-7 | RIO-200 | PK-913202_DI_1 | PK-913202 | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1330 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P5-TBDI1-8 | C5S1-8/P5-TBDI1-8 | P5-TBDI1-8/C5S1-8 | RIO-200 | HV-20204_DI_1 | HV-20204 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-202-PD-01 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | -
1331 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P5-TBDI1-9 | C5S1-9/P5-TBDI1-9 | P5-TBDI1-9/C5S1-9 | RIO-200 | HV-20205_DI_1 | HV-20205 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-202-PD-01 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | -
1332 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P5-TBDI1-10 | C5S1-10/P5-TBDI1-10 | P5-TBDI1-10/C5S1-10 | RIO-200 | HV-20206_DI_1 | HV-20206 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-202-PD-01 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | -
1333 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P5-TBDI1-11 | C5S1-11/P5-TBDI1-11 | P5-TBDI1-11/C5S1-11 | RIO-200 | HV-20207_DI_1 | HV-20207 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-202-PD-01 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | -
1334 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P5-TBDI1-12 | C5S1-12/P5-TBDI1-12 | P5-TBDI1-12/C5S1-12 | RIO-200 | HV-20208_DI_1 | HV-20208 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-202-PD-02 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | -
1335 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P5-TBDI1-13 | C5S1-13/P5-TBDI1-13 | P5-TBDI1-13/C5S1-13 | RIO-200 | HV-20209_DI_1 | HV-20209 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-202-PD-02 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | -
1336 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P5-TBDI1-14 | C5S1-14/P5-TBDI1-14 | P5-TBDI1-14/C5S1-14 | RIO-200 | HV-20210_DI_1 | HV-20210 | Manual Valve With Position Switch | Valve With Position Switch | 325-01-202-PD-02 | Dry Contact | On-Off | TeroFox / APL-HKC | TF-20DFS Manual Ball Valve + APL-210N Box | CVV 4Cx1.0 (Open/Close Limit Switches) | ACTIVE | -
1337 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P5-TBDI1-15 | C5S1-15/P5-TBDI1-15 | P5-TBDI1-15/C5S1-15 | RIO-200 | XA-80305A_DI_1 | XA-80305A | Process Instrument | Gas vaporizer Ready | 325-01-913-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1338 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P5-TBDI1-16 | C5S1-16/P5-TBDI1-16 | P5-TBDI1-16/C5S1-16 | RIO-200 | XA-80305B_DI_1 | XA-80305B | Process Instrument | Gas vaporizer Run | 325-01-913-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1339 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1340 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1341 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P5-TBDI1-17 | C5S1-19/P5-TBDI1-17 | P5-TBDI1-17/C5S1-19 | RIO-200 | XA-80305C_DI_1 | XA-80305C | Process Instrument | Gas vaporizer Failed | 325-01-913-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1342 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P5-TBDI1-18 | C5S1-20/P5-TBDI1-18 | P5-TBDI1-18/C5S1-20 | RIO-200 | XA-80305D_DI_1 | XA-80305D | Process Instrument | Gas vaporizer Overheated | 325-01-913-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1343 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P5-TBDI1-19 | C5S1-21/P5-TBDI1-19 | P5-TBDI1-19/C5S1-21 | RIO-200 | XA-80305E_DI_1 | XA-80305E | Process Instrument | Gas vaporizer Excessive flow tripped | 325-01-913-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1344 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P5-TBDI1-20 | C5S1-22/P5-TBDI1-20 | P5-TBDI1-20/C5S1-22 | RIO-200 | XA-80305F_DI_1 | XA-80305F | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1345 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P5-TBDI1-21 | C5S1-23/P5-TBDI1-21 | P5-TBDI1-21/C5S1-23 | RIO-200 | XA-80306A_DI_1 | XA-80306A | Process Instrument | Gas vaporizer Ready | 325-01-913-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1346 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P5-TBDI1-22 | C5S1-24/P5-TBDI1-22 | P5-TBDI1-22/C5S1-24 | RIO-200 | XA-80306B_DI_1 | XA-80306B | Process Instrument | Gas vaporizer Run | 325-01-913-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1347 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P5-TBDI1-23 | C5S1-25/P5-TBDI1-23 | P5-TBDI1-23/C5S1-25 | RIO-200 | XA-80306C_DI_1 | XA-80306C | Process Instrument | Gas vaporizer Failed | 325-01-913-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1348 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P5-TBDI1-24 | C5S1-26/P5-TBDI1-24 | P5-TBDI1-24/C5S1-26 | RIO-200 | XA-80306D_DI_1 | XA-80306D | Process Instrument | Gas vaporizer Overheated | 325-01-913-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1349 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P5-TBDI1-25 | C5S1-27/P5-TBDI1-25 | P5-TBDI1-25/C5S1-27 | RIO-200 | XA-80306E_DI_1 | XA-80306E | Process Instrument | Gas vaporizer Excessive flow tripped | 325-01-913-PD-02 | Dry Contact | On-Off | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1350 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P5-TBDI1-26 | C5S1-28/P5-TBDI1-26 | P5-TBDI1-26/C5S1-28 | RIO-200 | XA-80306F_DI_1 | XA-80306F | Process Instrument | Process Field Device | - | 24VDC Discrete | - | Industrial Process Equipment | Standard Process Field Device | CVV 2Cx1.5 / LiY-CY 1Px1.0 General Control | ACTIVE | -
1351 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P5-TBDI1-27 | C5S1-29/P5-TBDI1-27 | P5-TBDI1-27/C5S1-29 | RIO-200 | XV-20201_DI_1 | XV-20201 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1352 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P5-TBDI1-28 | C5S1-30/P5-TBDI1-28 | P5-TBDI1-28/C5S1-30 | RIO-200 | XV-20201_DI_2 | XV-20201 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1353 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P5-TBDI1-29 | C5S1-31/P5-TBDI1-29 | P5-TBDI1-29/C5S1-31 | RIO-200 | XV-20202_DI_1 | XV-20202 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1354 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P5-TBDI1-30 | C5S1-32/P5-TBDI1-30 | P5-TBDI1-30/C5S1-32 | RIO-200 | XV-20202_DI_2 | XV-20202 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1355 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P5-TBDI1-31 | C5S1-33/P5-TBDI1-31 | P5-TBDI1-31/C5S1-33 | RIO-200 | XV-20203_DI_1 | XV-20203 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1356 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P5-TBDI1-32 | C5S1-34/P5-TBDI1-32 | P5-TBDI1-32/C5S1-34 | RIO-200 | XV-20203_DI_2 | XV-20203 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1357 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1358 | C5 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1359 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 1 | IN-0 | P5-TBDI2-1 | C5S2-1/P5-TBDI2-1 | P5-TBDI2-1/C5S2-1 | RIO-200 | XV-20211_DI_1 | XV-20211 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1360 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 2 | IN-1 | P5-TBDI2-2 | C5S2-2/P5-TBDI2-2 | P5-TBDI2-2/C5S2-2 | RIO-200 | XV-20211_DI_2 | XV-20211 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1361 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 3 | IN-2 | P5-TBDI2-3 | C5S2-3/P5-TBDI2-3 | P5-TBDI2-3/C5S2-3 | RIO-200 | XV-20212_DI_1 | XV-20212 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1362 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 4 | IN-3 | P5-TBDI2-4 | C5S2-4/P5-TBDI2-4 | P5-TBDI2-4/C5S2-4 | RIO-200 | XV-20212_DI_2 | XV-20212 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1363 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 5 | IN-4 | P5-TBDI2-5 | C5S2-5/P5-TBDI2-5 | P5-TBDI2-5/C5S2-5 | RIO-200 | XV-20213_DI_1 | XV-20213 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1364 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 6 | IN-5 | P5-TBDI2-6 | C5S2-6/P5-TBDI2-6 | P5-TBDI2-6/C5S2-6 | RIO-200 | XV-20213_DI_2 | XV-20213 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1365 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 7 | IN-6 | P5-TBDI2-7 | C5S2-7/P5-TBDI2-7 | P5-TBDI2-7/C5S2-7 | RIO-200 | XV-913201_DI_1 | XV-913201 | Control Valve Position Feedback | Automatic on/off valve | 325-01-913-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1366 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 8 | IN-7 | P5-TBDI2-8 | C5S2-8/P5-TBDI2-8 | P5-TBDI2-8/C5S2-8 | RIO-200 | XV-913201_DI_1 | XV-913201 | Control Valve Position Feedback | Automatic on/off valve | 325-01-913-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1367 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 9 | IN-8 | P5-TBDI2-9 | C5S2-9/P5-TBDI2-9 | P5-TBDI2-9/C5S2-9 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1368 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 10 | IN-9 | P5-TBDI2-10 | C5S2-10/P5-TBDI2-10 | P5-TBDI2-10/C5S2-10 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1369 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 11 | IN-10 | P5-TBDI2-11 | C5S2-11/P5-TBDI2-11 | P5-TBDI2-11/C5S2-11 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1370 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 12 | IN-11 | P5-TBDI2-12 | C5S2-12/P5-TBDI2-12 | P5-TBDI2-12/C5S2-12 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1371 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 13 | IN-12 | P5-TBDI2-13 | C5S2-13/P5-TBDI2-13 | P5-TBDI2-13/C5S2-13 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1372 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 14 | IN-13 | P5-TBDI2-14 | C5S2-14/P5-TBDI2-14 | P5-TBDI2-14/C5S2-14 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1373 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 15 | IN-14 | P5-TBDI2-15 | C5S2-15/P5-TBDI2-15 | P5-TBDI2-15/C5S2-15 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1374 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 16 | IN-15 | P5-TBDI2-16 | C5S2-16/P5-TBDI2-16 | P5-TBDI2-16/C5S2-16 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1375 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 17 | GND-0 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1376 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 18 | GND-0 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1377 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 19 | IN-16 | P5-TBDI2-17 | C5S2-19/P5-TBDI2-17 | P5-TBDI2-17/C5S2-19 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1378 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 20 | IN-17 | P5-TBDI2-18 | C5S2-20/P5-TBDI2-18 | P5-TBDI2-18/C5S2-20 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1379 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 21 | IN-18 | P5-TBDI2-19 | C5S2-21/P5-TBDI2-19 | P5-TBDI2-19/C5S2-21 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1380 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 22 | IN-19 | P5-TBDI2-20 | C5S2-22/P5-TBDI2-20 | P5-TBDI2-20/C5S2-22 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1381 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 23 | IN-20 | P5-TBDI2-21 | C5S2-23/P5-TBDI2-21 | P5-TBDI2-21/C5S2-23 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1382 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 24 | IN-21 | P5-TBDI2-22 | C5S2-24/P5-TBDI2-22 | P5-TBDI2-22/C5S2-24 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1383 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 25 | IN-22 | P5-TBDI2-23 | C5S2-25/P5-TBDI2-23 | P5-TBDI2-23/C5S2-25 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1384 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 26 | IN-23 | P5-TBDI2-24 | C5S2-26/P5-TBDI2-24 | P5-TBDI2-24/C5S2-26 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1385 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 27 | IN-24 | P5-TBDI2-25 | C5S2-27/P5-TBDI2-25 | P5-TBDI2-25/C5S2-27 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1386 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 28 | IN-25 | P5-TBDI2-26 | C5S2-28/P5-TBDI2-26 | P5-TBDI2-26/C5S2-28 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1387 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 29 | IN-26 | P5-TBDI2-27 | C5S2-29/P5-TBDI2-27 | P5-TBDI2-27/C5S2-29 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1388 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 30 | IN-27 | P5-TBDI2-28 | C5S2-30/P5-TBDI2-28 | P5-TBDI2-28/C5S2-30 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1389 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 31 | IN-28 | P5-TBDI2-29 | C5S2-31/P5-TBDI2-29 | P5-TBDI2-29/C5S2-31 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1390 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IN-29 | P5-TBDI2-30 | C5S2-32/P5-TBDI2-30 | P5-TBDI2-30/C5S2-32 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1391 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 33 | IN-30 | P5-TBDI2-31 | C5S2-33/P5-TBDI2-31 | P5-TBDI2-31/C5S2-33 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1392 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 34 | IN-31 | P5-TBDI2-32 | C5S2-34/P5-TBDI2-32 | P5-TBDI2-32/C5S2-34 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1393 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 35 | GND1 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1394 | C5 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 36 | GND1 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1395 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 1 | OUT-0 | P5-TBRL1-1 | C5S3-1/P5-TBRL1-1 | P5-TBRL1-1/C5S3-1 | RIO-200 | XA-92201_DO_1 | XA-92201 | Process Instrument | Gas detector | 325-01-923-PD-03 | 4 - 20 mA | 0-10%LEL | Industrial Process Equipment | Standard Process Field Device | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1396 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 2 | OUT-1 | P5-TBRL1-2 | C5S3-2/P5-TBRL1-2 | P5-TBRL1-2/C5S3-2 | RIO-200 | XV-20201_DO_1 | XV-20201 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1397 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 3 | OUT-2 | P5-TBRL1-3 | C5S3-3/P5-TBRL1-3 | P5-TBRL1-3/C5S3-3 | RIO-200 | XV-20202_DO_1 | XV-20202 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1398 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 4 | OUT-3 | P5-TBRL1-4 | C5S3-4/P5-TBRL1-4 | P5-TBRL1-4/C5S3-4 | RIO-200 | XV-20203_DO_1 | XV-20203 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1399 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 5 | OUT-4 | P5-TBRL1-5 | C5S3-5/P5-TBRL1-5 | P5-TBRL1-5/C5S3-5 | RIO-200 | XV-20211_DO_1 | XV-20211 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1400 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 6 | OUT-5 | P5-TBRL1-6 | C5S3-6/P5-TBRL1-6 | P5-TBRL1-6/C5S3-6 | RIO-200 | XV-20212_DO_1 | XV-20212 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1401 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 7 | OUT-6 | P5-TBRL1-7 | C5S3-7/P5-TBRL1-7 | P5-TBRL1-7/C5S3-7 | RIO-200 | XV-20213_DO_1 | XV-20213 | Control Valve Position Feedback | Automatic on/off valve | 325-01-202-PD-01 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1402 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 8 | OUT-7 | P5-TBRL1-8 | C5S3-8/P5-TBRL1-8 | P5-TBRL1-8/C5S3-8 | RIO-200 | XV-913201_DO_1 | XV-913201 | Control Valve Position Feedback | Automatic on/off valve | 325-01-913-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1403 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 9 | OUT-8 | P5-TBRL1-9 | C5S3-9/P5-TBRL1-9 | P5-TBRL1-9/C5S3-9 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1404 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 10 | OUT-9 | P5-TBRL1-10 | C5S3-10/P5-TBRL1-10 | P5-TBRL1-10/C5S3-10 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1405 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 11 | OUT-10 | P5-TBRL1-11 | C5S3-11/P5-TBRL1-11 | P5-TBRL1-11/C5S3-11 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1406 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 12 | OUT-11 | P5-TBRL1-12 | C5S3-12/P5-TBRL1-12 | P5-TBRL1-12/C5S3-12 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1407 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 13 | OUT-12 | P5-TBRL1-13 | C5S3-13/P5-TBRL1-13 | P5-TBRL1-13/C5S3-13 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1408 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 14 | OUT-13 | P5-TBRL1-14 | C5S3-14/P5-TBRL1-14 | P5-TBRL1-14/C5S3-14 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1409 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 15 | OUT-14 | P5-TBRL1-15 | C5S3-15/P5-TBRL1-15 | P5-TBRL1-15/C5S3-15 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1410 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 16 | OUT-15 | P5-TBRL1-16 | C5S3-16/P5-TBRL1-16 | P5-TBRL1-16/C5S3-16 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1411 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 17 | RTN OUT-0 | P5-TBRL1-17 | C5S3-17/P5-TBRL1-17 | P5-TBRL1-17/C5S3-17 | RIO-200 | Spare_DO_17 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1412 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 18 | DC-0(+) | +24VDC | +24VDC | +24VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1413 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 19 | OUT-16 | P5-TBRL1-17 | C5S3-19/P5-TBRL1-17 | P5-TBRL1-17/C5S3-19 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1414 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 20 | OUT-17 | P5-TBRL1-18 | C5S3-20/P5-TBRL1-18 | P5-TBRL1-18/C5S3-20 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1415 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 21 | OUT-18 | P5-TBRL1-19 | C5S3-21/P5-TBRL1-19 | P5-TBRL1-19/C5S3-21 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1416 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 22 | OUT-19 | P5-TBRL1-20 | C5S3-22/P5-TBRL1-20 | P5-TBRL1-20/C5S3-22 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1417 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 23 | OUT-20 | P5-TBRL1-21 | C5S3-23/P5-TBRL1-21 | P5-TBRL1-21/C5S3-23 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1418 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 24 | OUT-21 | P5-TBRL1-22 | C5S3-24/P5-TBRL1-22 | P5-TBRL1-22/C5S3-24 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1419 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 25 | OUT-22 | P5-TBRL1-23 | C5S3-25/P5-TBRL1-23 | P5-TBRL1-23/C5S3-25 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1420 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 26 | OUT-23 | P5-TBRL1-24 | C5S3-26/P5-TBRL1-24 | P5-TBRL1-24/C5S3-26 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1421 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 27 | OUT-24 | P5-TBRL1-25 | C5S3-27/P5-TBRL1-25 | P5-TBRL1-25/C5S3-27 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1422 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 28 | OUT-25 | P5-TBRL1-26 | C5S3-28/P5-TBRL1-26 | P5-TBRL1-26/C5S3-28 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1423 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 29 | OUT-26 | P5-TBRL1-27 | C5S3-29/P5-TBRL1-27 | P5-TBRL1-27/C5S3-29 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1424 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 30 | OUT-27 | P5-TBRL1-28 | C5S3-30/P5-TBRL1-28 | P5-TBRL1-28/C5S3-30 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1425 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 31 | OUT-28 | P5-TBRL1-29 | C5S3-31/P5-TBRL1-29 | P5-TBRL1-29/C5S3-31 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1426 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 32 | OUT-29 | P5-TBRL1-30 | C5S3-32/P5-TBRL1-30 | P5-TBRL1-30/C5S3-32 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1427 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 33 | OUT-30 | P5-TBRL1-31 | C5S3-33/P5-TBRL1-31 | P5-TBRL1-31/C5S3-33 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1428 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 34 | OUT-31 | P5-TBRL1-32 | C5S3-34/P5-TBRL1-32 | P5-TBRL1-32/C5S3-34 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1429 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 35 | RTN OUT-1 | P5-TBRL1-35 | C5S3-35/P5-TBRL1-35 | P5-TBRL1-35/C5S3-35 | RIO-200 | Spare_DO_35 | Spare | Spare Reserve Channel | - | - | 24VDC Discrete | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1430 | C5 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 36 | DC-1(+) | +24VDC | +24VDC | +24VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 24VDC Discrete | - | - | - | - | COMMON | -
1431 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1 | i RTN-0 | P5-TBAI1-1(B) | C5S4-1/P5-TBAI1-1(B) | P5-TBAI1-1(B)/C5S4-1 | RIO-200 | EXT-BIILER_AI_1 | EXT-BIILER | External Boiler 4-20mA Interface | Process Field Device | - | 4-20mA Analog | - | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1432 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 2 | IN-0 | P5-TBAI1-1(A) | C5S4-2/P5-TBAI1-1(A) | P5-TBAI1-1(A)/C5S4-2 | RIO-200 | EXT-BIILER_AI_1 | EXT-BIILER | External Boiler 4-20mA Interface | Process Field Device | - | 4-20mA Analog | - | Industrial Process Equipment | Standard Process Field Device | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1433 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 3 | i RTN-1 | P5-TBAI1-2(B) | C5S4-3/P5-TBAI1-2(B) | P5-TBAI1-2(B)/C5S4-3 | RIO-200 | FT-913201_AI_1 | FT-913201 | Flow Transmitter | Coriolis Flow Transmitter | 325-01-913-PD-02 | 4 - 20 mA,Pulse | 0-1000kg/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1434 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 4 | IN-1 | P5-TBAI1-2(A) | C5S4-4/P5-TBAI1-2(A) | P5-TBAI1-2(A)/C5S4-4 | RIO-200 | FT-913201_AI_1 | FT-913201 | Flow Transmitter | Coriolis Flow Transmitter | 325-01-913-PD-02 | 4 - 20 mA,Pulse | 0-1000kg/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1435 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 5 | i RTN-2 | P5-TBAI1-3(B) | C5S4-5/P5-TBAI1-3(B) | P5-TBAI1-3(B)/C5S4-5 | RIO-200 | FT-913201_AI_2 | FT-913201 | Flow Transmitter | Coriolis Flow Transmitter | 325-01-913-PD-02 | 4 - 20 mA,Pulse | 0-1000kg/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1436 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 6 | IN-2 | P5-TBAI1-3(A) | C5S4-6/P5-TBAI1-3(A) | P5-TBAI1-3(A)/C5S4-6 | RIO-200 | FT-913201_AI_2 | FT-913201 | Flow Transmitter | Coriolis Flow Transmitter | 325-01-913-PD-02 | 4 - 20 mA,Pulse | 0-1000kg/hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1437 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 7 | i RTN-3 | P5-TBAI1-4(B) | C5S4-7/P5-TBAI1-4(B) | P5-TBAI1-4(B)/C5S4-7 | RIO-200 | FT-936201_AI_1 | FT-936201 | Flow Transmitter | Magnetic Flow Transmitter | 325-01-930-PD-01 | 4 - 20 mA,Pulse | 0-1000kg/m³ | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1438 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 8 | IN-3 | P5-TBAI1-4(A) | C5S4-8/P5-TBAI1-4(A) | P5-TBAI1-4(A)/C5S4-8 | RIO-200 | FT-936201_AI_1 | FT-936201 | Flow Transmitter | Magnetic Flow Transmitter | 325-01-930-PD-01 | 4 - 20 mA,Pulse | 0-1000kg/m³ | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1439 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 9 | RTN | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1440 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 10 | RTN | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1441 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 11 | i RTN-4 | P5-TBAI1-5(B) | C5S4-11/P5-TBAI1-5(B) | P5-TBAI1-5(B)/C5S4-11 | RIO-200 | FT-936202_AI_1 | FT-936202 | Flow Transmitter | Magnetic Flow Transmitter | 325-01-930-PD-02 | 4 - 20 mA,Pulse | 0 - 20 m3/ hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1442 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 12 | IN-4 | P5-TBAI1-5(A) | C5S4-12/P5-TBAI1-5(A) | P5-TBAI1-5(A)/C5S4-12 | RIO-200 | FT-936202_AI_1 | FT-936202 | Flow Transmitter | Magnetic Flow Transmitter | 325-01-930-PD-02 | 4 - 20 mA,Pulse | 0 - 20 m3/ hr | Endress+Hauser | Proline Series Flowmeter | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1443 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 13 | i RTN-5 | P5-TBAI1-6(B) | C5S4-13/P5-TBAI1-6(B) | P5-TBAI1-6(B)/C5S4-13 | RIO-200 | LT-913201_AI_1 | LT-913201 | Level Transmitter | Level transmitter | 325-01-913-PD-01 | 4 - 20 mA |  | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1444 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 14 | IN-5 | P5-TBAI1-6(A) | C5S4-14/P5-TBAI1-6(A) | P5-TBAI1-6(A)/C5S4-14 | RIO-200 | LT-913201_AI_1 | LT-913201 | Level Transmitter | Level transmitter | 325-01-913-PD-01 | 4 - 20 mA |  | Endress+Hauser | Cerabar PMP43 / PMP51B (Hydrostatic) | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1445 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 15 | i RTN-6 | P5-TBAI1-7(B) | C5S4-15/P5-TBAI1-7(B) | P5-TBAI1-7(B)/C5S4-15 | RIO-200 | PT-913201_AI_1 | PT-913201 | Pressure Transmitter | Pressure Transmitter | 325-01-913-PD-02 | 4 - 20 mA | 0 - 10 barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1446 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IN-6 | P5-TBAI1-7(A) | C5S4-16/P5-TBAI1-7(A) | P5-TBAI1-7(A)/C5S4-16 | RIO-200 | PT-913201_AI_1 | PT-913201 | Pressure Transmitter | Pressure Transmitter | 325-01-913-PD-02 | 4 - 20 mA | 0 - 10 barg | Endress+Hauser | Cerabar PMP51B / PMP43 | LiY-CY TP 1Px1.0 (Shielded Pair) | ACTIVE | -
1447 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 17 | i RTN-7 | P5-TBAI1-8(B) | C5S4-17/P5-TBAI1-8(B) | P5-TBAI1-8(B)/C5S4-17 | RIO-200 | XT-92201_AI_1 | XT-92201 | Speed / Position Transmitter | Gas detector | 325-01-923-PD-03 | 4 - 20 mA | 0-10%LEL | Industrial Process Equipment | Standard Process Field Device | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1448 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 18 | IN-7 | P5-TBAI1-8(A) | C5S4-18/P5-TBAI1-8(A) | P5-TBAI1-8(A)/C5S4-18 | RIO-200 | XT-92201_AI_1 | XT-92201 | Speed / Position Transmitter | Gas detector | 325-01-923-PD-03 | 4 - 20 mA | 0-10%LEL | Industrial Process Equipment | Standard Process Field Device | LiY-CY(EB) 1Px1.0 (Blue) | ACTIVE | Safety Barriers
1449 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 19 | i RTN-8 | P5-TBAI1-9(B) | C5S4-19/P5-TBAI1-9(B) | P5-TBAI1-9(B)/C5S4-19 | RIO-200 | XV-913201_AI_1 | XV-913201 | Control Valve Position Feedback | Automatic on/off valve | 325-01-913-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1450 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 20 | IN-8 | P5-TBAI1-9(A) | C5S4-20/P5-TBAI1-9(A) | P5-TBAI1-9(A)/C5S4-20 | RIO-200 | XV-913201_AI_1 | XV-913201 | Control Valve Position Feedback | Automatic on/off valve | 325-01-913-PD-02 | 24 VDC energized | On-Off | TeroFox / El-O-Matic | TF-20DFS Ball Valve + F-Actuator + ESV | CVV 3Cx1.5 (Solenoid) + CVV 4Cx1.0 (Limit Switches) | ACTIVE | -
1451 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 21 | i RTN-9 | P5-TBAI1-10(B) | C5S4-21/P5-TBAI1-10(B) | P5-TBAI1-10(B)/C5S4-21 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1452 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 22 | IN-9 | P5-TBAI1-10(A) | C5S4-22/P5-TBAI1-10(A) | P5-TBAI1-10(A)/C5S4-22 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1453 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 23 | i RTN-10 | P5-TBAI1-11(B) | C5S4-23/P5-TBAI1-11(B) | P5-TBAI1-11(B)/C5S4-23 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1454 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 24 | IN-10 | P5-TBAI1-11(A) | C5S4-24/P5-TBAI1-11(A) | P5-TBAI1-11(A)/C5S4-24 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1455 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 25 | i RTN-11 | P5-TBAI1-12(B) | C5S4-25/P5-TBAI1-12(B) | P5-TBAI1-12(B)/C5S4-25 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1456 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 26 | IN-11 | P5-TBAI1-12(A) | C5S4-26/P5-TBAI1-12(A) | P5-TBAI1-12(A)/C5S4-26 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1457 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 27 | RTN | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1458 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 28 | RTN | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | - | - | 4-20mA Analog | - | - | - | - | COMMON | -
1459 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 29 | i RTN-12 | P5-TBAI1-13(B) | C5S4-29/P5-TBAI1-13(B) | P5-TBAI1-13(B)/C5S4-29 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1460 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 30 | IN-12 | P5-TBAI1-13(A) | C5S4-30/P5-TBAI1-13(A) | P5-TBAI1-13(A)/C5S4-30 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1461 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 31 | i RTN-13 | P5-TBAI1-14(B) | C5S4-31/P5-TBAI1-14(B) | P5-TBAI1-14(B)/C5S4-31 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1462 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 32 | IN-13 | P5-TBAI1-14(A) | C5S4-32/P5-TBAI1-14(A) | P5-TBAI1-14(A)/C5S4-32 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1463 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 33 | i RTN-14 | P5-TBAI1-15(B) | C5S4-33/P5-TBAI1-15(B) | P5-TBAI1-15(B)/C5S4-33 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1464 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 34 | IN-14 | P5-TBAI1-15(A) | C5S4-34/P5-TBAI1-15(A) | P5-TBAI1-15(A)/C5S4-34 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1465 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 35 | i RTN-15 | P5-TBAI1-16(B) | C5S4-35/P5-TBAI1-16(B) | P5-TBAI1-16(B)/C5S4-35 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel
1466 | C5 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 36 | IN-15 | P5-TBAI1-16(A) | C5S4-36/P5-TBAI1-16(A) | P5-TBAI1-16(A)/C5S4-36 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | - | - | 4-20mA Analog | - | - | - | Reserved for Future Loop | SPARE | Spare Reserve Channel

## 03_Chassis_Slot_Directory
KALASIN ENGINEERING ¦ CHASSIS & SLOT HARDWARE DIRECTORY
Standardized 13-Slot Architecture (C1-C4) & 5-Slot Architecture (C5) Hardware Allocation Schedule
Chassis | Slot No | Slot Tag | Module Catalog | Signal Family | Terminal Block Type | Destination Area(s) | Total Channels | Active Points | Spare Points | Spare Margin %
C1 | 0 | C1S0 | 1756-L950TPSXT | CPU (Controller) | Integrated RJ45 / USB / SD | CA1 (Main Control Room) | 5 | 5 | 0 | 0.0%
C1 | 1 | C1S1 | 1756-EN4TR | COMM (EtherNet/IP) | Dual RJ45 1Gbps + USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | 0 | 0.0%
C1 | 2 | C1S2 | 1756-EN4TR | COMM (EtherNet/IP) | Dual RJ45 1Gbps + USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | 0 | 0.0%
C1 | 3 | C1S3 | 1756-EN4TR | COMM (EtherNet/IP) | Dual RJ45 1Gbps + USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | 0 | 0.0%
C1 | 4 | C1S4 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | CA1, JB-401 | 36 | 16 | 16 | 44.4%
C1 | 5 | C1S5 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-401 | 36 | 32 | 0 | 0.0%
C1 | 6 | C1S6 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-401, JB-601 | 36 | 12 | 20 | 55.6%
C1 | 7 | C1S7 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-601 | 36 | 23 | 9 | 25.0%
C1 | 8 | C1S8 | 1756-OB32 | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | CA1, JB-401 | 36 | 16 | 18 | 50.0%
C1 | 9 | C1S9 | 1756-OB32 | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | JB-401, JB-601 | 36 | 20 | 14 | 38.9%
C1 | 10 | C1S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-401 | 36 | 22 | 10 | 27.8%
C1 | 11 | C1S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-601 | 36 | 16 | 16 | 44.4%
C1 | 12 | C1S12 | 1756-N2 | EMPTY (Reserve Position) | Slot Blank Plate (Cover) | Unpopulated / Reserve | 1 | 0 | 0 | 0.0%
C2 | 0 | C2S0 | 1756-EN4TR | COMM (EtherNet/IP) | Dual RJ45 1Gbps + USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | 0 | 0.0%
C2 | 1 | C2S1 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-402 | 36 | 24 | 8 | 22.2%
C2 | 2 | C2S2 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-602 | 36 | 23 | 9 | 25.0%
C2 | 3 | C2S3 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-602, JB-607 | 36 | 29 | 3 | 8.3%
C2 | 4 | C2S4 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-607 | 36 | 32 | 0 | 0.0%
C2 | 5 | C2S5 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-607 | 36 | 20 | 12 | 33.3%
C2 | 6 | C2S6 | 1756-OB32 | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | JB-402, JB-602 | 36 | 12 | 22 | 61.1%
C2 | 7 | C2S7 | 1756-OB32 | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | JB-607 | 36 | 31 | 3 | 8.3%
C2 | 8 | C2S8 | 1756-OB32 | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | JB-607 | 36 | 9 | 25 | 69.4%
C2 | 9 | C2S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-402 | 36 | 14 | 18 | 50.0%
C2 | 10 | C2S10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-602 | 36 | 32 | 0 | 0.0%
C2 | 11 | C2S11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | CA1 | 36 | 0 | 32 | 88.9%
C2 | 12 | C2S12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | CA1 | 36 | 0 | 32 | 88.9%
C3 | 0 | C3S0 | 1756-EN4TR | COMM (EtherNet/IP) | Dual RJ45 1Gbps + USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | 0 | 0.0%
C3 | 1 | C3S1 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-606 | 36 | 4 | 28 | 77.8%
C3 | 2 | C3S2 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-612 | 36 | 17 | 15 | 41.7%
C3 | 3 | C3S3 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-618 | 36 | 12 | 20 | 55.6%
C3 | 4 | C3S4 | 1756-OB32 | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | JB-606, JB-612 | 36 | 16 | 18 | 50.0%
C3 | 5 | C3S5 | 1756-OB32 | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | JB-618 | 36 | 9 | 25 | 69.4%
C3 | 6 | C3S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-602, JB-606 | 36 | 30 | 2 | 5.6%
C3 | 7 | C3S7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-607 | 36 | 32 | 0 | 0.0%
C3 | 8 | C3S8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-607, JB-608 | 36 | 24 | 8 | 22.2%
C3 | 9 | C3S9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-612, JB-618 | 36 | 16 | 16 | 44.4%
C3 | 10 | C3S10 | 1756-N2 | EMPTY (Reserve Position) | Slot Blank Plate (Cover) | Unpopulated / Reserve | 1 | 0 | 0 | 0.0%
C3 | 11 | C3S11 | 1756-N2 | EMPTY (Reserve Position) | Slot Blank Plate (Cover) | Unpopulated / Reserve | 1 | 0 | 0 | 0.0%
C3 | 12 | C3S12 | 1756-OF8 | AO (4-20mA Analog Output) | 1756-TBNH (20-Pin RTB) | JB-402, JB-602, JB-607 | 20 | 5 | 3 | 15.0%
C4 | 0 | C4S0 | 1756-EN4TR | COMM (EtherNet/IP) | Dual RJ45 1Gbps + USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | 0 | 0.0%
C4 | 1 | C4S1 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | IS-JB-603, IS-JB-608 | 36 | 22 | 10 | 27.8%
C4 | 2 | C4S2 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | IS-JB-612 | 36 | 15 | 17 | 47.2%
C4 | 3 | C4S3 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | IS-JB-618 | 36 | 13 | 19 | 52.8%
C4 | 4 | C4S4 | 1756-OB32 | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | IS-JB-608, JB-618 | 36 | 1 | 33 | 91.7%
C4 | 5 | C4S5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | IS-JB-603, IS-JB-608 | 36 | 26 | 6 | 16.7%
C4 | 6 | C4S6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | IS-JB-612, IS-JB-618 | 36 | 22 | 10 | 27.8%
C4 | 7 | C4S7 | 1756-N2 | EMPTY (Reserve Position) | Slot Blank Plate (Cover) | Unpopulated / Reserve | 1 | 0 | 0 | 0.0%
C4 | 8 | C4S8 | 1756-N2 | EMPTY (Reserve Position) | Slot Blank Plate (Cover) | Unpopulated / Reserve | 1 | 0 | 0 | 0.0%
C4 | 9 | C4S9 | 1756-N2 | EMPTY (Reserve Position) | Slot Blank Plate (Cover) | Unpopulated / Reserve | 1 | 0 | 0 | 0.0%
C4 | 10 | C4S10 | 1756-N2 | EMPTY (Reserve Position) | Slot Blank Plate (Cover) | Unpopulated / Reserve | 1 | 0 | 0 | 0.0%
C4 | 11 | C4S11 | 1756-N2 | EMPTY (Reserve Position) | Slot Blank Plate (Cover) | Unpopulated / Reserve | 1 | 0 | 0 | 0.0%
C4 | 12 | C4S12 | 1756-N2 | EMPTY (Reserve Position) | Slot Blank Plate (Cover) | Unpopulated / Reserve | 1 | 0 | 0 | 0.0%
C5 | 0 | C5S0 | 1756-EN4TR | COMM (EtherNet/IP) | Dual RJ45 1Gbps + USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | 0 | 0.0%
C5 | 1 | C5S1 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | RIO-200 | 36 | 32 | 0 | 0.0%
C5 | 2 | C5S2 | 1756-IB32 | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | RIO-200 | 36 | 8 | 24 | 66.7%
C5 | 3 | C5S3 | 1756-OB32 | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | RIO-200 | 36 | 8 | 26 | 72.2%
C5 | 4 | C5S4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | RIO-200 | 36 | 18 | 14 | 38.9%
TOTAL HARDWARE CHANNELS ACROSS ALL SLOTS | [6 empty] | 1466 | 746 | 561 | 38.3%

## 04_Destination_JB_Matrix
KALASIN ENGINEERING ¦ FIELD ENCLOSURE & JUNCTION BOX I/O ALLOCATION MATRIX
Cross-Tabulation of Field Signals to Marshaling Cabinets, Local JBs & Intrinsically Safe (IS) Barrier Enclosures
Enclosure Tag | Enclosure Description / Location | Classification | DI (24VDC) | DO (24VDC) | AI (4-20mA) | AO (4-20mA) | Total Active Signals | Associated PLC Chassis | Suggested Field Trunk Cable
JB-607 | Spray Dryer Mid-Tower Junction Box (4th Fl) | Non-Ex / IP66 SS304 | 81 | 40 | 54 | 2 | 177 | C2, C3 | CVV 30Cx1.5 + LiY-CY 16Px0.75
JB-401 | Jet Cooker Main Field Junction Box | Non-Ex / IP66 SS304 | 50 | 24 | 22 | - | 96 | C1 | CVV 30Cx1.5 + LiY-CY 16Px0.75
JB-602 | Spray Dryer Cyclone & Exhaust Junction Box | Non-Ex / IP66 SS304 | 23 | 3 | 58 | 2 | 86 | C2, C3 | CVV 30Cx1.5 + LiY-CY 16Px0.75
RIO-200 | Slurry Building Remote I/O Cabinet (2nd Floor) | Slurry Prep Plant RIO | 40 | 8 | 18 | - | 66 | C5 | 1Gbps DLR Ethernet Ring + Local Trunks
JB-601 | Spray Dryer Ground Floor Junction Box | Non-Ex / IP66 SS304 | 33 | 12 | 16 | - | 61 | C1 | CVV 30Cx1.5 Control Trunk
JB-402 | Jet Cooker Auxiliary Field Junction Box | Non-Ex / IP66 SS304 | 24 | 9 | 14 | 1 | 48 | C2, C3 | CVV 30Cx1.5 + LiY-CY 16Px0.75
JB-612 | Spray Dryer Upper Tower Junction Box (6th Fl) | Non-Ex / IP66 SS304 | 17 | 15 | 8 | - | 40 | C3 | CVV 30Cx1.5 + LiY-CY 16Px0.75
IS-JB-618 | Intrinsically Safe Junction Box (Packing Ex i) | ATEX Ex ia / Blue Terminals | 13 | - | 18 | - | 31 | C4 | LiY-CY(EB) 16Px0.75 Blue IS Trunk
JB-618 | Packing Tower Field Junction Box | Non-Ex / IP66 SS304 | 12 | 9 | 8 | - | 29 | C3 | CVV 30Cx1.5 + LiY-CY 16Px0.75
IS-JB-603 | Intrinsically Safe Junction Box (Ex i Loops) | ATEX Ex ia / Blue Terminals | 15 | - | 14 | - | 29 | C4 | LiY-CY(EB) 16Px0.75 Blue IS Trunk
IS-JB-608 | Intrinsically Safe Junction Box (Ex i Loops) | ATEX Ex ia / Blue Terminals | 7 | 1 | 12 | - | 20 | C4 | LiY-CY(EB) 16Px0.75 Blue IS Trunk
IS-JB-612 | Intrinsically Safe Junction Box (Ex i Loops) | ATEX Ex ia / Blue Terminals | 15 | - | 4 | - | 19 | C4 | LiY-CY(EB) 16Px0.75 Blue IS Trunk
JB-606 | Spray Dryer Filter Cleaning Junction Box | Non-Ex / IP66 SS304 | 4 | 1 | 4 | - | 9 | C3 | CVV 20Cx1.5 Control Trunk
JB-608 | Field Area Terminal Enclosure | Industrial IP66 | - | - | 2 | - | 2 | C3 | Standard Multi-core Trunk
CA1 (Main Control Room) | Field Area Terminal Enclosure | Industrial IP66 | - | - | - | - | 0 | C1 | Standard Multi-core Trunk
CA1 | Main Control Room Marshaling Cabinet MCP | Main Automation Cabinet CA1 | - | - | - | - | 0 | C1 | Internal Panel Wiring / Pre-wired Cables
CA1 / Field RIO (EtherNet/IP DLR Trunk) | Field Area Terminal Enclosure | Industrial IP66 | - | - | - | - | 0 | C2, C3, C4, C5 | Standard Multi-core Trunk
TOTAL ACTIVE SIGNALS BY ENCLOSURE |  |  | 334 | 122 | 252 | 5 | 713 | C1 - C5 | Plant-wide Field Cable Schedule

## 05_Instrument_Catalog_Ref
KALASIN ENGINEERING ¦ MASTER INSTRUMENT CATALOG & HARDWARE REFERENCE
Approved Manufacturer Equipment Series, Process Connections, Electrical Signals & Recommended Field Cables
Package / Equipment Category | Instrument Type | Manufacturer | Approved Product Series / Model | Process Connection | Electrical Standard / Power | Suggested Field Cable | Typical Process Service
CS-DS-01 Dust Analyzer | Particulate / Dust Transmitter | ENVEA / PCME | PCME QAL 991 | DN100 Flange w/ Purge Air | 4-20mA Output + Alarm Relay / 24VDC | LiY-CY TP 2Px1.0 + CVV 3Cx1.5 | Exhaust Duct / Baghouse Stack Monitoring
CS-DS-01 Combustible Gas | LEL Combustible Gas Detector | Sensidyne / SmartGas | 925FGD Explosionproof | 3/4" NPT Conduit Entry | 4-20mA + Alarm Relays / 24VDC | LiY-CY TP 2Px1.0 (Ex d) | Gas Burner Area LEL Safety Monitoring
CS-DS-01 pH Analyzer | pH Analytical Measuring Loop | Mettler Toledo | M300G2 4-Wire + InPro3250i | DN25 Weld-in Socket / InTrac 777P | 4-20mA HART + Relays / 24VDC | LiY-CY TP 2Px1.0 + CVV 3Cx1.5 | Slurry Neutralization & Jet Cooker Feed pH
CS-DS-02 Diff Pressure Gauge | Diff. Pressure Indicator | Ashcroft | Model 1132 | 1/4" NPT Female w/ V03 Manifold | Local Mechanical Dial | None (Mechanical) | Filter Bag / Basket Strainer Differential DP
CS-DS-03 Diff Pressure Xmtr | Diff. Pressure Transmitter | Endress+Hauser | Deltabar PMD55B | 1/4" NPT w/ 5-Valve Manifold DA63M | 2-wire 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded) | Steam Filter & Baghouse Vent DP Monitoring
CS-DS-04 Flow Meter (Coriolis) | Mass Flow & Density Meter | Endress+Hauser | Promass F 300 / 83F | Flange ASME B16.5 Cl.150 RF | 4-20mA HART + Pulse / 24VDC | LiY-CY TP 3Px1.0 + CVV 3Cx1.5 | Jet Cooker Slurry & Condensed Milk Mass Flow
CS-DS-05 Flow Meter (Mag) | Electromagnetic Flowmeter | Endress+Hauser | Promag W 400 / 50W | Flange ASME B16.5 Cl.150 | 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded) | Water Feed, CIP Supply & Condensate Flow
CS-DS-06 Flow Meter (Thermal) | Thermal Mass Gas Flowmeter | Endress+Hauser | t-mass F 300 / I 300 | Flange Cl.150 or 1" NPT | 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded) | Combustion Air & Natural Gas Burner Flow
CS-DS-07 Flow Switch | Thermal / Paddle Flow Switch | Endress+Hauser | Flowswitch DCH / FSL | Thread 1/2" NPT / Clamp | 24VDC Dry Contact Relay | CVV 3Cx1.5 Control Cable | Cooling Water / Slurry Flow Low Alarm
CS-DS-08 Level Radar (80GHz) | Continuous Non-Contact Radar | Endress+Hauser | Micropilot FMR67B | Flange DN80 3" / Cl.150 | 2-wire 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Ex ia/tb) | Spray Dryer Powder Chamber & Silo Level
CS-DS-09 Level Hydrostatic | Hydrostatic Level Transmitter | Endress+Hauser | Cerabar PMP43 / PMP51B | Universal Hygienic Clamp | 2-wire 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded) | Slurry Feed Tank & Buffer Vessel Level
CS-DS-10 Level Switch (Solids) | Vibrating Fork for Powders | Endress+Hauser | Soliphant FTM51 | Thread 1-1/2" NPT / Flange | 24VDC Relay Contact Output | CVV 3Cx1.5 Control Cable | Powder Silo / Cyclone High Level Interlock
CS-DS-11 Level Switch (Liquids) | Vibrating Fork for Liquids | Endress+Hauser | Liquiphant FTL51B | Thread 3/4" NPT / Tri-Clamp | 24VDC Relay Contact Output | CVV 3Cx1.5 Control Cable | Slurry Tank High/Low Overflow Protection
CS-DS-12 Pressure Transmitter | Gauge / Absolute Pressure | Endress+Hauser | Cerabar PMP51B / PMP43 | 1/2" NPT Male / Tri-Clamp | 2-wire 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded) | Jet Cooker Steam Header & Slurry Line Pressure
CS-DS-13 Pressure Gauge | All Stainless Pressure Gauge | Ashcroft | Model T5500 | 1/2" NPT w/ 1098 Siphon | Local Mechanical Dial | None (Mechanical) | Field Local Dial Indication
CS-DS-14 Pressure Switch | Electronic Pressure Switch | Endress+Hauser | Ceraphant PTC31B | 1/2" NPT Male Thread | 24VDC Dry Contact Relay / PNP | CVV 3Cx1.5 Control Cable | Compressed Air Header Low Pressure Alarm
CS-DS-15 Temperature RTD | Pt100 RTD Sensor + Head Xmtr | Endress+Hauser | iTEMP TMT71 / TM411 | 1/2" NPT w/ Thermowell | 2-wire 4-20mA HART / 24VDC | LiY-CY TP 1Px1.0 (Shielded) | Jet Cooker Tube & Spray Dryer Air Temp
CS-DS-16 Thermometer | Bimetal Dial Thermometer | Ashcroft | Model FI Bimetal | 1/2" NPT Threaded Thermowell | Local Mechanical Dial | None (Mechanical) | Field Local Dial Indication
CS-DS-17 Control Valve (Globe) | Globe Control Valve + Positioner | Samson | Type 3241 + Trovis 3730-1 | Flange ASME B16.5 Cl.150/300 | 4-20mA Setpoint + 4-20mA Feedback | LiY-CY TP 2Px1.0 Shielded | Main Steam PRV, Temperature & Cooker Control
CS-DS-18 On/Off Ball Valve | Pneumatic Automated Ball Valve | TeroFox / El-O-Matic | TF-20DFS + F-Actuator + ESV | Flange Cl.150 RF / 1/4" Air Port | 24VDC Solenoid + 2x DI Limit Switches | CVV 3Cx1.5 + CVV 4Cx1.0 | Process Routing, CIP Isolation & Steam Stop
CS-DS-19 Limit Switch Box | Rotary Valve Position Monitor | APL-HKC | APL-210N / APL-510N | NAMUR VDI/VDE 3845 Direct Mount | Dry Contact SPDT Micro-switches | CVV 4Cx1.0 Control Cable | Valve Full Open / Full Close Feedback to PLC
CS-DS-20 Rupture Disk Sensor | Burst-Alert Membrane Monitor | BS&B / Fike | Burst-Alert Sensor | Cl.150 Flange Holder | Dry Contact NC Loop (DI) | LiY-CY(EB) 1Px1.0 (Ex ia) | Spray Dryer Explosion Vent Burst Detection