## Rev.3
PROJECT SPRINT 18K TPA SPRAY DRYER IN THAILAND
|  |  |  | INSTRUMENT I/O LIST | [10 empty] | AEC Industrial Engineering Co., Ltd.
Ingredion (Thailand) Co., Ltd. | [12 empty] | DATE |  | 02 OCT 2026 |  | REV.
[13 empty] | DOC.NO. |  | Instrument I/O List |  | 3.6
Item. | Tag. No. | New Tag. No. | P&ID No. | Description | Instrument | PLC Signal |  |  |  |  | Signal type | Signal to | Range | Function | Cable Type | Type of Protection | Remark
[5 empty] | Name | DO | DI | AO | AI | Bus
MAIN PLC/ SCADA
1 | AT-60241 | AT-60241 | 325-01-602-PD-05 | Dust Analyzer Transmitter for Exhaust Duct (DTEX-22) | Dust Analyzer Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 5000 mg | 0 - 100% |  | - | -
2 | DPT-60901 | DPT-60201 | 325-01-602-PD-09 | Steam filter pressure | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0-1 barg | 0 - 100% |  | - | -
3 | DPT-61301 | DPT-61301 | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 500 mBar./0 - 100% |  | Ex t/d | Safety Barriers
4 | DPT-61302 | DPT-61302 | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 500 mBar./0 - 100% |  | Ex t/d | Safety Barriers
5 | DPT-61310 | DPT-61310 | 325-01-613-PD-03 | Vent filter pressure | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 0-250 mbarg / 0 - 100% |  | Ex t/d | Safety Barriers
6 | DPT-61312 | DPT-61312 | 325-01-613-PD-05 | Vent filter pressure | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 0-250 mbarg / 0 - 100% |  | Ex t/d | Safety Barriers
7 | DPT-60202 | DPT-60202 | 325-01-602-PD-08 | Gas Pressure Differential Transmitter for Air Filter (FICA-31) | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 500 mBar | 0 to1000 |  | - | -
8 | DPT-60203 | DPT-60203 | 325-01-602-PD-03 | Gas Pressure Differential Transmitter for Air Filter (FICA-21) | Differential Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 500 mBar | 0-100 mbarg / 0 - 100% |  | - | -
9 |  | FSL-20201 | 325-01-202-PD-01 | Slurry low flow | Flow Switch | - | 1 | - | - | - | Dry Contact | PLC |  | n/a |  | - | Jet Cooker
10 |  | FSL-40201 | 325-01-402-PD-01 | Slurry low flow | Flow Switch | - | 1 | - | - | - | Dry Contact | PLC |  | n/a |  | - | Jet Cooker
11 |  | FSL-40202 | 325-01-402-PD-01 | Slurry low flow | Flow Switch | - | 1 | - | - | - | Dry Contact | PLC |  | n/a |  | - | Jet Cooker
12 |  | FS-40204 | 325-01-402-PD-01 | Jet Cooker | Flow Switch | - | 1 | - | - | - | Dry Contact | PLC |  | n/a |  | - | Jet Cooker
13 |  | FS-40205 | 325-01-402-PD-02 | Jet Cooker | Flow Switch | - | 1 | - | - | - | Dry Contact | PLC |  | n/a |  | - | Jet Cooker
14 | FT-40201 | FT-40201 | 325-01-402-PD-02 | Slurry flowrate & density check transfer line | Coriolis Flow Transmitter | - | 1 | - | 2 | - | 4 - 20 mA,Pulse | PLC | 0-15 m³/hr | Flow rate |  | - | -
15 | FT-40202 | FT-40202 | 325-01-402-PD-02 | Feed Slurry Flow Transmitter for Pipe (PIPE) | Magnetic Flow Transmitter | - | 1 | - | 1 | - | 4 - 20 mA,Pulse | PLC | 0 to 8,000 m³/hr | 0 - 100% |  | - | -
16 |  | FT-40221 | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter | - | 1 | - | 2 | - | 4 - 20 mA,Pulse | PLC | 0-6 m³/hr | Flow rate |  | - | Jet Cooker
17 |  | FT-40222 | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter | - | 1 | - | 2 | - | 4 - 20 mA,Pulse | PLC | 0-850 kg/hr | Flow rate |  | - | Jet Cooker
18 | FT-60221 | FT-60221 | 325-01-602-PD-04 | Cool air Flow | Thermal Mass Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 2500 m3/h | n/a |  | - | -
19 | FT-60201 | FT-60201 | 325-01-602-PD-08 | Gas Flow Transmitter for Cooling Conveying Cold Air Duct (DTCA-32) | Thermal Mass Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 70000 m3/h | 0 - 100% |  | - | -
20 | FT-60210 | FT-60210 | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) | Thermal Mass Flow Transmitter | - | - | - | 2 | - | 4 - 20 mA | PLC | 126000 m3/h | 0 - 100% |  | - | -
21 | FT-60211 | FT-60211 | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) | Thermal Mass Flow Transmitter | - | - | - | 2 | - | 4 - 20 mA | PLC | 126000 m3/h | 0 - 100% |  | - | -
22 | FT-60261FA | FT-60261FA | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #1 (AMTV-11A) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
23 | FT-60261FB | FT-60261FB | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #2 (AMTV-11A) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
24 | FT-60261FC | FT-60261FC | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #3 (AMTV-11A) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
25 | FT-60261FD | FT-60261FD | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #4 (AMTV-11A) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
26 | FT-60262FE | FT-60262FE | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #5 (AMTV-11B) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
27 | FT-60262FF | FT-60262FF | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #6 (AMTV-11B) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
28 | FT-60262FG | FT-60262FG | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #7 (AMTV-11B) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
29 | FT-60262FH | FT-60262FH | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #8 (AMTV-11B) | Ultrasonic Flow Transmitter | - | - |  | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
30 | FT-60263FJ | FT-60263FJ | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #9 (AMTV-11C) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
31 | FT-60263FK | FT-60263FK | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #10 (AMTV-11C) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
32 | FT-60263FL | FT-60263FL | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #11 (AMTV-11C) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
33 | FT-60263FM | FT-60263FM | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #12 (AMTV-11C) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
34 | FT-60264FN | FT-60264FN | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #13 (AMTV-11D) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
35 | FT-60264FP | FT-60264FP | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #14 (AMTV-11D) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
36 | FT-60264FQ | FT-60264FQ | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #15 (AMTV-11D) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
37 | FT-60264FR | FT-60264FR | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #16 (AMTV-11D) | Ultrasonic Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% |  | - | -
38 | FT-61307 | FT-61307 | 325-01-613-PD-04 | Compressed air Flow | Thermal Mass Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 1000 m3/hr | 0 - 100% |  | - | -
39 | FT-60901 | FT-60203 | 325-01-602-PD-09 | Culinary steam feed to Spray dryer | Vortex Flow Transmitter | - | 1 | - | 1 | - | 4 - 20 mA | PLC | 0 - 7000 kg/hr | 0 - 100% |  | - | -
40 | FT-60902 | FT-60202 | 325-01-602-PD-09 | Steam feed to Spray dryer | Vortex Flow Transmitter | - | 1 | - | 1 | - | 4 - 20 mA | PLC | 0 - 2000 kg/hr | 0 - 100% |  | - | -
41 | FT-61101 | FT-60204 | 325-01-602-PD-10 | Compressed air Flow | Thermal Mass Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 1000 m3/hr | 0 - 100% |  | - | -
42 | FT-90301 | FT-936201 | 325-01-930-PD-01 | Process Water | Magnetic Flow Transmitter | - | 1 | - | 1 | - | 4 - 20 mA,Pulse | PLC | 0-1000kg/m³ | Flow rate |  | - | -
43 | FT-93001 | FT-936202 | 325-01-930-PD-02 | Process Water | Magnetic Flow Transmitter | - | 1 | - | 1 | - | 4 - 20 mA,Pulse | PLC | 0 - 20 m3/ hr | 0 - 100% |  | - | -
44 | HS-61307A | HS-61307A | 325-01-613-PD-03 | Start/Stop | Hand Switch | - | 2 | - | - | - | Dry Contact | PLC |  |  |  | Ex d | -
45 | HS-61307B | HS-61307B | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
46 | HS-61307C | HS-61307C | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
47 | HS-61307D | HS-61307D | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
48 | HS-61307E | HS-61307E | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
49 | HS-61307F | HS-61307F | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
50 | HS-61307G | HS-61307G | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
51 | HS-61307H | HS-61307H | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
52 | HS-61307I | HS-61307I | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
53 | HS-61307J | HS-61307J | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
54 | HS-61307K | HS-61307K | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
55 | HS-61307L | HS-61307L | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
56 | HS-61307M | HS-61307M | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
57 | HS-61307N | HS-61307N | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
58 | HS-61307O | HS-61307O | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
59 | HS-61307P | HS-61307P | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
60 | HS-61307Q | HS-61307Q | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
61 | HS-61307R | HS-61307R | 325-01-613-PD-03 | Start/Stop | Hand Switch |  |  |  |  | - | Dry Contact | PLC |  |  |  | Ex d | -
62 | HV-4106 | HV-40203 | 325-01-402-PD-01 | Slurry Drain tank TS-40201 | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | - | -
63 | HV-4108 | HV-40201 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | - | -
64 | HV-4126 | HV-40204 | 325-01-402-PD-01 | Slurry Drain tank TS-40202 | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | - | -
65 | HV-4128 | HV-40202 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | - | -
66 | HV-4208 | HV-40206 | 325-01-402-PD-01 | Slurry Drain tank TS-40203 | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | - | -
67 | HV-4210 | HV-40205 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | - | -
68 |  | HV-40207 | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | - | Jet Cooker
69 |  | HV-40208 | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close |  | - | Jet Cooker
70 | LSH-60230 | LSH-60230 | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-21) | Level switch |  | 1 |  |  | - | Dry Contact | PLC |  | Detected " high" / Overfill |  | Ex t/d | Safety Barriers
71 | LSH-60231 | LSH-60231 | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-22) | Level switch |  | 1 |  |  | - | Dry Contact | PLC |  | Detected " high" / Overfill |  | Ex t/d | Safety Barriers
72 | LSH-60240 | LSH-60240 | 325-01-602-PD-05 | Powder Level Switch High for Bag House (BGHS-21) | Level switch |  | 1 |  |  | - | Dry Contact | PLC |  | Detected " high" / Overfill |  | Ex t/d | Safety Barriers
73 | LSH-60250 | LSH-60250 | 325-01-602-PD-05 | Water Level Switch High for Fire Deluge Pipe (FWDP-21) | Level switch |  | 1 |  |  | - | Dry Contact | PLC |  | Detected " high" / Overfill |  | - | -
74 | LSH-60251 | LSH-60251 | 325-01-602-PD-04 | Water Level Switch High for Fire Deluge Pipe (FWDP-22) | Level switch |  | 1 |  |  | - | Dry Contact | PLC |  | Detected " high" / Overfill |  | - | -
75 | LSL-61101 | LSL-60201 | 325-01-602-PD-11 | Level low switch | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " Low " / Run dry protection |  | - | -
76 | LSH-61301 | LSH-61301 | 325-01-613-PD-01 | Level alarm high | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " Full " / Overfill |  | Ex t/d | Safety Barriers
77 | LSL-61302 | LSL-61302 | 325-01-613-PD-01 | Level alarm low | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " Low " / Overfill |  | Ex t/d | Safety Barriers
78 | LS-61303 | LS-61303 | 325-01-613-PD-01 | Level switch | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " high" / Overfill |  | Ex t/d | Safety Barriers
79 | LSH-61304 | LSH-61304 | 325-01-613-PD-03 | Big bag level alarm high | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill |  | Ex t/d | Safety Barriers
80 | LSH-61305 | LSH-61305 | 325-01-613-PD-05 | Big bag level alarm high | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill |  | Ex t/d | Safety Barriers
81 | LSH-61306 | LSH-61306 | 325-01-613-PD-01 | Level alarm high | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill |  | Ex t/d | Safety Barriers
82 |  | LSH-61307 | 325-01-613-PD-01 | High Level alarm reject screen | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill |  | Ex t/d | Safety Barriers
83 |  | LSH-61308 | 325-01-613-PD-01 | High Level alarm Cooling cyclone | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill |  | Ex t/d | Safety Barriers
84 | LSH-61312 | LSH-61312 | 325-01-613-PD-05 | Level alarm high | Level switch | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill |  | Ex t/d | Safety Barriers
85 | LSL-81001 | LSL-814201 | 325-01-814-PD-01 | Low Level alarm |  | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " Low " / Overfill |  | Ex t/d | Safety Barriers
86 | LT-40101 | LT-40201 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 1 | Level transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 m. | 0 - 100% |  | - | -
87 | LT-40102 | LT-40202 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 2 | Level transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 m. | 0 - 100% |  | - | -
88 | LT-40201 | LT-40203 | 325-01-402-PD-02 | Level transmitter in Spray dryer infeed tank | Level transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 m. | 0 - 100% |  | - | -
89 | LT-61301 | LT-61301 | 325-01-613-PD-01 | Level powder in silo | Level transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 0 - 100% |  | Ex ia | Safety Barriers
90 | pHT-40101 | pHT-40201 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 1 | pH Analyzer | - | 1 | - | 1 | - | 4 - 20 mA | PLC | 0-14 | 0 - 100% |  | - | -
91 | pHT-40102 | pHT-40202 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 2 | pH Analyzer | - | 1 | - | 1 | - | 4 - 20 mA | PLC | 0-14 | 0 - 100% |  | - | -
92 | PSL-60220 | PSL-60220 | 325-01-602-PD-04 | Gas Pressure Switch Low for Spray Chamber (CHAM-21) | Pressure switch |  | 1 |  |  | - | Dry Contact | Hard Wired to MCC FANE-21 | -0.01 mbar | 0 to (- 20,000) Pa |  | - | -
93 |  | PSL-61301 | 325-01-613-PD-01 | Pressure alarm low | Pressure switch | - | 1 | - | - | - | Dry Contact | PLC | 0.3-0.7barg | 1 barg / Under pressure |  | - | -
94 | PSL-61302 | PSL-61302 | 325-01-613-PD-01 | Pressure alarm low | Pressure switch | - | 1 | - | - | - | Dry Contact | PLC | 40 mbarg | 1 barg / Under pressure |  | - | -
95 | PSL-61305 | PSL-61305 | 325-01-613-PD-03 | Pressure alarm low | Pressure switch | - | 1 | - | - | - | Dry Contact | PLC |  | 1 barg / Under pressure |  | - | -
96 | PSL-61306 | PSL-61306 | 325-01-613-PD-05 | Pressure alarm low | Pressure switch | - | 1 | - | - | - | Dry Contact | PLC |  | 1 barg / Under pressure |  | - | -
97 | PSL-61311 | PSL-61311 | 325-01-613-PD-04 | Pressure alarm low | Pressure switch | - | 1 | - | - | - | Dry Contact | PLC |  | 1 barg / Under pressure |  | - | -
98 | PT-40201 | PT-40201 | 325-01-402-PD-02 | Pressure Transmitter for Inlet Filter Strainer (FSTR-11) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 500 mBar | 0-250 mbarg / 0 - 100% |  | - | -
99 | PT-40202 | PT-40202 | 325-01-402-PD-02 | Feed Slurry Pressure Transmitter for Pipe (PIPE) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 10'barg | 0 to 500 |  | - | -
100 |  | PT-40222 | 325-01-402-PD-02 | Jet Cooker | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 12'barg | 0 to 500 |  | - | Jet Cooker
101 | PT-60201 | PT-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 20 bar | Control Pressure |  | - | -
102 | PT-60202 |  | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 to 500 bar | 0-100% |  | - | -
103 | PT-60203 | PT-60203 | 325-01-602-PD-08 | Gas Pressure Transmitter for Cool Air Duct (DTCA-32) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% |  | - | -
104 | PT-60210 | PT-60210 | 325-01-602-PD-03 | Gas Pressure Transmitter for Hot Air Duct (DTHA-21) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% |  | - | -
105 | PT-60215 | PT-60215 | 325-01-602-PD-03 | 15% Polypropylene Glycol Pressure Indicator Transmitter for Heat Recovery Pumping Skid (PUCF-21) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 6 bar | 0-100% |  | - | -
106 | PT-60216 | PT-60216 | 325-01-602-PD-03 | Gas Pressure Transmitter for Combustion Air Burner Duct (DTCB-21) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 100 mbar | 0-100% |  | - | -
107 | PT-60220 | PT-60220 | 325-01-602-PD-04 | Gas Pressure Transmitter for Chamber (CHAM-21) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | -100 - 100 mbar | 0-100% |  | Ex ic | Safety Barriers
108 | PT-60221 | PT-60221 | 325-01-602-PD-04 | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% |  | - | -
109 | PT-60230 | PT-60230 | 325-01-602-PD-04 | Gas Pressure Transmitter for Conveying Duct (DTCO-21) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% |  | Ex ic | Safety Barriers
110 | PT-60231 | PT-60231 | 325-01-602-PD-04 | Gas Pressure Transmitter for Cyclone Exhaust Duct (DTCE-21) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% |  | Ex ic | Safety Barriers
111 | PT-60240 | PT-60240 | 325-01-602-PD-05 | Gas Pressure Transmitter for Bag House Exhaust Duct (DTEX-22) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% |  | - | -
112 | PT-60241 | PT-60241 | 325-01-602-PD-05 | Gas Pressure Transmitter for Exhaust Fan (FANE-21) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% |  | - | -
113 | PT-61101 | PT-60204 | 325-01-602-PD-10 | Pressure transmitter | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 barg | 0-100% |  | - | -
114 | PT-61301 | PT-61301 | 325-01-613-PD-01 | Pressure in silo | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 1 barg | 0-100% |  | Ex ic | Safety Barriers
115 | PT-61302 | PT-61302 | 325-01-613-PD-03 | Pressure in vacuum line | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 - 100 mbarg | 0-100% |  | - | -
116 | PT-61303 | PT-61303 | 325-01-613-PD-01 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% |  | Ex ic | Safety Barriers
117 | PT-61304 | PT-61304 | 325-01-613-PD-01 | Gas Pressure Transmitter for Storage Bin Cyclone Inlet Duct (CYCL-31) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% |  | Ex ic | Safety Barriers
118 | PT-61305 | PT-61305 | 325-01-613-PD-01 | Gas Pressure Transmitter for Exhaust Duct (DTEX-31) | Pressure Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% |  | Ex ic | Safety Barriers
119 | PT-61309 | PT-61309 | 325-01-613-PD-04 | Pressure transmitter | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 barg | 0 - 8 barg / 0-100% |  | - | -
120 | PV-60201 | PCV-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic Control valve | - | - | 1 | - | - | 4 - 20 mA | PLC | 0 - 100% | Position O/C./0 - 100% |  | - | -
121 | SV-40101 | SV-40201 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 1 | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
122 | SV-40102 | SV-40202 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 2 | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
123 | SV-40103 | SV-40203 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 1 | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
124 | SV-40104 | SV-40204 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 2 | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
125 | SV-60220 | SV-60220 | 325-01-602-PD-04 | PA On/Off Valve for Chamber PSE purge air (CHAM-21) | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
126 | SV-60230 | SV-60230 | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 27 (CYCL-21) | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
127 | SV-60231 | SV-60231 | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 28 (CYCL-22) | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
128 | SV-60240A | SV-60240A | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29A (BGHS-21) | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
129 | SV-60240B | SV-60240B | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29B (BGHS-21) | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
130 | SV-60240C | SV-60240C | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29C (BGHS-21) | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
131 | SV-61301 | SV-61301 | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve | - | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
132 | SV-61302 | SV-61302 | 325-01-613-PD-01 | Air service | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
132 |  | SV-61306 | 325-01-613-PD-01 | Air service | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
133 | SV-61303 | SV-61303 | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve | - | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
134 | SV-61305 | SV-61305 | 325-01-613-PD-01 | Air service | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
135 | SV-61308 | SV-61308 | 325-01-613-PD-03 | Timer compress air pluse solenoid valve | Solenoid valve | - | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
136 | SV-61309 | SV-61309 | 325-01-613-PD-03 | Air service | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
137 | SV-61310 | SV-61310 | 325-01-613-PD-05 | Timer compress air pluse solenoid valve | Solenoid valve | - | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
138 | SV-61311 | SV-61311 | 325-01-613-PD-05 | Air service | Solenoid valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
139 | TSH-60230 | TSH-60230 | 325-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | Temperature Switch |  | 1 |  |  | - | Dry Contact | PLC | 0 - 140 C | 140 |  | Ex d | Switch มี 2 contact เข้า PLC กับ Fire Deluge
140 | TSH-60240 | TSH-60240 | 325-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | Temperature Switch |  | 1 |  |  | - | Dry Contact | PLC | 0 - 140 C | 140 |  | Ex d | Switch มี 2 contact เข้า PLC กับ Fire Deluge
141 |  | TT-40221 | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 120 C | 0 - 300 C |  | - | Jet Cooker
142 |  | TT-40222 | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 200 C | 0 - 300 C |  | - | Jet Cooker
143 | TT-60201 | TT-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 300 C | 0 - 300 C |  | - | -
144 | TT-60210 | TT-60210 | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | - | -
145 | TT-60212A | TT-60210A | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 100 C | 0 to 150 |  | - | -
146 | TT-60212B | TT-60210B | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 100 C | 0 to 150 |  | - | -
147 | TT-60211 | TT-60211 | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | - | -
148 | TT-60214 | TT-60214 | 325-01-602-PD-03 | Steam Temperature Transmitter for Cold Air Duct (DTCA-23) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | -10 to 250°C | -10 to 250 |  | - | -
149 | TT-60215A | TT-60215A | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | -10 to 150°C | -10 to 150 |  | - | -
150 | TT-60215B | TT-60215B | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | -10 to 150°C | -10 to 150 |  | - | -
151 | TT-60216 | TT-60216 | 325-01-602-PD-03 | Gas Temperature Transmitter for Combustion Air Burner Duct (DTCB-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 200'°C | 0 to 200 |  | - | -
152 | TT-60220 | TT-60220 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic | Safety Barriers
153 | TT-60221 | TT-60221 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic | Safety Barriers
154 | TT-60222 | TT-60222 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic | Safety Barriers
155 | TT-60223 | TT-60223 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic | Safety Barriers
156 | TT-60224 | TT-60224 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic | Safety Barriers
157 | TT-60225 | TT-60225 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic | Safety Barriers
158 | TT-60226 | TT-60226 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic | Safety Barriers
159 | TT-60227 | TT-60227 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic | Safety Barriers
160 | TT-60230 | TT-60230 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Conveying Duct (DTCO-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic | Safety Barriers
161 | TT-60240 | TT-60240 | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Fan (FANE-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | - | -
162 | TT-60241A | TT-60241A | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 100 C | 0 to 150 |  | - | -
163 | TT-60241B | TT-60241B | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 100 C | 0 to 150 |  | - | -
164 | TT-60245 | TT-60245 | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Stack (DTXS-21) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | -10 to 150°C | -10 to 150 |  | - | -
165 | TT-60702 | TT-60202 | 325-01-602-PD-07 | Compress air temp to camera | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 40 C | Control Temperature |  | - | -
166 | TT-61301 | TT-61301 | 325-01-613-PD-01 | Gas Temperature Transmitter for Cold Air Duct (DTCA-32) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic | Safety Barriers
167 | TT-61302 | TT-61302 | 325-01-613-PD-01 | Gas and Powder Temperature Transmitter for Cooling Cyclone (CYCL-31) | Temperature Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 |  | Ex ic | Safety Barriers
168 |  | TCV-40222 | 325-01-402-PD-02 | Jet Cooker | Automatic Control valve | - | - | 1 | - | - | 4 - 20 mA | PLC | 0 - 100% | Command |  | - | Jet Cooker
169 | TV-60214 | TCV-60214 | 325-01-602-PD-03 | Steam Temperature Valve for Pre-Heat Steam Heat Exchanger (HXCH-21) | Automatic Control valve | - | - | 1 | - | - | 4 - 20 mA | PLC | 0 - 100% | Command |  | - | -
170 | TV-60702 | TCV-60202 | 325-01-602-PD-07 | Chiller water control valve | 3-way Control valve | - | - | 1 |  | - | 4 - 20 mA | PLC | 0 - 100% | Position O/C./0 - 100% |  | - | -
171 | VT-60210A | VT-60210A | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | mm/sec | 0 to 15 |  | - | -
172 | VT-60210B | VT-60210B | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | mm/sec | 0 to 15 |  | - | -
173 | VT-60241A | VT-60241A | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | mm/sec | 0 to 15 |  | - | -
174 | VT-60241B | VT-60241B | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter |  |  |  | 1 | - | 4 - 20 mA | PLC | mm/sec | 0 to 15 |  | - | -
175 | XT-60301 | XT-60201 | 325-01-402-PD-03 | LEL gas analyzer | Gas detector | - | - | - | 1 | - | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% |  | Ex ic | Safety Barriers
176 | XA-60301 | XA-60201 | 325-01-402-PD-03 | LEL gas Buzzer Alarm | Gas detector | 1 | - | - |  | - | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% |  | Ex ic | Safety Barriers
177 | XT-92201 | XT-92201 | 325-01-923-PD-03 | LEL gas analyzer | Gas detector | - | - | - | 1 | - | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% |  | Ex ic | Safety Barriers
178 | XA-92201 | XA-92201 | 325-01-923-PD-03 | LEL gas Buzzer Alarm | Gas detector | 1 | - | - |  | - | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% |  | Ex ic | Safety Barriers
179 | XV-40101A | XV-40201A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
180 | XV-40101B | XV-40201B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
181 | XV-40101C | XV-40201C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
182 | XV-40101D | XV-40201D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
183 | XV-40101E | XV-40201E | 325-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
184 | XV-40101F | XV-40201F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
185 | XV-40101G | XV-40201G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
186 | XV-40101H | XV-40201H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
187 | XV-40102A | XV-40202A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
188 | XV-40102B | XV-40202B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
189 | XV-40102C | XV-40202C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
190 | XV-40102D | XV-40202D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
191 | XV-40102E | XV-40202E | 325-01-402-PD-01 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
192 | XV-40102F | XV-40202F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
193 | XV-40102G | XV-40202G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
194 | XV-40102H | XV-40202H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
195 | XV-40201B | XV-40203B | 325-01-402-PD-02 | Slurry feed-out Spray dryer infeed tank | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
196 | XV-40201C | XV-40203C | 325-01-402-PD-02 | Water washing line outlet Spray dryer infeed tank | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
197 | XV-40201D | XV-40203D | 325-01-402-PD-02 | CIP water washing Spray dryer infeed tank | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
198 | XV-40201E | XV-40203E | 325-01-402-PD-02 | CIP hight pressure water washing Spray dryer infeed tank | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
199 |  | XV-40203F | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | Jet Cooker
200 |  | XV-40204B | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | Jet Cooker
201 |  | XV-40204C | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | Jet Cooker
202 |  | XV-40205A | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | Jet Cooker
203 |  | XV-40205B | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | Jet Cooker
204 |  | XV-40205C | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | Jet Cooker
205 |  | XV-40205D | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | Jet Cooker
206 |  | XV-40205F | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | Jet Cooker
207 |  | XV-40222 | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | Jet Cooker
208 | XV-60201 | XV-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
209 | XV-60251 | XV-60251 | 325-01-602-PD-01 | Liquid On/Off Valve for Drain Pipe (PIPE) | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
210 | XV-60301 | XV-60214 | 325-01-602-PD-03 | Steam feed to Spray dryer | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
211 | XV-61101 | XV-60202 | 325-01-602-PD-11 | High Pressure Water On/Off Valve for Drain Pipe | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | - | -
212 | HV-61301 | XV-61301 | 325-01-613-PD-01 | Product feed-out Packing silo | Automatic on/off valve | - | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | Ex d | -
213 | XV-61302 | XV-61302 | 325-01-613-PD-02 | Dust collector feed vent | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | Ex d | -
214 | XV-61303 | XV-61303 | 325-01-613-PD-02 | Dust collector feed from packer | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | Ex d | -
215 |  | DV-61301 | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61301 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | Ex d | -
216 |  | DV-61302 | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61302 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C |  | Ex d | -
217 | ZS-60201A | ZS-60201A | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
218 | ZS-60201B | ZS-60201B | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
219 | ZS-60201C | ZS-60201C | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
220 | ZS-60201D | ZS-60201D | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
221 | ZS-60201E | ZS-60201E | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
222 |  | ZS-60229 | 325-01-602-PD-04 | Limit Switch for CY-60230 (Door Service) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
223 |  | ZS-60230 | 325-01-602-PD-04 | Limit Switch for CY-60231 (Door Service) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
224 | ZS-60231A | ZS-60231A | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Spectacle Inserted) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
225 | ZS-60231B | ZS-60231B | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Blind Inserted) | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
226 | ZS-60231C | ZS-60231C | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Spool Inserted) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
227 | ZS-60231D | ZS-60231D | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Blind Inserted) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
228 | ZS-60231E | ZS-60231E | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Spool Inserted) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
229 | ZS-60231F | ZS-60231F | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Blind Inserted) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
230 |  | ZS-60240 | 325-01-602-PD-05 | Limit Switch for FA-60240 (Door Service) | Limit Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
231 | ZS-61310 | ZS-61310 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a |  | Ex ic | Safety Barriers
232 | ZS-61311 | ZS-61311 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic | Safety Barriers
233 | ZS-61312 | ZS-61312 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic | Safety Barriers
234 | ZS-61313 | ZS-61313 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic | Safety Barriers
235 |  |  |  | Lototo-01 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
236 |  |  |  | Lototo-02 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
237 |  |  |  | Lototo-03 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
238 |  |  |  | Lototo-04 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
239 |  |  |  | Lototo-05 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
240 |  |  |  | Lototo-06 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
241 |  |  |  | Lototo-07 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
242 |  |  |  | Lototo-08 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
243 |  |  |  | Lototo-09 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
244 |  |  |  | Lototo-10 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
245 |  |  |  | Lototo-11 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
246 |  |  |  | Lototo-12 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active
246 |  | ES-60201 |  | Emergency stop activated @ Spray Nozzle 7th Floor | E-Stop Swtich | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  |  | Emergency Function
246 |  | ES-60202 |  | Emergency stop activated @ Sight glass 6th Floor | E-Stop Swtich | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  |  | Emergency Function
246 |  | ES-60203 |  | Emergency stop activated @ Control Room | E-Stop Swtich | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  |  | Emergency Function
246 |  | ES-61301 |  | Emergency stop activated @ SC-61301,SC-61302 | E-Stop Swtich | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  |  | Emergency Function
247 | DEDERT SUPPLY EQUIPMENT
248 | FT-60701 | FT-60207 | 325-01-602-PD-07 | Instr. Air Flow Transmitter for Camera #4 (ACAM-21) | Flow Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC
249 | PT-60701 | PT-60207 | 325-01-602-PD-07 | Instr. Air Pressure Transmitter for Camera #4 (ACAM-21) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC
250 | SV-60240D | XV-60240D | 325-01-602-PD-05 | PA On/Off Valve for Bag House Tank Valve (BGHS-21) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off
251 | SV-60701 | SV-60207 | 325-01-602-PD-07 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) | On/Off Valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off
252 | SV-60201 | SV-60201 | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) | On/Off Valve | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off
|  | SSL-60201 | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-21) | Low Speed Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off
|  | ZS-60201 | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-21/ RV-60201) Casing Closed | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off
253 | SV-60202 | SV-60202 | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off
|  | SSL-60202 | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-22) | Low Speed Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off
|  | ZS-60202 | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-22/ RV-60202) Casing Closed | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off
254 | SV-60203 | SV-60203 | 325-01-602-PD-08 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off
|  | SSL-60203 | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-23) | Low Speed Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off
|  | ZS-60203 | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-23/ RV-60203) Casing Closed | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off
255 | SV-61304 | SV-61304 | 325-01-613-PD-01 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off
|  | SSL-61304 | 325-01-613-PD-01 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-31) | Low Speed Switch | - | 1 | - | - | - | Switch PNP | PLC | On-Off
|  | ZS-61304 | 325-01-613-PD-01 | Position - Rotary Valve (RVAL-31/ RV-61304) Casing Closed | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off
256 | TT-60701 | TT-60207 | 325-01-602-PD-07 | Instr. Air Temperature Transmitter for Air Manifold - Camera #4 (ACAM-21) | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC
257 | XV-60261FA | XV-60261FA | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
258 | XV-60261FB | XV-60261FB | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
259 | XV-60261FC | XV-60261FC | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
260 | XV-60261FD | XV-60261FD | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
261 | XV-60261SA | XV-60261SA | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
262 | XV-60261SB | XV-60261SB | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
263 | XV-60261SC | XV-60261SC | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
264 | XV-60261SD | XV-60261SD | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
265 | XV-60262FE | XV-60262FE | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
266 | XV-60262FF | XV-60262FF | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
267 | XV-60262FG | XV-60262FG | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
268 | XV-60262FH | XV-60262FH | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
269 | XV-60262SE | XV-60262SE | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
270 | XV-60262SF | XV-60262SF | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
271 | XV-60262SG | XV-60262SG | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
272 | XV-60262SH | XV-60262SH | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
273 | XV-60263FJ | XV-60263FJ | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
274 | XV-60263FK | XV-60263FK | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
275 | XV-60263FL | XV-60263FL | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
276 | XV-60263FM | XV-60263FM | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
277 | XV-60263SJ | XV-60263SJ | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
278 | XV-60263SK | XV-60263SK | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
279 | XV-60263SL | XV-60263SL | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
280 | XV-60263SM | XV-60263SM | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
281 | XV-60264FN | XV-60264FN | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
282 | XV-60264FP | XV-60264FP | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
283 | XV-60264FQ | XV-60264FQ | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
284 | XV-60264FR | XV-60264FR | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
285 | XV-60264SN | XV-60264SN | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
286 | XV-60264SP | XV-60264SP | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
287 | XV-60264SQ | XV-60264SQ | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
288 | XV-60264SR | XV-60264SR | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
289 |  | XV-60261DA | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11A | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
290 |  | XV-60262DE | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11B | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
291 |  | XV-60263DN | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11C | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
292 |  | XV-60264DJ | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11D | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C
293 | XV-60241 | XV-60241 | 325-01-602-PD-05 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off
294 | XV-60240 | XV-60240 | 325-01-602-PD-08 | Powder On/Off Valve for Diverter Valve (DVTR-21) | On/Off Valve | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off
295 | Machine Equipment Supply
296 | PSE-61300 | PSE-61300 | 325-01-613-PD-01 | Explosion Vent PSE-61300 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic | Safety Barriers
297 | PSE-61301 | PSE-61301 | 325-01-613-PD-01 | Explosion Vent PSE-61301 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic | Safety Barriers
298 | ISV-61302 | ISV-61302 | 325-01-613-PD-01 | Explosion isolation flap valve ISV-61302 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic | Safety Barriers
299 | PSE-61302 | PSE-61302 | 325-01-613-PD-03 | Explosion Vent PSE-61302 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic | Safety Barriers
300 | PSE-61303 | PSE-61303 | 325-01-613-PD-05 | Explosion Vent PSE-61303 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic | Safety Barriers
301 | PSE-61304 | PSE-61304 | 325-01-613-PD-01 | Explosion Vent PSE-61304 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic | Safety Barriers
302 | PSV-61301A | ZS-61306 | 325-01-613-PD-01 | Position Brether Valve High Pressure PSV-61301 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic | Safety Barriers
303 | PSV-61301B | ZS-61307 | 325-01-613-PD-01 | Position Brether Valve Vacuum Pressure PSV-61301 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic | Safety Barriers
304 | ISV-61303 | ISV-61303 | 325-01-613-PD-03 | Explosion isolation flap valve ISV-61303 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic | Safety Barriers
305 | ISV-61304 | ISV-61304 | 325-01-613-PD-05 | Explosion isolation flap valve ISV-61304 | Position switch | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active |  | Ex ic | Safety Barriers
306 | MCC ROOM
307 | ATY-40101 | AT-40201 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40201 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
308 | ATY-40102 | AT-40202 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40202 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
309 | ATY-40201 | AT-40203 | 325-01-402-PD-02 | Start / Stop Command for VSD AT-40203 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
310 | BFY-60210 | BF-60210 | 325-01-602-PD-03 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
311 | BFY-60211 | BF-60211 | 325-01-602-PD-03 | Start / Stop Command for VSD FANC-21 (Combustion Fan) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
312 | BFY-60240 | BF-60240 | 325-01-602-PD-05 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
313 | BFY-60220 | BF-60220 | 325-01-602-PD-04 | Start / Stop Command for VSD FANS-22 (Cooling Fan) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
314 | BFY-60206 | BF-60206 | 325-01-602-PD-08 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
315 | BFY-61301 | BF-61301 | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
316 | BFY-61302 | BF-61302 | 325-01-613-PD-05 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
317 | BFY-61303 | BF-61303 | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
318 | BLM-61302 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | เปลี่ยนไปจ่ายเป็น Power Feeder | - | - | - | - | - | 24 VDC energized | PLC | On-Off
319 | PCM-60205-B | PD-60202B | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Oil Pump ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
320 | PCM-60205-C | PD-60202C | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 1 ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
321 | PCM-60205-D | PD-60202D | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 2 ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
322 | PCM-60205-E | PD-60202E | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Main motor Fan ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
323 | PCY-40201 | PC-40203 | 325-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
324 | PCY-40101 | PC-40201 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40201 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
325 | PCY-40102 | PC-40202 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40202 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
326 |  | PD-40204 | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40204 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off |  |  | - | Jet Cooker
327 |  | PD-40205 | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40205 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off |  |  | - | Jet Cooker
328 | PCY-60205-A | PD-60202A | 325-01-602-PD-01 | Start / Stop Command for VSD PUPD-11 (Positive Displacement Pump ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
329 | PCY-60215 |  | 325-01-602-PD-03 | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
330 | PVM-61301 | BL-61301 | 325-01-613-PD-03 | Start / Stop Command for FVNR PV-61301 (Vacuum Cleaning Fan) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
331 | RVM-60201 |  | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
332 | RVM-60202 |  | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
333 | RVM-60203 |  | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
334 | RVM-60204 |  | 325-01-602-PD-08 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
335 | RVM-61301 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61301 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
336 | RVM-61302 |  | 325-01-613-PD-03 | Start / Stop Command for FVNR RV-61302 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
337 | RVM-61303 |  | 325-01-613-PD-05 | Start / Stop Command for FVNR RV-61303 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
338 | RVM-61304 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61304 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
339 | RVM-61305 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61305 |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
340 | SCM-61301 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61301 (Sifter ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
341 | SCM-61302 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61302 (Sifter ) |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off
342 | B&B Packing
343 | XA-61301A | XA-61301A | 325-01-613-PD-02 | Request filter plant (Fugitive) | Request filter plant | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
344 | XA-61301B | XA-61301B | 325-01-613-PD-02 | Request material transport | Request material transport | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
345 | XA-61301C | XA-61301C | 325-01-613-PD-02 | Request belt plant | Request belt plant | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
346 | XA-61301D | XA-61301D | 325-01-613-PD-02 | Machine in operation | Machine in operation | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
347 | XA-61301E | XA-61301E | 325-01-613-PD-02 | General Fault | General Fault | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
348 | XA-61301F | XA-61301F | 325-01-613-PD-02 | Machine is ready | Machine is ready | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
349 | XA-61301G | XA-61301G | 325-01-613-PD-02 | Emergency stop activated | Emergency stop activated | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
350 | XA-61301H | XA-61301H | 325-01-613-PD-02 | Silo minimum | Silo minimum | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
351 | XA-61301J | XA-61301J | 325-01-613-PD-02 | Silo maximum | Silo maximum | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
352 | XS-61301A | XS-61301A | 325-01-613-PD-02 | Filter plant in operation | Filter plant in operation | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
353 | XS-61301B | XS-61301B | 325-01-613-PD-02 | Material transport in operation | Material transport in operation | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
354 | XS-61301C | XS-61301C | 325-01-613-PD-02 | Belt plant in operation | Belt plant in operation | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
355 | XS-61301D | XS-61301D | 325-01-613-PD-02 | Sequence Stop | Sequence Stop | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
356 | XS-61301E | XS-61301E | 325-01-613-PD-02 | Status from Customer Emergency stop | Status from Customer Emergency stop | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
357 | XS-61301F | XS-61301F | 325-01-613-PD-02 | Operation Release | Operation Release | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
358 |  |  | 325-01-613-PD-02 | Spare |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
359 |  |  | 325-01-613-PD-02 | Spare |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
360 |  |  | 325-01-613-PD-02 | Spare |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
361 |  |  | 325-01-613-PD-02 | Communication Signal |  | - | - | - | - | 1 | Communication Signal | PLC | On-Off |  |  | - | -
362 | Boiler
363 |  | XA-92201B | 325-01-922-PD-03 | Boiler common alarm |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | Recheck
363 |  | XA-92201C | 325-01-922-PD-03 | Boiler Trip |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | Recheck
363 |  | XA-92212B | 325-01-922-PD-03 | Burner Trip |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | Recheck
363 |  | XL-92201B | 325-01-922-PD-03 | Boiler Operate |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | Recheck
363 |  | XL-92201C | 325-01-922-PD-03 | Remote Setpoint Activated |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | Recheck
363 |  | ZL-92201 | 325-01-922-PD-03 | Remote Setpoint Status |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | Recheck
363 |  |  | 325-01-922-PD-03 | Communication Signal |  | - | - | - | - | 1 | Communication Signal | PLC | On-Off |  |  | - | Recheck
Bin Vent Filter (FA-61301)
363 |  | XA-FA-61301A | 325-01-613-PD-01 | Start / Stop Command for FA-61301 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
364 |  | XA-FA-61301B | 325-01-613-PD-01 | Compress air low (Spare) |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
365 |  | XS-FA-61301 | 325-01-613-PD-01 | Alarm 1 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
Fugitive Dust Filter (FA-61310)
363 |  | XA-FA-61310A | 325-01-613-PD-01 | Start / Stop Command for FA-61310 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
364 |  | XA-FA-61310B | 325-01-613-PD-01 | Compress air low (Spare) |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
365 |  | XS-FA-61310 | 325-01-613-PD-01 | Alarm 1 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
Vacuum Cleaner Filter (FA-61311)
363 |  | XA-FA-61311A | 325-01-613-PD-03 | Start / Stop Command for FA-61311 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
364 |  | XA-FA-61311B | 325-01-613-PD-03 | Compress air low (Spare) |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
365 |  | XS-FA-61311 | 325-01-613-PD-03 | Alarm 1 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
Local Exhaust Ventilation Filter (FA-61312)
363 |  | XA-FA-61312A | 325-01-613-PD-05 | Start / Stop Command for FA-61311 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
364 |  | XA-FA-61312B | 325-01-613-PD-05 | Compress air low (Spare) |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
365 |  | XS-FA-61312 | 325-01-613-PD-05 | Alarm 1 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
362 | Bag Filter Control Panel (FA-60240)
363 | XS-60240A | XS-60240A | 325-01-602-PD-05 | Start / Stop Command for BGHS-21 (Bag House Air Pulsing) |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
364 | XS-60240B | XS-60240B | 325-01-602-PD-05 | Fan Command for BGHS-21 (Bag House Air Pulsing) |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
365 | XA-60240A | XA-60240A | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
366 | XA-60240B | XA-60240B | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
367 | DPI-60240 |  | 325-01-602-PD-05 | Gas Pressure Differntial Pressure (Bag House Air Pulsing) |  | - | - | - | 1 | - | 4 - 20 mA | PLC |  |  |  | - | -
368 | HTRE-21 Heater Control Panel (TRACING)
369 | XS-60241A | XS-60241A | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | Waiting
370 | XA-60241A | XA-60241A | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | Waiting
371 | XA-60241B | XA-60241B | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | Waiting
372 | TSH-60241A | TSH-60241A | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch |  | 1 |  |  | - | Dry Contact | Heat Control Panel (HTRE-21) | 0 - 100 C | 140 |  | Ex d | Waiting
373 | TSL-60241B | TSL-60241B | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch |  | 1 |  |  | - | Dry Contact | Heat Control Panel (HTRE-21) | 0 - 100 C | 140 |  | Ex d | Waiting
374 | HTRE-22 Heater Control Panel (TRACING)
375 | XS-60242A | XS-60242A | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | Waiting
376 | XA-60242A | XA-60242A | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | Waiting
377 | XA-60242B | XA-60242B | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | Waiting
378 | TSH-60242A | TSH-60242A | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch |  | 1 |  |  | - | Dry Contact | Heat Control Panel (HTRE-22) | 0 - 100 C | 140 |  | Ex d | Waiting
379 | TSL-60242B | TSL-60242B | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch |  | 1 |  |  | - | Dry Contact | Heat Control Panel (HTRE-22) | 0 - 100 C | 140 |  | Ex d | Waiting
380 | HTRE-23 Heater Control Panel (TRACING)
381 | XS-60243A | XS-60243A | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | Waiting
382 | XA-60243A | XA-60243A | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | Waiting
383 | XA-60243B | XA-60243B | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | Waiting
384 | TSH-60243A | TSH-60243A | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch |  | 1 |  |  | - | Dry Contact | Heat Control Panel (HTRE-23) | 0 - 100 C | 140 |  | Ex d | Waiting
385 | TSL-60243B | TSL-60243B | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch |  | 1 |  |  | - | Dry Contact | Heat Control Panel (HTRE-23) | 0 - 100 C | 140 |  | Ex d | Waiting
386 | Air Heater Burner Control Panel (PK-60210)
387 | XA-FH-60210A | XA-FH-60210A | 325-01-602-PD-06 | BMS PANEL POWER ON for AHTR-21 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
388 | XA-FH-60210B | XA-FH-60210B | 325-01-602-PD-06 | BMS Burner High Fire Purge for AHTR-21 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
389 | XA-FH-60210C | XA-FH-60210C | 325-01-602-PD-06 | BMS Burner On for AHTR-21 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
390 | XA-FH-60210D | XA-FH-60210D | 325-01-602-PD-06 | BMS BMS Lockout for AHTR-21 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
391 | XA-FH-60210E | XA-FH-60210E | 325-01-602-PD-06 | BMS Remote Modet for AHTR-21 |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
392 | XS-FH-60210A | XS-FH-60210A | 325-01-602-PD-06 | Burner Remote Start for AHTR-21 |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
393 | XS-FH-60210B | XS-FH-60210B | 325-01-602-PD-06 | Dryer Interlocks for AHTR-21 |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
394 | XS-FH-60210C | XS-FH-60210C | 325-01-602-PD-06 | Remote Reset for AHTR-21 |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
395 | XS-FH-60210D | XS-FH-60210D | 325-01-602-PD-06 | Spare |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
396 |  | XS-FH-60210E | 325-01-602-PD-06 | Exhaust fan run status BF-60240 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
397 |  | XS-FH-60210F | 325-01-602-PD-06 | Supply fan run status BF-60210 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
398 |  | XS-FH-60210G | 325-01-602-PD-06 | Combusion fan run status BF-60211 |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
399 | TI-FH-60210 | TI-FH-60210 | 325-01-602-PD-06 | Gas Burner Firing Rate Temp Signal |  | - | - | - | 1 | - | 4 - 20 mA | PLC | On-Off |  |  | - | -
400 | UY-FH-60210A | UY-FH-60210A | 325-01-602-PD-06 | Comb fan VFD Speed Control |  | - | - | - | 1 | - | 4 - 20 mA | PLC | On-Off |  |  | - | -
401 | UY-FH-60210B | UY-FH-60210B | 325-01-602-PD-06 | Demand Signal |  | - | - | 1 | - | - | 4 - 20 mA | PLC | On-Off |  |  | - | -
402 | COM-FH-60210B | COM-FH-60210B | 325-01-602-PD-06 | Communication Signal |  | - | - | - | - | 1 | Modbus RTU | PLC |  |  |  | - | -
403 | TE-60212 | TE-60212 |  | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Element | [5 empty] | T/C Type K | AHTR Control Panel(HCP) |  |  |  | - | -
404 | DPHL-60230 | DPHL-60230 |  | Gas Pressure Differntial Switch Low for Exhaust Fan (FANE-21) | Pressure Differntial Switch Low | [5 empty] | Dry Contact | AHTR Control Panel(HCP) |  |  |  | - | -
405 | DPSL-60211 | DPSL-60211 |  | Gas Pressure Differential Switch Low for Combustion Fan (FANC-21) | Pressure Differential Switch Low | [5 empty] | Dry Contact | AHTR Control Panel(HCP) |  |  |  | - | -
406 | FCV-60211B | FCV-60211B |  | Gas Flow Control Damper (Valve) for Burner Combustion Air Duct (DTCB-21) | Flow Control Damper (Valve) | [5 empty] | Internal wiring | AHTR Control Panel(HCP) |  |  |  | - | -
407 | ZT-60211B | ZT-60211B |  | Gas Position Transmitter for Combustion Air Damper Actuator (DTCB-21) | Position Transmitter | [5 empty] | Internal wiring | AHTR Control Panel(HCP) |  |  |  | - | -
408 | ZSL-60211B | ZSL-60211B |  | Gas Position Switch Low for Combustion Air Damper Actuator (DTCB-21) | Position Switch Low | [5 empty] | Internal wiring | AHTR Control Panel(HCP) |  |  |  | - | -
409 | ZSH-60211B | ZSH-60211B |  | Gas Position Switch High for Combustion Air Damper Actuator (DTCB-21) | Position Switch High | [5 empty] | Internal wiring | AHTR Control Panel(HCP) |  |  |  | - | -
410 | VJ-01 (24VDC) | VJ-01 (24VDC) |  | Valve train J-BOX | Control Box | [5 empty] | Internal wiring | AHTR Control Panel(HCP) |  |  |  | - | -
411 | VJ-01 (220VAC) | VJ-01 (220VAC) |  | Valve train J-BOX | Control Box | [5 empty] | Internal wiring | AHTR Control Panel(HCP) |  |  |  | - | -
412 | UJ-01 (24VDC) | UJ-01 (24VDC) |  | Valve train J-BOX | Control Box | [5 empty] | Internal wiring | AHTR Control Panel(HCP) |  |  |  | - | -
413 | UJ-01 (220VAC) | UJ-01 (220VAC) |  | Valve train J-BOX | Control Box | [5 empty] | Internal wiring | AHTR Control Panel(HCP) |  |  |  | - | -
414 | PV-60210A | PV-60210A |  | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | [5 empty] | Internal wiring | AHTR Control Panel
415 | PV-60210B | PV-60210B |  | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | [5 empty] | Internal wiring | AHTR Control Panel
416 | DPT-60210 | DPT-60210 |  | Gas Pressure Differential Switch Low for Main Supply Air Fan (FANS-21) | Pressure Differential Switch Low | [5 empty] | Internal wiring | AHTR Control Panel
417 | DPSL-60210B | DPSL-60210B |  | Gas Pressure Differential Switch Low for Air Heater (AHTR-21) | Pressure Differential Switch Low | [5 empty] | Internal wiring | AHTR Control Panel
418 | DPSH-60210C | DPSH-60210C |  | Gas Pressure Differential Switch High for Air Heater (AHTR-21) | Pressure Differential Switch High | [5 empty] | Internal wiring | AHTR Control Panel
419 | BE-60210A | BE-60210A |  | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | [5 empty] | Internal wiring | AHTR Control Panel
420 | BE-60210B | BE-60210B |  | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | [5 empty] | Internal wiring | AHTR Control Panel
421 | IX-60210A | IX-60210A |  | Gas Ignition Transformer for Air Heater (AHTR-21) | Ignition Transformer | [5 empty] | Internal wiring | AHTR Control Panel
422 | FCV-60210A | FCV-60210A |  | Gas Flow Control Valve for Air Heater Gas Train (GTRN-21) | Flow Control Valve | [5 empty] | Internal wiring | AHTR Control Panel
423 | ZSL-60210A | ZSL-60210A |  | Gas Position Switch Low for Air Heater Gas Train (GTRN-21) | Position Switch Low | [5 empty] | Internal wiring | AHTR Control Panel
424 | ZT-60210A | ZT-60210A |  | Gas Position Transmitter for Air Heater Gas Train (GTRN-21) | Position Transmitter | [5 empty] | Internal wiring | AHTR Control Panel
425 | PSH-60210 | PSH-60210 |  | Gas Pressure Switch High for Air Heater Gas Train (GTRN-21) | Pressure Switch High | [5 empty] | Internal wiring | AHTR Control Panel
426 | BV-60210B | BV-60210B |  | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | [5 empty] | Internal wiring | AHTR Control Panel
427 | ZSO-60210B | ZSO-60210B |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | [5 empty] | Internal wiring | AHTR Control Panel
428 | ZSC-60210B | ZSC-60210B |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | [5 empty] | Internal wiring | AHTR Control Panel
429 | VV-60210 | VV-60210 |  | Gas Venting Valve (main gas) for Air Heater Gas Train (GTRN-21) | Venting Valve (main gas) | [5 empty] | Internal wiring | AHTR Control Panel
430 | ZSO-60210C | ZSO-60210C |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | [5 empty] | Internal wiring | AHTR Control Panel
431 | ZSC-60210C | ZSC-60210C |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | [5 empty] | Internal wiring | AHTR Control Panel
432 | PSL-60210 | PSL-60210 |  | Gas Pressure Switch Low for Air Heater Gas Train (GTRN-21) | Pressure Switch Low | [5 empty] | Internal wiring | AHTR Control Panel
433 | BV-60210A | BV-60210A |  | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | [5 empty] | Internal wiring | AHTR Control Panel
434 | ZSO-60210A | ZSO-60210A |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | [5 empty] | Internal wiring | AHTR Control Panel
435 | ZSC-60210A | ZSC-60210A |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | [5 empty] | Internal wiring | AHTR Control Panel
436 | High Pressure Pump (PD-60202)
437 | ES-60202 | XS-60202 | 325-01-602-PD-01 | E-Stop for PUPD-11 (Positive Displacement Pump ) | E-Stop |  | 1 |  |  |  | Dry Contact | PLC |  | n/a |  | - | -
438 |  | XA-60202 | 325-01-602-PD-01 | High Oil Pressure Alarm | Lamp | 1 |  |  |  |  | 24 VDC energized | PLC |  | n/a |  | - | -
439 | PT-60205 | PT-60202 | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC
440 | FS-60205 | FS-60202 | 325-01-602-PD-01 | Cooling Water Return Flow Switch for Positive Displacement Pump (PUPD-11) | Flow Switch | - | 1 | - | - | - |  | PLC |  |  |  | - | -
441 | XS-60205 | XS-60205 | 325-01-602-PD-01 | Start / Stop Command for PUPD-11 (Positive Displacement Pump ) | Start / Stop Command |  | - | - | - | - |  | PLC
442 | VS-60205 | VS-60202 | 325-01-602-PD-01 | Vibration Gear Box Vibration Switch for Switch Vibration for PUPD-11 (PUPD-11) | Vibration Switch | - | - | - | 1 | - | 4 - 20 mA | PLC
443 | XV-60205A | XV-60202A | 325-01-602-PD-01 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) | On/Off Valve | 1 | - | - | - | - | 24 VDC energized | PLC |  | Energized " Open" / Position O/C
444 |  | PS-60202 | 325-01-602-PD-01 | Oil Pressure Switch for Positive Displacement Pump (PUPD-11) | Flow Switch | - | 1 | - | - | - |  | PLC |  |  |  | - | -
445 |  | TT-60202A | 325-01-602-PD-01 | Temperature for Positive Displacement Pump (PUPD-11) | TC / Temperature Transmitter | - | - | - | 1 | - |  | PLC |  |  |  | - | Add Transmitter
446 |  | TT-60202B | 325-01-602-PD-01 | Temperature for Positive Displacement Pump (PUPD-11) | TC / Temperature Transmitter | - | - | - | 1 | - |  | PLC |  |  |  | - | Add Transmitter
447 | YA-60205 | YA-60205 | 325-01-602-PD-01 | Fault Command | [7 empty] | PLC
448 | YI-60205 | YI-60205 | 325-01-602-PD-01 | Run Command | [7 empty] | PLC
449 | Suppression Panel
450 | PSH-61301 | PSH-61301 | 325-01-613-PD-01 | Gas and Powder Pressure Switch High for Storage Bin Cyclone Inlet Duct (####-##) | Pressure Switch High | [6 empty] | Suppression Sys. Panel
451 | PSH-60220 | PSH-60220 | 325-01-602-PD-04 | Gas Pressure Switch High for Spray Chamber (CHAM-21) | Pressure Switch High | [6 empty] | Suppression Sys. Panel
452 | PSH-60230 | PSH-60230 | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-21) | Pressure Switch High | [6 empty] | Suppression Sys. Panel
453 | PSH-60231 | PSH-60231 | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-22) | Pressure Switch High | [6 empty] | Suppression Sys. Panel
454 | PSH-60224 | PSH-60224 | 325-01-602-PD-05 | Gas and Powder Pressure Switch High for Bag House (BGHS-21) | Pressure Switch High | [6 empty] | Suppression Sys. Panel
455 | XA-60202A | XA-60202A | 325-01-602-PD-08 | General Alarm Emergency Stop Actuation for XSUP-5601 (Supression Panel) | General Alarm Emergency Stop Actuation | - | 1 | - | - | - | Dry Contact | PLC | On-Off
456 | XA-60202B | XA-60202B | 325-01-602-PD-08 | General Fault Controlled Stop for XSUP-5601 (Supression Panel) | General Fault Controlled Stop | - | 1 | - | - | - | Dry Contact | PLC | On-Off
457 | XA-60202C | XA-60202C | 325-01-602-PD-08 | General Armed Status Indicator for XSUP-5601 (Supression Panel) | General Armed Status Indicator | - | 1 | - | - | - | Dry Contact | PLC | On-Off
458 | XA-60202D | XA-60202D | 325-01-602-PD-08 | Power Fault Status Indicator for XSUP-5601 (Supression Panel) | Power Fault Status Indicator | - | 1 | - | - | - | Dry Contact | PLC | On-Off
459 | XA-60202E | XA-60202E | 325-01-602-PD-08 | Dryer CHAM-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | Dryer CHAM-21 Emergency Stop Actuation | - | 1 | - | - | - | Dry Contact | PLC | On-Off
460 | XA-60202F | XA-60202F | 325-01-602-PD-08 | CHAM-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CHAM-21 Controlled Stop Trouble (No Protection) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
461 | XA-60202G | XA-60202G | 325-01-602-PD-08 | CYCL-21/22 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-21/22 Emergency Stop Actuation | - | 1 | - | - | - | Dry Contact | PLC | On-Off
462 | XA-60202H | XA-60202H | 325-01-602-PD-08 | CYCL-21/22 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-21/22 Controlled Stop Trouble (No Protection) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
463 | XA-60202J | XA-60202J | 325-01-602-PD-08 | BGHS-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | BGHS-21 Emergency Stop Actuation | - | 1 | - | - | - | Dry Contact | PLC | On-Off
464 | XA-60202K | XA-60202K | 325-01-602-PD-08 | BGHS-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | BGHS-21 Controlled Stop Trouble (No Protection) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
465 | XA-60202L | XA-60202L | 325-01-602-PD-08 | CYCL-31 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-31 Emergency Stop Actuation | - | 1 | - | - | - | Dry Contact | PLC | On-Off
466 | XA-60202M | XA-60202M | 325-01-602-PD-08 | CYCL-31 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-31 Controlled Stop Trouble (No Protection) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
467 | Fire Deluge PK-60221
468 | XA-60261 | XA-60221A | 325-01-602-PD-04 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Fire Deluge Fault (No Protection) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
469 | XA-60262 | XA-60221B | 325-01-602-PD-04 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Fire Deluge Alarm (Deluge Activated) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
470 | XS-60260 | XS-60221 | 325-01-602-PD-04 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off
139 |  | TSH-60230 | 325-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | Temperature Switch |  |  |  |  | - | Dry Contact | Fire Deluge Control Panel | 0 - 140 C | 140 |  |  | Switch มี 2 contact เข้า PLC กับ Fire Deluge
471 | Fire Deluge PK-60222
472 |  | XA-60222A | 325-01-602-PD-05 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Fire Deluge Fault (No Protection) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
473 |  | XA-60222B | 325-01-602-PD-05 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Fire Deluge Alarm (Deluge Activated) | - | 1 | - | - | - | Dry Contact | PLC | On-Off
474 |  | XS-60222 | 325-01-602-PD-05 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off
|  | XV-60240D | 325-01-602-PD-05 | Drain Valve |  | - | 1 | - | - | - | 24 VDC energized | PLC | On-Off |  |  |  | ส่งcommand เปิดวาวล์เข้า PLC ก่อน
140 |  | TSH-60240 | 325-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | Temperature Switch |  |  |  |  | - | Dry Contact | Fire Deluge Control Panel | 0 - 140 C | 140 |  |  | Switch มี 2 contact เข้า PLC กับ Fire Deluge
475 | Keaser Air Blower
476 |  | XS-61302 | 325-01-613-PD-01 | Start / Stop Command for Bin Aerator Blower | Start / Stop Command | 1 | - | - | - | - | Dry Contact | PLC | On-Off
477 |  | XA-61302A | 325-01-613-PD-01 | Operational / Running status |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off
478 |  | XA-61302B | 325-01-613-PD-01 | Local / Remote status |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off
479 |  | XA-61302C | 325-01-613-PD-01 | Fault / Trip condition |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off
480 |  | XA-61302D | 325-01-613-PD-01 | Warning condition |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off
481 | REMOTE I-O Area-200
482 | HV-2022 | HV-20204 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | - | -
483 | HV-2024 | HV-20205 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | - | -
484 | HV-2026 | HV-20206 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | - | -
485 | HV-2030 | HV-20207 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | - | -
486 | HV-2032 | HV-20208 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | - | -
487 | HV-2035 | HV-20209 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | - | -
488 | HV-2038 | HV-20210 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close |  | - | -
489 | XV-20201 | XV-20201 | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d | -
490 | XV-20202 | XV-20202 | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d | -
491 | XV-20203 | XV-20203 | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d | -
492 | XV-20211 | XV-20211 | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d | -
493 | XV-20212 | XV-20212 | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d | -
494 | XV-20213 | XV-20213 | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d | -
495 | LS-81001 | LS-814201 | 325-01-814-PD-01 | Level alarm low | Level switch | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Nondetected " Empty " / Overfill |  | Ex ic | Safety Barriers
496 | PCM-2030 | PC-20201 | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2030 |  | - | - | - | - | 1 | 24 VDC energized | RIO-200 | On-Off |  |  |  | Preparation area
497 | PCM-2031 |  | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2031 | ยกเลิก | 2 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off |  |  |  | Preparation area
498 | PCY-81001 | PC-814201 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81001 |  | - | - | - | - | 1 | 24 VDC energized | RIO-200 | On-Off |  |  |  | CIP
499 | PCY-81002 | PC-814202 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81002 |  | - | - | - | - | 1 | 24 VDC energized | RIO-200 | On-Off |  |  |  | CIP
500 | LPG Station
501 | FT-80301 | FT-913201 | 325-01-913-PD-02 | Flow outlet LPG line | Coriolis Flow Transmitter | - | 1 | - | 2 | - | 4 - 20 mA,Pulse | RIO-200 | 0-1000kg/hr | Flow rate |  | Ex d | -
502 | LT-80301 | LT-913201 | 325-01-913-PD-01 | Level LPG in storage | Level transmitter | - | - | - | 1 | - | 4 - 20 mA | RIO-200 |  | 0 - 100% |  | Ex ia | Safety Barriers
503 | PT-80302 | PT-913201 | 325-01-913-PD-02 | Pressure outlet LPG line | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | RIO-200 | 0 - 10 barg | 0 - 8 barg / 0-100% |  | Ex d | -
504 |  | XV-913201 | 325-01-913-PD-02 | Outlet LPG line | Automatic on/off valve | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C |  | Ex d | -
505 | Gas Vaporizer 4
506 | XA-80305A | XA-913201A | 325-01-913-PD-02 | Gas Vaporizer 4 Run Status | Gas vaporizer Ready | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
507 | XA-80305B | XA-913201B | 325-01-913-PD-02 | Gas Vaporizer 4 Alarm status | Gas vaporizer Run | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
508 | XA-80305C | XA-913201C | 325-01-913-PD-02 | Gas Vaporizer 4 High Temp Shut-Down status | Gas vaporizer Failed | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
509 | XA-80305D | XA-913201D | 325-01-913-PD-02 | Gas Vaporizer 4 Working Temp Shun-Off status | Gas vaporizer Overheated | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
510 | XA-80305E | XA-913201E | 325-01-913-PD-02 | Gas Vaporizer 4 Low Water Shun-Off status | Gas vaporizer Excessive flow tripped | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
512 | XS-80305A | XS-913201A | 325-01-913-PD-02 | Start Command for Gas Vaporizer 4 | Start Command | 1 | - | - | - | - | 24 VDC energized | RIO-200 | On-Off |  |  | - | -
512 | XS-80305B | XS-913201B | 325-01-913-PD-02 | Stop Command for Gas Vaporizer 4 | Stop Command | 1 | - | - | - | - | 24 VDC energized | RIO-200 | On-Off |  |  | - | -
513 | Gas Vaporizer 5
514 | XA-80306A | XA-913202A | 325-01-913-PD-02 | Gas Vaporizer 5 Run Status | Gas vaporizer Ready | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
515 | XA-80306B | XA-913202B | 325-01-913-PD-02 | Gas Vaporizer 5 Alarm status | Gas vaporizer Run | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
516 | XA-80306C | XA-913202C | 325-01-913-PD-02 | Gas Vaporizer 5 High Temp Shut-Down status | Gas vaporizer Failed | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
517 | XA-80306D | XA-913202D | 325-01-913-PD-02 | Gas Vaporizer 5 Working Temp Shun-Off status | Gas vaporizer Overheated | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
518 | XA-80306E | XA-913202E | 325-01-913-PD-02 | Gas Vaporizer 5 Low Water Shun-Off status | Gas vaporizer Excessive flow tripped | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
519 | XS-80306A | XS-913202A | 325-01-913-PD-02 | Start Command for Gas Vaporizer 5 | Start Command | 1 | - | - | - | - | 24 VDC energized | RIO-200 | On-Off |  |  | - | -
520 | XS-80306B | XS-913202B | 325-01-913-PD-02 | Stop Command for Gas Vaporizer 5 | Stop Command | 1 | - | - | - | - | 24 VDC energized | RIO-200 | On-Off |  |  | - | -
Note on B228: jaturong: เปลี่ยนชื่อจาก XV-61304
Note on C228: jaturong: เปลี่ยนชื่อจาก XV-61304
Note on G331: jaturong: Start/Stop
Note on H331: jaturong: RUN/Fault/Mode
Note on K331: jaturong: TCP/IP
Note on G358: jaturong: Start Stop
Note on H358: jaturong: Emer+Lototo Overload
Note on H359: jaturong: Emer+Lototo Overload
Note on H362: jaturong: Emer+Lototo Overload
Note on H363: jaturong: Emer+Lototo Overload

## All IO List by PLC Config
KALASIN ENGINEERING ¦ ALL MASTER INSTRUMENT I/O LIST CROSS-REFERENCED TO PLC SLOT CONFIGURATION
Client Master Instrument Schedule (Rev.3.6a) Mapped to ControlLogix 1756 Standardized PLC Hardware Slots (Rev.3.6a-R01)
Item No. | Original Tag | New Tag | Active Working Tag | P&ID No. | Description | Instrument Name | Signal Req. | Signal Range | Protection | PLC Status | PLC Chassis | PLC Slot | Module Catalog | Terminal Pin | PLC Wire Tag | Destination Area
1 | AT-60241 | AT-60241 | AT-60241 | 325-01-602-PD-05 | Dust Analyzer Transmitter for Exhaust Duct (DTEX-22) | Dust Analyzer Transmitter | AI | 5000 mg | - | MAPPED | C2 | C2S10 | 1756-IF16 | P2-TBAI2-1(B) | C2S10-1/P2-TBAI2-1(B) | JB-602
2 | DPT-60901 | DPT-60201 | DPT-60201 | 325-01-602-PD-09 | Steam filter pressure | Differential Pressure Transmitter | AI | 0-1 barg | - | MAPPED | C3 | C3S6 | 1756-IF16 | P3-TBAI1-15(B) | C3S6-33/P3-TBAI1-15(B) | JB-606
3 | DPT-61301 | DPT-61301 | DPT-61301 | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | AI |  | Ex t/d | MAPPED | C4 | C4S6 | 1756-IF16 | P4-TBAI2-5(B) | C4S6-11/P4-TBAI2-5(B) | IS-JB-618
4 | DPT-61302 | DPT-61302 | DPT-61302 | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | AI |  | Ex t/d | MAPPED | C4 | C4S6 | 1756-IF16 | P4-TBAI2-6(B) | C4S6-13/P4-TBAI2-6(B) | IS-JB-618
5 | DPT-61310 | DPT-61310 | DPT-61310 | 325-01-613-PD-03 | Vent filter pressure | Differential Pressure Transmitter | AI |  | Ex t/d | MAPPED | C4 | C4S6 | 1756-IF16 | P4-TBAI2-1(B) | C4S6-1/P4-TBAI2-1(B) | IS-JB-612
6 | DPT-61312 | DPT-61312 | DPT-61312 | 325-01-613-PD-05 | Vent filter pressure | Differential Pressure Transmitter | AI |  | Ex t/d | MAPPED | C4 | C4S6 | 1756-IF16 | P4-TBAI2-2(B) | C4S6-3/P4-TBAI2-2(B) | IS-JB-612
7 | DPT-60202 | DPT-60202 | DPT-60202 | 325-01-602-PD-08 | Gas Pressure Differential Transmitter for Air Filter (FICA-31) | Differential Pressure Transmitter | AI | -100 to 500 mBar | - | MAPPED | C1 | C1S11 | 1756-IF16 | P1-TBAI2-2(B) | C1S11-3/P1-TBAI2-2(B) | JB-601
8 | DPT-60203 | DPT-60203 | DPT-60203 | 325-01-602-PD-03 | Gas Pressure Differential Transmitter for Air Filter (FICA-21) | Differential Pressure Transmitter | AI | -100 to 500 mBar | - | MAPPED | C2 | C2S10 | 1756-IF16 | P2-TBAI2-2(B) | C2S10-3/P2-TBAI2-2(B) | JB-602
9 |  | FSL-20201 | FSL-20201 | 325-01-202-PD-01 | Slurry low flow | Flow Switch | DI |  | - | MISSING | - | - | - | - | - | -
10 |  | FSL-40201 | FSL-40201 | 325-01-402-PD-01 | Slurry low flow | Flow Switch | DI |  | - | MAPPED | C1 | C1S4 | 1756-IB32 | P1-TBDI1-17 | C1S4-19/P1-TBDI1-17 | JB-401
11 |  | FSL-40202 | FSL-40202 | 325-01-402-PD-01 | Slurry low flow | Flow Switch | DI |  | - | MAPPED | C1 | C1S4 | 1756-IB32 | P1-TBDI1-18 | C1S4-20/P1-TBDI1-18 | JB-401
12 |  | FS-40204 | FS-40204 | 325-01-402-PD-01 | Jet Cooker | Flow Switch | DI |  | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-1 | C2S1-1/P2-TBDI1-1 | JB-402
13 |  | FS-40205 | FS-40205 | 325-01-402-PD-02 | Jet Cooker | Flow Switch | DI |  | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-2 | C2S1-2/P2-TBDI1-2 | JB-402
14 | FT-40201 | FT-40201 | FT-40201 | 325-01-402-PD-02 | Slurry flowrate & density check transfer line | Coriolis Flow Transmitter | DI, AI | 0-15 m³/hr | - | MAPPED | C1 | C1S4 | 1756-IB32 | P1-TBDI1-19 | C1S4-21/P1-TBDI1-19 | JB-401
15 | FT-40202 | FT-40202 | FT-40202 | 325-01-402-PD-02 | Feed Slurry Flow Transmitter for Pipe (PIPE) | Magnetic Flow Transmitter | DI, AI | 0 to 8,000 m³/hr | - | MAPPED | C1 | C1S4 | 1756-IB32 | P1-TBDI1-20 | C1S4-22/P1-TBDI1-20 | JB-401
16 |  | FT-40221 | FT-40221 | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter | DI, AI | 0-6 m³/hr | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-3 | C2S1-3/P2-TBDI1-3 | JB-402
17 |  | FT-40222 | FT-40222 | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter | DI, AI | 0-850 kg/hr | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-4 | C2S1-4/P2-TBDI1-4 | JB-402
18 | FT-60221 | FT-60221 | FT-60221 | 325-01-602-PD-04 | Cool air Flow | Thermal Mass Flow Transmitter | AI | 2500 m3/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-2(B) | C3S7-3/P3-TBAI2-2(B) | JB-607
19 | FT-60201 | FT-60201 | FT-60201 | 325-01-602-PD-08 | Gas Flow Transmitter for Cooling Conveying Cold Air Duct (DTCA-32) | Thermal Mass Flow Transmitter | AI | 70000 m3/h | - | MAPPED | C1 | C1S11 | 1756-IF16 | P1-TBAI2-3(B) | C1S11-5/P1-TBAI2-3(B) | JB-601
20 | FT-60210 | FT-60210 | FT-60210 | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) | Thermal Mass Flow Transmitter | AI | 126000 m3/h | - | MAPPED | C3 | C3S6 | 1756-IF16 | P3-TBAI1-10(B) | C3S6-21/P3-TBAI1-10(B) | JB-602
21 | FT-60211 | FT-60211 | FT-60211 | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) | Thermal Mass Flow Transmitter | AI | 126000 m3/h | - | MAPPED | C3 | C3S6 | 1756-IF16 | P3-TBAI1-11(B) | C3S6-23/P3-TBAI1-11(B) | JB-602
22 | FT-60261FA | FT-60261FA | FT-60261FA | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #1 (AMTV-11A) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-3(B) | C3S7-5/P3-TBAI2-3(B) | JB-607
23 | FT-60261FB | FT-60261FB | FT-60261FB | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #2 (AMTV-11A) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-4(B) | C3S7-7/P3-TBAI2-4(B) | JB-607
24 | FT-60261FC | FT-60261FC | FT-60261FC | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #3 (AMTV-11A) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-5(B) | C3S7-11/P3-TBAI2-5(B) | JB-607
25 | FT-60261FD | FT-60261FD | FT-60261FD | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #4 (AMTV-11A) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-6(B) | C3S7-13/P3-TBAI2-6(B) | JB-607
26 | FT-60262FE | FT-60262FE | FT-60262FE | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #5 (AMTV-11B) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-7(B) | C3S7-15/P3-TBAI2-7(B) | JB-607
27 | FT-60262FF | FT-60262FF | FT-60262FF | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #6 (AMTV-11B) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-8(B) | C3S7-17/P3-TBAI2-8(B) | JB-607
28 | FT-60262FG | FT-60262FG | FT-60262FG | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #7 (AMTV-11B) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-9(B) | C3S7-19/P3-TBAI2-9(B) | JB-607
29 | FT-60262FH | FT-60262FH | FT-60262FH | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #8 (AMTV-11B) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-10(B) | C3S7-21/P3-TBAI2-10(B) | JB-607
30 | FT-60263FJ | FT-60263FJ | FT-60263FJ | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #9 (AMTV-11C) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-11(B) | C3S7-23/P3-TBAI2-11(B) | JB-607
31 | FT-60263FK | FT-60263FK | FT-60263FK | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #10 (AMTV-11C) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-12(B) | C3S7-25/P3-TBAI2-12(B) | JB-607
32 | FT-60263FL | FT-60263FL | FT-60263FL | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #11 (AMTV-11C) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-13(B) | C3S7-29/P3-TBAI2-13(B) | JB-607
33 | FT-60263FM | FT-60263FM | FT-60263FM | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #12 (AMTV-11C) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-14(B) | C3S7-31/P3-TBAI2-14(B) | JB-607
34 | FT-60264FN | FT-60264FN | FT-60264FN | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #13 (AMTV-11D) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-15(B) | C3S7-33/P3-TBAI2-15(B) | JB-607
35 | FT-60264FP | FT-60264FP | FT-60264FP | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #14 (AMTV-11D) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-16(B) | C3S7-35/P3-TBAI2-16(B) | JB-607
36 | FT-60264FQ | FT-60264FQ | FT-60264FQ | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #15 (AMTV-11D) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S8 | 1756-IF16 | P3-TBAI3-1(B) | C3S8-1/P3-TBAI3-1(B) | JB-607
37 | FT-60264FR | FT-60264FR | FT-60264FR | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #16 (AMTV-11D) | Ultrasonic Flow Transmitter | AI | 0 to 100 l/h | - | MAPPED | C3 | C3S8 | 1756-IF16 | P3-TBAI3-2(B) | C3S8-3/P3-TBAI3-2(B) | JB-607
38 | FT-61307 | FT-61307 | FT-61307 | 325-01-613-PD-04 | Compressed air Flow | Thermal Mass Flow Transmitter | AI | 0 - 1000 m3/hr | - | MAPPED | C1 | C1S11 | 1756-IF16 | P1-TBAI2-5(B) | C1S11-11/P1-TBAI2-5(B) | JB-601
39 | FT-60901 | FT-60203 | FT-60203 | 325-01-602-PD-09 | Culinary steam feed to Spray dryer | Vortex Flow Transmitter | DI, AI | 0 - 7000 kg/hr | - | MAPPED | C3 | C3S1 | 1756-IB32 | P3-TBDI1-17 | C3S1-19/P3-TBDI1-17 | JB-606
40 | FT-60902 | FT-60202 | FT-60202 | 325-01-602-PD-09 | Steam feed to Spray dryer | Vortex Flow Transmitter | DI, AI | 0 - 2000 kg/hr | - | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-1 | C2S2-1/P2-TBDI2-1 | JB-602
41 | FT-61101 | FT-60204 | FT-60204 | 325-01-602-PD-10 | Compressed air Flow | Thermal Mass Flow Transmitter | AI | 0 - 1000 m3/hr | - | MAPPED | C1 | C1S11 | 1756-IF16 | P1-TBAI2-4(B) | C1S11-7/P1-TBAI2-4(B) | JB-601
42 | FT-90301 | FT-936201 | FT-936201 | 325-01-930-PD-01 | Process Water | Magnetic Flow Transmitter | DI, AI | 0-1000kg/m³ | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-3 | C5S1-3/P5-TBDI1-3 | RIO-200
43 | FT-93001 | FT-936202 | FT-936202 | 325-01-930-PD-02 | Process Water | Magnetic Flow Transmitter | DI, AI | 0 - 20 m3/ hr | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-4 | C5S1-4/P5-TBDI1-4 | RIO-200
44 | HS-61307A | HS-61307A | HS-61307A | 325-01-613-PD-03 | Start/Stop | Hand Switch | DI |  | Ex d | MISSING | - | - | - | - | - | -
45 | HS-61307B | HS-61307B | HS-61307B | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
46 | HS-61307C | HS-61307C | HS-61307C | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
47 | HS-61307D | HS-61307D | HS-61307D | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
48 | HS-61307E | HS-61307E | HS-61307E | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
49 | HS-61307F | HS-61307F | HS-61307F | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
50 | HS-61307G | HS-61307G | HS-61307G | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
51 | HS-61307H | HS-61307H | HS-61307H | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
52 | HS-61307I | HS-61307I | HS-61307I | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
53 | HS-61307J | HS-61307J | HS-61307J | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
54 | HS-61307K | HS-61307K | HS-61307K | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
55 | HS-61307L | HS-61307L | HS-61307L | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
56 | HS-61307M | HS-61307M | HS-61307M | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
57 | HS-61307N | HS-61307N | HS-61307N | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
58 | HS-61307O | HS-61307O | HS-61307O | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
59 | HS-61307P | HS-61307P | HS-61307P | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
60 | HS-61307Q | HS-61307Q | HS-61307Q | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
61 | HS-61307R | HS-61307R | HS-61307R | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE |  | Ex d | MISSING | - | - | - | - | - | -
62 | HV-4106 | HV-40203 | HV-40203 | 325-01-402-PD-01 | Slurry Drain tank TS-40201 | Valve With Position Switch | DI | On-Off | - | MAPPED | C1 | C1S4 | 1756-IB32 | P1-TBDI1-23 | C1S4-25/P1-TBDI1-23 | JB-401
63 | HV-4108 | HV-40201 | HV-40201 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | DI | On-Off | - | MAPPED | C1 | C1S4 | 1756-IB32 | P1-TBDI1-21 | C1S4-23/P1-TBDI1-21 | JB-401
64 | HV-4126 | HV-40204 | HV-40204 | 325-01-402-PD-01 | Slurry Drain tank TS-40202 | Valve With Position Switch | DI | On-Off | - | MAPPED | C1 | C1S4 | 1756-IB32 | P1-TBDI1-24 | C1S4-26/P1-TBDI1-24 | JB-401
65 | HV-4128 | HV-40202 | HV-40202 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | DI | On-Off | - | MAPPED | C1 | C1S4 | 1756-IB32 | P1-TBDI1-22 | C1S4-24/P1-TBDI1-22 | JB-401
66 | HV-4208 | HV-40206 | HV-40206 | 325-01-402-PD-01 | Slurry Drain tank TS-40203 | Valve With Position Switch | DI | On-Off | - | MAPPED | C1 | C1S4 | 1756-IB32 | P1-TBDI1-26 | C1S4-28/P1-TBDI1-26 | JB-401
67 | HV-4210 | HV-40205 | HV-40205 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | DI | On-Off | - | MAPPED | C1 | C1S4 | 1756-IB32 | P1-TBDI1-25 | C1S4-27/P1-TBDI1-25 | JB-401
68 |  | HV-40207 | HV-40207 | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch | DI | On-Off | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-5 | C2S1-5/P2-TBDI1-5 | JB-402
69 |  | HV-40208 | HV-40208 | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch | DI | On-Off | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-6 | C2S1-6/P2-TBDI1-6 | JB-402
70 | LSH-60230 | LSH-60230 | LSH-60230 | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-21) | Level switch | DI |  | Ex t/d | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-4 | C4S1-4/P4-TBDI1-4 | IS-JB-603
71 | LSH-60231 | LSH-60231 | LSH-60231 | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-22) | Level switch | DI |  | Ex t/d | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-5 | C4S1-5/P4-TBDI1-5 | IS-JB-603
72 | LSH-60240 | LSH-60240 | LSH-60240 | 325-01-602-PD-05 | Powder Level Switch High for Bag House (BGHS-21) | Level switch | DI |  | Ex t/d | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-6 | C4S1-6/P4-TBDI1-6 | IS-JB-603
73 | LSH-60250 | LSH-60250 | LSH-60250 | 325-01-602-PD-05 | Water Level Switch High for Fire Deluge Pipe (FWDP-21) | Level switch | DI |  | - | MAPPED | C3 | C3S1 | 1756-IB32 | P3-TBDI1-18 | C3S1-20/P3-TBDI1-18 | JB-606
74 | LSH-60251 | LSH-60251 | LSH-60251 | 325-01-602-PD-04 | Water Level Switch High for Fire Deluge Pipe (FWDP-22) | Level switch | DI |  | - | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-2 | C2S2-2/P2-TBDI2-2 | JB-602
75 | LSL-61101 | LSL-60201 | LSL-60201 | 325-01-602-PD-11 | Level low switch | Level switch | DI |  | - | MAPPED | C1 | C1S6 | 1756-IB32 | P1-TBDI3-19 | C1S6-21/P1-TBDI3-19 | JB-601
76 | LSH-61301 | LSH-61301 | LSH-61301 | 325-01-613-PD-01 | Level alarm high | Level switch | DI |  | Ex t/d | MAPPED | C4 | C4S3 | 1756-IB32 | P4-TBDI3-2 | C4S3-2/P4-TBDI3-2 | IS-JB-618
77 | LSL-61302 | LSL-61302 | LSL-61302 | 325-01-613-PD-01 | Level alarm low | Level switch | DI |  | Ex t/d | MAPPED | C4 | C4S3 | 1756-IB32 | P4-TBDI3-6 | C4S3-6/P4-TBDI3-6 | IS-JB-618
78 | LS-61303 | LS-61303 | LS-61303 | 325-01-613-PD-01 | Level switch | Level switch | DI |  | Ex t/d | MAPPED | C3 | C3S3 | 1756-IB32 | P3-TBDI3-5 | C3S3-5/P3-TBDI3-5 | JB-618
79 | LSH-61304 | LSH-61304 | LSH-61304 | 325-01-613-PD-03 | Big bag level alarm high | Level switch | DI |  | Ex t/d | MAPPED | C4 | C4S2 | 1756-IB32 | P4-TBDI2-3 | C4S2-3/P4-TBDI2-3 | IS-JB-612
80 | LSH-61305 | LSH-61305 | LSH-61305 | 325-01-613-PD-05 | Big bag level alarm high | Level switch | DI |  | Ex t/d | MAPPED | C4 | C4S2 | 1756-IB32 | P4-TBDI2-4 | C4S2-4/P4-TBDI2-4 | IS-JB-612
81 | LSH-61306 | LSH-61306 | LSH-61306 | 325-01-613-PD-01 | Level alarm high | Level switch | DI |  | Ex t/d | MAPPED | C4 | C4S3 | 1756-IB32 | P4-TBDI3-4 | C4S3-4/P4-TBDI3-4 | IS-JB-618
82 |  | LSH-61307 | LSH-61307 | 325-01-613-PD-01 | High Level alarm reject screen | Level switch | DI |  | Ex t/d | MAPPED | C4 | C4S2 | 1756-IB32 | P4-TBDI2-5 | C4S2-5/P4-TBDI2-5 | IS-JB-612
83 |  | LSH-61308 | LSH-61308 | 325-01-613-PD-01 | High Level alarm Cooling cyclone | Level switch | DI |  | Ex t/d | MAPPED | C4 | C4S3 | 1756-IB32 | P4-TBDI3-5 | C4S3-5/P4-TBDI3-5 | IS-JB-618
84 | LSH-61312 | LSH-61312 | LSH-61312 | 325-01-613-PD-05 | Level alarm high | Level switch | DI |  | Ex t/d | MAPPED | C4 | C4S2 | 1756-IB32 | P4-TBDI2-6 | C4S2-6/P4-TBDI2-6 | IS-JB-612
85 | LSL-81001 | LSL-814201 | LSL-814201 | 325-01-814-PD-01 | Low Level alarm |  | DI |  | Ex t/d | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-5 | C5S1-5/P5-TBDI1-5 | RIO-200
86 | LT-40101 | LT-40201 | LT-40201 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 1 | Level transmitter | AI | 0 - 10 m. | - | MISSING | - | - | - | - | - | -
87 | LT-40102 | LT-40202 | LT-40202 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 2 | Level transmitter | AI | 0 - 10 m. | - | MAPPED | C1 | C1S10 | 1756-IF16 | P1-TBAI1-6(B) | C1S10-13/P1-TBAI1-6(B) | JB-401
88 | LT-40201 | LT-40203 | LT-40203 | 325-01-402-PD-02 | Level transmitter in Spray dryer infeed tank | Level transmitter | AI | 0 - 10 m. | - | MAPPED | C1 | C1S10 | 1756-IF16 | P1-TBAI1-4(B) | C1S10-7/P1-TBAI1-4(B) | JB-401
89 | LT-61301 | LT-61301 | LT-61301 | 325-01-613-PD-01 | Level powder in silo | Level transmitter | AI |  | Ex ia | MAPPED | C4 | C4S6 | 1756-IF16 | P4-TBAI2-7(B) | C4S6-15/P4-TBAI2-7(B) | IS-JB-618
90 | pHT-40101 | pHT-40201 | pHT-40201 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 1 | pH Analyzer | DI, AI | 0-14 | - | MAPPED | C1 | C1S10 | 1756-IF16 | P1-TBAI1-7(B) | C1S10-15/P1-TBAI1-7(B) | JB-401
91 | pHT-40102 | pHT-40202 | pHT-40202 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 2 | pH Analyzer | DI, AI | 0-14 | - | MAPPED | C1 | C1S10 | 1756-IF16 | P1-TBAI1-8(B) | C1S10-17/P1-TBAI1-8(B) | JB-401
92 | PSL-60220 | PSL-60220 | PSL-60220 | 325-01-602-PD-04 | Gas Pressure Switch Low for Spray Chamber (CHAM-21) | Pressure switch | DI | -0.01 mbar | - | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-3 | C2S2-3/P2-TBDI2-3 | JB-602
93 |  | PSL-61301 | PSL-61301 | 325-01-613-PD-01 | Pressure alarm low | Pressure switch | DI | 0.3-0.7barg | - | MAPPED | C3 | C3S3 | 1756-IB32 | P3-TBDI3-6 | C3S3-6/P3-TBDI3-6 | JB-618
94 | PSL-61302 | PSL-61302 | PSL-61302 | 325-01-613-PD-01 | Pressure alarm low | Pressure switch | DI | 40 mbarg | - | MAPPED | C3 | C3S3 | 1756-IB32 | P3-TBDI3-7 | C3S3-7/P3-TBDI3-7 | JB-618
95 | PSL-61305 | PSL-61305 | PSL-61305 | 325-01-613-PD-03 | Pressure alarm low | Pressure switch | DI |  | - | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-1 | C3S2-1/P3-TBDI2-1 | JB-612
96 | PSL-61306 | PSL-61306 | PSL-61306 | 325-01-613-PD-05 | Pressure alarm low | Pressure switch | DI |  | - | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-2 | C3S2-2/P3-TBDI2-2 | JB-612
97 | PSL-61311 | PSL-61311 | PSL-61311 | 325-01-613-PD-04 | Pressure alarm low | Pressure switch | DI |  | - | MAPPED | C3 | C3S3 | 1756-IB32 | P3-TBDI3-8 | C3S3-8/P3-TBDI3-8 | JB-618
98 | PT-40201 | PT-40201 | PT-40201 | 325-01-402-PD-02 | Pressure Transmitter for Inlet Filter Strainer (FSTR-11) | Pressure Transmitter | AI | -100 to 500 mBar | - | MAPPED | C1 | C1S10 | 1756-IF16 | P1-TBAI1-9(B) | C1S10-19/P1-TBAI1-9(B) | JB-401
99 | PT-40202 | PT-40202 | PT-40202 | 325-01-402-PD-02 | Feed Slurry Pressure Transmitter for Pipe (PIPE) | Pressure Transmitter | AI | 0 - 10'barg | - | MAPPED | C1 | C1S10 | 1756-IF16 | P1-TBAI1-10(B) | C1S10-21/P1-TBAI1-10(B) | JB-401
100 |  | PT-40222 | PT-40222 | 325-01-402-PD-02 | Jet Cooker | Pressure Transmitter | AI | 0 - 12'barg | - | MAPPED | C2 | C2S9 | 1756-IF16 | P2-TBAI1-5(B) | C2S9-11/P2-TBAI1-5(B) | JB-402
101 | PT-60201 | PT-60201 | PT-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Pressure Transmitter | AI | 0 - 20 bar | - | MAPPED | C3 | C3S8 | 1756-IF16 | P3-TBAI3-3(B) | C3S8-5/P3-TBAI3-3(B) | JB-607
102 | PT-60202 |  | PT-60202 | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter | AI | 0 to 500 bar | - | MAPPED | C1 | C1S10 | 1756-IF16 | P1-TBAI1-11(B) | C1S10-23/P1-TBAI1-11(B) | JB-401
103 | PT-60203 | PT-60203 | PT-60203 | 325-01-602-PD-08 | Gas Pressure Transmitter for Cool Air Duct (DTCA-32) | Pressure Transmitter | AI | 0 - 0.1 mbar | - | MAPPED | C1 | C1S11 | 1756-IF16 | P1-TBAI2-6(B) | C1S11-13/P1-TBAI2-6(B) | JB-601
104 | PT-60210 | PT-60210 | PT-60210 | 325-01-602-PD-03 | Gas Pressure Transmitter for Hot Air Duct (DTHA-21) | Pressure Transmitter | AI | 0 - 0.1 mbar | - | MAPPED | C2 | C2S10 | 1756-IF16 | P2-TBAI2-4(B) | C2S10-7/P2-TBAI2-4(B) | JB-602
105 | PT-60215 | PT-60215 | PT-60215 | 325-01-602-PD-03 | 15% Polypropylene Glycol Pressure Indicator Transmitter for Heat Recovery Pumping Skid (PUCF-21) | Pressure Transmitter | AI | 0 - 6 bar | - | MAPPED | C2 | C2S10 | 1756-IF16 | P2-TBAI2-5(B) | C2S10-11/P2-TBAI2-5(B) | JB-602
106 | PT-60216 | PT-60216 | PT-60216 | 325-01-602-PD-03 | Gas Pressure Transmitter for Combustion Air Burner Duct (DTCB-21) | Pressure Transmitter | AI | 0 - 100 mbar | - | MAPPED | C2 | C2S10 | 1756-IF16 | P2-TBAI2-6(B) | C2S10-13/P2-TBAI2-6(B) | JB-602
107 | PT-60220 | PT-60220 | PT-60220 | 325-01-602-PD-04 | Gas Pressure Transmitter for Chamber (CHAM-21) | Pressure Transmitter | AI | -100 - 100 mbar | Ex ic | MAPPED | C4 | C4S5 | 1756-IF16 | P4-TBAI1-9(B) | C4S5-19/P4-TBAI1-9(B) | IS-JB-608
108 | PT-60221 | PT-60221 | PT-60221 | 325-01-602-PD-04 | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25) | Pressure Transmitter | AI | 0 - 0.1 mbar | - | MAPPED | C3 | C3S8 | 1756-IF16 | P3-TBAI3-5(B) | C3S8-11/P3-TBAI3-5(B) | JB-607
109 | PT-60230 | PT-60230 | PT-60230 | 325-01-602-PD-04 | Gas Pressure Transmitter for Conveying Duct (DTCO-21) | Pressure Transmitter | AI | 0 - 0.1 mbar | Ex ic | MAPPED | C4 | C4S5 | 1756-IF16 | P4-TBAI1-1(B) | C4S5-1/P4-TBAI1-1(B) | IS-JB-603
110 | PT-60231 | PT-60231 | PT-60231 | 325-01-602-PD-04 | Gas Pressure Transmitter for Cyclone Exhaust Duct (DTCE-21) | Pressure Transmitter | AI | -100 to 200 mbar | Ex ic | MAPPED | C4 | C4S5 | 1756-IF16 | P4-TBAI1-2(B) | C4S5-3/P4-TBAI1-2(B) | IS-JB-603
111 | PT-60240 | PT-60240 | PT-60240 | 325-01-602-PD-05 | Gas Pressure Transmitter for Bag House Exhaust Duct (DTEX-22) | Pressure Transmitter | AI | -100 to 200 mbar | - | MAPPED | C2 | C2S10 | 1756-IF16 | P2-TBAI2-7(B) | C2S10-15/P2-TBAI2-7(B) | JB-602
112 | PT-60241 | PT-60241 | PT-60241 | 325-01-602-PD-05 | Gas Pressure Transmitter for Exhaust Fan (FANE-21) | Pressure Transmitter | AI | 0 - 0.1 mbar | - | MAPPED | C2 | C2S10 | 1756-IF16 | P2-TBAI2-8(B) | C2S10-17/P2-TBAI2-8(B) | JB-602
113 | PT-61101 | PT-60204 | PT-60204 | 325-01-602-PD-10 | Pressure transmitter | Pressure Transmitter | AI | 0 - 10 barg | - | MAPPED | C1 | C1S11 | 1756-IF16 | P1-TBAI2-7(B) | C1S11-15/P1-TBAI2-7(B) | JB-601
114 | PT-61301 | PT-61301 | PT-61301 | 325-01-613-PD-01 | Pressure in silo | Pressure Transmitter | AI | 0 - 1 barg | Ex ic | MAPPED | C4 | C4S6 | 1756-IF16 | P4-TBAI2-8(B) | C4S6-17/P4-TBAI2-8(B) | IS-JB-618
115 | PT-61302 | PT-61302 | PT-61302 | 325-01-613-PD-03 | Pressure in vacuum line | Pressure Transmitter | AI | -100 - 100 mbarg | - | MAPPED | C3 | C3S9 | 1756-IF16 | P3-TBAI4-9(B) | C3S9-19/P3-TBAI4-9(B) | JB-612
116 | PT-61303 | PT-61303 | PT-61303 | 325-01-613-PD-01 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) | Pressure Transmitter | AI | -100 to 200 mbar | Ex ic | MAPPED | C3 | C3S9 | 1756-IF16 | P3-TBAI4-1(B) | C3S9-1/P3-TBAI4-1(B) | JB-618
117 | PT-61304 | PT-61304 | PT-61304 | 325-01-613-PD-01 | Gas Pressure Transmitter for Storage Bin Cyclone Inlet Duct (CYCL-31) | Pressure Transmitter | AI | -100 to 200 mbar | Ex ic | MAPPED | C4 | C4S6 | 1756-IF16 | P4-TBAI2-10(B) | C4S6-21/P4-TBAI2-10(B) | IS-JB-618
118 | PT-61305 | PT-61305 | PT-61305 | 325-01-613-PD-01 | Gas Pressure Transmitter for Exhaust Duct (DTEX-31) | Pressure Transmitter | AI | -100 to 200 mbar | Ex ic | MAPPED | C4 | C4S6 | 1756-IF16 | P4-TBAI2-11(B) | C4S6-23/P4-TBAI2-11(B) | IS-JB-618
119 | PT-61309 | PT-61309 | PT-61309 | 325-01-613-PD-04 | Pressure transmitter | Pressure Transmitter | AI | 0 - 10 barg | - | MAPPED | C3 | C3S9 | 1756-IF16 | P3-TBAI4-10(B) | C3S9-21/P3-TBAI4-10(B) | JB-612
120 | PV-60201 | PCV-60201 | PCV-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic Control valve | AO | 0 - 100% | - | MAPPED | C3 | C3S12 | 1756-OF8 | P3-TBAO1-4 | C3S12-19/P3-TBAO1-4 | JB-607
121 | SV-40101 | SV-40201 | SV-40201 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 1 | Solenoid valve | DO | On-Off | - | MAPPED | C1 | C1S8 | 1756-OB32 | P1-TBRL1-25 | C1S8-27/P1-TBRL1-25 | JB-401
122 | SV-40102 | SV-40202 | SV-40202 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 2 | Solenoid valve | DO | On-Off | - | MAPPED | C1 | C1S8 | 1756-OB32 | P1-TBRL1-26 | C1S8-28/P1-TBRL1-26 | JB-401
123 | SV-40103 | SV-40203 | SV-40203 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 1 | Solenoid valve | DO | On-Off | - | MAPPED | C1 | C1S8 | 1756-OB32 | P1-TBRL1-27 | C1S8-29/P1-TBRL1-27 | JB-401
124 | SV-40104 | SV-40204 | SV-40204 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 2 | Solenoid valve | DO | On-Off | - | MAPPED | C1 | C1S8 | 1756-OB32 | P1-TBRL1-28 | C1S8-30/P1-TBRL1-28 | JB-401
125 | SV-60220 | SV-60220 | SV-60220 | 325-01-602-PD-04 | PA On/Off Valve for Chamber PSE purge air (CHAM-21) | Solenoid valve | DO | On-Off | - | MAPPED | C3 | C3S4 | 1756-OB32 | P3-TBRL1-9 | C3S4-9/P3-TBRL1-9 | JB-606
126 | SV-60230 | SV-60230 | SV-60230 | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 27 (CYCL-21) | Solenoid valve | DO | On-Off | - | MAPPED | C1 | C1S9 | 1756-OB32 | P1-TBRL2-19 | C1S9-21/P1-TBRL2-19 | JB-601
127 | SV-60231 | SV-60231 | SV-60231 | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 28 (CYCL-22) | Solenoid valve | DO | On-Off | - | MAPPED | C1 | C1S9 | 1756-OB32 | P1-TBRL2-22 | C1S9-24/P1-TBRL2-22 | JB-601
128 | SV-60240A | SV-60240A | SV-60240A | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29A (BGHS-21) | Solenoid valve | DO | On-Off | - | MAPPED | C1 | C1S9 | 1756-OB32 | P1-TBRL2-21 | C1S9-23/P1-TBRL2-21 | JB-601
129 | SV-60240B | SV-60240B | SV-60240B | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29B (BGHS-21) | Solenoid valve | DO | On-Off | - | MAPPED | C1 | C1S9 | 1756-OB32 | P1-TBRL2-23 | C1S9-25/P1-TBRL2-23 | JB-601
130 | SV-60240C | SV-60240C | SV-60240C | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29C (BGHS-21) | Solenoid valve | DO | On-Off | - | MAPPED | C1 | C1S9 | 1756-OB32 | P1-TBRL2-24 | C1S9-26/P1-TBRL2-24 | JB-601
131 | SV-61301 | SV-61301 | SV-61301 | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve | LOCAL / NONE | On-Off | - | MAPPED | C3 | C3S5 | 1756-OB32 | P3-TBRL2-3 | C3S5-3/P3-TBRL2-3 | JB-618
132 | SV-61302 | SV-61302 | SV-61302 | 325-01-613-PD-01 | Air service | Solenoid valve | DO | On-Off | - | MAPPED | C3 | C3S5 | 1756-OB32 | P3-TBRL2-4 | C3S5-4/P3-TBRL2-4 | JB-618
132 |  | SV-61306 | SV-61306 | 325-01-613-PD-01 | Air service | Solenoid valve | DO | On-Off | - | MAPPED | C3 | C3S5 | 1756-OB32 | P3-TBRL2-8 | C3S5-8/P3-TBRL2-8 | JB-618
133 | SV-61303 | SV-61303 | SV-61303 | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve | LOCAL / NONE | On-Off | - | MAPPED | C3 | C3S5 | 1756-OB32 | P3-TBRL2-5 | C3S5-5/P3-TBRL2-5 | JB-618
134 | SV-61305 | SV-61305 | SV-61305 | 325-01-613-PD-01 | Air service | Solenoid valve | DO | On-Off | - | MAPPED | C3 | C3S5 | 1756-OB32 | P3-TBRL2-7 | C3S5-7/P3-TBRL2-7 | JB-618
135 | SV-61308 | SV-61308 | SV-61308 | 325-01-613-PD-03 | Timer compress air pluse solenoid valve | Solenoid valve | LOCAL / NONE | On-Off | - | MAPPED | C3 | C3S4 | 1756-OB32 | P3-TBRL1-20 | C3S4-22/P3-TBRL1-20 | JB-612
136 | SV-61309 | SV-61309 | SV-61309 | 325-01-613-PD-03 | Air service | Solenoid valve | DO | On-Off | - | MAPPED | C3 | C3S4 | 1756-OB32 | P3-TBRL1-21 | C3S4-23/P3-TBRL1-21 | JB-612
137 | SV-61310 | SV-61310 | SV-61310 | 325-01-613-PD-05 | Timer compress air pluse solenoid valve | Solenoid valve | LOCAL / NONE | On-Off | - | MAPPED | C3 | C3S4 | 1756-OB32 | P3-TBRL1-22 | C3S4-24/P3-TBRL1-22 | JB-612
138 | SV-61311 | SV-61311 | SV-61311 | 325-01-613-PD-05 | Air service | Solenoid valve | DO | On-Off | - | MAPPED | C3 | C3S4 | 1756-OB32 | P3-TBRL1-23 | C3S4-25/P3-TBRL1-23 | JB-612
139 | TSH-60230 | TSH-60230 | TSH-60230 | 325-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | Temperature Switch | DI | 0 - 140 C | Ex d | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-4 | C2S2-4/P2-TBDI2-4 | JB-602
140 | TSH-60240 | TSH-60240 | TSH-60240 | 325-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | Temperature Switch | DI | 0 - 140 C | Ex d | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-5 | C2S2-5/P2-TBDI2-5 | JB-602
141 |  | TT-40221 | TT-40221 | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter | AI | 0 - 120 C | - | MAPPED | C2 | C2S9 | 1756-IF16 | P2-TBAI1-6(B) | C2S9-13/P2-TBAI1-6(B) | JB-402
142 |  | TT-40222 | TT-40222 | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter | AI | 0 - 200 C | - | MAPPED | C2 | C2S9 | 1756-IF16 | P2-TBAI1-7(B) | C2S9-15/P2-TBAI1-7(B) | JB-402
143 | TT-60201 | TT-60201 | TT-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Temperature Transmitter | AI | 0 - 300 C | - | MAPPED | C3 | C3S8 | 1756-IF16 | P3-TBAI3-8(B) | C3S8-17/P3-TBAI3-8(B) | JB-607
144 | TT-60210 | TT-60210 | TT-60210 | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter | AI | 0 - 400'°C | - | MAPPED | C2 | C2S10 | 1756-IF16 | P2-TBAI2-9(B) | C2S10-19/P2-TBAI2-9(B) | JB-602
145 | TT-60212A | TT-60210A | TT-60210A | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter | AI | 0 - 100 C | - | MAPPED | C2 | C2S10 | 1756-IF16 | P2-TBAI2-10(B) | C2S10-21/P2-TBAI2-10(B) | JB-602
146 | TT-60212B | TT-60210B | TT-60210B | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter | AI | 0 - 100 C | - | MAPPED | C2 | C2S10 | 1756-IF16 | P2-TBAI2-11(B) | C2S10-23/P2-TBAI2-11(B) | JB-602
147 | TT-60211 | TT-60211 | TT-60211 | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter | AI | 0 - 400'°C | - | MAPPED | C2 | C2S10 | 1756-IF16 | P2-TBAI2-12(B) | C2S10-25/P2-TBAI2-12(B) | JB-602
148 | TT-60214 | TT-60214 | TT-60214 | 325-01-602-PD-03 | Steam Temperature Transmitter for Cold Air Duct (DTCA-23) | Temperature Transmitter | AI | -10 to 250°C | - | MAPPED | C2 | C2S10 | 1756-IF16 | P2-TBAI2-15(B) | C2S10-33/P2-TBAI2-15(B) | JB-602
149 | TT-60215A | TT-60215A | TT-60215A | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter | AI | -10 to 150°C | - | MAPPED | C2 | C2S10 | 1756-IF16 | P2-TBAI2-16(B) | C2S10-35/P2-TBAI2-16(B) | JB-602
150 | TT-60215B | TT-60215B | TT-60215B | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter | AI | -10 to 150°C | - | MAPPED | C3 | C3S6 | 1756-IF16 | P3-TBAI1-1(B) | C3S6-1/P3-TBAI1-1(B) | JB-602
151 | TT-60216 | TT-60216 | TT-60216 | 325-01-602-PD-03 | Gas Temperature Transmitter for Combustion Air Burner Duct (DTCB-21) | Temperature Transmitter | AI | 0 - 200'°C | - | MAPPED | C3 | C3S6 | 1756-IF16 | P3-TBAI1-2(B) | C3S6-3/P3-TBAI1-2(B) | JB-602
152 | TT-60220 | TT-60220 | TT-60220 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 0 - 400'°C | Ex ic | MAPPED | C4 | C4S5 | 1756-IF16 | P4-TBAI1-10(B) | C4S5-21/P4-TBAI1-10(B) | IS-JB-608
153 | TT-60221 | TT-60221 | TT-60221 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 0 - 400'°C | Ex ic | MAPPED | C4 | C4S5 | 1756-IF16 | P4-TBAI1-11(B) | C4S5-23/P4-TBAI1-11(B) | IS-JB-608
154 | TT-60222 | TT-60222 | TT-60222 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 0 - 400'°C | Ex ic | MAPPED | C4 | C4S5 | 1756-IF16 | P4-TBAI1-12(B) | C4S5-25/P4-TBAI1-12(B) | IS-JB-608
155 | TT-60223 | TT-60223 | TT-60223 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 0 - 400'°C | Ex ic | MAPPED | C4 | C4S5 | 1756-IF16 | P4-TBAI1-13(B) | C4S5-29/P4-TBAI1-13(B) | IS-JB-608
156 | TT-60224 | TT-60224 | TT-60224 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 0 - 400'°C | Ex ic | MAPPED | C4 | C4S5 | 1756-IF16 | P4-TBAI1-3(B) | C4S5-5/P4-TBAI1-3(B) | IS-JB-603
157 | TT-60225 | TT-60225 | TT-60225 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 0 - 400'°C | Ex ic | MAPPED | C4 | C4S5 | 1756-IF16 | P4-TBAI1-4(B) | C4S5-7/P4-TBAI1-4(B) | IS-JB-603
158 | TT-60226 | TT-60226 | TT-60226 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 0 - 400'°C | Ex ic | MAPPED | C4 | C4S5 | 1756-IF16 | P4-TBAI1-5(B) | C4S5-11/P4-TBAI1-5(B) | IS-JB-603
159 | TT-60227 | TT-60227 | TT-60227 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 0 - 400'°C | Ex ic | MAPPED | C4 | C4S5 | 1756-IF16 | P4-TBAI1-6(B) | C4S5-13/P4-TBAI1-6(B) | IS-JB-603
160 | TT-60230 | TT-60230 | TT-60230 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Conveying Duct (DTCO-21) | Temperature Transmitter | AI | 0 - 400'°C | Ex ic | MAPPED | C4 | C4S5 | 1756-IF16 | P4-TBAI1-7(B) | C4S5-15/P4-TBAI1-7(B) | IS-JB-603
161 | TT-60240 | TT-60240 | TT-60240 | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Fan (FANE-21) | Temperature Transmitter | AI | 0 - 400'°C | - | MAPPED | C3 | C3S6 | 1756-IF16 | P3-TBAI1-3(B) | C3S6-5/P3-TBAI1-3(B) | JB-602
162 | TT-60241A | TT-60241A | TT-60241A | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter | AI | 0 - 100 C | - | MAPPED | C3 | C3S6 | 1756-IF16 | P3-TBAI1-4(B) | C3S6-7/P3-TBAI1-4(B) | JB-602
163 | TT-60241B | TT-60241B | TT-60241B | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter | AI | 0 - 100 C | - | MAPPED | C3 | C3S6 | 1756-IF16 | P3-TBAI1-5(B) | C3S6-11/P3-TBAI1-5(B) | JB-602
164 | TT-60245 | TT-60245 | TT-60245 | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Stack (DTXS-21) | Temperature Transmitter | AI | -10 to 150°C | - | MAPPED | C3 | C3S8 | 1756-IF16 | P3-TBAI3-16(B) | C3S8-35/P3-TBAI3-16(B) | JB-608
165 | TT-60702 | TT-60202 | TT-60202 | 325-01-602-PD-07 | Compress air temp to camera | Temperature Transmitter | AI | 0 - 40 C | - | MAPPED | C3 | C3S8 | 1756-IF16 | P3-TBAI3-9(B) | C3S8-19/P3-TBAI3-9(B) | JB-607
166 | TT-61301 | TT-61301 | TT-61301 | 325-01-613-PD-01 | Gas Temperature Transmitter for Cold Air Duct (DTCA-32) | Temperature Transmitter | AI | 0 - 400'°C | Ex ic | MAPPED | C4 | C4S6 | 1756-IF16 | P4-TBAI2-12(B) | C4S6-25/P4-TBAI2-12(B) | IS-JB-618
167 | TT-61302 | TT-61302 | TT-61302 | 325-01-613-PD-01 | Gas and Powder Temperature Transmitter for Cooling Cyclone (CYCL-31) | Temperature Transmitter | AI | 0 - 400'°C | Ex ic | MAPPED | C4 | C4S6 | 1756-IF16 | P4-TBAI2-13(B) | C4S6-29/P4-TBAI2-13(B) | IS-JB-618
168 |  | TCV-40222 | TCV-40222 | 325-01-402-PD-02 | Jet Cooker | Automatic Control valve | AO | 0 - 100% | - | MAPPED | C3 | C3S12 | 1756-OF8 | P3-TBAO1-1 | C3S12-3/P3-TBAO1-1 | JB-402
169 | TV-60214 | TCV-60214 | TCV-60214 | 325-01-602-PD-03 | Steam Temperature Valve for Pre-Heat Steam Heat Exchanger (HXCH-21) | Automatic Control valve | AO | 0 - 100% | - | MAPPED | C3 | C3S12 | 1756-OF8 | P3-TBAO1-3 | C3S12-13/P3-TBAO1-3 | JB-602
170 | TV-60702 | TCV-60202 | TCV-60202 | 325-01-602-PD-07 | Chiller water control valve | 3-way Control valve | AO | 0 - 100% | - | MISSING | - | - | - | - | - | -
171 | VT-60210A | VT-60210A | VT-60210A | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter | AI | mm/sec | - | MAPPED | C3 | C3S6 | 1756-IF16 | P3-TBAI1-6(B) | C3S6-13/P3-TBAI1-6(B) | JB-602
172 | VT-60210B | VT-60210B | VT-60210B | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter | AI | mm/sec | - | MAPPED | C3 | C3S6 | 1756-IF16 | P3-TBAI1-7(B) | C3S6-15/P3-TBAI1-7(B) | JB-602
173 | VT-60241A | VT-60241A | VT-60241A | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter | AI | mm/sec | - | MAPPED | C3 | C3S6 | 1756-IF16 | P3-TBAI1-8(B) | C3S6-17/P3-TBAI1-8(B) | JB-602
174 | VT-60241B | VT-60241B | VT-60241B | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter | AI | mm/sec | - | MAPPED | C3 | C3S6 | 1756-IF16 | P3-TBAI1-9(B) | C3S6-19/P3-TBAI1-9(B) | JB-602
175 | XT-60301 | XT-60201 | XT-60201 | 325-01-402-PD-03 | LEL gas analyzer | Gas detector | AI | 0-10%LEL | Ex ic | MAPPED | C4 | C4S5 | 1756-IF16 | P4-TBAI1-14(B) | C4S5-31/P4-TBAI1-14(B) | IS-JB-608
176 | XA-60301 | XA-60201 | XA-60201 | 325-01-402-PD-03 | LEL gas Buzzer Alarm | Gas detector | DO | 0-10%LEL | Ex ic | MAPPED | C4 | C4S4 | 1756-OB32 | P4-TBRL1-9 | C4S4-9/P4-TBRL1-9 | IS-JB-608
177 | XT-92201 | XT-92201 | XT-92201 | 325-01-923-PD-03 | LEL gas analyzer | Gas detector | AI | 0-10%LEL | Ex ic | MAPPED | C5 | C5S4 | 1756-IF16 | P5-TBAI1-8(B) | C5S4-17/P5-TBAI1-8(B) | RIO-200
178 | XA-92201 | XA-92201 | XA-92201 | 325-01-923-PD-03 | LEL gas Buzzer Alarm | Gas detector | DO | 0-10%LEL | Ex ic | MAPPED | C5 | C5S3 | 1756-OB32 | P5-TBRL1-1 | C5S3-1/P5-TBRL1-1 | RIO-200
179 | XV-40101A | XV-40201A | XV-40201A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 1 | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S4 | 1756-IB32 | P1-TBDI1-27 | C1S4-29/P1-TBDI1-27 | JB-401
180 | XV-40101B | XV-40201B | XV-40201B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1 | Automatic on/off valve | DO, DI | On-Off | - | MISSING | - | - | - | - | - | -
181 | XV-40101C | XV-40201C | XV-40201C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1 | Automatic on/off valve | DO, DI | On-Off | - | MISSING | - | - | - | - | - | -
182 | XV-40101D | XV-40201D | XV-40201D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 1 | Automatic on/off valve | DO, DI | On-Off | - | MISSING | - | - | - | - | - | -
183 | XV-40101E | XV-40201E | XV-40201E | 325-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | Automatic on/off valve | DO, DI | On-Off | - | MISSING | - | - | - | - | - | -
184 | XV-40101F | XV-40201F | XV-40201F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S5 | 1756-IB32 | P1-TBDI2-5 | C1S5-5/P1-TBDI2-5 | JB-401
185 | XV-40101G | XV-40201G | XV-40201G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 1 | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S5 | 1756-IB32 | P1-TBDI2-7 | C1S5-7/P1-TBDI2-7 | JB-401
186 | XV-40101H | XV-40201H | XV-40201H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 1 | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S5 | 1756-IB32 | P1-TBDI2-9 | C1S5-9/P1-TBDI2-9 | JB-401
187 | XV-40102A | XV-40202A | XV-40202A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 2 | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S5 | 1756-IB32 | P1-TBDI2-11 | C1S5-11/P1-TBDI2-11 | JB-401
188 | XV-40102B | XV-40202B | XV-40202B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 2 | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S5 | 1756-IB32 | P1-TBDI2-12 | C1S5-12/P1-TBDI2-12 | JB-401
189 | XV-40102C | XV-40202C | XV-40202C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 2 | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S5 | 1756-IB32 | P1-TBDI2-14 | C1S5-14/P1-TBDI2-14 | JB-401
190 | XV-40102D | XV-40202D | XV-40202D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 2 | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S5 | 1756-IB32 | P1-TBDI2-16 | C1S5-16/P1-TBDI2-16 | JB-401
191 | XV-40102E | XV-40202E | XV-40202E | 325-01-402-PD-01 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S5 | 1756-IB32 | P1-TBDI2-18 | C1S5-20/P1-TBDI2-18 | JB-401
192 | XV-40102F | XV-40202F | XV-40202F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S5 | 1756-IB32 | P1-TBDI2-21 | C1S5-23/P1-TBDI2-21 | JB-401
193 | XV-40102G | XV-40202G | XV-40202G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 2 | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S5 | 1756-IB32 | P1-TBDI2-23 | C1S5-25/P1-TBDI2-23 | JB-401
194 | XV-40102H | XV-40202H | XV-40202H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 2 | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S5 | 1756-IB32 | P1-TBDI2-25 | C1S5-27/P1-TBDI2-25 | JB-401
195 | XV-40201B | XV-40203B | XV-40203B | 325-01-402-PD-02 | Slurry feed-out Spray dryer infeed tank | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S4 | 1756-IB32 | P1-TBDI1-29 | C1S4-31/P1-TBDI1-29 | JB-401
196 | XV-40201C | XV-40203C | XV-40203C | 325-01-402-PD-02 | Water washing line outlet Spray dryer infeed tank | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S4 | 1756-IB32 | P1-TBDI1-31 | C1S4-33/P1-TBDI1-31 | JB-401
197 | XV-40201D | XV-40203D | XV-40203D | 325-01-402-PD-02 | CIP water washing Spray dryer infeed tank | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S5 | 1756-IB32 | P1-TBDI2-1 | C1S5-1/P1-TBDI2-1 | JB-401
198 | XV-40201E | XV-40203E | XV-40203E | 325-01-402-PD-02 | CIP hight pressure water washing Spray dryer infeed tank | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S5 | 1756-IB32 | P1-TBDI2-3 | C1S5-3/P1-TBDI2-3 | JB-401
199 |  | XV-40203F | XV-40203F | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-7 | C2S1-7/P2-TBDI1-7 | JB-402
200 |  | XV-40204B | XV-40204B | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-9 | C2S1-9/P2-TBDI1-9 | JB-402
201 |  | XV-40204C | XV-40204C | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-11 | C2S1-11/P2-TBDI1-11 | JB-402
202 |  | XV-40205A | XV-40205A | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-13 | C2S1-13/P2-TBDI1-13 | JB-402
203 |  | XV-40205B | XV-40205B | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-15 | C2S1-15/P2-TBDI1-15 | JB-402
204 |  | XV-40205C | XV-40205C | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-17 | C2S1-19/P2-TBDI1-17 | JB-402
205 |  | XV-40205D | XV-40205D | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-19 | C2S1-21/P2-TBDI1-19 | JB-402
206 |  | XV-40205F | XV-40205F | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-21 | C2S1-23/P2-TBDI1-21 | JB-402
207 |  | XV-40222 | XV-40222 | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C2 | C2S1 | 1756-IB32 | P2-TBDI1-23 | C2S1-25/P2-TBDI1-23 | JB-402
208 | XV-60201 | XV-60201 | XV-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-17 | C2S3-19/P2-TBDI3-17 | JB-607
209 | XV-60251 | XV-60251 | XV-60251 | 325-01-602-PD-01 | Liquid On/Off Valve for Drain Pipe (PIPE) | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S9 | 1756-OB32 | P1-TBRL2-26 | C1S9-28/P1-TBRL2-26 | JB-601
210 | XV-60301 | XV-60214 | XV-60214 | 325-01-602-PD-03 | Steam feed to Spray dryer | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-20 | C2S2-22/P2-TBDI2-20 | JB-602
211 | XV-61101 | XV-60202 | XV-60202 | 325-01-602-PD-11 | High Pressure Water On/Off Valve for Drain Pipe | Automatic on/off valve | DO, DI | On-Off | - | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-14 | C1S7-14/P1-TBDI4-14 | JB-601
212 | HV-61301 | XV-61301 | XV-61301 | 325-01-613-PD-01 | Product feed-out Packing silo | Automatic on/off valve | DI | On-Off | Ex d | MAPPED | C3 | C3S3 | 1756-IB32 | P3-TBDI3-11 | C3S3-11/P3-TBDI3-11 | JB-618
213 | XV-61302 | XV-61302 | XV-61302 | 325-01-613-PD-02 | Dust collector feed vent | Automatic on/off valve | DO, DI | On-Off | Ex d | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-14 | C3S2-14/P3-TBDI2-14 | JB-612
214 | XV-61303 | XV-61303 | XV-61303 | 325-01-613-PD-02 | Dust collector feed from packer | Automatic on/off valve | DO, DI | On-Off | Ex d | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-16 | C3S2-16/P3-TBDI2-16 | JB-612
215 |  | DV-61301 | DV-61301 | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61301 | Automatic on/off valve | DO, DI | On-Off | Ex d | MAPPED | C3 | C3S3 | 1756-IB32 | P3-TBDI3-1 | C3S3-1/P3-TBDI3-1 | JB-618
216 |  | DV-61302 | DV-61302 | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61302 | Automatic on/off valve | DO, DI | On-Off | Ex d | MAPPED | C3 | C3S3 | 1756-IB32 | P3-TBDI3-3 | C3S3-3/P3-TBDI3-3 | JB-618
217 | ZS-60201A | ZS-60201A | ZS-60201A | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-17 | C4S1-19/P4-TBDI1-17 | IS-JB-608
218 | ZS-60201B | ZS-60201B | ZS-60201B | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-18 | C4S1-20/P4-TBDI1-18 | IS-JB-608
219 | ZS-60201C | ZS-60201C | ZS-60201C | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-9 | C4S1-9/P4-TBDI1-9 | IS-JB-603
220 | ZS-60201D | ZS-60201D | ZS-60201D | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-10 | C4S1-10/P4-TBDI1-10 | IS-JB-603
221 | ZS-60201E | ZS-60201E | ZS-60201E | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-11 | C4S1-11/P4-TBDI1-11 | IS-JB-603
222 |  | ZS-60229 | ZS-60229 | 325-01-602-PD-04 | Limit Switch for CY-60230 (Door Service) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-12 | C4S1-12/P4-TBDI1-12 | IS-JB-603
223 |  | ZS-60230 | ZS-60230 | 325-01-602-PD-04 | Limit Switch for CY-60231 (Door Service) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-13 | C4S1-13/P4-TBDI1-13 | IS-JB-603
224 | ZS-60231A | ZS-60231A | ZS-60231A | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Spectacle Inserted) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-14 | C4S1-14/P4-TBDI1-14 | IS-JB-603
225 | ZS-60231B | ZS-60231B | ZS-60231B | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Blind Inserted) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-15 | C4S1-15/P4-TBDI1-15 | IS-JB-603
226 | ZS-60231C | ZS-60231C | ZS-60231C | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Spool Inserted) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-19 | C4S1-21/P4-TBDI1-19 | IS-JB-608
227 | ZS-60231D | ZS-60231D | ZS-60231D | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Blind Inserted) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-20 | C4S1-22/P4-TBDI1-20 | IS-JB-608
228 | ZS-60231E | ZS-60231E | ZS-60231E | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Spool Inserted) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-21 | C4S1-23/P4-TBDI1-21 | IS-JB-608
229 | ZS-60231F | ZS-60231F | ZS-60231F | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Blind Inserted) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-22 | C4S1-24/P4-TBDI1-22 | IS-JB-608
230 |  | ZS-60240 | ZS-60240 | 325-01-602-PD-05 | Limit Switch for FA-60240 (Door Service) | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-23 | C4S1-25/P4-TBDI1-23 | IS-JB-608
231 | ZS-61310 | ZS-61310 | ZS-61310 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S3 | 1756-IB32 | P4-TBDI3-12 | C4S3-12/P4-TBDI3-12 | IS-JB-618
232 | ZS-61311 | ZS-61311 | ZS-61311 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S3 | 1756-IB32 | P4-TBDI3-13 | C4S3-13/P4-TBDI3-13 | IS-JB-618
233 | ZS-61312 | ZS-61312 | ZS-61312 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S2 | 1756-IB32 | P4-TBDI2-14 | C4S2-14/P4-TBDI2-14 | IS-JB-612
234 | ZS-61313 | ZS-61313 | ZS-61313 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S2 | 1756-IB32 | P4-TBDI2-15 | C4S2-15/P4-TBDI2-15 | IS-JB-612
246 |  | ES-60201 | ES-60201 |  | Emergency stop activated @ Spray Nozzle 7th Floor | E-Stop Swtich | DI | On-Off |  | MISSING | - | - | - | - | - | -
246 |  | ES-60202 | ES-60202 |  | Emergency stop activated @ Sight glass 6th Floor | E-Stop Swtich | DI | On-Off |  | MISSING | - | - | - | - | - | -
246 |  | ES-60203 | ES-60203 |  | Emergency stop activated @ Control Room | E-Stop Swtich | DI | On-Off |  | MISSING | - | - | - | - | - | -
246 |  | ES-61301 | ES-61301 |  | Emergency stop activated @ SC-61301,SC-61302 | E-Stop Swtich | DI | On-Off |  | MISSING | - | - | - | - | - | -
247 | DEDERT SUPPLY EQUIPMENT |  | DEDERT SUPPLY EQUIPMENT |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
248 | FT-60701 | FT-60207 | FT-60207 | 325-01-602-PD-07 | Instr. Air Flow Transmitter for Camera #4 (ACAM-21) | Flow Transmitter | AI |  |  | MAPPED | C3 | C3S7 | 1756-IF16 | P3-TBAI2-1(B) | C3S7-1/P3-TBAI2-1(B) | JB-607
249 | PT-60701 | PT-60207 | PT-60207 | 325-01-602-PD-07 | Instr. Air Pressure Transmitter for Camera #4 (ACAM-21) | Pressure Transmitter | AI |  |  | MAPPED | C3 | C3S8 | 1756-IF16 | P3-TBAI3-4(B) | C3S8-7/P3-TBAI3-4(B) | JB-607
250 | SV-60240D | XV-60240D | XV-60240D | 325-01-602-PD-05 | PA On/Off Valve for Bag House Tank Valve (BGHS-21) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-18 | C1S7-20/P1-TBDI4-18 | JB-601
251 | SV-60701 | SV-60207 | SV-60207 | 325-01-602-PD-07 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) | On/Off Valve | DO | On-Off |  | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-9 | C2S3-9/P2-TBDI3-9 | JB-607
252 | SV-60201 | SV-60201 | SV-60201 | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) | On/Off Valve | DO | On-Off |  | MAPPED | C1 | C1S6 | 1756-IB32 | P1-TBDI3-20 | C1S6-22/P1-TBDI3-20 | JB-601
|  | SSL-60201 | SSL-60201 | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-21) | Low Speed Switch | DI | On-Off |  | MISSING | - | - | - | - | - | -
|  | ZS-60201 | ZS-60201 | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-21/ RV-60201) Casing Closed | Position switch | DI | On-Off |  | MISSING | - | - | - | - | - | -
253 | SV-60202 | SV-60202 | SV-60202 | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C1 | C1S6 | 1756-IB32 | P1-TBDI3-22 | C1S6-24/P1-TBDI3-22 | JB-601
|  | SSL-60202 | SSL-60202 | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-22) | Low Speed Switch | DI | On-Off |  | MISSING | - | - | - | - | - | -
|  | ZS-60202 | ZS-60202 | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-22/ RV-60202) Casing Closed | Position switch | DI | On-Off |  | MISSING | - | - | - | - | - | -
254 | SV-60203 | SV-60203 | SV-60203 | 325-01-602-PD-08 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C1 | C1S6 | 1756-IB32 | P1-TBDI3-24 | C1S6-26/P1-TBDI3-24 | JB-601
|  | SSL-60203 | SSL-60203 | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-23) | Low Speed Switch | DI | On-Off |  | MISSING | - | - | - | - | - | -
|  | ZS-60203 | ZS-60203 | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-23/ RV-60203) Casing Closed | Position switch | DI | On-Off |  | MISSING | - | - | - | - | - | -
255 | SV-61304 | SV-61304 | SV-61304 | 325-01-613-PD-01 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C3 | C3S3 | 1756-IB32 | P3-TBDI3-9 | C3S3-9/P3-TBDI3-9 | JB-618
|  | SSL-61304 | SSL-61304 | 325-01-613-PD-01 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-31) | Low Speed Switch | DI | On-Off |  | MISSING | - | - | - | - | - | -
|  | ZS-61304 | ZS-61304 | 325-01-613-PD-01 | Position - Rotary Valve (RVAL-31/ RV-61304) Casing Closed | Position switch | DI | On-Off |  | MISSING | - | - | - | - | - | -
256 | TT-60701 | TT-60207 | TT-60207 | 325-01-602-PD-07 | Instr. Air Temperature Transmitter for Air Manifold - Camera #4 (ACAM-21) | Temperature Transmitter | AI |  |  | MAPPED | C3 | C3S8 | 1756-IF16 | P3-TBAI3-10(B) | C3S8-21/P3-TBAI3-10(B) | JB-607
257 | XV-60261FA | XV-60261FA | XV-60261FA | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-25 | C2S3-27/P2-TBDI3-25 | JB-607
258 | XV-60261FB | XV-60261FB | XV-60261FB | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-29 | C2S3-31/P2-TBDI3-29 | JB-607
259 | XV-60261FC | XV-60261FC | XV-60261FC | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-1 | C2S4-1/P2-TBDI4-1 | JB-607
260 | XV-60261FD | XV-60261FD | XV-60261FD | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-5 | C2S4-5/P2-TBDI4-5 | JB-607
261 | XV-60261SA | XV-60261SA | XV-60261SA | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-9 | C2S4-9/P2-TBDI4-9 | JB-607
262 | XV-60261SB | XV-60261SB | XV-60261SB | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-11 | C2S4-11/P2-TBDI4-11 | JB-607
263 | XV-60261SC | XV-60261SC | XV-60261SC | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-13 | C2S4-13/P2-TBDI4-13 | JB-607
264 | XV-60261SD | XV-60261SD | XV-60261SD | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-15 | C2S4-15/P2-TBDI4-15 | JB-607
265 | XV-60262FE | XV-60262FE | XV-60262FE | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-19 | C2S4-21/P2-TBDI4-19 | JB-607
266 | XV-60262FF | XV-60262FF | XV-60262FF | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-21 | C2S4-23/P2-TBDI4-21 | JB-607
267 | XV-60262FG | XV-60262FG | XV-60262FG | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-23 | C2S4-25/P2-TBDI4-23 | JB-607
268 | XV-60262FH | XV-60262FH | XV-60262FH | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-25 | C2S4-27/P2-TBDI4-25 | JB-607
269 | XV-60262SE | XV-60262SE | XV-60262SE | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-27 | C2S4-29/P2-TBDI4-27 | JB-607
270 | XV-60262SF | XV-60262SF | XV-60262SF | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-29 | C2S4-31/P2-TBDI4-29 | JB-607
271 | XV-60262SG | XV-60262SG | XV-60262SG | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-31 | C2S4-33/P2-TBDI4-31 | JB-607
272 | XV-60262SH | XV-60262SH | XV-60262SH | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S5 | 1756-IB32 | P2-TBDI5-1 | C2S5-1/P2-TBDI5-1 | JB-607
273 | XV-60263FJ | XV-60263FJ | XV-60263FJ | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S5 | 1756-IB32 | P2-TBDI5-5 | C2S5-5/P2-TBDI5-5 | JB-607
274 | XV-60263FK | XV-60263FK | XV-60263FK | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S5 | 1756-IB32 | P2-TBDI5-7 | C2S5-7/P2-TBDI5-7 | JB-607
275 | XV-60263FL | XV-60263FL | XV-60263FL | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S5 | 1756-IB32 | P2-TBDI5-9 | C2S5-9/P2-TBDI5-9 | JB-607
276 | XV-60263FM | XV-60263FM | XV-60263FM | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S5 | 1756-IB32 | P2-TBDI5-11 | C2S5-11/P2-TBDI5-11 | JB-607
277 | XV-60263SJ | XV-60263SJ | XV-60263SJ | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S5 | 1756-IB32 | P2-TBDI5-13 | C2S5-13/P2-TBDI5-13 | JB-607
278 | XV-60263SK | XV-60263SK | XV-60263SK | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S5 | 1756-IB32 | P2-TBDI5-15 | C2S5-15/P2-TBDI5-15 | JB-607
279 | XV-60263SL | XV-60263SL | XV-60263SL | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S5 | 1756-IB32 | P2-TBDI5-17 | C2S5-19/P2-TBDI5-17 | JB-607
280 | XV-60263SM | XV-60263SM | XV-60263SM | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S5 | 1756-IB32 | P2-TBDI5-19 | C2S5-21/P2-TBDI5-19 | JB-607
281 | XV-60264FN | XV-60264FN | XV-60264FN | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-13 | C2S3-13/P2-TBDI3-13 | JB-607
282 | XV-60264FP | XV-60264FP | XV-60264FP | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-15 | C2S3-15/P2-TBDI3-15 | JB-607
283 | XV-60264FQ | XV-60264FQ | XV-60264FQ | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-19 | C2S3-21/P2-TBDI3-19 | JB-607
284 | XV-60264FR | XV-60264FR | XV-60264FR | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-23 | C2S3-25/P2-TBDI3-23 | JB-607
285 | XV-60264SN | XV-60264SN | XV-60264SN | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-27 | C2S3-29/P2-TBDI3-27 | JB-607
286 | XV-60264SP | XV-60264SP | XV-60264SP | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-31 | C2S3-33/P2-TBDI3-31 | JB-607
287 | XV-60264SQ | XV-60264SQ | XV-60264SQ | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-3 | C2S4-3/P2-TBDI4-3 | JB-607
288 | XV-60264SR | XV-60264SR | XV-60264SR | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S4 | 1756-IB32 | P2-TBDI4-7 | C2S4-7/P2-TBDI4-7 | JB-607
289 |  | XV-60261DA | XV-60261DA | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11A | On/Off Valve | DO, DI | On-Off |  | MISSING | - | - | - | - | - | -
290 |  | XV-60262DE | XV-60262DE | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11B | On/Off Valve | DO, DI | On-Off |  | MISSING | - | - | - | - | - | -
291 |  | XV-60263DN | XV-60263DN | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11C | On/Off Valve | DO, DI | On-Off |  | MISSING | - | - | - | - | - | -
292 |  | XV-60264DJ | XV-60264DJ | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11D | On/Off Valve | DO, DI | On-Off |  | MISSING | - | - | - | - | - | -
293 | XV-60241 | XV-60241 | XV-60241 | 325-01-602-PD-05 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | On/Off Valve | DO, DI | On-Off |  | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-22 | C2S2-24/P2-TBDI2-22 | JB-602
294 | XV-60240 | XV-60240 | XV-60240 | 325-01-602-PD-08 | Powder On/Off Valve for Diverter Valve (DVTR-21) | On/Off Valve | DO, DI | On-Off |  | MISSING | - | - | - | - | - | -
295 | Machine Equipment Supply |  | Machine Equipment Supply |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
296 | PSE-61300 | PSE-61300 | PSE-61300 | 325-01-613-PD-01 | Explosion Vent PSE-61300 | Position switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S3 | 1756-IB32 | P4-TBDI3-7 | C4S3-7/P4-TBDI3-7 | IS-JB-618
297 | PSE-61301 | PSE-61301 | PSE-61301 | 325-01-613-PD-01 | Explosion Vent PSE-61301 | Position switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S3 | 1756-IB32 | P4-TBDI3-8 | C4S3-8/P4-TBDI3-8 | IS-JB-618
298 | ISV-61302 | ISV-61302 | ISV-61302 | 325-01-613-PD-01 | Explosion isolation flap valve ISV-61302 | Position switch | DI | On-Off | Ex ic | MISSING | - | - | - | - | - | -
299 | PSE-61302 | PSE-61302 | PSE-61302 | 325-01-613-PD-03 | Explosion Vent PSE-61302 | Position switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S2 | 1756-IB32 | P4-TBDI2-7 | C4S2-7/P4-TBDI2-7 | IS-JB-612
300 | PSE-61303 | PSE-61303 | PSE-61303 | 325-01-613-PD-05 | Explosion Vent PSE-61303 | Position switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S2 | 1756-IB32 | P4-TBDI2-8 | C4S2-8/P4-TBDI2-8 | IS-JB-612
301 | PSE-61304 | PSE-61304 | PSE-61304 | 325-01-613-PD-01 | Explosion Vent PSE-61304 | Position switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S3 | 1756-IB32 | P4-TBDI3-9 | C4S3-9/P4-TBDI3-9 | IS-JB-618
302 | PSV-61301A | ZS-61306 | ZS-61306 | 325-01-613-PD-01 | Position Brether Valve High Pressure PSV-61301 | Position switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S3 | 1756-IB32 | P4-TBDI3-10 | C4S3-10/P4-TBDI3-10 | IS-JB-618
303 | PSV-61301B | ZS-61307 | ZS-61307 | 325-01-613-PD-01 | Position Brether Valve Vacuum Pressure PSV-61301 | Position switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S3 | 1756-IB32 | P4-TBDI3-11 | C4S3-11/P4-TBDI3-11 | IS-JB-618
304 | ISV-61303 | ISV-61303 | ISV-61303 | 325-01-613-PD-03 | Explosion isolation flap valve ISV-61303 | Position switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S2 | 1756-IB32 | P4-TBDI2-1 | C4S2-1/P4-TBDI2-1 | IS-JB-612
305 | ISV-61304 | ISV-61304 | ISV-61304 | 325-01-613-PD-05 | Explosion isolation flap valve ISV-61304 | Position switch | DI | On-Off | Ex ic | MAPPED | C4 | C4S2 | 1756-IB32 | P4-TBDI2-2 | C4S2-2/P4-TBDI2-2 | IS-JB-612
306 | MCC ROOM |  | MCC ROOM |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
307 | ATY-40101 | AT-40201 | AT-40201 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40201 |  | BUS | On-Off |  | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-1 | C4S1-1/P4-TBDI1-1 | IS-JB-603
308 | ATY-40102 | AT-40202 | AT-40202 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40202 |  | BUS | On-Off |  | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-2 | C4S1-2/P4-TBDI1-2 | IS-JB-603
309 | ATY-40201 | AT-40203 | AT-40203 | 325-01-402-PD-02 | Start / Stop Command for VSD AT-40203 |  | BUS | On-Off |  | MAPPED | C4 | C4S1 | 1756-IB32 | P4-TBDI1-3 | C4S1-3/P4-TBDI1-3 | IS-JB-603
310 | BFY-60210 | BF-60210 | BF-60210 | 325-01-602-PD-03 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
311 | BFY-60211 | BF-60211 | BF-60211 | 325-01-602-PD-03 | Start / Stop Command for VSD FANC-21 (Combustion Fan) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
312 | BFY-60240 | BF-60240 | BF-60240 | 325-01-602-PD-05 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
313 | BFY-60220 | BF-60220 | BF-60220 | 325-01-602-PD-04 | Start / Stop Command for VSD FANS-22 (Cooling Fan) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
314 | BFY-60206 | BF-60206 | BF-60206 | 325-01-602-PD-08 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
315 | BFY-61301 | BF-61301 | BF-61301 | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
316 | BFY-61302 | BF-61302 | BF-61302 | 325-01-613-PD-05 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
317 | BFY-61303 | BF-61303 | BF-61303 | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
318 | BLM-61302 |  | BLM-61302 | 325-01-613-PD-01 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | เปลี่ยนไปจ่ายเป็น Power Feeder | LOCAL / NONE | On-Off |  | MISSING | - | - | - | - | - | -
319 | PCM-60205-B | PD-60202B | PD-60202B | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Oil Pump ) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
320 | PCM-60205-C | PD-60202C | PD-60202C | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 1 ) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
321 | PCM-60205-D | PD-60202D | PD-60202D | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 2 ) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
322 | PCM-60205-E | PD-60202E | PD-60202E | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Main motor Fan ) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
323 | PCY-40201 | PC-40203 | PC-40203 | 325-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
324 | PCY-40101 | PC-40201 | PC-40201 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40201 |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
325 | PCY-40102 | PC-40202 | PC-40202 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40202 |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
326 |  | PD-40204 | PD-40204 | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40204 |  | BUS | On-Off | - | MISSING | - | - | - | - | - | -
327 |  | PD-40205 | PD-40205 | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40205 |  | BUS | On-Off | - | MISSING | - | - | - | - | - | -
328 | PCY-60205-A | PD-60202A | PD-60202A | 325-01-602-PD-01 | Start / Stop Command for VSD PUPD-11 (Positive Displacement Pump ) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
329 | PCY-60215 |  | PCY-60215 | 325-01-602-PD-03 | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
330 | PVM-61301 | BL-61301 | BL-61301 | 325-01-613-PD-03 | Start / Stop Command for FVNR PV-61301 (Vacuum Cleaning Fan) |  | BUS | On-Off |  | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-3 | C3S2-3/P3-TBDI2-3 | JB-612
331 | RVM-60201 |  | RVM-60201 | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
332 | RVM-60202 |  | RVM-60202 | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
333 | RVM-60203 |  | RVM-60203 | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
334 | RVM-60204 |  | RVM-60204 | 325-01-602-PD-08 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
335 | RVM-61301 |  | RVM-61301 | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61301 |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
336 | RVM-61302 |  | RVM-61302 | 325-01-613-PD-03 | Start / Stop Command for FVNR RV-61302 |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
337 | RVM-61303 |  | RVM-61303 | 325-01-613-PD-05 | Start / Stop Command for FVNR RV-61303 |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
338 | RVM-61304 |  | RVM-61304 | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61304 |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
339 | RVM-61305 |  | RVM-61305 | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61305 |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
340 | SCM-61301 |  | SCM-61301 | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61301 (Sifter ) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
341 | SCM-61302 |  | SCM-61302 | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61302 (Sifter ) |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
342 | B&B Packing |  | B&B Packing |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
343 | XA-61301A | XA-61301A | XA-61301A | 325-01-613-PD-02 | Request filter plant (Fugitive) | Request filter plant | DI | On-Off | - | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-5 | C3S2-5/P3-TBDI2-5 | JB-612
344 | XA-61301B | XA-61301B | XA-61301B | 325-01-613-PD-02 | Request material transport | Request material transport | DI | On-Off | - | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-6 | C3S2-6/P3-TBDI2-6 | JB-612
345 | XA-61301C | XA-61301C | XA-61301C | 325-01-613-PD-02 | Request belt plant | Request belt plant | DI | On-Off | - | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-7 | C3S2-7/P3-TBDI2-7 | JB-612
346 | XA-61301D | XA-61301D | XA-61301D | 325-01-613-PD-02 | Machine in operation | Machine in operation | DI | On-Off | - | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-8 | C3S2-8/P3-TBDI2-8 | JB-612
347 | XA-61301E | XA-61301E | XA-61301E | 325-01-613-PD-02 | General Fault | General Fault | DI | On-Off | - | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-9 | C3S2-9/P3-TBDI2-9 | JB-612
348 | XA-61301F | XA-61301F | XA-61301F | 325-01-613-PD-02 | Machine is ready | Machine is ready | DI | On-Off | - | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-10 | C3S2-10/P3-TBDI2-10 | JB-612
349 | XA-61301G | XA-61301G | XA-61301G | 325-01-613-PD-02 | Emergency stop activated | Emergency stop activated | DI | On-Off | - | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-11 | C3S2-11/P3-TBDI2-11 | JB-612
350 | XA-61301H | XA-61301H | XA-61301H | 325-01-613-PD-02 | Silo minimum | Silo minimum | DI | On-Off | - | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-12 | C3S2-12/P3-TBDI2-12 | JB-612
351 | XA-61301J | XA-61301J | XA-61301J | 325-01-613-PD-02 | Silo maximum | Silo maximum | DI | On-Off | - | MAPPED | C3 | C3S2 | 1756-IB32 | P3-TBDI2-13 | C3S2-13/P3-TBDI2-13 | JB-612
352 | XS-61301A | XS-61301A | XS-61301A | 325-01-613-PD-02 | Filter plant in operation | Filter plant in operation | DO | On-Off | - | MAPPED | C3 | C3S4 | 1756-OB32 | P3-TBRL1-24 | C3S4-26/P3-TBRL1-24 | JB-612
353 | XS-61301B | XS-61301B | XS-61301B | 325-01-613-PD-02 | Material transport in operation | Material transport in operation | DO | On-Off | - | MAPPED | C3 | C3S4 | 1756-OB32 | P3-TBRL1-25 | C3S4-27/P3-TBRL1-25 | JB-612
354 | XS-61301C | XS-61301C | XS-61301C | 325-01-613-PD-02 | Belt plant in operation | Belt plant in operation | DO | On-Off | - | MAPPED | C3 | C3S4 | 1756-OB32 | P3-TBRL1-26 | C3S4-28/P3-TBRL1-26 | JB-612
355 | XS-61301D | XS-61301D | XS-61301D | 325-01-613-PD-02 | Sequence Stop | Sequence Stop | DO | On-Off | - | MAPPED | C3 | C3S4 | 1756-OB32 | P3-TBRL1-27 | C3S4-29/P3-TBRL1-27 | JB-612
356 | XS-61301E | XS-61301E | XS-61301E | 325-01-613-PD-02 | Status from Customer Emergency stop | Status from Customer Emergency stop | DO | On-Off | - | MAPPED | C3 | C3S4 | 1756-OB32 | P3-TBRL1-28 | C3S4-30/P3-TBRL1-28 | JB-612
357 | XS-61301F | XS-61301F | XS-61301F | 325-01-613-PD-02 | Operation Release | Operation Release | DO | On-Off | - | MAPPED | C3 | C3S4 | 1756-OB32 | P3-TBRL1-29 | C3S4-31/P3-TBRL1-29 | JB-612
362 | Boiler |  | Boiler |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
363 |  | XA-92201B | XA-92201B | 325-01-922-PD-03 | Boiler common alarm |  | DI | On-Off | - | MISSING | - | - | - | - | - | -
363 |  | XA-92201C | XA-92201C | 325-01-922-PD-03 | Boiler Trip |  | DI | On-Off | - | MISSING | - | - | - | - | - | -
363 |  | XA-92212B | XA-92212B | 325-01-922-PD-03 | Burner Trip |  | DI | On-Off | - | MISSING | - | - | - | - | - | -
363 |  | XL-92201B | XL-92201B | 325-01-922-PD-03 | Boiler Operate |  | DI | On-Off | - | MISSING | - | - | - | - | - | -
363 |  | XL-92201C | XL-92201C | 325-01-922-PD-03 | Remote Setpoint Activated |  | DI | On-Off | - | MISSING | - | - | - | - | - | -
363 |  | ZL-92201 | ZL-92201 | 325-01-922-PD-03 | Remote Setpoint Status |  | DI | On-Off | - | MISSING | - | - | - | - | - | -
| Bin Vent Filter (FA-61301) |  | Bin Vent Filter (FA-61301) |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
363 |  | XA-FA-61301A | XA-FA-61301A | 325-01-613-PD-01 | Start / Stop Command for FA-61301 |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
364 |  | XA-FA-61301B | XA-FA-61301B | 325-01-613-PD-01 | Compress air low (Spare) |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
365 |  | XS-FA-61301 | XS-FA-61301 | 325-01-613-PD-01 | Alarm 1 |  | DI | On-Off | - | MISSING | - | - | - | - | - | -
| Fugitive Dust Filter (FA-61310) |  | Fugitive Dust Filter (FA-61310) |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
363 |  | XA-FA-61310A | XA-FA-61310A | 325-01-613-PD-01 | Start / Stop Command for FA-61310 |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
364 |  | XA-FA-61310B | XA-FA-61310B | 325-01-613-PD-01 | Compress air low (Spare) |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
365 |  | XS-FA-61310 | XS-FA-61310 | 325-01-613-PD-01 | Alarm 1 |  | DI | On-Off | - | MISSING | - | - | - | - | - | -
| Vacuum Cleaner Filter (FA-61311) |  | Vacuum Cleaner Filter (FA-61311) |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
363 |  | XA-FA-61311A | XA-FA-61311A | 325-01-613-PD-03 | Start / Stop Command for FA-61311 |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
364 |  | XA-FA-61311B | XA-FA-61311B | 325-01-613-PD-03 | Compress air low (Spare) |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
365 |  | XS-FA-61311 | XS-FA-61311 | 325-01-613-PD-03 | Alarm 1 |  | DI | On-Off | - | MISSING | - | - | - | - | - | -
| Local Exhaust Ventilation Filter (FA-61312) |  | Local Exhaust Ventilation Filter (FA-61312) |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
363 |  | XA-FA-61312A | XA-FA-61312A | 325-01-613-PD-05 | Start / Stop Command for FA-61311 |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
364 |  | XA-FA-61312B | XA-FA-61312B | 325-01-613-PD-05 | Compress air low (Spare) |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
365 |  | XS-FA-61312 | XS-FA-61312 | 325-01-613-PD-05 | Alarm 1 |  | DI | On-Off | - | MISSING | - | - | - | - | - | -
362 | Bag Filter Control Panel (FA-60240) |  | Bag Filter Control Panel (FA-60240) |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
363 | XS-60240A | XS-60240A | XS-60240A | 325-01-602-PD-05 | Start / Stop Command for BGHS-21 (Bag House Air Pulsing) |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
364 | XS-60240B | XS-60240B | XS-60240B | 325-01-602-PD-05 | Fan Command for BGHS-21 (Bag House Air Pulsing) |  | DO | On-Off | - | MAPPED | C2 | C2S6 | 1756-OB32 | P2-TBRL1-17 | C2S6-19/P2-TBRL1-17 | JB-602
365 | XA-60240A | XA-60240A | XA-60240A | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | DI | On-Off | - | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-12 | C2S2-12/P2-TBDI2-12 | JB-602
366 | XA-60240B | XA-60240B | XA-60240B | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | DI | On-Off | - | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-13 | C2S2-13/P2-TBDI2-13 | JB-602
367 | DPI-60240 |  | DPI-60240 | 325-01-602-PD-05 | Gas Pressure Differntial Pressure (Bag House Air Pulsing) |  | AI |  | - | MAPPED | C1 | C1S11 | 1756-IF16 | P1-TBAI2-1(B) | C1S11-1/P1-TBAI2-1(B) | JB-601
368 | HTRE-21 Heater Control Panel (TRACING) |  | HTRE-21 Heater Control Panel (TRACING) |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
369 | XS-60241A | XS-60241A | XS-60241A | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
370 | XA-60241A | XA-60241A | XA-60241A | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | DI | On-Off | - | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-14 | C2S2-14/P2-TBDI2-14 | JB-602
371 | XA-60241B | XA-60241B | XA-60241B | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | DI | On-Off | - | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-15 | C2S2-15/P2-TBDI2-15 | JB-602
372 | TSH-60241A | TSH-60241A | TSH-60241A | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | DI | 0 - 100 C | Ex d | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-6 | C2S2-6/P2-TBDI2-6 | JB-602
373 | TSL-60241B | TSL-60241B | TSL-60241B | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | DI | 0 - 100 C | Ex d | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-9 | C2S2-9/P2-TBDI2-9 | JB-602
374 | HTRE-22 Heater Control Panel (TRACING) |  | HTRE-22 Heater Control Panel (TRACING) |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
375 | XS-60242A | XS-60242A | XS-60242A | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
376 | XA-60242A | XA-60242A | XA-60242A | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | DI | On-Off | - | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-16 | C2S2-16/P2-TBDI2-16 | JB-602
377 | XA-60242B | XA-60242B | XA-60242B | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | DI | On-Off | - | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-17 | C2S2-19/P2-TBDI2-17 | JB-602
378 | TSH-60242A | TSH-60242A | TSH-60242A | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | DI | 0 - 100 C | Ex d | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-7 | C2S2-7/P2-TBDI2-7 | JB-602
379 | TSL-60242B | TSL-60242B | TSL-60242B | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | DI | 0 - 100 C | Ex d | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-10 | C2S2-10/P2-TBDI2-10 | JB-602
380 | HTRE-23 Heater Control Panel (TRACING) |  | HTRE-23 Heater Control Panel (TRACING) |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
381 | XS-60243A | XS-60243A | XS-60243A | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
382 | XA-60243A | XA-60243A | XA-60243A | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  | DI | On-Off | - | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-18 | C2S2-20/P2-TBDI2-18 | JB-602
383 | XA-60243B | XA-60243B | XA-60243B | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  | DI | On-Off | - | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-19 | C2S2-21/P2-TBDI2-19 | JB-602
384 | TSH-60243A | TSH-60243A | TSH-60243A | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch | DI | 0 - 100 C | Ex d | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-8 | C2S2-8/P2-TBDI2-8 | JB-602
385 | TSL-60243B | TSL-60243B | TSL-60243B | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch | DI | 0 - 100 C | Ex d | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-11 | C2S2-11/P2-TBDI2-11 | JB-602
386 | Air Heater Burner Control Panel (PK-60210) |  | Air Heater Burner Control Panel (PK-60210) |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
387 | XA-FH-60210A | XA-FH-60210A | XA-FH-60210A | 325-01-602-PD-06 | BMS PANEL POWER ON for AHTR-21 |  | DI | On-Off | - | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-1 | C2S3-1/P2-TBDI3-1 | JB-607
388 | XA-FH-60210B | XA-FH-60210B | XA-FH-60210B | 325-01-602-PD-06 | BMS Burner High Fire Purge for AHTR-21 |  | DI | On-Off | - | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-2 | C2S3-2/P2-TBDI3-2 | JB-607
389 | XA-FH-60210C | XA-FH-60210C | XA-FH-60210C | 325-01-602-PD-06 | BMS Burner On for AHTR-21 |  | DI | On-Off | - | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-3 | C2S3-3/P2-TBDI3-3 | JB-607
390 | XA-FH-60210D | XA-FH-60210D | XA-FH-60210D | 325-01-602-PD-06 | BMS BMS Lockout for AHTR-21 |  | DI | On-Off | - | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-4 | C2S3-4/P2-TBDI3-4 | JB-607
391 | XA-FH-60210E | XA-FH-60210E | XA-FH-60210E | 325-01-602-PD-06 | BMS Remote Modet for AHTR-21 |  | DI | On-Off | - | MAPPED | C2 | C2S3 | 1756-IB32 | P2-TBDI3-5 | C2S3-5/P2-TBDI3-5 | JB-607
392 | XS-FH-60210A | XS-FH-60210A | XS-FH-60210A | 325-01-602-PD-06 | Burner Remote Start for AHTR-21 |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
393 | XS-FH-60210B | XS-FH-60210B | XS-FH-60210B | 325-01-602-PD-06 | Dryer Interlocks for AHTR-21 |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
394 | XS-FH-60210C | XS-FH-60210C | XS-FH-60210C | 325-01-602-PD-06 | Remote Reset for AHTR-21 |  | DO | On-Off | - | MAPPED | C2 | C2S7 | 1756-OB32 | P2-TBRL2-2 | C2S7-2/P2-TBRL2-2 | JB-607
395 | XS-FH-60210D | XS-FH-60210D | XS-FH-60210D | 325-01-602-PD-06 | Spare |  | DO | On-Off | - | MAPPED | C2 | C2S7 | 1756-OB32 | P2-TBRL2-3 | C2S7-3/P2-TBRL2-3 | JB-607
396 |  | XS-FH-60210E | XS-FH-60210E | 325-01-602-PD-06 | Exhaust fan run status BF-60240 |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
397 |  | XS-FH-60210F | XS-FH-60210F | 325-01-602-PD-06 | Supply fan run status BF-60210 |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
398 |  | XS-FH-60210G | XS-FH-60210G | 325-01-602-PD-06 | Combusion fan run status BF-60211 |  | DO | On-Off | - | MISSING | - | - | - | - | - | -
399 | TI-FH-60210 | TI-FH-60210 | TI-FH-60210 | 325-01-602-PD-06 | Gas Burner Firing Rate Temp Signal |  | AI | On-Off | - | MAPPED | C3 | C3S8 | 1756-IF16 | P3-TBAI3-7(B) | C3S8-15/P3-TBAI3-7(B) | JB-607
400 | UY-FH-60210A | UY-FH-60210A | UY-FH-60210A | 325-01-602-PD-06 | Comb fan VFD Speed Control |  | AI | On-Off | - | MAPPED | C3 | C3S8 | 1756-IF16 | P3-TBAI3-11(B) | C3S8-23/P3-TBAI3-11(B) | JB-607
401 | UY-FH-60210B | UY-FH-60210B | UY-FH-60210B | 325-01-602-PD-06 | Demand Signal |  | AO | On-Off | - | MAPPED | C3 | C3S12 | 1756-OF8 | P3-TBAO1-5 | C3S12-4/P3-TBAO1-5 | JB-607
402 | COM-FH-60210B | COM-FH-60210B | COM-FH-60210B | 325-01-602-PD-06 | Communication Signal |  | BUS |  | - | MISSING | - | - | - | - | - | -
403 | TE-60212 | TE-60212 | TE-60212 |  | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Element | LOCAL / NONE |  | - | MISSING | - | - | - | - | - | -
404 | DPHL-60230 | DPHL-60230 | DPHL-60230 |  | Gas Pressure Differntial Switch Low for Exhaust Fan (FANE-21) | Pressure Differntial Switch Low | LOCAL / NONE |  | - | MISSING | - | - | - | - | - | -
405 | DPSL-60211 | DPSL-60211 | DPSL-60211 |  | Gas Pressure Differential Switch Low for Combustion Fan (FANC-21) | Pressure Differential Switch Low | LOCAL / NONE |  | - | MISSING | - | - | - | - | - | -
406 | FCV-60211B | FCV-60211B | FCV-60211B |  | Gas Flow Control Damper (Valve) for Burner Combustion Air Duct (DTCB-21) | Flow Control Damper (Valve) | LOCAL / NONE |  | - | MISSING | - | - | - | - | - | -
407 | ZT-60211B | ZT-60211B | ZT-60211B |  | Gas Position Transmitter for Combustion Air Damper Actuator (DTCB-21) | Position Transmitter | LOCAL / NONE |  | - | MISSING | - | - | - | - | - | -
408 | ZSL-60211B | ZSL-60211B | ZSL-60211B |  | Gas Position Switch Low for Combustion Air Damper Actuator (DTCB-21) | Position Switch Low | LOCAL / NONE |  | - | MISSING | - | - | - | - | - | -
409 | ZSH-60211B | ZSH-60211B | ZSH-60211B |  | Gas Position Switch High for Combustion Air Damper Actuator (DTCB-21) | Position Switch High | LOCAL / NONE |  | - | MISSING | - | - | - | - | - | -
410 | VJ-01 (24VDC) | VJ-01 (24VDC) | VJ-01 (24VDC) |  | Valve train J-BOX | Control Box | LOCAL / NONE |  | - | MISSING | - | - | - | - | - | -
411 | VJ-01 (220VAC) | VJ-01 (220VAC) | VJ-01 (220VAC) |  | Valve train J-BOX | Control Box | LOCAL / NONE |  | - | MISSING | - | - | - | - | - | -
412 | UJ-01 (24VDC) | UJ-01 (24VDC) | UJ-01 (24VDC) |  | Valve train J-BOX | Control Box | LOCAL / NONE |  | - | MISSING | - | - | - | - | - | -
413 | UJ-01 (220VAC) | UJ-01 (220VAC) | UJ-01 (220VAC) |  | Valve train J-BOX | Control Box | LOCAL / NONE |  | - | MISSING | - | - | - | - | - | -
414 | PV-60210A | PV-60210A | PV-60210A |  | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
415 | PV-60210B | PV-60210B | PV-60210B |  | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
416 | DPT-60210 | DPT-60210 | DPT-60210 |  | Gas Pressure Differential Switch Low for Main Supply Air Fan (FANS-21) | Pressure Differential Switch Low | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
417 | DPSL-60210B | DPSL-60210B | DPSL-60210B |  | Gas Pressure Differential Switch Low for Air Heater (AHTR-21) | Pressure Differential Switch Low | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
418 | DPSH-60210C | DPSH-60210C | DPSH-60210C |  | Gas Pressure Differential Switch High for Air Heater (AHTR-21) | Pressure Differential Switch High | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
419 | BE-60210A | BE-60210A | BE-60210A |  | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
420 | BE-60210B | BE-60210B | BE-60210B |  | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
421 | IX-60210A | IX-60210A | IX-60210A |  | Gas Ignition Transformer for Air Heater (AHTR-21) | Ignition Transformer | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
422 | FCV-60210A | FCV-60210A | FCV-60210A |  | Gas Flow Control Valve for Air Heater Gas Train (GTRN-21) | Flow Control Valve | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
423 | ZSL-60210A | ZSL-60210A | ZSL-60210A |  | Gas Position Switch Low for Air Heater Gas Train (GTRN-21) | Position Switch Low | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
424 | ZT-60210A | ZT-60210A | ZT-60210A |  | Gas Position Transmitter for Air Heater Gas Train (GTRN-21) | Position Transmitter | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
425 | PSH-60210 | PSH-60210 | PSH-60210 |  | Gas Pressure Switch High for Air Heater Gas Train (GTRN-21) | Pressure Switch High | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
426 | BV-60210B | BV-60210B | BV-60210B |  | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
427 | ZSO-60210B | ZSO-60210B | ZSO-60210B |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
428 | ZSC-60210B | ZSC-60210B | ZSC-60210B |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
429 | VV-60210 | VV-60210 | VV-60210 |  | Gas Venting Valve (main gas) for Air Heater Gas Train (GTRN-21) | Venting Valve (main gas) | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
430 | ZSO-60210C | ZSO-60210C | ZSO-60210C |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
431 | ZSC-60210C | ZSC-60210C | ZSC-60210C |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
432 | PSL-60210 | PSL-60210 | PSL-60210 |  | Gas Pressure Switch Low for Air Heater Gas Train (GTRN-21) | Pressure Switch Low | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
433 | BV-60210A | BV-60210A | BV-60210A |  | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
434 | ZSO-60210A | ZSO-60210A | ZSO-60210A |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
435 | ZSC-60210A | ZSC-60210A | ZSC-60210A |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
436 | High Pressure Pump (PD-60202) |  | High Pressure Pump (PD-60202) |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
437 | ES-60202 | XS-60202 | XS-60202 | 325-01-602-PD-01 | E-Stop for PUPD-11 (Positive Displacement Pump ) | E-Stop | DI |  | - | MAPPED | C1 | C1S6 | 1756-IB32 | P1-TBDI3-17 | C1S6-19/P1-TBDI3-17 | JB-601
438 |  | XA-60202 | XA-60202 | 325-01-602-PD-01 | High Oil Pressure Alarm | Lamp | DO |  | - | MISSING | - | - | - | - | - | -
439 | PT-60205 | PT-60202 | PT-60202 | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter | AI |  |  | MAPPED | C1 | C1S10 | 1756-IF16 | P1-TBAI1-11(B) | C1S10-23/P1-TBAI1-11(B) | JB-401
440 | FS-60205 | FS-60202 | FS-60202 | 325-01-602-PD-01 | Cooling Water Return Flow Switch for Positive Displacement Pump (PUPD-11) | Flow Switch | DI |  | - | MAPPED | C1 | C1S6 | 1756-IB32 | P1-TBDI3-18 | C1S6-20/P1-TBDI3-18 | JB-601
441 | XS-60205 | XS-60205 | XS-60205 | 325-01-602-PD-01 | Start / Stop Command for PUPD-11 (Positive Displacement Pump ) | Start / Stop Command | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
442 | VS-60205 | VS-60202 | VS-60202 | 325-01-602-PD-01 | Vibration Gear Box Vibration Switch for Switch Vibration for PUPD-11 (PUPD-11) | Vibration Switch | AI |  |  | MAPPED | C1 | C1S6 | 1756-IB32 | P1-TBDI3-26 | C1S6-28/P1-TBDI3-26 | JB-601
443 | XV-60205A | XV-60202A | XV-60202A | 325-01-602-PD-01 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) | On/Off Valve | DO |  |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-16 | C1S7-16/P1-TBDI4-16 | JB-601
444 |  | PS-60202 | PS-60202 | 325-01-602-PD-01 | Oil Pressure Switch for Positive Displacement Pump (PUPD-11) | Flow Switch | DI |  | - | MISSING | - | - | - | - | - | -
445 |  | TT-60202A | TT-60202A | 325-01-602-PD-01 | Temperature for Positive Displacement Pump (PUPD-11) | TC / Temperature Transmitter | AI |  | - | MISSING | - | - | - | - | - | -
446 |  | TT-60202B | TT-60202B | 325-01-602-PD-01 | Temperature for Positive Displacement Pump (PUPD-11) | TC / Temperature Transmitter | AI |  | - | MISSING | - | - | - | - | - | -
447 | YA-60205 | YA-60205 | YA-60205 | 325-01-602-PD-01 | Fault Command |  | LOCAL / NONE |  |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-22 | C1S7-24/P1-TBDI4-22 | JB-601
448 | YI-60205 | YI-60205 | YI-60205 | 325-01-602-PD-01 | Run Command |  | LOCAL / NONE |  |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-23 | C1S7-25/P1-TBDI4-23 | JB-601
449 | Suppression Panel |  | Suppression Panel |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
450 | PSH-61301 | PSH-61301 | PSH-61301 | 325-01-613-PD-01 | Gas and Powder Pressure Switch High for Storage Bin Cyclone Inlet Duct (####-##) | Pressure Switch High | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
451 | PSH-60220 | PSH-60220 | PSH-60220 | 325-01-602-PD-04 | Gas Pressure Switch High for Spray Chamber (CHAM-21) | Pressure Switch High | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
452 | PSH-60230 | PSH-60230 | PSH-60230 | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-21) | Pressure Switch High | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
453 | PSH-60231 | PSH-60231 | PSH-60231 | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-22) | Pressure Switch High | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
454 | PSH-60224 | PSH-60224 | PSH-60224 | 325-01-602-PD-05 | Gas and Powder Pressure Switch High for Bag House (BGHS-21) | Pressure Switch High | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
455 | XA-60202A | XA-60202A | XA-60202A | 325-01-602-PD-08 | General Alarm Emergency Stop Actuation for XSUP-5601 (Supression Panel) | General Alarm Emergency Stop Actuation | DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-1 | C1S7-1/P1-TBDI4-1 | JB-601
456 | XA-60202B | XA-60202B | XA-60202B | 325-01-602-PD-08 | General Fault Controlled Stop for XSUP-5601 (Supression Panel) | General Fault Controlled Stop | DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-2 | C1S7-2/P1-TBDI4-2 | JB-601
457 | XA-60202C | XA-60202C | XA-60202C | 325-01-602-PD-08 | General Armed Status Indicator for XSUP-5601 (Supression Panel) | General Armed Status Indicator | DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-3 | C1S7-3/P1-TBDI4-3 | JB-601
458 | XA-60202D | XA-60202D | XA-60202D | 325-01-602-PD-08 | Power Fault Status Indicator for XSUP-5601 (Supression Panel) | Power Fault Status Indicator | DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-4 | C1S7-4/P1-TBDI4-4 | JB-601
459 | XA-60202E | XA-60202E | XA-60202E | 325-01-602-PD-08 | Dryer CHAM-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | Dryer CHAM-21 Emergency Stop Actuation | DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-5 | C1S7-5/P1-TBDI4-5 | JB-601
460 | XA-60202F | XA-60202F | XA-60202F | 325-01-602-PD-08 | CHAM-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CHAM-21 Controlled Stop Trouble (No Protection) | DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-6 | C1S7-6/P1-TBDI4-6 | JB-601
461 | XA-60202G | XA-60202G | XA-60202G | 325-01-602-PD-08 | CYCL-21/22 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-21/22 Emergency Stop Actuation | DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-7 | C1S7-7/P1-TBDI4-7 | JB-601
462 | XA-60202H | XA-60202H | XA-60202H | 325-01-602-PD-08 | CYCL-21/22 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-21/22 Controlled Stop Trouble (No Protection) | DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-8 | C1S7-8/P1-TBDI4-8 | JB-601
463 | XA-60202J | XA-60202J | XA-60202J | 325-01-602-PD-08 | BGHS-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | BGHS-21 Emergency Stop Actuation | DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-10 | C1S7-10/P1-TBDI4-10 | JB-601
464 | XA-60202K | XA-60202K | XA-60202K | 325-01-602-PD-08 | BGHS-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | BGHS-21 Controlled Stop Trouble (No Protection) | DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-11 | C1S7-11/P1-TBDI4-11 | JB-601
465 | XA-60202L | XA-60202L | XA-60202L | 325-01-602-PD-08 | CYCL-31 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-31 Emergency Stop Actuation | DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-12 | C1S7-12/P1-TBDI4-12 | JB-601
466 | XA-60202M | XA-60202M | XA-60202M | 325-01-602-PD-08 | CYCL-31 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-31 Controlled Stop Trouble (No Protection) | DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-13 | C1S7-13/P1-TBDI4-13 | JB-601
467 | Fire Deluge PK-60221 |  | Fire Deluge PK-60221 |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
468 | XA-60261 | XA-60221A | XA-60221A | 325-01-602-PD-04 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Fire Deluge Fault (No Protection) | DI | On-Off |  | MAPPED | C3 | C3S1 | 1756-IB32 | P3-TBDI1-19 | C3S1-21/P3-TBDI1-19 | JB-606
469 | XA-60262 | XA-60221B | XA-60221B | 325-01-602-PD-04 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Fire Deluge Alarm (Deluge Activated) | DI | On-Off |  | MAPPED | C3 | C3S1 | 1756-IB32 | P3-TBDI1-20 | C3S1-22/P3-TBDI1-20 | JB-606
470 | XS-60260 | XS-60221 | XS-60221 | 325-01-602-PD-04 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command | DO | On-Off |  | MISSING | - | - | - | - | - | -
139 |  | TSH-60230 | TSH-60230 | 325-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | Temperature Switch | LOCAL / NONE | 0 - 140 C |  | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-4 | C2S2-4/P2-TBDI2-4 | JB-602
471 | Fire Deluge PK-60222 |  | Fire Deluge PK-60222 |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
472 |  | XA-60222A | XA-60222A | 325-01-602-PD-05 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Fire Deluge Fault (No Protection) | DI | On-Off |  | MISSING | - | - | - | - | - | -
473 |  | XA-60222B | XA-60222B | 325-01-602-PD-05 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Fire Deluge Alarm (Deluge Activated) | DI | On-Off |  | MISSING | - | - | - | - | - | -
474 |  | XS-60222 | XS-60222 | 325-01-602-PD-05 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command | DO | On-Off |  | MISSING | - | - | - | - | - | -
|  | XV-60240D | XV-60240D | 325-01-602-PD-05 | Drain Valve |  | DI | On-Off |  | MAPPED | C1 | C1S7 | 1756-IB32 | P1-TBDI4-18 | C1S7-20/P1-TBDI4-18 | JB-601
140 |  | TSH-60240 | TSH-60240 | 325-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | Temperature Switch | LOCAL / NONE | 0 - 140 C |  | MAPPED | C2 | C2S2 | 1756-IB32 | P2-TBDI2-5 | C2S2-5/P2-TBDI2-5 | JB-602
475 | Keaser Air Blower |  | Keaser Air Blower |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
476 |  | XS-61302 | XS-61302 | 325-01-613-PD-01 | Start / Stop Command for Bin Aerator Blower | Start / Stop Command | DO | On-Off |  | MISSING | - | - | - | - | - | -
477 |  | XA-61302A | XA-61302A | 325-01-613-PD-01 | Operational / Running status |  | DI | On-Off |  | MISSING | - | - | - | - | - | -
478 |  | XA-61302B | XA-61302B | 325-01-613-PD-01 | Local / Remote status |  | DI | On-Off |  | MISSING | - | - | - | - | - | -
479 |  | XA-61302C | XA-61302C | 325-01-613-PD-01 | Fault / Trip condition |  | DI | On-Off |  | MISSING | - | - | - | - | - | -
480 |  | XA-61302D | XA-61302D | 325-01-613-PD-01 | Warning condition |  | DI | On-Off |  | MISSING | - | - | - | - | - | -
481 | REMOTE I-O Area-200 |  | REMOTE I-O Area-200 |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
482 | HV-2022 | HV-20204 | HV-20204 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-8 | C5S1-8/P5-TBDI1-8 | RIO-200
483 | HV-2024 | HV-20205 | HV-20205 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-9 | C5S1-9/P5-TBDI1-9 | RIO-200
484 | HV-2026 | HV-20206 | HV-20206 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-10 | C5S1-10/P5-TBDI1-10 | RIO-200
485 | HV-2030 | HV-20207 | HV-20207 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-11 | C5S1-11/P5-TBDI1-11 | RIO-200
486 | HV-2032 | HV-20208 | HV-20208 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-12 | C5S1-12/P5-TBDI1-12 | RIO-200
487 | HV-2035 | HV-20209 | HV-20209 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-13 | C5S1-13/P5-TBDI1-13 | RIO-200
488 | HV-2038 | HV-20210 | HV-20210 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-14 | C5S1-14/P5-TBDI1-14 | RIO-200
489 | XV-20201 | XV-20201 | XV-20201 | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | DO, DI | On-Off | Ex d | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-27 | C5S1-29/P5-TBDI1-27 | RIO-200
490 | XV-20202 | XV-20202 | XV-20202 | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | DO, DI | On-Off | Ex d | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-29 | C5S1-31/P5-TBDI1-29 | RIO-200
491 | XV-20203 | XV-20203 | XV-20203 | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve | DO, DI | On-Off | Ex d | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-31 | C5S1-33/P5-TBDI1-31 | RIO-200
492 | XV-20211 | XV-20211 | XV-20211 | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | DO, DI | On-Off | Ex d | MAPPED | C5 | C5S2 | 1756-IB32 | P5-TBDI2-1 | C5S2-1/P5-TBDI2-1 | RIO-200
493 | XV-20212 | XV-20212 | XV-20212 | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | DO, DI | On-Off | Ex d | MAPPED | C5 | C5S2 | 1756-IB32 | P5-TBDI2-3 | C5S2-3/P5-TBDI2-3 | RIO-200
494 | XV-20213 | XV-20213 | XV-20213 | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve | DO, DI | On-Off | Ex d | MAPPED | C5 | C5S2 | 1756-IB32 | P5-TBDI2-5 | C5S2-5/P5-TBDI2-5 | RIO-200
495 | LS-81001 | LS-814201 | LS-814201 | 325-01-814-PD-01 | Level alarm low | Level switch | DI | On-Off | Ex ic | MISSING | - | - | - | - | - | -
496 | PCM-2030 | PC-20201 | PC-20201 | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2030 |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
497 | PCM-2031 |  | PCM-2031 | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2031 | ยกเลิก | DO, DI | On-Off |  | MISSING | - | - | - | - | - | -
498 | PCY-81001 | PC-814201 | PC-814201 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81001 |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
499 | PCY-81002 | PC-814202 | PC-814202 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81002 |  | BUS | On-Off |  | MISSING | - | - | - | - | - | -
500 | LPG Station |  | LPG Station |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
501 | FT-80301 | FT-913201 | FT-913201 | 325-01-913-PD-02 | Flow outlet LPG line | Coriolis Flow Transmitter | DI, AI | 0-1000kg/hr | Ex d | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-2 | C5S1-2/P5-TBDI1-2 | RIO-200
502 | LT-80301 | LT-913201 | LT-913201 | 325-01-913-PD-01 | Level LPG in storage | Level transmitter | AI |  | Ex ia | MAPPED | C5 | C5S4 | 1756-IF16 | P5-TBAI1-6(B) | C5S4-13/P5-TBAI1-6(B) | RIO-200
503 | PT-80302 | PT-913201 | PT-913201 | 325-01-913-PD-02 | Pressure outlet LPG line | Pressure Transmitter | AI | 0 - 10 barg | Ex d | MAPPED | C5 | C5S4 | 1756-IF16 | P5-TBAI1-7(B) | C5S4-15/P5-TBAI1-7(B) | RIO-200
504 |  | XV-913201 | XV-913201 | 325-01-913-PD-02 | Outlet LPG line | Automatic on/off valve | DO, DI | On-Off | Ex d | MAPPED | C5 | C5S2 | 1756-IB32 | P5-TBDI2-7 | C5S2-7/P5-TBDI2-7 | RIO-200
505 | Gas Vaporizer 4 |  | Gas Vaporizer 4 |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
506 | XA-80305A | XA-913201A | XA-913201A | 325-01-913-PD-02 | Gas Vaporizer 4 Run Status | Gas vaporizer Ready | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-15 | C5S1-15/P5-TBDI1-15 | RIO-200
507 | XA-80305B | XA-913201B | XA-913201B | 325-01-913-PD-02 | Gas Vaporizer 4 Alarm status | Gas vaporizer Run | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-16 | C5S1-16/P5-TBDI1-16 | RIO-200
508 | XA-80305C | XA-913201C | XA-913201C | 325-01-913-PD-02 | Gas Vaporizer 4 High Temp Shut-Down status | Gas vaporizer Failed | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-17 | C5S1-19/P5-TBDI1-17 | RIO-200
509 | XA-80305D | XA-913201D | XA-913201D | 325-01-913-PD-02 | Gas Vaporizer 4 Working Temp Shun-Off status | Gas vaporizer Overheated | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-18 | C5S1-20/P5-TBDI1-18 | RIO-200
510 | XA-80305E | XA-913201E | XA-913201E | 325-01-913-PD-02 | Gas Vaporizer 4 Low Water Shun-Off status | Gas vaporizer Excessive flow tripped | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-19 | C5S1-21/P5-TBDI1-19 | RIO-200
512 | XS-80305A | XS-913201A | XS-913201A | 325-01-913-PD-02 | Start Command for Gas Vaporizer 4 | Start Command | DO | On-Off | - | MISSING | - | - | - | - | - | -
512 | XS-80305B | XS-913201B | XS-913201B | 325-01-913-PD-02 | Stop Command for Gas Vaporizer 4 | Stop Command | DO | On-Off | - | MISSING | - | - | - | - | - | -
513 | Gas Vaporizer 5 |  | Gas Vaporizer 5 |  |  |  | LOCAL / NONE |  |  | MISSING | - | - | - | - | - | -
514 | XA-80306A | XA-913202A | XA-913202A | 325-01-913-PD-02 | Gas Vaporizer 5 Run Status | Gas vaporizer Ready | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-21 | C5S1-23/P5-TBDI1-21 | RIO-200
515 | XA-80306B | XA-913202B | XA-913202B | 325-01-913-PD-02 | Gas Vaporizer 5 Alarm status | Gas vaporizer Run | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-22 | C5S1-24/P5-TBDI1-22 | RIO-200
516 | XA-80306C | XA-913202C | XA-913202C | 325-01-913-PD-02 | Gas Vaporizer 5 High Temp Shut-Down status | Gas vaporizer Failed | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-23 | C5S1-25/P5-TBDI1-23 | RIO-200
517 | XA-80306D | XA-913202D | XA-913202D | 325-01-913-PD-02 | Gas Vaporizer 5 Working Temp Shun-Off status | Gas vaporizer Overheated | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-24 | C5S1-26/P5-TBDI1-24 | RIO-200
518 | XA-80306E | XA-913202E | XA-913202E | 325-01-913-PD-02 | Gas Vaporizer 5 Low Water Shun-Off status | Gas vaporizer Excessive flow tripped | DI | On-Off | - | MAPPED | C5 | C5S1 | 1756-IB32 | P5-TBDI1-25 | C5S1-27/P5-TBDI1-25 | RIO-200
519 | XS-80306A | XS-913202A | XS-913202A | 325-01-913-PD-02 | Start Command for Gas Vaporizer 5 | Start Command | DO | On-Off | - | MISSING | - | - | - | - | - | -
520 | XS-80306B | XS-913202B | XS-913202B | 325-01-913-PD-02 | Stop Command for Gas Vaporizer 5 | Stop Command | DO | On-Off | - | MISSING | - | - | - | - | - | -

## Missing IO List
KALASIN ENGINEERING ¦ MISSING / UNMAPPED I/O AUDIT REPORT (REV.3.6a vs PLC SLOT CONFIG)
Instruments & Signals from Client Master Schedule (Rev.3.6a) NOT Currently Assigned to ControlLogix 1756 PLC Hardware Slots
TOTAL MASTER INSTRUMENTS |  |  | MAPPED TO PLC CONFIG |  |  | MISSING / UNMAPPED I/O |  |  | AUDIT ACTION REQUIRED
543 |  |  | 357 |  |  | 186 |  |  | HIGH PRIORITY
Client Rev.3.6a Master Schedule |  |  | Compliance Rate: 65.7% |  |  | Unassigned Rate: 34.3% |  |  | Review Unassigned Tags below
DETAILED SCHEDULE OF MISSING / UNMAPPED I/O INSTRUMENTS & SIGNALS
Item No. | Tag No. | New Tag No. | Active Working Tag | P&ID No. | Description | Instrument / Equipment Name | Required Signal | Signal To (Client) | Missing Category / Technical Cause | Engineering Action Required
9 |  | FSL-20201 | FSL-20201 | 325-01-202-PD-01 | Slurry low flow | Flow Switch | DI | PLC | Field Process Instrument missing from Hardware Slot Config | Assign available Spare AI/DI channel in nearest Remote I/O Slot
44 | HS-61307A | HS-61307A | HS-61307A | 325-01-613-PD-03 | Start/Stop | Hand Switch | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
45 | HS-61307B | HS-61307B | HS-61307B | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
46 | HS-61307C | HS-61307C | HS-61307C | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
47 | HS-61307D | HS-61307D | HS-61307D | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
48 | HS-61307E | HS-61307E | HS-61307E | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
49 | HS-61307F | HS-61307F | HS-61307F | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
50 | HS-61307G | HS-61307G | HS-61307G | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
51 | HS-61307H | HS-61307H | HS-61307H | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
52 | HS-61307I | HS-61307I | HS-61307I | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
53 | HS-61307J | HS-61307J | HS-61307J | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
54 | HS-61307K | HS-61307K | HS-61307K | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
55 | HS-61307L | HS-61307L | HS-61307L | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
56 | HS-61307M | HS-61307M | HS-61307M | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
57 | HS-61307N | HS-61307N | HS-61307N | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
58 | HS-61307O | HS-61307O | HS-61307O | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
59 | HS-61307P | HS-61307P | HS-61307P | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
60 | HS-61307Q | HS-61307Q | HS-61307Q | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
61 | HS-61307R | HS-61307R | HS-61307R | 325-01-613-PD-03 | Start/Stop | Hand Switch | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
86 | LT-40101 | LT-40201 | LT-40201 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 1 | Level transmitter | AI | PLC | Field Process Instrument missing from Hardware Slot Config | Assign available Spare AI/DI channel in nearest Remote I/O Slot
170 | TV-60702 | TCV-60202 | TCV-60202 | 325-01-602-PD-07 | Chiller water control valve | 3-way Control valve | AO | PLC | Unmapped Control / Solenoid Valve | Allocate DO channel for solenoid and AI/AO for positioner
180 | XV-40101B | XV-40201B | XV-40201B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1 | Automatic on/off valve | DO, DI | PLC | Unmapped Control / Solenoid Valve | Allocate DO channel for solenoid and AI/AO for positioner
181 | XV-40101C | XV-40201C | XV-40201C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1 | Automatic on/off valve | DO, DI | PLC | Unmapped Control / Solenoid Valve | Allocate DO channel for solenoid and AI/AO for positioner
182 | XV-40101D | XV-40201D | XV-40201D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 1 | Automatic on/off valve | DO, DI | PLC | Unmapped Control / Solenoid Valve | Allocate DO channel for solenoid and AI/AO for positioner
183 | XV-40101E | XV-40201E | XV-40201E | 325-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | Automatic on/off valve | DO, DI | PLC | Unmapped Control / Solenoid Valve | Allocate DO channel for solenoid and AI/AO for positioner
246 |  | ES-60201 | ES-60201 |  | Emergency stop activated @ Spray Nozzle 7th Floor | E-Stop Swtich | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
246 |  | ES-60202 | ES-60202 |  | Emergency stop activated @ Sight glass 6th Floor | E-Stop Swtich | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
246 |  | ES-60203 | ES-60203 |  | Emergency stop activated @ Control Room | E-Stop Swtich | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
246 |  | ES-61301 | ES-61301 |  | Emergency stop activated @ SC-61301,SC-61302 | E-Stop Swtich | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
247 | DEDERT SUPPLY EQUIPMENT |  | DEDERT SUPPLY EQUIPMENT |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
|  | SSL-60201 | SSL-60201 | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-21) | Low Speed Switch | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
|  | ZS-60201 | ZS-60201 | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-21/ RV-60201) Casing Closed | Position switch | DI | PLC | Field Process Instrument missing from Hardware Slot Config | Assign available Spare AI/DI channel in nearest Remote I/O Slot
|  | SSL-60202 | SSL-60202 | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-22) | Low Speed Switch | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
|  | ZS-60202 | ZS-60202 | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-22/ RV-60202) Casing Closed | Position switch | DI | PLC | Field Process Instrument missing from Hardware Slot Config | Assign available Spare AI/DI channel in nearest Remote I/O Slot
|  | SSL-60203 | SSL-60203 | 325-01-602-PD-08 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-23) | Low Speed Switch | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
|  | ZS-60203 | ZS-60203 | 325-01-602-PD-08 | Position - Rotary Valve (RVAL-23/ RV-60203) Casing Closed | Position switch | DI | PLC | Field Process Instrument missing from Hardware Slot Config | Assign available Spare AI/DI channel in nearest Remote I/O Slot
|  | SSL-61304 | SSL-61304 | 325-01-613-PD-01 | Speed Switch Low for Bin Cyclone Rotary Valve (RVAL-31) | Low Speed Switch | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
|  | ZS-61304 | ZS-61304 | 325-01-613-PD-01 | Position - Rotary Valve (RVAL-31/ RV-61304) Casing Closed | Position switch | DI | PLC | Field Process Instrument missing from Hardware Slot Config | Assign available Spare AI/DI channel in nearest Remote I/O Slot
289 |  | XV-60261DA | XV-60261DA | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11A | On/Off Valve | DO, DI | PLC | Unmapped Control / Solenoid Valve | Allocate DO channel for solenoid and AI/AO for positioner
290 |  | XV-60262DE | XV-60262DE | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11B | On/Off Valve | DO, DI | PLC | Unmapped Control / Solenoid Valve | Allocate DO channel for solenoid and AI/AO for positioner
291 |  | XV-60263DN | XV-60263DN | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11C | On/Off Valve | DO, DI | PLC | Unmapped Control / Solenoid Valve | Allocate DO channel for solenoid and AI/AO for positioner
292 |  | XV-60264DJ | XV-60264DJ | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11D | On/Off Valve | DO, DI | PLC | Unmapped Control / Solenoid Valve | Allocate DO channel for solenoid and AI/AO for positioner
294 | XV-60240 | XV-60240 | XV-60240 | 325-01-602-PD-08 | Powder On/Off Valve for Diverter Valve (DVTR-21) | On/Off Valve | DO, DI | PLC | Unmapped Control / Solenoid Valve | Allocate DO channel for solenoid and AI/AO for positioner
295 | Machine Equipment Supply |  | Machine Equipment Supply |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
298 | ISV-61302 | ISV-61302 | ISV-61302 | 325-01-613-PD-01 | Explosion isolation flap valve ISV-61302 | Position switch | DI | PLC | Unmapped Control / Solenoid Valve | Allocate DO channel for solenoid and AI/AO for positioner
306 | MCC ROOM |  | MCC ROOM |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
310 | BFY-60210 | BF-60210 | BF-60210 | 325-01-602-PD-03 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
311 | BFY-60211 | BF-60211 | BF-60211 | 325-01-602-PD-03 | Start / Stop Command for VSD FANC-21 (Combustion Fan) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
312 | BFY-60240 | BF-60240 | BF-60240 | 325-01-602-PD-05 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
313 | BFY-60220 | BF-60220 | BF-60220 | 325-01-602-PD-04 | Start / Stop Command for VSD FANS-22 (Cooling Fan) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
314 | BFY-60206 | BF-60206 | BF-60206 | 325-01-602-PD-08 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
315 | BFY-61301 | BF-61301 | BF-61301 | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
316 | BFY-61302 | BF-61302 | BF-61302 | 325-01-613-PD-05 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
317 | BFY-61303 | BF-61303 | BF-61303 | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
318 | BLM-61302 |  | BLM-61302 | 325-01-613-PD-01 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) | เปลี่ยนไปจ่ายเป็น Power Feeder | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
319 | PCM-60205-B | PD-60202B | PD-60202B | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Oil Pump ) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
320 | PCM-60205-C | PD-60202C | PD-60202C | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 1 ) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
321 | PCM-60205-D | PD-60202D | PD-60202D | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 2 ) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
322 | PCM-60205-E | PD-60202E | PD-60202E | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Main motor Fan ) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
323 | PCY-40201 | PC-40203 | PC-40203 | 325-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
324 | PCY-40101 | PC-40201 | PC-40201 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40201 |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
325 | PCY-40102 | PC-40202 | PC-40202 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40202 |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
326 |  | PD-40204 | PD-40204 | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40204 |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
327 |  | PD-40205 | PD-40205 | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40205 |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
328 | PCY-60205-A | PD-60202A | PD-60202A | 325-01-602-PD-01 | Start / Stop Command for VSD PUPD-11 (Positive Displacement Pump ) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
329 | PCY-60215 |  | PCY-60215 | 325-01-602-PD-03 | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
331 | RVM-60201 |  | RVM-60201 | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
332 | RVM-60202 |  | RVM-60202 | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
333 | RVM-60203 |  | RVM-60203 | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
334 | RVM-60204 |  | RVM-60204 | 325-01-602-PD-08 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
335 | RVM-61301 |  | RVM-61301 | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61301 |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
336 | RVM-61302 |  | RVM-61302 | 325-01-613-PD-03 | Start / Stop Command for FVNR RV-61302 |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
337 | RVM-61303 |  | RVM-61303 | 325-01-613-PD-05 | Start / Stop Command for FVNR RV-61303 |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
338 | RVM-61304 |  | RVM-61304 | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61304 |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
339 | RVM-61305 |  | RVM-61305 | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61305 |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
340 | SCM-61301 |  | SCM-61301 | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61301 (Sifter ) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
341 | SCM-61302 |  | SCM-61302 | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61302 (Sifter ) |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
342 | B&B Packing |  | B&B Packing |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
362 | Boiler |  | Boiler |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
363 |  | XA-92201B | XA-92201B | 325-01-922-PD-03 | Boiler common alarm |  | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
363 |  | XA-92201C | XA-92201C | 325-01-922-PD-03 | Boiler Trip |  | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
363 |  | XA-92212B | XA-92212B | 325-01-922-PD-03 | Burner Trip |  | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
363 |  | XL-92201B | XL-92201B | 325-01-922-PD-03 | Boiler Operate |  | DI | PLC | Field Process Instrument missing from Hardware Slot Config | Assign available Spare AI/DI channel in nearest Remote I/O Slot
363 |  | XL-92201C | XL-92201C | 325-01-922-PD-03 | Remote Setpoint Activated |  | DI | PLC | Field Process Instrument missing from Hardware Slot Config | Assign available Spare AI/DI channel in nearest Remote I/O Slot
363 |  | ZL-92201 | ZL-92201 | 325-01-922-PD-03 | Remote Setpoint Status |  | DI | PLC | Field Process Instrument missing from Hardware Slot Config | Assign available Spare AI/DI channel in nearest Remote I/O Slot
| Bin Vent Filter (FA-61301) |  | Bin Vent Filter (FA-61301) |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
363 |  | XA-FA-61301A | XA-FA-61301A | 325-01-613-PD-01 | Start / Stop Command for FA-61301 |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
364 |  | XA-FA-61301B | XA-FA-61301B | 325-01-613-PD-01 | Compress air low (Spare) |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
365 |  | XS-FA-61301 | XS-FA-61301 | 325-01-613-PD-01 | Alarm 1 |  | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
| Fugitive Dust Filter (FA-61310) |  | Fugitive Dust Filter (FA-61310) |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
363 |  | XA-FA-61310A | XA-FA-61310A | 325-01-613-PD-01 | Start / Stop Command for FA-61310 |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
364 |  | XA-FA-61310B | XA-FA-61310B | 325-01-613-PD-01 | Compress air low (Spare) |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
365 |  | XS-FA-61310 | XS-FA-61310 | 325-01-613-PD-01 | Alarm 1 |  | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
| Vacuum Cleaner Filter (FA-61311) |  | Vacuum Cleaner Filter (FA-61311) |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
363 |  | XA-FA-61311A | XA-FA-61311A | 325-01-613-PD-03 | Start / Stop Command for FA-61311 |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
364 |  | XA-FA-61311B | XA-FA-61311B | 325-01-613-PD-03 | Compress air low (Spare) |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
365 |  | XS-FA-61311 | XS-FA-61311 | 325-01-613-PD-03 | Alarm 1 |  | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
| Local Exhaust Ventilation Filter (FA-61312) |  | Local Exhaust Ventilation Filter (FA-61312) |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
363 |  | XA-FA-61312A | XA-FA-61312A | 325-01-613-PD-05 | Start / Stop Command for FA-61311 |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
364 |  | XA-FA-61312B | XA-FA-61312B | 325-01-613-PD-05 | Compress air low (Spare) |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
365 |  | XS-FA-61312 | XS-FA-61312 | 325-01-613-PD-05 | Alarm 1 |  | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
362 | Bag Filter Control Panel (FA-60240) |  | Bag Filter Control Panel (FA-60240) |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
363 | XS-60240A | XS-60240A | XS-60240A | 325-01-602-PD-05 | Start / Stop Command for BGHS-21 (Bag House Air Pulsing) |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
368 | HTRE-21 Heater Control Panel (TRACING) |  | HTRE-21 Heater Control Panel (TRACING) |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
369 | XS-60241A | XS-60241A | XS-60241A | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
374 | HTRE-22 Heater Control Panel (TRACING) |  | HTRE-22 Heater Control Panel (TRACING) |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
375 | XS-60242A | XS-60242A | XS-60242A | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
380 | HTRE-23 Heater Control Panel (TRACING) |  | HTRE-23 Heater Control Panel (TRACING) |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
381 | XS-60243A | XS-60243A | XS-60243A | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
386 | Air Heater Burner Control Panel (PK-60210) |  | Air Heater Burner Control Panel (PK-60210) |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
392 | XS-FH-60210A | XS-FH-60210A | XS-FH-60210A | 325-01-602-PD-06 | Burner Remote Start for AHTR-21 |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
393 | XS-FH-60210B | XS-FH-60210B | XS-FH-60210B | 325-01-602-PD-06 | Dryer Interlocks for AHTR-21 |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
396 |  | XS-FH-60210E | XS-FH-60210E | 325-01-602-PD-06 | Exhaust fan run status BF-60240 |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
397 |  | XS-FH-60210F | XS-FH-60210F | 325-01-602-PD-06 | Supply fan run status BF-60210 |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
398 |  | XS-FH-60210G | XS-FH-60210G | 325-01-602-PD-06 | Combusion fan run status BF-60211 |  | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
402 | COM-FH-60210B | COM-FH-60210B | COM-FH-60210B | 325-01-602-PD-06 | Communication Signal |  | BUS | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
403 | TE-60212 | TE-60212 | TE-60212 |  | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Element | LOCAL / NONE | AHTR Control Panel(HCP) | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
404 | DPHL-60230 | DPHL-60230 | DPHL-60230 |  | Gas Pressure Differntial Switch Low for Exhaust Fan (FANE-21) | Pressure Differntial Switch Low | LOCAL / NONE | AHTR Control Panel(HCP) | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
405 | DPSL-60211 | DPSL-60211 | DPSL-60211 |  | Gas Pressure Differential Switch Low for Combustion Fan (FANC-21) | Pressure Differential Switch Low | LOCAL / NONE | AHTR Control Panel(HCP) | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
406 | FCV-60211B | FCV-60211B | FCV-60211B |  | Gas Flow Control Damper (Valve) for Burner Combustion Air Duct (DTCB-21) | Flow Control Damper (Valve) | LOCAL / NONE | AHTR Control Panel(HCP) | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
407 | ZT-60211B | ZT-60211B | ZT-60211B |  | Gas Position Transmitter for Combustion Air Damper Actuator (DTCB-21) | Position Transmitter | LOCAL / NONE | AHTR Control Panel(HCP) | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
408 | ZSL-60211B | ZSL-60211B | ZSL-60211B |  | Gas Position Switch Low for Combustion Air Damper Actuator (DTCB-21) | Position Switch Low | LOCAL / NONE | AHTR Control Panel(HCP) | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
409 | ZSH-60211B | ZSH-60211B | ZSH-60211B |  | Gas Position Switch High for Combustion Air Damper Actuator (DTCB-21) | Position Switch High | LOCAL / NONE | AHTR Control Panel(HCP) | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
410 | VJ-01 (24VDC) | VJ-01 (24VDC) | VJ-01 (24VDC) |  | Valve train J-BOX | Control Box | LOCAL / NONE | AHTR Control Panel(HCP) | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
411 | VJ-01 (220VAC) | VJ-01 (220VAC) | VJ-01 (220VAC) |  | Valve train J-BOX | Control Box | LOCAL / NONE | AHTR Control Panel(HCP) | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
412 | UJ-01 (24VDC) | UJ-01 (24VDC) | UJ-01 (24VDC) |  | Valve train J-BOX | Control Box | LOCAL / NONE | AHTR Control Panel(HCP) | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
413 | UJ-01 (220VAC) | UJ-01 (220VAC) | UJ-01 (220VAC) |  | Valve train J-BOX | Control Box | LOCAL / NONE | AHTR Control Panel(HCP) | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
414 | PV-60210A | PV-60210A | PV-60210A |  | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
415 | PV-60210B | PV-60210B | PV-60210B |  | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
416 | DPT-60210 | DPT-60210 | DPT-60210 |  | Gas Pressure Differential Switch Low for Main Supply Air Fan (FANS-21) | Pressure Differential Switch Low | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
417 | DPSL-60210B | DPSL-60210B | DPSL-60210B |  | Gas Pressure Differential Switch Low for Air Heater (AHTR-21) | Pressure Differential Switch Low | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
418 | DPSH-60210C | DPSH-60210C | DPSH-60210C |  | Gas Pressure Differential Switch High for Air Heater (AHTR-21) | Pressure Differential Switch High | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
419 | BE-60210A | BE-60210A | BE-60210A |  | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
420 | BE-60210B | BE-60210B | BE-60210B |  | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
421 | IX-60210A | IX-60210A | IX-60210A |  | Gas Ignition Transformer for Air Heater (AHTR-21) | Ignition Transformer | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
422 | FCV-60210A | FCV-60210A | FCV-60210A |  | Gas Flow Control Valve for Air Heater Gas Train (GTRN-21) | Flow Control Valve | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
423 | ZSL-60210A | ZSL-60210A | ZSL-60210A |  | Gas Position Switch Low for Air Heater Gas Train (GTRN-21) | Position Switch Low | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
424 | ZT-60210A | ZT-60210A | ZT-60210A |  | Gas Position Transmitter for Air Heater Gas Train (GTRN-21) | Position Transmitter | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
425 | PSH-60210 | PSH-60210 | PSH-60210 |  | Gas Pressure Switch High for Air Heater Gas Train (GTRN-21) | Pressure Switch High | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
426 | BV-60210B | BV-60210B | BV-60210B |  | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
427 | ZSO-60210B | ZSO-60210B | ZSO-60210B |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
428 | ZSC-60210B | ZSC-60210B | ZSC-60210B |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
429 | VV-60210 | VV-60210 | VV-60210 |  | Gas Venting Valve (main gas) for Air Heater Gas Train (GTRN-21) | Venting Valve (main gas) | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
430 | ZSO-60210C | ZSO-60210C | ZSO-60210C |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
431 | ZSC-60210C | ZSC-60210C | ZSC-60210C |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
432 | PSL-60210 | PSL-60210 | PSL-60210 |  | Gas Pressure Switch Low for Air Heater Gas Train (GTRN-21) | Pressure Switch Low | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
433 | BV-60210A | BV-60210A | BV-60210A |  | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
434 | ZSO-60210A | ZSO-60210A | ZSO-60210A |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
435 | ZSC-60210A | ZSC-60210A | ZSC-60210A |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | LOCAL / NONE | AHTR Control Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
436 | High Pressure Pump (PD-60202) |  | High Pressure Pump (PD-60202) |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
438 |  | XA-60202 | XA-60202 | 325-01-602-PD-01 | High Oil Pressure Alarm | Lamp | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
441 | XS-60205 | XS-60205 | XS-60205 | 325-01-602-PD-01 | Start / Stop Command for PUPD-11 (Positive Displacement Pump ) | Start / Stop Command | LOCAL / NONE | PLC | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
444 |  | PS-60202 | PS-60202 | 325-01-602-PD-01 | Oil Pressure Switch for Positive Displacement Pump (PUPD-11) | Flow Switch | DI | PLC | Field Process Instrument missing from Hardware Slot Config | Assign available Spare AI/DI channel in nearest Remote I/O Slot
445 |  | TT-60202A | TT-60202A | 325-01-602-PD-01 | Temperature for Positive Displacement Pump (PUPD-11) | TC / Temperature Transmitter | AI | PLC | Field Process Instrument missing from Hardware Slot Config | Assign available Spare AI/DI channel in nearest Remote I/O Slot
446 |  | TT-60202B | TT-60202B | 325-01-602-PD-01 | Temperature for Positive Displacement Pump (PUPD-11) | TC / Temperature Transmitter | AI | PLC | Field Process Instrument missing from Hardware Slot Config | Assign available Spare AI/DI channel in nearest Remote I/O Slot
449 | Suppression Panel |  | Suppression Panel |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
450 | PSH-61301 | PSH-61301 | PSH-61301 | 325-01-613-PD-01 | Gas and Powder Pressure Switch High for Storage Bin Cyclone Inlet Duct (####-##) | Pressure Switch High | LOCAL / NONE | Suppression Sys. Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
451 | PSH-60220 | PSH-60220 | PSH-60220 | 325-01-602-PD-04 | Gas Pressure Switch High for Spray Chamber (CHAM-21) | Pressure Switch High | LOCAL / NONE | Suppression Sys. Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
452 | PSH-60230 | PSH-60230 | PSH-60230 | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-21) | Pressure Switch High | LOCAL / NONE | Suppression Sys. Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
453 | PSH-60231 | PSH-60231 | PSH-60231 | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-22) | Pressure Switch High | LOCAL / NONE | Suppression Sys. Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
454 | PSH-60224 | PSH-60224 | PSH-60224 | 325-01-602-PD-05 | Gas and Powder Pressure Switch High for Bag House (BGHS-21) | Pressure Switch High | LOCAL / NONE | Suppression Sys. Panel | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
467 | Fire Deluge PK-60221 |  | Fire Deluge PK-60221 |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
470 | XS-60260 | XS-60221 | XS-60221 | 325-01-602-PD-04 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
471 | Fire Deluge PK-60222 |  | Fire Deluge PK-60222 |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
472 |  | XA-60222A | XA-60222A | 325-01-602-PD-05 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Fire Deluge Fault (No Protection) | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
473 |  | XA-60222B | XA-60222B | 325-01-602-PD-05 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Fire Deluge Alarm (Deluge Activated) | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
474 |  | XS-60222 | XS-60222 | 325-01-602-PD-05 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
475 | Keaser Air Blower |  | Keaser Air Blower |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
476 |  | XS-61302 | XS-61302 | 325-01-613-PD-01 | Start / Stop Command for Bin Aerator Blower | Start / Stop Command | DO | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
477 |  | XA-61302A | XA-61302A | 325-01-613-PD-01 | Operational / Running status |  | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
478 |  | XA-61302B | XA-61302B | 325-01-613-PD-01 | Local / Remote status |  | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
479 |  | XA-61302C | XA-61302C | 325-01-613-PD-01 | Fault / Trip condition |  | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
480 |  | XA-61302D | XA-61302D | 325-01-613-PD-01 | Warning condition |  | DI | PLC | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
481 | REMOTE I-O Area-200 |  | REMOTE I-O Area-200 |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
495 | LS-81001 | LS-814201 | LS-814201 | 325-01-814-PD-01 | Level alarm low | Level switch | DI | RIO-200 | Field Process Instrument missing from Hardware Slot Config | Assign available Spare AI/DI channel in nearest Remote I/O Slot
496 | PCM-2030 | PC-20201 | PC-20201 | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2030 |  | BUS | RIO-200 | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
497 | PCM-2031 |  | PCM-2031 | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2031 | ยกเลิก | DO, DI | RIO-200 | MCC Motor Starter / Drive Control Signal | Route to MCC Control Cabinet or hardwired VFD interlock
498 | PCY-81001 | PC-814201 | PC-814201 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81001 |  | BUS | RIO-200 | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
499 | PCY-81002 | PC-814202 | PC-814202 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81002 |  | BUS | RIO-200 | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
500 | LPG Station |  | LPG Station |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
505 | Gas Vaporizer 4 |  | Gas Vaporizer 4 |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
512 | XS-80305A | XS-913201A | XS-913201A | 325-01-913-PD-02 | Start Command for Gas Vaporizer 4 | Start Command | DO | RIO-200 | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
512 | XS-80305B | XS-913201B | XS-913201B | 325-01-913-PD-02 | Stop Command for Gas Vaporizer 4 | Stop Command | DO | RIO-200 | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
513 | Gas Vaporizer 5 |  | Gas Vaporizer 5 |  |  |  | LOCAL / NONE |  | Local Mechanical Device / Bus Communication | Verify if hardwired I/O or RS485/EtherNet/IP bus interface required
519 | XS-80306A | XS-913202A | XS-913202A | 325-01-913-PD-02 | Start Command for Gas Vaporizer 5 | Start Command | DO | RIO-200 | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block
520 | XS-80306B | XS-913202B | XS-913202B | 325-01-913-PD-02 | Stop Command for Gas Vaporizer 5 | Stop Command | DO | RIO-200 | Unassigned Digital Pushbutton / Switch / Interlock | Assign spare DI/DO channel on Panel P1-P4 marshaling terminal block