## 00_Executive_Summary
SAFETY BARRIER I/O COUNT & HARDWARE SPECIFICATION SUMMARY
Project: Ingredion Sprint 18K TPA Spray Dryer Project (Kalasin Engineering Baseline Rev 3.6a)
TOTAL SAFETY BARRIERS |  | ANALOG INPUT (AI) |  | DIGITAL INPUT (DI) |  | DIGITAL OUTPUT (DO)
70 |  | 26 |  | 42 |  | 2
1. Safety Barrier I/O Signal Type Summary
I/O Signal Category | Signal Description | Tag / Channel Count | Percentage (%) | Target Hardware Module
Analog Input (AI) | 4-20mA IS Transmitter / Transducer Input | 26 | 37.14% | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
Digital Input (DI) | 24VDC Dry Contact / NAMUR Proximity Switch | 42 | 60% | P&F HiC2821 (1/2-Ch DI Switch Amplifier)
Digital Output (DO) | 24VDC IS Solenoid Valve / Alarm Horn Driver | 2 | 2.857% | P&F HiC2871 (1-Ch DO Solenoid Driver)
Analog Output (AO) | 4-20mA IS Valve Positioner / I/P Converter | 0 | 0% | P&F HiC2031 (1-Ch AO Isolated Barrier)
Total Safety Barrier Points | All IS Field Loops | 70 | 100% | 100% IS Signal Coverage
2. Safety Barrier Count Summary by Junction Box
Junction Box Tag | Location / Area Description | AI Barriers | DI Barriers | DO Barriers | Total Signals | P&F Module BoQ
IS-JB-603 | Spray Dryer 3rd Floor Intrinsically Safe JB (Chamber Access Zone 1/21) | 8 | 13 | 1 | 22 | 22 Modules
IS-JB-608 | Spray Dryer 8th Floor Intrinsically Safe JB (Atomizer Deck Zone 0/20) | 5 | 6 | 0 | 11 | 11 Modules
IS-JB-612 | Packing Tower 2nd Floor Intrinsically Safe JB (Product Discharge Zone 21/22) | 2 | 10 | 0 | 12 | 12 Modules
IS-JB-618 | Packing Tower 8th Floor Intrinsically Safe JB (Vapor / Explosion Vent Zone 1/21) | 9 | 11 | 0 | 20 | 20 Modules
JB-800 | CIP Tank Farm Junction Box (Chemical Area Ex-proof) | 1 | 2 | 0 | 3 | 3 Modules
RIO-200 | Remote I/O Box RIO-200 (Field Local Monitoring) | 1 | 0 | 1 | 2 | 2 Modules
Total | All Junction Boxes | 26 | 42 | 2 | 70 | 70 Active Modules

## 01_Safety_Barrier_List
Item | Tag No. | New Tag No. | Junction Box | P&ID No. | Description | Instrument Name | I/O Type | AI Points | DI Points | DO Points | AO Points | Signal Type | Signal To | Range / Scale | Function | Cable Type | Protection Rating | Remark | Recommended Barrier Hardware
3 | DPT-61301 | DPT-61301 | IS-JB-618 | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | - | 500 mBar./0 - 100% | - | Ex t/d | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
4 | DPT-61302 | DPT-61302 | IS-JB-618 | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | - | 500 mBar./0 - 100% | - | Ex t/d | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
5 | DPT-61310 | DPT-61310 | IS-JB-612 | 325-01-613-PD-03 | Vent filter pressure | Differential Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | - | 0-250 mbarg / 0 - 100% | - | Ex t/d | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
6 | DPT-61312 | DPT-61312 | IS-JB-612 | 325-01-613-PD-05 | Vent filter pressure | Differential Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | - | 0-250 mbarg / 0 - 100% | - | Ex t/d | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
70 | LSH-60230 | LSH-60230 | IS-JB-603 | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-21) | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | - | Detected " high" / Overfill | - | Ex t/d | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
71 | LSH-60231 | LSH-60231 | IS-JB-603 | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-22) | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | - | Detected " high" / Overfill | - | Ex t/d | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
72 | LSH-60240 | LSH-60240 | IS-JB-603 | 325-01-602-PD-05 | Powder Level Switch High for Bag House (BGHS-21) | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | - | Detected " high" / Overfill | - | Ex t/d | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
76 | LSH-61301 | LSH-61301 | IS-JB-618 | 325-01-613-PD-01 | Level alarm high | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | - | Detected " Full " / Overfill | - | Ex t/d | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
77 | LSL-61302 | LSL-61302 | IS-JB-618 | 325-01-613-PD-01 | Level alarm low | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | - | Detected " Low " / Overfill | - | Ex t/d | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
78 | LS-61303 | LS-61303 | IS-JB-618 | 325-01-613-PD-01 | Level switch | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | - | Detected " high" / Overfill | - | Ex t/d | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
79 | LSH-61304 | LSH-61304 | IS-JB-612 | 325-01-613-PD-03 | Big bag level alarm high | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | - | Nondetected " Empty " / Overfill | - | Ex t/d | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
80 | LSH-61305 | LSH-61305 | IS-JB-612 | 325-01-613-PD-05 | Big bag level alarm high | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | - | Nondetected " Empty " / Overfill | - | Ex t/d | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
81 | LSH-61306 | LSH-61306 | IS-JB-618 | 325-01-613-PD-01 | Level alarm high | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | - | Nondetected " Empty " / Overfill | - | Ex t/d | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
82 | - | LSH-61307 | IS-JB-603 | 325-01-613-PD-01 | High Level alarm reject screen | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | - | Nondetected " Empty " / Overfill | - | Ex t/d | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
83 | - | LSH-61308 | IS-JB-603 | 325-01-613-PD-01 | High Level alarm Cooling cyclone | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | - | Nondetected " Empty " / Overfill | - | Ex t/d | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
84 | LSH-61312 | LSH-61312 | IS-JB-612 | 325-01-613-PD-05 | Level alarm high | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | - | Nondetected " Empty " / Overfill | - | Ex t/d | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
85 | LSL-81001 | LSL-814201 | JB-800 | 325-01-814-PD-01 | Low Level alarm | - | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | - | Detected " Low " / Overfill | - | Ex t/d | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
89 | LT-61301 | LT-61301 | IS-JB-618 | 325-01-613-PD-01 | Level powder in silo | Level transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | - | 0 - 100% | - | Ex ia | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
107 | PT-60220 | PT-60220 | IS-JB-608 | 325-01-602-PD-04 | Gas Pressure Transmitter for Chamber (CHAM-21) | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | -100 - 100 mbar | 0-100% | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
109 | PT-60230 | PT-60230 | IS-JB-603 | 325-01-602-PD-04 | Gas Pressure Transmitter for Conveying Duct (DTCO-21) | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
110 | PT-60231 | PT-60231 | IS-JB-603 | 325-01-602-PD-04 | Gas Pressure Transmitter for Cyclone Exhaust Duct (DTCE-21) | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
114 | PT-61301 | PT-61301 | IS-JB-618 | 325-01-613-PD-01 | Pressure in silo | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0 - 1 barg | 0-100% | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
116 | PT-61303 | PT-61303 | IS-JB-618 | 325-01-613-PD-01 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
117 | PT-61304 | PT-61304 | IS-JB-618 | 325-01-613-PD-01 | Gas Pressure Transmitter for Storage Bin Cyclone Inlet Duct (CYCL-31) | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
118 | PT-61305 | PT-61305 | IS-JB-618 | 325-01-613-PD-01 | Gas Pressure Transmitter for Exhaust Duct (DTEX-31) | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
152 | TT-60220 | TT-60220 | IS-JB-608 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
153 | TT-60221 | TT-60221 | IS-JB-608 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
154 | TT-60222 | TT-60222 | IS-JB-608 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
155 | TT-60223 | TT-60223 | IS-JB-608 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
156 | TT-60224 | TT-60224 | IS-JB-603 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
157 | TT-60225 | TT-60225 | IS-JB-603 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
158 | TT-60226 | TT-60226 | IS-JB-603 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
159 | TT-60227 | TT-60227 | IS-JB-603 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
160 | TT-60230 | TT-60230 | IS-JB-603 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Conveying Duct (DTCO-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
166 | TT-61301 | TT-61301 | IS-JB-618 | 325-01-613-PD-01 | Gas Temperature Transmitter for Cold Air Duct (DTCA-32) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
167 | TT-61302 | TT-61302 | IS-JB-618 | 325-01-613-PD-01 | Gas and Powder Temperature Transmitter for Cooling Cyclone (CYCL-31) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
175 | XT-60301 | XT-60201 | IS-JB-603 | 325-01-402-PD-03 | LEL gas analyzer | Gas detector | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
176 | XA-60301 | XA-60201 | IS-JB-603 | 325-01-402-PD-03 | LEL gas Buzzer Alarm | Gas detector | DO | 0 | 0 | 1 | 0 | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% | - | Ex ic | Safety Barriers | P&F HiC2871 (1-Ch DO Solenoid Driver Barrier)
177 | XT-92201 | XT-92201 | RIO-200 | 325-01-923-PD-03 | LEL gas analyzer | Gas detector | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% | - | Ex ic | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
178 | XA-92201 | XA-92201 | RIO-200 | 325-01-923-PD-03 | LEL gas Buzzer Alarm | Gas detector | DO | 0 | 0 | 1 | 0 | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% | - | Ex ic | Safety Barriers | P&F HiC2871 (1-Ch DO Solenoid Driver Barrier)
217 | ZS-60201A | ZS-60201A | IS-JB-608 | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
218 | ZS-60201B | ZS-60201B | IS-JB-608 | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
219 | ZS-60201C | ZS-60201C | IS-JB-603 | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
220 | ZS-60201D | ZS-60201D | IS-JB-603 | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
221 | ZS-60201E | ZS-60201E | IS-JB-603 | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
222 | - | ZS-60229 | IS-JB-603 | 325-01-602-PD-04 | Limit Switch for CY-60230 (Door Service) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
223 | - | ZS-60230 | IS-JB-603 | 325-01-602-PD-04 | Limit Switch for CY-60231 (Door Service) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
224 | ZS-60231A | ZS-60231A | IS-JB-603 | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Spectacle Inserted) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
225 | ZS-60231B | ZS-60231B | IS-JB-603 | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Blind Inserted) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
226 | ZS-60231C | ZS-60231C | IS-JB-608 | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Spool Inserted) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
227 | ZS-60231D | ZS-60231D | IS-JB-608 | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Blind Inserted) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
228 | ZS-60231E | ZS-60231E | IS-JB-608 | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Spool Inserted) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
229 | ZS-60231F | ZS-60231F | IS-JB-608 | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Blind Inserted) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
230 | - | ZS-60240 | IS-JB-603 | 325-01-602-PD-05 | Limit Switch for FA-60240 (Door Service) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
231 | ZS-61310 | ZS-61310 | IS-JB-618 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | - | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
232 | ZS-61311 | ZS-61311 | IS-JB-618 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | Detected " Fail " / Active | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
233 | ZS-61312 | ZS-61312 | IS-JB-612 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | Detected " Fail " / Active | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
234 | ZS-61313 | ZS-61313 | IS-JB-612 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | Detected " Fail " / Active | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
296 | PSE-61300 | PSE-61300 | IS-JB-618 | 325-01-613-PD-01 | Explosion Vent PSE-61300 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | Detected " Fail " / Active | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
297 | PSE-61301 | PSE-61301 | IS-JB-618 | 325-01-613-PD-01 | Explosion Vent PSE-61301 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | Detected " Fail " / Active | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
298 | ISV-61302 | ISV-61302 | IS-JB-612 | 325-01-613-PD-01 | Explosion isolation flap valve ISV-61302 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | Detected " Fail " / Active | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
299 | PSE-61302 | PSE-61302 | IS-JB-612 | 325-01-613-PD-03 | Explosion Vent PSE-61302 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | Detected " Fail " / Active | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
300 | PSE-61303 | PSE-61303 | IS-JB-612 | 325-01-613-PD-05 | Explosion Vent PSE-61303 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | Detected " Fail " / Active | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
301 | PSE-61304 | PSE-61304 | IS-JB-618 | 325-01-613-PD-01 | Explosion Vent PSE-61304 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | Detected " Fail " / Active | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
302 | PSV-61301A | ZS-61306 | IS-JB-618 | 325-01-613-PD-01 | Position Brether Valve High Pressure PSV-61301 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | Detected " Fail " / Active | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
303 | PSV-61301B | ZS-61307 | IS-JB-618 | 325-01-613-PD-01 | Position Brether Valve Vacuum Pressure PSV-61301 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | Detected " Fail " / Active | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
304 | ISV-61303 | ISV-61303 | IS-JB-612 | 325-01-613-PD-03 | Explosion isolation flap valve ISV-61303 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | Detected " Fail " / Active | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
305 | ISV-61304 | ISV-61304 | IS-JB-612 | 325-01-613-PD-05 | Explosion isolation flap valve ISV-61304 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | On-Off | Detected " Fail " / Active | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
495 | LS-81001 | LS-814201 | JB-800 | 325-01-814-PD-01 | Level alarm low | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | RIO-200 | On-Off | Nondetected " Empty " / Overfill | - | Ex ic | Safety Barriers | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
502 | LT-80301 | LT-913201 | JB-800 | 325-01-913-PD-01 | Level LPG in storage | Level transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | RIO-200 | - | 0 - 100% | - | Ex ia | Safety Barriers | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
Total | 70 Items | [5 empty] | I/O Points | 26 | 42 | 2 | 0

## 02_By_Junction_Box
JUNCTION BOX: IS-JB-603 --- Spray Dryer 3rd Floor Intrinsically Safe JB (Chamber Access Zone 1/21) (Total Barriers: 22 ¦ AI: 8, DI: 13, DO: 1)
Item | Tag No. | New Tag No. | P&ID No. | Description | Instrument Name | I/O Type | AI Points | DI Points | DO Points | AO Points | Signal Type | Signal To | Protection Rating | Recommended Barrier Hardware
70 | LSH-60230 | LSH-60230 | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-21) | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex t/d | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
71 | LSH-60231 | LSH-60231 | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-22) | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex t/d | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
72 | LSH-60240 | LSH-60240 | 325-01-602-PD-05 | Powder Level Switch High for Bag House (BGHS-21) | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex t/d | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
82 | - | LSH-61307 | 325-01-613-PD-01 | High Level alarm reject screen | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex t/d | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
83 | - | LSH-61308 | 325-01-613-PD-01 | High Level alarm Cooling cyclone | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex t/d | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
109 | PT-60230 | PT-60230 | 325-01-602-PD-04 | Gas Pressure Transmitter for Conveying Duct (DTCO-21) | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
110 | PT-60231 | PT-60231 | 325-01-602-PD-04 | Gas Pressure Transmitter for Cyclone Exhaust Duct (DTCE-21) | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
156 | TT-60224 | TT-60224 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
157 | TT-60225 | TT-60225 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
158 | TT-60226 | TT-60226 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
159 | TT-60227 | TT-60227 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
160 | TT-60230 | TT-60230 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Conveying Duct (DTCO-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
175 | XT-60301 | XT-60201 | 325-01-402-PD-03 | LEL gas analyzer | Gas detector | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
176 | XA-60301 | XA-60201 | 325-01-402-PD-03 | LEL gas Buzzer Alarm | Gas detector | DO | 0 | 0 | 1 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2871 (1-Ch DO Solenoid Driver Barrier)
219 | ZS-60201C | ZS-60201C | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
220 | ZS-60201D | ZS-60201D | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
221 | ZS-60201E | ZS-60201E | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
222 | - | ZS-60229 | 325-01-602-PD-04 | Limit Switch for CY-60230 (Door Service) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
223 | - | ZS-60230 | 325-01-602-PD-04 | Limit Switch for CY-60231 (Door Service) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
224 | ZS-60231A | ZS-60231A | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Spectacle Inserted) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
225 | ZS-60231B | ZS-60231B | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Blind Inserted) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
230 | - | ZS-60240 | 325-01-602-PD-05 | Limit Switch for FA-60240 (Door Service) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
Subtotal (IS-JB-603) | 22 Items |  |  |  |  | Subtotal Points | 8 | 13 | 1 | 0
JUNCTION BOX: IS-JB-608 --- Spray Dryer 8th Floor Intrinsically Safe JB (Atomizer Deck Zone 0/20) (Total Barriers: 11 ¦ AI: 5, DI: 6, DO: 0)
Item | Tag No. | New Tag No. | P&ID No. | Description | Instrument Name | I/O Type | AI Points | DI Points | DO Points | AO Points | Signal Type | Signal To | Protection Rating | Recommended Barrier Hardware
107 | PT-60220 | PT-60220 | 325-01-602-PD-04 | Gas Pressure Transmitter for Chamber (CHAM-21) | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
152 | TT-60220 | TT-60220 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
153 | TT-60221 | TT-60221 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
154 | TT-60222 | TT-60222 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
155 | TT-60223 | TT-60223 | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
217 | ZS-60201A | ZS-60201A | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
218 | ZS-60201B | ZS-60201B | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
226 | ZS-60231C | ZS-60231C | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Spool Inserted) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
227 | ZS-60231D | ZS-60231D | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Blind Inserted) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
228 | ZS-60231E | ZS-60231E | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Spool Inserted) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
229 | ZS-60231F | ZS-60231F | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Blind Inserted) | Limit Switch | DI | 0 | 1 | 0 | 0 | Switch PNP | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
Subtotal (IS-JB-608) | 11 Items |  |  |  |  | Subtotal Points | 5 | 6 | 0 | 0
JUNCTION BOX: IS-JB-612 --- Packing Tower 2nd Floor Intrinsically Safe JB (Product Discharge Zone 21/22) (Total Barriers: 12 ¦ AI: 2, DI: 10, DO: 0)
Item | Tag No. | New Tag No. | P&ID No. | Description | Instrument Name | I/O Type | AI Points | DI Points | DO Points | AO Points | Signal Type | Signal To | Protection Rating | Recommended Barrier Hardware
5 | DPT-61310 | DPT-61310 | 325-01-613-PD-03 | Vent filter pressure | Differential Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex t/d | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
6 | DPT-61312 | DPT-61312 | 325-01-613-PD-05 | Vent filter pressure | Differential Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex t/d | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
79 | LSH-61304 | LSH-61304 | 325-01-613-PD-03 | Big bag level alarm high | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex t/d | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
80 | LSH-61305 | LSH-61305 | 325-01-613-PD-05 | Big bag level alarm high | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex t/d | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
84 | LSH-61312 | LSH-61312 | 325-01-613-PD-05 | Level alarm high | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex t/d | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
233 | ZS-61312 | ZS-61312 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
234 | ZS-61313 | ZS-61313 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
298 | ISV-61302 | ISV-61302 | 325-01-613-PD-01 | Explosion isolation flap valve ISV-61302 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
299 | PSE-61302 | PSE-61302 | 325-01-613-PD-03 | Explosion Vent PSE-61302 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
300 | PSE-61303 | PSE-61303 | 325-01-613-PD-05 | Explosion Vent PSE-61303 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
304 | ISV-61303 | ISV-61303 | 325-01-613-PD-03 | Explosion isolation flap valve ISV-61303 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
305 | ISV-61304 | ISV-61304 | 325-01-613-PD-05 | Explosion isolation flap valve ISV-61304 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
Subtotal (IS-JB-612) | 12 Items |  |  |  |  | Subtotal Points | 2 | 10 | 0 | 0
JUNCTION BOX: IS-JB-618 --- Packing Tower 8th Floor Intrinsically Safe JB (Vapor / Explosion Vent Zone 1/21) (Total Barriers: 20 ¦ AI: 9, DI: 11, DO: 0)
Item | Tag No. | New Tag No. | P&ID No. | Description | Instrument Name | I/O Type | AI Points | DI Points | DO Points | AO Points | Signal Type | Signal To | Protection Rating | Recommended Barrier Hardware
3 | DPT-61301 | DPT-61301 | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex t/d | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
4 | DPT-61302 | DPT-61302 | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex t/d | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
76 | LSH-61301 | LSH-61301 | 325-01-613-PD-01 | Level alarm high | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex t/d | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
77 | LSL-61302 | LSL-61302 | 325-01-613-PD-01 | Level alarm low | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex t/d | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
78 | LS-61303 | LS-61303 | 325-01-613-PD-01 | Level switch | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex t/d | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
81 | LSH-61306 | LSH-61306 | 325-01-613-PD-01 | Level alarm high | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex t/d | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
89 | LT-61301 | LT-61301 | 325-01-613-PD-01 | Level powder in silo | Level transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ia | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
114 | PT-61301 | PT-61301 | 325-01-613-PD-01 | Pressure in silo | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
116 | PT-61303 | PT-61303 | 325-01-613-PD-01 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
117 | PT-61304 | PT-61304 | 325-01-613-PD-01 | Gas Pressure Transmitter for Storage Bin Cyclone Inlet Duct (CYCL-31) | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
118 | PT-61305 | PT-61305 | 325-01-613-PD-01 | Gas Pressure Transmitter for Exhaust Duct (DTEX-31) | Pressure Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
166 | TT-61301 | TT-61301 | 325-01-613-PD-01 | Gas Temperature Transmitter for Cold Air Duct (DTCA-32) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
167 | TT-61302 | TT-61302 | 325-01-613-PD-01 | Gas and Powder Temperature Transmitter for Cooling Cyclone (CYCL-31) | Temperature Transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
231 | ZS-61310 | ZS-61310 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
232 | ZS-61311 | ZS-61311 | 325-01-613-PD-01 | Position Magnet Door | Limit Switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
296 | PSE-61300 | PSE-61300 | 325-01-613-PD-01 | Explosion Vent PSE-61300 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
297 | PSE-61301 | PSE-61301 | 325-01-613-PD-01 | Explosion Vent PSE-61301 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
301 | PSE-61304 | PSE-61304 | 325-01-613-PD-01 | Explosion Vent PSE-61304 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
302 | PSV-61301A | ZS-61306 | 325-01-613-PD-01 | Position Brether Valve High Pressure PSV-61301 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
303 | PSV-61301B | ZS-61307 | 325-01-613-PD-01 | Position Brether Valve Vacuum Pressure PSV-61301 | Position switch | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
Subtotal (IS-JB-618) | 20 Items |  |  |  |  | Subtotal Points | 9 | 11 | 0 | 0
JUNCTION BOX: JB-800 --- CIP Tank Farm Junction Box (Chemical Area Ex-proof) (Total Barriers: 3 ¦ AI: 1, DI: 2, DO: 0)
Item | Tag No. | New Tag No. | P&ID No. | Description | Instrument Name | I/O Type | AI Points | DI Points | DO Points | AO Points | Signal Type | Signal To | Protection Rating | Recommended Barrier Hardware
85 | LSL-81001 | LSL-814201 | 325-01-814-PD-01 | Low Level alarm | - | DI | 0 | 1 | 0 | 0 | Dry Contact | PLC | Ex t/d | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
495 | LS-81001 | LS-814201 | 325-01-814-PD-01 | Level alarm low | Level switch | DI | 0 | 1 | 0 | 0 | Dry Contact | RIO-200 | Ex ic | P&F HiC2821 (1/2-Ch DI Switch Amplifier Barrier)
502 | LT-80301 | LT-913201 | 325-01-913-PD-01 | Level LPG in storage | Level transmitter | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | RIO-200 | Ex ia | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
Subtotal (JB-800) | 3 Items |  |  |  |  | Subtotal Points | 1 | 2 | 0 | 0
JUNCTION BOX: RIO-200 --- Remote I/O Box RIO-200 (Field Local Monitoring) (Total Barriers: 2 ¦ AI: 1, DI: 0, DO: 1)
Item | Tag No. | New Tag No. | P&ID No. | Description | Instrument Name | I/O Type | AI Points | DI Points | DO Points | AO Points | Signal Type | Signal To | Protection Rating | Recommended Barrier Hardware
177 | XT-92201 | XT-92201 | 325-01-923-PD-03 | LEL gas analyzer | Gas detector | AI | 1 | 0 | 0 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2025 / HiC2831 (1-Ch AI Isolated Barrier)
178 | XA-92201 | XA-92201 | 325-01-923-PD-03 | LEL gas Buzzer Alarm | Gas detector | DO | 0 | 0 | 1 | 0 | 4 - 20 mA | PLC | Ex ic | P&F HiC2871 (1-Ch DO Solenoid Driver Barrier)
Subtotal (RIO-200) | 2 Items |  |  |  |  | Subtotal Points | 1 | 0 | 1 | 0
GRAND TOTAL ALL JUNCTION BOXES: 70 Safety Barriers (AI: 26, DI: 42, DO: 2)