## 00_Conflict_Summary
KALASIN ENGINEERING xCIP-1545 — I/O LIST AUDIT & CONFLICT REPORT
Comparison between DWG Schematic Extractions and IO_List-By_SlotConfig_rev02.xlsx Specification
Metric | Value
Total Slot Sheets Analyzed | 57
Total Discrepancies Found | 813
High Severity Conflicts (Tags / Terminals) | 790
Medium Severity Conflicts (Areas / Descriptions) | 23
Chassis | Slot Sheet | DWG Active Points | REF Active Points | Conflict Count | Audit Status
C1 | C1S0 | 5 | 5 | 0 | PASSED
C1 | C1S1 | 4 | 4 | 2 | CONFLICT DETECTED
C1 | C1S2 | 4 | 4 | 2 | CONFLICT DETECTED
C1 | C1S3 | 4 | 4 | 2 | CONFLICT DETECTED
C1 | C1S4 | 16 | 16 | 18 | CONFLICT DETECTED
C1 | C1S5 | 32 | 32 | 18 | CONFLICT DETECTED
C1 | C1S6 | 12 | 12 | 20 | CONFLICT DETECTED
C1 | C1S7 | 23 | 23 | 15 | CONFLICT DETECTED
C1 | C1S8 | 16 | 16 | 18 | CONFLICT DETECTED
C1 | C1S9 | 20 | 20 | 22 | CONFLICT DETECTED
C1 | C1S10 | 22 | 22 | 32 | CONFLICT DETECTED
C1 | C1S11 | 16 | 16 | 26 | CONFLICT DETECTED
C1 | C1S12 | 0 | 0 | 2 | CONFLICT DETECTED
C2 | C2S0 | 4 | 4 | 2 | CONFLICT DETECTED
C2 | C2S1 | 24 | 24 | 18 | CONFLICT DETECTED
C2 | C2S2 | 23 | 23 | 17 | CONFLICT DETECTED
C2 | C2S3 | 29 | 29 | 20 | CONFLICT DETECTED
C2 | C2S4 | 32 | 32 | 18 | CONFLICT DETECTED
C2 | C2S5 | 20 | 20 | 14 | CONFLICT DETECTED
C2 | C2S6 | 12 | 12 | 15 | CONFLICT DETECTED
C2 | C2S7 | 31 | 31 | 18 | CONFLICT DETECTED
C2 | C2S8 | 9 | 9 | 6 | CONFLICT DETECTED
C2 | C2S9 | 14 | 14 | 24 | CONFLICT DETECTED
C2 | C2S10 | 32 | 32 | 28 | CONFLICT DETECTED
C2 | C2S11 | 0 | 0 | 32 | CONFLICT DETECTED
C2 | C2S12 | 0 | 0 | 32 | CONFLICT DETECTED
C3 | C3S0 | 4 | 4 | 2 | CONFLICT DETECTED
C3 | C3S1 | 4 | 4 | 14 | CONFLICT DETECTED
C3 | C3S2 | 17 | 17 | 10 | CONFLICT DETECTED
C3 | C3S3 | 12 | 12 | 8 | CONFLICT DETECTED
C3 | C3S4 | 16 | 16 | 20 | CONFLICT DETECTED
C3 | C3S5 | 9 | 9 | 6 | CONFLICT DETECTED
C3 | C3S6 | 30 | 30 | 30 | CONFLICT DETECTED
C3 | C3S7 | 32 | 32 | 28 | CONFLICT DETECTED
C3 | C3S8 | 24 | 24 | 30 | CONFLICT DETECTED
C3 | C3S9 | 16 | 16 | 30 | CONFLICT DETECTED
C3 | C3S10 | 0 | 0 | 2 | CONFLICT DETECTED
C3 | C3S11 | 0 | 0 | 2 | CONFLICT DETECTED
C3 | C3S12 | 5 | 5 | 2 | CONFLICT DETECTED
C4 | C4S0 | 4 | 4 | 2 | CONFLICT DETECTED
C4 | C4S1 | 22 | 22 | 48 | CONFLICT DETECTED
C4 | C4S2 | 15 | 15 | 8 | CONFLICT DETECTED
C4 | C4S3 | 13 | 13 | 2 | CONFLICT DETECTED
C4 | C4S4 | 1 | 1 | 2 | CONFLICT DETECTED
C4 | C4S5 | 26 | 26 | 38 | CONFLICT DETECTED
C4 | C4S6 | 22 | 22 | 34 | CONFLICT DETECTED
C4 | C4S7 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S8 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S9 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S10 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S11 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S12 | 0 | 0 | 2 | CONFLICT DETECTED
C5 | C5S0 | 4 | 4 | 2 | CONFLICT DETECTED
C5 | C5S1 | 32 | 32 | 18 | CONFLICT DETECTED
C5 | C5S2 | 8 | 8 | 8 | CONFLICT DETECTED
C5 | C5S3 | 8 | 8 | 6 | CONFLICT DETECTED
C5 | C5S4 | 18 | 18 | 28 | CONFLICT DETECTED

## Channel_Level_Conflicts
CHANNEL-LEVEL CONFLICT AUDIT LOG
Conflict ID | Chassis | Sheet | Terminal No | Discrepancy Field | DWG Drawing Value | Excel Reference Value | Severity | Recommended Action
CONF-0001 | C1 | C1S1 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0002 | C1 | C1S1 | RJ45-1 | Terminal Row | Missing in DWG | Terminal RJ45-1 | HIGH | Add Terminal to DWG Schematic
CONF-0003 | C1 | C1S2 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0004 | C1 | C1S2 | RJ45-1 | Terminal Row | Missing in DWG | Terminal RJ45-1 | HIGH | Add Terminal to DWG Schematic
CONF-0005 | C1 | C1S3 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0006 | C1 | C1S3 | RJ45-1 | Terminal Row | Missing in DWG | Terminal RJ45-1 | HIGH | Add Terminal to DWG Schematic
CONF-0007 | C1 | C1S4 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0008 | C1 | C1S4 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0009 | C1 | C1S4 | 19 | PLC_Tag | Internal Power Common | FSL-40201_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0010 | C1 | C1S4 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0011 | C1 | C1S4 | 20 | PLC_Tag | Internal Power Common | FSL-40202_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0012 | C1 | C1S4 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0013 | C1 | C1S4 | 21 | PLC_Tag | FSL-40201_DI_1 | FT-40201_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0014 | C1 | C1S4 | 22 | PLC_Tag | FSL-40202_DI_1 | FT-40202_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0015 | C1 | C1S4 | 23 | PLC_Tag | FT-40201_DI_1 | HV-40201_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0016 | C1 | C1S4 | 24 | PLC_Tag | FT-40202_DI_1 | HV-40202_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0017 | C1 | C1S4 | 25 | PLC_Tag | HV-40201_DI_1 | HV-40203_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0018 | C1 | C1S4 | 26 | PLC_Tag | HV-40202_DI_1 | HV-40204_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0019 | C1 | C1S4 | 27 | PLC_Tag | HV-40203_DI_1 | HV-40205_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0020 | C1 | C1S4 | 28 | PLC_Tag | HV-40204_DI_1 | HV-40206_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0021 | C1 | C1S4 | 29 | PLC_Tag | HV-40205_DI_1 | XV-40201A_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0022 | C1 | C1S4 | 30 | PLC_Tag | HV-40206_DI_1 | XV-40201A_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0023 | C1 | C1S4 | 31 | PLC_Tag | XV-40201A_DI_1 | XV-40201B_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0024 | C1 | C1S4 | 32 | PLC_Tag | XV-40201A_DI_2 | XV-40201B_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0025 | C1 | C1S5 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0026 | C1 | C1S5 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0027 | C1 | C1S5 | 19 | PLC_Tag | Internal Power Common | XV-40202D_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0028 | C1 | C1S5 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0029 | C1 | C1S5 | 20 | PLC_Tag | Internal Power Common | XV-40202E_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0030 | C1 | C1S5 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0031 | C1 | C1S5 | 21 | PLC_Tag | XV-40202D_DI_2 | XV-40202A_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0032 | C1 | C1S5 | 22 | PLC_Tag | XV-40202E_DI_1 | XV-40202E_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0033 | C1 | C1S5 | 23 | PLC_Tag | XV-40202A_DI_1 | XV-40202F_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0034 | C1 | C1S5 | 24 | PLC_Tag | XV-40202E_DI_2 | XV-40202F_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0035 | C1 | C1S5 | 25 | PLC_Tag | XV-40202F_DI_1 | XV-40202G_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0036 | C1 | C1S5 | 26 | PLC_Tag | XV-40202F_DI_2 | XV-40202G_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0037 | C1 | C1S5 | 27 | PLC_Tag | XV-40202G_DI_1 | XV-40202H_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0038 | C1 | C1S5 | 28 | PLC_Tag | XV-40202G_DI_2 | XV-40202H_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0039 | C1 | C1S5 | 29 | PLC_Tag | XV-40202H_DI_1 | XV-40203B_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0040 | C1 | C1S5 | 30 | PLC_Tag | XV-40202H_DI_2 | XV-40203B_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0041 | C1 | C1S5 | 31 | PLC_Tag | XV-40203B_DI_1 | XV-40203C_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0042 | C1 | C1S5 | 32 | PLC_Tag | XV-40203B_DI_2 | XV-40203C_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0043 | C1 | C1S6 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0044 | C1 | C1S6 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0045 | C1 | C1S6 | 19 | PLC_Tag | Internal Power Common | ES-60202_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0046 | C1 | C1S6 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0047 | C1 | C1S6 | 20 | PLC_Tag | Internal Power Common | FS-60205_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0048 | C1 | C1S6 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0049 | C1 | C1S6 | 21 | PLC_Tag | ES-60202_DI_1 | LSL-60201_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0050 | C1 | C1S6 | 22 | PLC_Tag | FS-60205_DI_1 | SV-60201_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0051 | C1 | C1S6 | 23 | PLC_Tag | LSL-60201_DI_1 | SV-60201_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0052 | C1 | C1S6 | 24 | PLC_Tag | SV-60201_DI_1 | SV-60202_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0053 | C1 | C1S6 | 25 | PLC_Tag | SV-60201_DI_2 | SV-60202_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0054 | C1 | C1S6 | 26 | PLC_Tag | SV-60202_DI_1 | SV-60203_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0055 | C1 | C1S6 | 27 | PLC_Tag | SV-60202_DI_2 | SV-60203_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0056 | C1 | C1S6 | 28 | PLC_Tag | SV-60203_DI_1 | VS-60205_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0057 | C1 | C1S6 | 29 | PLC_Tag | SV-60203_DI_2 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0058 | C1 | C1S6 | 29 | Instrument_Tag | SV-60203 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0059 | C1 | C1S6 | 29 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0060 | C1 | C1S6 | 30 | PLC_Tag | VS-60205_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0061 | C1 | C1S6 | 30 | Instrument_Tag | VS-60205 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0062 | C1 | C1S6 | 30 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0063 | C1 | C1S7 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0064 | C1 | C1S7 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0065 | C1 | C1S7 | 19 | PLC_Tag | Internal Power Common | XV-60205A_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0066 | C1 | C1S7 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0067 | C1 | C1S7 | 20 | PLC_Tag | Internal Power Common | XV-60240D_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0068 | C1 | C1S7 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0069 | C1 | C1S7 | 21 | PLC_Tag | XV-60205A_DI_2 | XV-60240D_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0070 | C1 | C1S7 | 24 | PLC_Tag | XV-60240D_DI_1 | YA-60205_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0071 | C1 | C1S7 | 25 | PLC_Tag | XV-60240D_DI_2 | YI-60205_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0072 | C1 | C1S7 | 26 | PLC_Tag | YA-60205_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0073 | C1 | C1S7 | 26 | Instrument_Tag | YA-60205 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0074 | C1 | C1S7 | 26 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0075 | C1 | C1S7 | 27 | PLC_Tag | YI-60205_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0076 | C1 | C1S7 | 27 | Instrument_Tag | YI-60205 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0077 | C1 | C1S7 | 27 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0078 | C1 | C1S8 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0079 | C1 | C1S8 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0080 | C1 | C1S8 | 19 | PLC_Tag | Spare_DO_17 | XV-40202E_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0081 | C1 | C1S8 | 19 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0082 | C1 | C1S8 | 20 | PLC_Tag | Internal Power Common | XV-40202F_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0083 | C1 | C1S8 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0084 | C1 | C1S8 | 21 | PLC_Tag | XV-40202E_DO_1 | XV-40202G_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0085 | C1 | C1S8 | 22 | PLC_Tag | XV-40202F_DO_1 | XV-40202H_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0086 | C1 | C1S8 | 23 | PLC_Tag | XV-40202G_DO_1 | XV-40203B_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0087 | C1 | C1S8 | 24 | PLC_Tag | XV-40202H_DO_1 | XV-40203C_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0088 | C1 | C1S8 | 25 | PLC_Tag | XV-40203B_DO_1 | XV-40203D_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0089 | C1 | C1S8 | 26 | PLC_Tag | XV-40203C_DO_1 | XV-40203E_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0090 | C1 | C1S8 | 27 | PLC_Tag | XV-40203D_DO_1 | SV-40201_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0091 | C1 | C1S8 | 28 | PLC_Tag | XV-40203E_DO_1 | SV-40202_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0092 | C1 | C1S8 | 29 | PLC_Tag | SV-40201_DO_1 | SV-40203_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0093 | C1 | C1S8 | 30 | PLC_Tag | SV-40202_DO_1 | SV-40204_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0094 | C1 | C1S8 | 31 | PLC_Tag | SV-40203_DO_1 | XV-40201A_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0095 | C1 | C1S8 | 32 | PLC_Tag | SV-40204_DO_1 | XV-40201B_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0096 | C1 | C1S9 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0097 | C1 | C1S9 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0098 | C1 | C1S9 | 19 | PLC_Tag | Spare_DO_17 | SV-60201_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0099 | C1 | C1S9 | 19 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0100 | C1 | C1S9 | 20 | PLC_Tag | Internal Power Common | SV-60202_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0101 | C1 | C1S9 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0102 | C1 | C1S9 | 21 | PLC_Tag | SV-60201_DO_1 | SV-60230_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0103 | C1 | C1S9 | 22 | PLC_Tag | SV-60202_DO_1 | SV-60203_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0104 | C1 | C1S9 | 23 | PLC_Tag | SV-60230_DO_1 | SV-60240A_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0105 | C1 | C1S9 | 24 | PLC_Tag | SV-60203_DO_1 | SV-60231_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0106 | C1 | C1S9 | 25 | PLC_Tag | SV-60240A_DO_1 | SV-60240B_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0107 | C1 | C1S9 | 26 | PLC_Tag | SV-60231_DO_1 | SV-60240C_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0108 | C1 | C1S9 | 27 | PLC_Tag | SV-60240B_DO_1 | XV-60240D_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0109 | C1 | C1S9 | 28 | PLC_Tag | SV-60240C_DO_1 | XV-60251_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0110 | C1 | C1S9 | 29 | PLC_Tag | XV-60240D_DO_1 | XV-60202_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0111 | C1 | C1S9 | 30 | PLC_Tag | XV-60251_DO_1 | XV-60205A_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0112 | C1 | C1S9 | 31 | PLC_Tag | XV-60202_DO_1 | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0113 | C1 | C1S9 | 31 | Instrument_Tag | XV-60202 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0114 | C1 | C1S9 | 31 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0115 | C1 | C1S9 | 32 | PLC_Tag | XV-60205A_DO_1 | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0116 | C1 | C1S9 | 32 | Instrument_Tag | XV-60205A | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0117 | C1 | C1S9 | 32 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0118 | C1 | C1S10 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0119 | C1 | C1S10 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0120 | C1 | C1S10 | 11 | PLC_Tag | Internal Power Common | LT-40201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0121 | C1 | C1S10 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0122 | C1 | C1S10 | 12 | PLC_Tag | Internal Power Common | LT-40201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0123 | C1 | C1S10 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0124 | C1 | C1S10 | 13 | PLC_Tag | LT-40201_AI_1 | LT-40202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0125 | C1 | C1S10 | 14 | PLC_Tag | LT-40201_AI_1 | LT-40202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0126 | C1 | C1S10 | 15 | PLC_Tag | LT-40202_AI_1 | pHT-40201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0127 | C1 | C1S10 | 16 | PLC_Tag | LT-40202_AI_1 | pHT-40201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0128 | C1 | C1S10 | 17 | PLC_Tag | pHT-40201_AI_1 | pHT-40202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0129 | C1 | C1S10 | 18 | PLC_Tag | pHT-40201_AI_1 | pHT-40202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0130 | C1 | C1S10 | 19 | PLC_Tag | pHT-40202_AI_1 | PT-40201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0131 | C1 | C1S10 | 20 | PLC_Tag | pHT-40202_AI_1 | PT-40201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0132 | C1 | C1S10 | 21 | PLC_Tag | PT-40201_AI_1 | PT-40202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0133 | C1 | C1S10 | 22 | PLC_Tag | PT-40201_AI_1 | PT-40202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0134 | C1 | C1S10 | 23 | PLC_Tag | PT-40202_AI_1 | PT-60202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0135 | C1 | C1S10 | 24 | PLC_Tag | PT-40202_AI_1 | PT-60202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0136 | C1 | C1S10 | 25 | PLC_Tag | PT-60202_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0137 | C1 | C1S10 | 25 | Instrument_Tag | PT-60202 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0138 | C1 | C1S10 | 25 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0139 | C1 | C1S10 | 26 | PLC_Tag | PT-60202_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0140 | C1 | C1S10 | 26 | Instrument_Tag | PT-60202 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0141 | C1 | C1S10 | 26 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0142 | C1 | C1S10 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0143 | C1 | C1S10 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0144 | C1 | C1S10 | 31 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0145 | C1 | C1S10 | 31 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0146 | C1 | C1S10 | 31 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0147 | C1 | C1S10 | 32 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0148 | C1 | C1S10 | 32 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0149 | C1 | C1S10 | 32 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0150 | C1 | C1S11 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0151 | C1 | C1S11 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0152 | C1 | C1S11 | 11 | PLC_Tag | Internal Power Common | FT-61307_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0153 | C1 | C1S11 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0154 | C1 | C1S11 | 12 | PLC_Tag | Internal Power Common | FT-61307_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0155 | C1 | C1S11 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0156 | C1 | C1S11 | 13 | PLC_Tag | FT-61307_AI_1 | PT-60203_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0157 | C1 | C1S11 | 14 | PLC_Tag | FT-61307_AI_1 | PT-60203_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0158 | C1 | C1S11 | 15 | PLC_Tag | PT-60203_AI_1 | PT-60204_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0159 | C1 | C1S11 | 16 | PLC_Tag | PT-60203_AI_1 | PT-60204_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0160 | C1 | C1S11 | 17 | PLC_Tag | PT-60204_AI_1 | PT-60205_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0161 | C1 | C1S11 | 18 | PLC_Tag | PT-60204_AI_1 | PT-60205_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0162 | C1 | C1S11 | 19 | PLC_Tag | PT-60205_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0163 | C1 | C1S11 | 19 | Instrument_Tag | PT-60205 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0164 | C1 | C1S11 | 19 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0165 | C1 | C1S11 | 20 | PLC_Tag | PT-60205_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0166 | C1 | C1S11 | 20 | Instrument_Tag | PT-60205 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0167 | C1 | C1S11 | 20 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0168 | C1 | C1S11 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0169 | C1 | C1S11 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0170 | C1 | C1S11 | 31 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0171 | C1 | C1S11 | 31 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0172 | C1 | C1S11 | 31 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0173 | C1 | C1S11 | 32 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0174 | C1 | C1S11 | 32 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0175 | C1 | C1S11 | 32 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0176 | C1 | C1S12 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0177 | C1 | C1S12 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal