## 00_Conflict_Summary
KALASIN ENGINEERING xCIP-1545 — I/O LIST AUDIT & CONFLICT REPORT
Comparison between DWG Schematic Extractions and IO_List-By_SlotConfig_rev02.xlsx Specification
Metric | Value
Total Slot Sheets Analyzed | 57
Total Discrepancies Found | 813
High Severity Conflicts (Tags / Terminals) | 790
Medium Severity Conflicts (Areas / Descriptions) | 23
Chassis | Slot Sheet | DWG Active Points | REF Active Points | Conflict Count | Audit Status
C1 | C1S0 | 5 | 5 | 0 | PASSED
C1 | C1S1 | 4 | 4 | 2 | CONFLICT DETECTED
C1 | C1S2 | 4 | 4 | 2 | CONFLICT DETECTED
C1 | C1S3 | 4 | 4 | 2 | CONFLICT DETECTED
C1 | C1S4 | 16 | 16 | 18 | CONFLICT DETECTED
C1 | C1S5 | 32 | 32 | 18 | CONFLICT DETECTED
C1 | C1S6 | 12 | 12 | 20 | CONFLICT DETECTED
C1 | C1S7 | 23 | 23 | 15 | CONFLICT DETECTED
C1 | C1S8 | 16 | 16 | 18 | CONFLICT DETECTED
C1 | C1S9 | 20 | 20 | 22 | CONFLICT DETECTED
C1 | C1S10 | 22 | 22 | 32 | CONFLICT DETECTED
C1 | C1S11 | 16 | 16 | 26 | CONFLICT DETECTED
C1 | C1S12 | 0 | 0 | 2 | CONFLICT DETECTED
C2 | C2S0 | 4 | 4 | 2 | CONFLICT DETECTED
C2 | C2S1 | 24 | 24 | 18 | CONFLICT DETECTED
C2 | C2S2 | 23 | 23 | 17 | CONFLICT DETECTED
C2 | C2S3 | 29 | 29 | 20 | CONFLICT DETECTED
C2 | C2S4 | 32 | 32 | 18 | CONFLICT DETECTED
C2 | C2S5 | 20 | 20 | 14 | CONFLICT DETECTED
C2 | C2S6 | 12 | 12 | 15 | CONFLICT DETECTED
C2 | C2S7 | 31 | 31 | 18 | CONFLICT DETECTED
C2 | C2S8 | 9 | 9 | 6 | CONFLICT DETECTED
C2 | C2S9 | 14 | 14 | 24 | CONFLICT DETECTED
C2 | C2S10 | 32 | 32 | 28 | CONFLICT DETECTED
C2 | C2S11 | 0 | 0 | 32 | CONFLICT DETECTED
C2 | C2S12 | 0 | 0 | 32 | CONFLICT DETECTED
C3 | C3S0 | 4 | 4 | 2 | CONFLICT DETECTED
C3 | C3S1 | 4 | 4 | 14 | CONFLICT DETECTED
C3 | C3S2 | 17 | 17 | 10 | CONFLICT DETECTED
C3 | C3S3 | 12 | 12 | 8 | CONFLICT DETECTED
C3 | C3S4 | 16 | 16 | 20 | CONFLICT DETECTED
C3 | C3S5 | 9 | 9 | 6 | CONFLICT DETECTED
C3 | C3S6 | 30 | 30 | 30 | CONFLICT DETECTED
C3 | C3S7 | 32 | 32 | 28 | CONFLICT DETECTED
C3 | C3S8 | 24 | 24 | 30 | CONFLICT DETECTED
C3 | C3S9 | 16 | 16 | 30 | CONFLICT DETECTED
C3 | C3S10 | 0 | 0 | 2 | CONFLICT DETECTED
C3 | C3S11 | 0 | 0 | 2 | CONFLICT DETECTED
C3 | C3S12 | 5 | 5 | 2 | CONFLICT DETECTED
C4 | C4S0 | 4 | 4 | 2 | CONFLICT DETECTED
C4 | C4S1 | 22 | 22 | 48 | CONFLICT DETECTED
C4 | C4S2 | 15 | 15 | 8 | CONFLICT DETECTED
C4 | C4S3 | 13 | 13 | 2 | CONFLICT DETECTED
C4 | C4S4 | 1 | 1 | 2 | CONFLICT DETECTED
C4 | C4S5 | 26 | 26 | 38 | CONFLICT DETECTED
C4 | C4S6 | 22 | 22 | 34 | CONFLICT DETECTED
C4 | C4S7 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S8 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S9 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S10 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S11 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S12 | 0 | 0 | 2 | CONFLICT DETECTED
C5 | C5S0 | 4 | 4 | 2 | CONFLICT DETECTED
C5 | C5S1 | 32 | 32 | 18 | CONFLICT DETECTED
C5 | C5S2 | 8 | 8 | 8 | CONFLICT DETECTED
C5 | C5S3 | 8 | 8 | 6 | CONFLICT DETECTED
C5 | C5S4 | 18 | 18 | 28 | CONFLICT DETECTED

## Channel_Level_Conflicts
CHANNEL-LEVEL CONFLICT AUDIT LOG
Conflict ID | Chassis | Sheet | Terminal No | Discrepancy Field | DWG Drawing Value | Excel Reference Value | Severity | Recommended Action
CONF-0001 | C1 | C1S1 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0606 | C4 | C4S0 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0607 | C4 | C4S0 | RJ45-1 | Terminal Row | Missing in DWG | Terminal RJ45-1 | HIGH | Add Terminal to DWG Schematic
CONF-0608 | C4 | C4S1 | 1 | Instrument_Tag | ISV-61303 | AT-40201 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0609 | C4 | C4S1 | 2 | Instrument_Tag | ISV-61304 | AT-40202 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0610 | C4 | C4S1 | 3 | Instrument_Tag | LSH-61304 | AT-40203 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0611 | C4 | C4S1 | 4 | Instrument_Tag | LSH-61305 | LSH-60230 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0612 | C4 | C4S1 | 5 | Instrument_Tag | LSH-61307 | LSH-60231 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0613 | C4 | C4S1 | 6 | Instrument_Tag | LSH-61312 | LSH-60240 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0614 | C4 | C4S1 | 7 | Instrument_Tag | PSE-61302 | PD-60202 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0615 | C4 | C4S1 | 8 | Instrument_Tag | PSE-61303 | RV-60204 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0616 | C4 | C4S1 | 9 | Instrument_Tag | RV-61301 | ZS-60201C | HIGH | Align Excel Instrument_Tag with DWG
CONF-0617 | C4 | C4S1 | 10 | Instrument_Tag | RV-61304 | ZS-60201D | HIGH | Align Excel Instrument_Tag with DWG
CONF-0618 | C4 | C4S1 | 11 | Instrument_Tag | RV-61305 | ZS-60201E | HIGH | Align Excel Instrument_Tag with DWG
CONF-0619 | C4 | C4S1 | 12 | Instrument_Tag | SC-61301 | ZS-60229 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0620 | C4 | C4S1 | 13 | Instrument_Tag | SC-61302 | ZS-60230 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0621 | C4 | C4S1 | 14 | Instrument_Tag | ZS-61312 | ZS-60231A | HIGH | Align Excel Instrument_Tag with DWG
CONF-0622 | C4 | C4S1 | 15 | Instrument_Tag | ZS-61313 | ZS-60231B | HIGH | Align Excel Instrument_Tag with DWG
CONF-0623 | C4 | C4S1 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0624 | C4 | C4S1 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0625 | C4 | C4S1 | 19 | Destination_Area | IS-JB-603 | IS-JB-608 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0626 | C4 | C4S1 | 19 | PLC_Tag | Internal Power Common | ZS-60201A_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0627 | C4 | C4S1 | 19 | Instrument_Tag |  | ZS-60201A | HIGH | Verify DWG Instrument_Tag
CONF-0628 | C4 | C4S1 | 19 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0629 | C4 | C4S1 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0630 | C4 | C4S1 | 20 | Destination_Area | IS-JB-603 | IS-JB-608 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0631 | C4 | C4S1 | 20 | PLC_Tag | Internal Power Common | ZS-60201B_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0632 | C4 | C4S1 | 20 | Instrument_Tag |  | ZS-60201B | HIGH | Verify DWG Instrument_Tag
CONF-0633 | C4 | C4S1 | 20 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0634 | C4 | C4S1 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0635 | C4 | C4S1 | 21 | PLC_Tag | ZS-60201A_DI_1 | ZS-60231C_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0636 | C4 | C4S1 | 21 | Instrument_Tag | ZS-60201A | ZS-60231C | HIGH | Align Excel Instrument_Tag with DWG
CONF-0637 | C4 | C4S1 | 21 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0638 | C4 | C4S1 | 22 | PLC_Tag | ZS-60201B_DI_1 | ZS-60231D_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0639 | C4 | C4S1 | 22 | Instrument_Tag | ZS-60201B | ZS-60231D | HIGH | Align Excel Instrument_Tag with DWG
CONF-0640 | C4 | C4S1 | 22 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0641 | C4 | C4S1 | 23 | PLC_Tag | ZS-60231C_DI_1 | ZS-60231E_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0642 | C4 | C4S1 | 23 | Instrument_Tag | ZS-60231C | ZS-60231E | HIGH | Align Excel Instrument_Tag with DWG
CONF-0643 | C4 | C4S1 | 23 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0644 | C4 | C4S1 | 24 | PLC_Tag | ZS-60231D_DI_1 | ZS-60231F_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0645 | C4 | C4S1 | 24 | Instrument_Tag | ZS-60231D | ZS-60231F | HIGH | Align Excel Instrument_Tag with DWG
CONF-0646 | C4 | C4S1 | 24 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0647 | C4 | C4S1 | 25 | PLC_Tag | ZS-60231E_DI_1 | ZS-60240_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0648 | C4 | C4S1 | 25 | Instrument_Tag | ZS-60231E | ZS-60240 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0649 | C4 | C4S1 | 25 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0650 | C4 | C4S1 | 26 | PLC_Tag | ZS-60231F_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0651 | C4 | C4S1 | 26 | Instrument_Tag | ZS-60231F | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0652 | C4 | C4S1 | 26 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0653 | C4 | C4S1 | 27 | PLC_Tag | ZS-60240_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0654 | C4 | C4S1 | 27 | Instrument_Tag | ZS-60240 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0655 | C4 | C4S1 | 27 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0656 | C4 | C4S2 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0657 | C4 | C4S2 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0658 | C4 | C4S2 | 19 | PLC_Tag | Internal Power Common | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0659 | C4 | C4S2 | 19 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0660 | C4 | C4S2 | 19 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0661 | C4 | C4S2 | 20 | PLC_Tag | Internal Power Common | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0662 | C4 | C4S2 | 20 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0663 | C4 | C4S2 | 20 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0664 | C4 | C4S3 | 1 | Terminal Row | Missing in DWG | Terminal 1 | HIGH | Add Terminal to DWG Schematic
CONF-0665 | C4 | C4S3 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0666 | C4 | C4S4 | 1 | Terminal Row | Missing in DWG | Terminal 1 | HIGH | Add Terminal to DWG Schematic
CONF-0667 | C4 | C4S4 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0668 | C4 | C4S5 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0669 | C4 | C4S5 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0670 | C4 | C4S5 | 11 | PLC_Tag | Internal Power Common | TT-60226_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0671 | C4 | C4S5 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0672 | C4 | C4S5 | 12 | PLC_Tag | Internal Power Common | TT-60226_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0673 | C4 | C4S5 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0674 | C4 | C4S5 | 13 | PLC_Tag | TT-60226_AI_1 | TT-60227_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0675 | C4 | C4S5 | 14 | PLC_Tag | TT-60226_AI_1 | TT-60227_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0676 | C4 | C4S5 | 15 | PLC_Tag | TT-60227_AI_1 | TT-60230_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0677 | C4 | C4S5 | 16 | PLC_Tag | TT-60227_AI_1 | TT-60230_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0678 | C4 | C4S5 | 17 | PLC_Tag | TT-60230_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0679 | C4 | C4S5 | 17 | Instrument_Tag | TT-60230 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0680 | C4 | C4S5 | 17 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0681 | C4 | C4S5 | 18 | PLC_Tag | TT-60230_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0682 | C4 | C4S5 | 18 | Instrument_Tag | TT-60230 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0683 | C4 | C4S5 | 18 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0684 | C4 | C4S5 | 19 | Destination_Area | IS-JB-603 | IS-JB-608 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0685 | C4 | C4S5 | 19 | PLC_Tag | Spare_AI_0 | PT-60220_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0686 | C4 | C4S5 | 19 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0687 | C4 | C4S5 | 20 | Destination_Area | IS-JB-603 | IS-JB-608 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0688 | C4 | C4S5 | 20 | PLC_Tag | Spare_AI_0 | PT-60220_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0689 | C4 | C4S5 | 20 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0690 | C4 | C4S5 | 21 | PLC_Tag | PT-60220_AI_1 | TT-60220_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0691 | C4 | C4S5 | 22 | PLC_Tag | PT-60220_AI_1 | TT-60220_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0692 | C4 | C4S5 | 23 | PLC_Tag | TT-60220_AI_1 | TT-60221_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0693 | C4 | C4S5 | 24 | PLC_Tag | TT-60220_AI_1 | TT-60221_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0694 | C4 | C4S5 | 25 | PLC_Tag | TT-60221_AI_1 | TT-60222_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0695 | C4 | C4S5 | 26 | PLC_Tag | TT-60221_AI_1 | TT-60222_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0696 | C4 | C4S5 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0697 | C4 | C4S5 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0698 | C4 | C4S5 | 29 | PLC_Tag | TT-60222_AI_1 | TT-60223_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0699 | C4 | C4S5 | 30 | PLC_Tag | TT-60222_AI_1 | TT-60223_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0700 | C4 | C4S5 | 31 | Destination_Area | IS-JB-603 | IS-JB-608 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0701 | C4 | C4S5 | 31 | PLC_Tag | Internal Power Common | XT-60201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0702 | C4 | C4S5 | 31 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0703 | C4 | C4S5 | 32 | Destination_Area | IS-JB-603 | IS-JB-608 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0704 | C4 | C4S5 | 32 | PLC_Tag | Internal Power Common | XT-60201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0705 | C4 | C4S5 | 32 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0706 | C4 | C4S6 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0707 | C4 | C4S6 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0708 | C4 | C4S6 | 11 | Destination_Area | IS-JB-612 | IS-JB-618 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0709 | C4 | C4S6 | 11 | PLC_Tag | Internal Power Common | DPT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0710 | C4 | C4S6 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0711 | C4 | C4S6 | 12 | Destination_Area | IS-JB-612 | IS-JB-618 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0712 | C4 | C4S6 | 12 | PLC_Tag | Internal Power Common | DPT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0713 | C4 | C4S6 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0714 | C4 | C4S6 | 13 | PLC_Tag | DPT-61301_AI_1 | DPT-61302_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0715 | C4 | C4S6 | 14 | PLC_Tag | DPT-61301_AI_1 | DPT-61302_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0716 | C4 | C4S6 | 15 | PLC_Tag | DPT-61302_AI_1 | LT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0717 | C4 | C4S6 | 16 | PLC_Tag | DPT-61302_AI_1 | LT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0718 | C4 | C4S6 | 17 | PLC_Tag | LT-61301_AI_1 | PT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0719 | C4 | C4S6 | 18 | PLC_Tag | LT-61301_AI_1 | PT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0720 | C4 | C4S6 | 19 | PLC_Tag | PT-61301_AI_1 | PT-61303_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0721 | C4 | C4S6 | 20 | PLC_Tag | PT-61301_AI_1 | PT-61303_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0722 | C4 | C4S6 | 21 | PLC_Tag | PT-61303_AI_1 | PT-61304_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0723 | C4 | C4S6 | 22 | PLC_Tag | PT-61303_AI_1 | PT-61304_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0724 | C4 | C4S6 | 23 | PLC_Tag | PT-61304_AI_1 | PT-61305_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0725 | C4 | C4S6 | 24 | PLC_Tag | PT-61304_AI_1 | PT-61305_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0726 | C4 | C4S6 | 25 | PLC_Tag | PT-61305_AI_1 | TT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0727 | C4 | C4S6 | 26 | PLC_Tag | PT-61305_AI_1 | TT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0728 | C4 | C4S6 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0729 | C4 | C4S6 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0730 | C4 | C4S6 | 29 | PLC_Tag | TT-61301_AI_1 | TT-61302_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0731 | C4 | C4S6 | 30 | PLC_Tag | TT-61301_AI_1 | TT-61302_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0732 | C4 | C4S6 | 31 | Destination_Area | IS-JB-612 | IS-JB-618 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0733 | C4 | C4S6 | 31 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0734 | C4 | C4S6 | 31 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0735 | C4 | C4S6 | 31 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0736 | C4 | C4S6 | 32 | Destination_Area | IS-JB-612 | IS-JB-618 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0737 | C4 | C4S6 | 32 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0738 | C4 | C4S6 | 32 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0739 | C4 | C4S6 | 32 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0740 | C4 | C4S7 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0741 | C4 | C4S7 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0742 | C4 | C4S8 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0743 | C4 | C4S8 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0744 | C4 | C4S9 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0745 | C4 | C4S9 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0746 | C4 | C4S10 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0747 | C4 | C4S10 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0748 | C4 | C4S11 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0749 | C4 | C4S11 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0750 | C4 | C4S12 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0751 | C4 | C4S12 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal