## 00_Conflict_Summary
KALASIN ENGINEERING xCIP-1545 — I/O LIST AUDIT & CONFLICT REPORT
Comparison between DWG Schematic Extractions and IO_List-By_SlotConfig_rev02.xlsx Specification
Metric | Value
Total Slot Sheets Analyzed | 57
Total Discrepancies Found | 813
High Severity Conflicts (Tags / Terminals) | 790
Medium Severity Conflicts (Areas / Descriptions) | 23
Chassis | Slot Sheet | DWG Active Points | REF Active Points | Conflict Count | Audit Status
C1 | C1S0 | 5 | 5 | 0 | PASSED
C1 | C1S1 | 4 | 4 | 2 | CONFLICT DETECTED
C1 | C1S2 | 4 | 4 | 2 | CONFLICT DETECTED
C1 | C1S3 | 4 | 4 | 2 | CONFLICT DETECTED
C1 | C1S4 | 16 | 16 | 18 | CONFLICT DETECTED
C1 | C1S5 | 32 | 32 | 18 | CONFLICT DETECTED
C1 | C1S6 | 12 | 12 | 20 | CONFLICT DETECTED
C1 | C1S7 | 23 | 23 | 15 | CONFLICT DETECTED
C1 | C1S8 | 16 | 16 | 18 | CONFLICT DETECTED
C1 | C1S9 | 20 | 20 | 22 | CONFLICT DETECTED
C1 | C1S10 | 22 | 22 | 32 | CONFLICT DETECTED
C1 | C1S11 | 16 | 16 | 26 | CONFLICT DETECTED
C1 | C1S12 | 0 | 0 | 2 | CONFLICT DETECTED
C2 | C2S0 | 4 | 4 | 2 | CONFLICT DETECTED
C2 | C2S1 | 24 | 24 | 18 | CONFLICT DETECTED
C2 | C2S2 | 23 | 23 | 17 | CONFLICT DETECTED
C2 | C2S3 | 29 | 29 | 20 | CONFLICT DETECTED
C2 | C2S4 | 32 | 32 | 18 | CONFLICT DETECTED
C2 | C2S5 | 20 | 20 | 14 | CONFLICT DETECTED
C2 | C2S6 | 12 | 12 | 15 | CONFLICT DETECTED
C2 | C2S7 | 31 | 31 | 18 | CONFLICT DETECTED
C2 | C2S8 | 9 | 9 | 6 | CONFLICT DETECTED
C2 | C2S9 | 14 | 14 | 24 | CONFLICT DETECTED
C2 | C2S10 | 32 | 32 | 28 | CONFLICT DETECTED
C2 | C2S11 | 0 | 0 | 32 | CONFLICT DETECTED
C2 | C2S12 | 0 | 0 | 32 | CONFLICT DETECTED
C3 | C3S0 | 4 | 4 | 2 | CONFLICT DETECTED
C3 | C3S1 | 4 | 4 | 14 | CONFLICT DETECTED
C3 | C3S2 | 17 | 17 | 10 | CONFLICT DETECTED
C3 | C3S3 | 12 | 12 | 8 | CONFLICT DETECTED
C3 | C3S4 | 16 | 16 | 20 | CONFLICT DETECTED
C3 | C3S5 | 9 | 9 | 6 | CONFLICT DETECTED
C3 | C3S6 | 30 | 30 | 30 | CONFLICT DETECTED
C3 | C3S7 | 32 | 32 | 28 | CONFLICT DETECTED
C3 | C3S8 | 24 | 24 | 30 | CONFLICT DETECTED
C3 | C3S9 | 16 | 16 | 30 | CONFLICT DETECTED
C3 | C3S10 | 0 | 0 | 2 | CONFLICT DETECTED
C3 | C3S11 | 0 | 0 | 2 | CONFLICT DETECTED
C3 | C3S12 | 5 | 5 | 2 | CONFLICT DETECTED
C4 | C4S0 | 4 | 4 | 2 | CONFLICT DETECTED
C4 | C4S1 | 22 | 22 | 48 | CONFLICT DETECTED
C4 | C4S2 | 15 | 15 | 8 | CONFLICT DETECTED
C4 | C4S3 | 13 | 13 | 2 | CONFLICT DETECTED
C4 | C4S4 | 1 | 1 | 2 | CONFLICT DETECTED
C4 | C4S5 | 26 | 26 | 38 | CONFLICT DETECTED
C4 | C4S6 | 22 | 22 | 34 | CONFLICT DETECTED
C4 | C4S7 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S8 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S9 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S10 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S11 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S12 | 0 | 0 | 2 | CONFLICT DETECTED
C5 | C5S0 | 4 | 4 | 2 | CONFLICT DETECTED
C5 | C5S1 | 32 | 32 | 18 | CONFLICT DETECTED
C5 | C5S2 | 8 | 8 | 8 | CONFLICT DETECTED
C5 | C5S3 | 8 | 8 | 6 | CONFLICT DETECTED
C5 | C5S4 | 18 | 18 | 28 | CONFLICT DETECTED

## Channel_Level_Conflicts
CHANNEL-LEVEL CONFLICT AUDIT LOG
Conflict ID | Chassis | Sheet | Terminal No | Discrepancy Field | DWG Drawing Value | Excel Reference Value | Severity | Recommended Action
CONF-0001 | C1 | C1S1 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0752 | C5 | C5S0 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0753 | C5 | C5S0 | RJ45-1 | Terminal Row | Missing in DWG | Terminal RJ45-1 | HIGH | Add Terminal to DWG Schematic
CONF-0754 | C5 | C5S1 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0755 | C5 | C5S1 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0756 | C5 | C5S1 | 19 | PLC_Tag | Internal Power Common | XA-80305C_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0757 | C5 | C5S1 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0758 | C5 | C5S1 | 20 | PLC_Tag | Internal Power Common | XA-80305D_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0759 | C5 | C5S1 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0760 | C5 | C5S1 | 21 | PLC_Tag | XA-80305C_DI_1 | XA-80305E_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0761 | C5 | C5S1 | 22 | PLC_Tag | XA-80305D_DI_1 | XA-80305F_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0762 | C5 | C5S1 | 23 | PLC_Tag | XA-80305E_DI_1 | XA-80306A_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0763 | C5 | C5S1 | 24 | PLC_Tag | XA-80305F_DI_1 | XA-80306B_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0764 | C5 | C5S1 | 25 | PLC_Tag | XA-80306A_DI_1 | XA-80306C_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0765 | C5 | C5S1 | 26 | PLC_Tag | XA-80306B_DI_1 | XA-80306D_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0766 | C5 | C5S1 | 27 | PLC_Tag | XA-80306C_DI_1 | XA-80306E_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0767 | C5 | C5S1 | 28 | PLC_Tag | XA-80306D_DI_1 | XA-80306F_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0768 | C5 | C5S1 | 29 | PLC_Tag | XA-80306E_DI_1 | XV-20201_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0769 | C5 | C5S1 | 30 | PLC_Tag | XA-80306F_DI_1 | XV-20201_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0770 | C5 | C5S1 | 31 | PLC_Tag | XV-20201_DI_1 | XV-20202_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0771 | C5 | C5S1 | 32 | PLC_Tag | XV-20201_DI_2 | XV-20202_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0772 | C5 | C5S2 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0773 | C5 | C5S2 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0774 | C5 | C5S2 | 19 | PLC_Tag | Internal Power Common | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0775 | C5 | C5S2 | 19 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0776 | C5 | C5S2 | 19 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0777 | C5 | C5S2 | 20 | PLC_Tag | Internal Power Common | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0778 | C5 | C5S2 | 20 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0779 | C5 | C5S2 | 20 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0780 | C5 | C5S3 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0781 | C5 | C5S3 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0782 | C5 | C5S3 | 19 | PLC_Tag | Spare_DO_17 | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0783 | C5 | C5S3 | 20 | PLC_Tag | Internal Power Common | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0784 | C5 | C5S3 | 20 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0785 | C5 | C5S3 | 20 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0786 | C5 | C5S4 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0787 | C5 | C5S4 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0788 | C5 | C5S4 | 11 | PLC_Tag | Internal Power Common | FT-936202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0789 | C5 | C5S4 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0790 | C5 | C5S4 | 12 | PLC_Tag | Internal Power Common | FT-936202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0791 | C5 | C5S4 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0792 | C5 | C5S4 | 13 | PLC_Tag | FT-936202_AI_1 | LT-913201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0793 | C5 | C5S4 | 14 | PLC_Tag | FT-936202_AI_1 | LT-913201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0794 | C5 | C5S4 | 15 | PLC_Tag | LT-913201_AI_1 | PT-913201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0795 | C5 | C5S4 | 16 | PLC_Tag | LT-913201_AI_1 | PT-913201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0796 | C5 | C5S4 | 17 | PLC_Tag | PT-913201_AI_1 | XT-92201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0797 | C5 | C5S4 | 18 | PLC_Tag | PT-913201_AI_1 | XT-92201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0798 | C5 | C5S4 | 19 | PLC_Tag | XT-92201_AI_1 | XV-913201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0799 | C5 | C5S4 | 20 | PLC_Tag | XT-92201_AI_1 | XV-913201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0800 | C5 | C5S4 | 21 | PLC_Tag | XV-913201_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0801 | C5 | C5S4 | 21 | Instrument_Tag | XV-913201 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0802 | C5 | C5S4 | 21 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0803 | C5 | C5S4 | 22 | PLC_Tag | XV-913201_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0804 | C5 | C5S4 | 22 | Instrument_Tag | XV-913201 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0805 | C5 | C5S4 | 22 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0806 | C5 | C5S4 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0807 | C5 | C5S4 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0808 | C5 | C5S4 | 31 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0809 | C5 | C5S4 | 31 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0810 | C5 | C5S4 | 31 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0811 | C5 | C5S4 | 32 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0812 | C5 | C5S4 | 32 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0813 | C5 | C5S4 | 32 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG