## 00_JB_Summary
KALASIN ENGINEERING xCIP-1545 — JUNCTION BOX & I/O MAPPING SUMMARY
Summary of I/O Channel Allocations and Destination Junction Boxes Extracted from CAD Drawings
Junction Box / Destination Area | Connected Slots | Active DI | Active DO | Active AI | Active AO | Comm / Diagnostic | Total Active Channels | Spare Channels | Total Channel Capacity
CA1 | C1S1, C1S2, C1S3, C1S4, C1S8, C2S11, C2S12 | 0 | 0 | 0 | 0 | 12 | 12 | 98 | 124
CA1 (Main Control Room) | C1S0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 5
CA1 / Field RIO (EtherNet/IP DLR Trunk) | C2S0, C3S0, C4S0, C5S0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 16
IS-JB-603 | C4S1, C4S5 | 15 | 0 | 14 | 0 | 0 | 29 | 3 | 40
IS-JB-608 | C4S1, C4S5 | 7 | 0 | 12 | 0 | 0 | 19 | 13 | 32
IS-JB-612 | C4S2, C4S6 | 15 | 0 | 4 | 0 | 0 | 19 | 17 | 44
IS-JB-618 | C4S6 | 0 | 0 | 18 | 0 | 0 | 18 | 10 | 28
JB-401 | C1S10, C1S4, C1S5, C1S6, C1S8, C1S9 | 50 | 24 | 22 | 0 | 0 | 96 | 34 | 144
JB-402 | C2S1, C2S6, C2S9, C3S12 | 24 | 10 | 14 | 0 | 0 | 48 | 35 | 105
JB-601 | C1S11, C1S6, C1S7, C1S9 | 33 | 12 | 16 | 0 | 0 | 61 | 35 | 104
JB-602 | C2S10, C2S2, C2S3, C2S6, C3S12, C3S6 | 23 | 5 | 58 | 0 | 0 | 86 | 27 | 129
JB-606 | C3S1, C3S4, C3S6 | 4 | 1 | 4 | 0 | 0 | 9 | 45 | 60
JB-607 | C2S3, C2S4, C2S5, C2S7, C2S8, C3S12, C3S7, C3S8 | 81 | 42 | 54 | 0 | 0 | 177 | 51 | 248
JB-608 | C3S8 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2
JB-612 | C3S2, C3S4, C3S9 | 17 | 15 | 8 | 0 | 0 | 40 | 32 | 80
JB-618 | C3S3, C3S5, C3S9 | 12 | 9 | 8 | 0 | 0 | 29 | 45 | 80
RIO-200 | C5S1, C5S2, C5S3, C5S4 | 40 | 8 | 18 | 0 | 0 | 66 | 64 | 144

## IO_Allocation_By_Drawing
I/O ALLOCATION SUMMARY BY DRAWING & SLOT
Detailed mapping showing which Junction Box and I/O channels are supported by each drawing frame
Chassis | Slot Tag | Drawing DXF File | Hardware Module | Signal Family | Destination Junction Box | Terminal Pin Range | I/O Channel Range | Active Points | Spare Points | Total Points | Connected Instruments / Devices
C1 | C1S0 | C1S0-L950TPSXT.dxf | 1756-L950TPSXT | COMM | CA1 (Main Control Room) | RJ45-1 .. DISP-1 | Embedded 1Gbps EtherNet/IP Port (SCADA / Enterprise Network) .. 4-Character Alphanumeric Diagnostic Display & Status LEDs (RUN, FORCE, SD, OK) | 5 | 0 | 5 | 1756-ESMCAP, 1784-SD2, DIAG-LED, PLC-01, USB-PGM
C1 | C1S1 | C1S1-EN4TR.dxf | 1756-EN4TR | COMM | CA1 | RJ45-1 .. DISP-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) .. 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | 4 | 0 | 4 | DIAG-LED, ETH-01, ETH-02, USB-CFG
C1 | C1S2 | C1S2-EN4TR.dxf | 1756-EN4TR | COMM | CA1 | RJ45-1 .. DISP-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) .. 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | 4 | 0 | 4 | DIAG-LED, ETH-01, ETH-02, USB-CFG
C1 | C1S3 | C1S3-EN4TR.dxf | 1756-EN4TR | COMM | CA1 | RJ45-1 .. DISP-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) .. 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | 4 | 0 | 4 | DIAG-LED, ETH-01, ETH-02, USB-CFG
C1 | C1S4 | C1S4-IB32.dxf | 1756-IB32 | DI | CA1 | Term 1 .. Term 36 | IN-0 .. GND1 | 0 | 16 | 20 | -
C1 | C1S4 | C1S4-IB32.dxf | 1756-IB32 | DI | JB-401 | Term 19 .. Term 34 | IN-16 .. IN-31 | 16 | 0 | 16 | FSL-40201, FSL-40202, FT-40201, FT-40202, HV-40201, HV-40202, HV-40203, HV-40204, HV-40205, HV-40206, XV-40201A, XV-40201B, XV-40201C
C1 | C1S5 | C1S5-IB32.dxf | 1756-IB32 | DI | JB-401 | Term 1 .. Term 36 | IN-0 .. GND1 | 32 | 0 | 36 | XV-40201D, XV-40201E, XV-40201F, XV-40201G, XV-40201H, XV-40202A, XV-40202B, XV-40202C, XV-40202D, XV-40202E, XV-40202F, XV-40202G, XV-40202H, XV-40203B, XV-40203C, XV-40203D
C1 | C1S6 | C1S6-IB32.dxf | 1756-IB32 | DI | JB-401 | Term 1 .. Term 36 | IN-0 .. GND1 | 2 | 14 | 20 | XV-40203E
C1 | C1S6 | C1S6-IB32.dxf | 1756-IB32 | DI | JB-601 | Term 19 .. Term 34 | IN-16 .. IN-31 | 10 | 6 | 16 | ES-60202, FS-60205, LSL-60201, SV-60201, SV-60202, SV-60203, VS-60205
C1 | C1S7 | C1S7-IB32.dxf | 1756-IB32 | DI | JB-601 | Term 1 .. Term 36 | IN-0 .. GND1 | 23 | 9 | 36 | XA-60202A, XA-60202B, XA-60202C, XA-60202D, XA-60202E, XA-60202F, XA-60202G, XA-60202H, XA-60202I, XA-60202J, XA-60202K, XA-60202L, XA-60202M, XV-60202, XV-60205A, XV-60240D, YA-60205, YI-60205
C1 | C1S8 | C1S8-OB32.dxf | 1756-OB32 | DO | CA1 | Term 1 .. Term 36 | OUT-0 .. DC-1(+) | 0 | 18 | 20 | -
C1 | C1S8 | C1S8-OB32.dxf | 1756-OB32 | DO | JB-401 | Term 19 .. Term 34 | OUT-16 .. OUT-31 | 16 | 0 | 16 | SV-40201, SV-40202, SV-40203, SV-40204, XV-40201A, XV-40201B, XV-40201C, XV-40201D, XV-40202E, XV-40202F, XV-40202G, XV-40202H, XV-40203B, XV-40203C, XV-40203D, XV-40203E
C1 | C1S9 | C1S9-OB32.dxf | 1756-OB32 | DO | JB-401 | Term 1 .. Term 36 | OUT-0 .. DC-1(+) | 8 | 10 | 20 | XV-40201E, XV-40201F, XV-40201G, XV-40201H, XV-40202A, XV-40202B, XV-40202C, XV-40202D
C1 | C1S9 | C1S9-OB32.dxf | 1756-OB32 | DO | JB-601 | Term 19 .. Term 34 | OUT-16 .. OUT-31 | 12 | 4 | 16 | SV-60201, SV-60202, SV-60203, SV-60230, SV-60231, SV-60240A, SV-60240B, SV-60240C, XV-60202, XV-60205A, XV-60240D, XV-60251
C1 | C1S10 | C1S10-IF16.dxf | 1756-IF16 | AI | JB-401 | Term 1 .. Term 36 | i RTN-0 .. IN-15 | 22 | 10 | 36 | FT-40201, FT-40202, LT-40201, LT-40202, LT-40203, PT-40201, PT-40202, PT-60202, pHT-40201, pHT-40202
C1 | C1S11 | C1S11-IF16.dxf | 1756-IF16 | AI | JB-601 | Term 1 .. Term 36 | i RTN-0 .. IN-15 | 16 | 16 | 36 | DPI-60240, DPT-60202, FT-60201, FT-60204, FT-61307, PT-60203, PT-60204, PT-60205
C1 | C1S12 | C1S12-N2.dxf | 1756-N2 | EMPTY | Unpopulated / Reserve | - | - | 0 | 0 | 0 | -

## IO_Grouped_By_JunctionBox
I/O ALLOCATION SUMMARY GROUPED BY JUNCTION BOX
Grouped overview listing all slot drawings and I/O channels feeding into each Junction Box
Destination Junction Box | Chassis | Slot Tag | Drawing DXF File | Hardware Module | Signal Family | Terminal Pin Range | I/O Channel Range | Active Points | Connected Instruments / Devices
CA1 | C1 | C1S1 | C1S1-EN4TR.dxf | 1756-EN4TR | COMM | RJ45-1 .. DISP-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) .. 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | 4 | DIAG-LED, ETH-01, ETH-02, USB-CFG
CA1 | C1 | C1S2 | C1S2-EN4TR.dxf | 1756-EN4TR | COMM | RJ45-1 .. DISP-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) .. 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | 4 | DIAG-LED, ETH-01, ETH-02, USB-CFG
CA1 | C1 | C1S3 | C1S3-EN4TR.dxf | 1756-EN4TR | COMM | RJ45-1 .. DISP-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) .. 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | 4 | DIAG-LED, ETH-01, ETH-02, USB-CFG
CA1 | C1 | C1S4 | C1S4-IB32.dxf | 1756-IB32 | DI | Term 1 .. Term 36 | IN-0 .. GND1 | 0 | -
CA1 | C1 | C1S8 | C1S8-OB32.dxf | 1756-OB32 | DO | Term 1 .. Term 36 | OUT-0 .. DC-1(+) | 0 | -
CA1 (Main Control Room) | C1 | C1S0 | C1S0-L950TPSXT.dxf | 1756-L950TPSXT | COMM | RJ45-1 .. DISP-1 | Embedded 1Gbps EtherNet/IP Port (SCADA / Enterprise Network) .. 4-Character Alphanumeric Diagnostic Display & Status LEDs (RUN, FORCE, SD, OK) | 5 | 1756-ESMCAP, 1784-SD2, DIAG-LED, PLC-01, USB-PGM
JB-401 | C1 | C1S10 | C1S10-IF16.dxf | 1756-IF16 | AI | Term 1 .. Term 36 | i RTN-0 .. IN-15 | 22 | FT-40201, FT-40202, LT-40201, LT-40202, LT-40203, PT-40201, PT-40202, PT-60202, pHT-40201, pHT-40202
JB-401 | C1 | C1S4 | C1S4-IB32.dxf | 1756-IB32 | DI | Term 19 .. Term 34 | IN-16 .. IN-31 | 16 | FSL-40201, FSL-40202, FT-40201, FT-40202, HV-40201, HV-40202, HV-40203, HV-40204, HV-40205, HV-40206, XV-40201A, XV-40201B, XV-40201C
JB-401 | C1 | C1S5 | C1S5-IB32.dxf | 1756-IB32 | DI | Term 1 .. Term 36 | IN-0 .. GND1 | 32 | XV-40201D, XV-40201E, XV-40201F, XV-40201G, XV-40201H, XV-40202A, XV-40202B, XV-40202C, XV-40202D, XV-40202E, XV-40202F, XV-40202G, XV-40202H, XV-40203B, XV-40203C, XV-40203D
JB-401 | C1 | C1S6 | C1S6-IB32.dxf | 1756-IB32 | DI | Term 1 .. Term 36 | IN-0 .. GND1 | 2 | XV-40203E
JB-401 | C1 | C1S8 | C1S8-OB32.dxf | 1756-OB32 | DO | Term 19 .. Term 34 | OUT-16 .. OUT-31 | 16 | SV-40201, SV-40202, SV-40203, SV-40204, XV-40201A, XV-40201B, XV-40201C, XV-40201D, XV-40202E, XV-40202F, XV-40202G, XV-40202H, XV-40203B, XV-40203C, XV-40203D, XV-40203E
JB-401 | C1 | C1S9 | C1S9-OB32.dxf | 1756-OB32 | DO | Term 1 .. Term 36 | OUT-0 .. DC-1(+) | 8 | XV-40201E, XV-40201F, XV-40201G, XV-40201H, XV-40202A, XV-40202B, XV-40202C, XV-40202D
JB-601 | C1 | C1S11 | C1S11-IF16.dxf | 1756-IF16 | AI | Term 1 .. Term 36 | i RTN-0 .. IN-15 | 16 | DPI-60240, DPT-60202, FT-60201, FT-60204, FT-61307, PT-60203, PT-60204, PT-60205
JB-601 | C1 | C1S6 | C1S6-IB32.dxf | 1756-IB32 | DI | Term 19 .. Term 34 | IN-16 .. IN-31 | 10 | ES-60202, FS-60205, LSL-60201, SV-60201, SV-60202, SV-60203, VS-60205
JB-601 | C1 | C1S7 | C1S7-IB32.dxf | 1756-IB32 | DI | Term 1 .. Term 36 | IN-0 .. GND1 | 23 | XA-60202A, XA-60202B, XA-60202C, XA-60202D, XA-60202E, XA-60202F, XA-60202G, XA-60202H, XA-60202I, XA-60202J, XA-60202K, XA-60202L, XA-60202M, XV-60202, XV-60205A, XV-60240D, YA-60205, YI-60205
JB-601 | C1 | C1S9 | C1S9-OB32.dxf | 1756-OB32 | DO | Term 19 .. Term 34 | OUT-16 .. OUT-31 | 12 | SV-60201, SV-60202, SV-60203, SV-60230, SV-60231, SV-60240A, SV-60240B, SV-60240C, XV-60202, XV-60205A, XV-60240D, XV-60251
Unpopulated / Reserve | C1 | C1S12 | C1S12-N2.dxf | 1756-N2 | EMPTY | - | - | 0 | -

## Junction_Box_List_By_Slot
KALASIN ENGINEERING xCIP-1545 — JUNCTION BOX LIST BY SLOT
Detailed breakdown per Chassis & Slot drawing showing Junction Boxes, Terminal Pin Ranges (From..To), and I/O Point Ranges (From..To)
Chassis | Slot Tag | Drawing DXF File | Hardware Module | Destination Junction Box | Terminal Pin From | Terminal Pin To | I/O Point From | I/O Point To | Signal Family | Active Points | Spare Points | Connected Devices / Channel Notes
C1 | C1S0 | C1S0-L950TPSXT.dxf | 1756-L950TPSXT | CA1 (Main Control Room) | RJ45-1 | DISP-1 | Embedded 1Gbps EtherNet/IP Port (SCADA / Enterprise Network) | 4-Character Alphanumeric Diagnostic Display & Status LEDs (RUN, FORCE, SD, OK) | COMM | 5 | 0 | 1756-ESMCAP, 1784-SD2, DIAG-LED, PLC-01, USB-PGM
C1 | C1S1 | C1S1-EN4TR.dxf | 1756-EN4TR | CA1 | RJ45-1 | DISP-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | COMM | 4 | 0 | DIAG-LED, ETH-01, ETH-02, USB-CFG
C1 | C1S2 | C1S2-EN4TR.dxf | 1756-EN4TR | CA1 | RJ45-1 | DISP-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | COMM | 4 | 0 | DIAG-LED, ETH-01, ETH-02, USB-CFG
C1 | C1S3 | C1S3-EN4TR.dxf | 1756-EN4TR | CA1 | RJ45-1 | DISP-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | COMM | 4 | 0 | DIAG-LED, ETH-01, ETH-02, USB-CFG
C1 | C1S4 | C1S4-IB32.dxf | 1756-IB32 | CA1 | Term 1 | Term 36 | IN-0 | GND1 | DI | 0 | 16 | Spare Reserve Channels
C1 | C1S4 | C1S4-IB32.dxf | 1756-IB32 | JB-401 | Term 19 | Term 34 | IN-16 | IN-31 | DI | 16 | 0 | FSL-40201, FSL-40202, FT-40201, FT-40202, HV-40201, HV-40202, HV-40203, HV-40204, HV-40205, HV-40206, XV-40201A, XV-40201B, XV-40201C
C1 | C1S5 | C1S5-IB32.dxf | 1756-IB32 | JB-401 | Term 1 | Term 36 | IN-0 | GND1 | DI | 32 | 0 | XV-40201D, XV-40201E, XV-40201F, XV-40201G, XV-40201H, XV-40202A, XV-40202B, XV-40202C, XV-40202D, XV-40202E, XV-40202F, XV-40202G, XV-40202H, XV-40203B, XV-40203C, XV-40203D
C1 | C1S6 | C1S6-IB32.dxf | 1756-IB32 | JB-401 | Term 1 | Term 36 | IN-0 | GND1 | DI | 2 | 14 | XV-40203E
C1 | C1S6 | C1S6-IB32.dxf | 1756-IB32 | JB-601 | Term 19 | Term 34 | IN-16 | IN-31 | DI | 10 | 6 | ES-60202, FS-60205, LSL-60201, SV-60201, SV-60202, SV-60203, VS-60205
C1 | C1S7 | C1S7-IB32.dxf | 1756-IB32 | JB-601 | Term 1 | Term 36 | IN-0 | GND1 | DI | 23 | 9 | XA-60202A, XA-60202B, XA-60202C, XA-60202D, XA-60202E, XA-60202F, XA-60202G, XA-60202H, XA-60202I, XA-60202J, XA-60202K, XA-60202L, XA-60202M, XV-60202, XV-60205A, XV-60240D, YA-60205, YI-60205
C1 | C1S8 | C1S8-OB32.dxf | 1756-OB32 | CA1 | Term 1 | Term 36 | OUT-0 | DC-1(+) | DO | 0 | 18 | Spare Reserve Channels
C1 | C1S8 | C1S8-OB32.dxf | 1756-OB32 | JB-401 | Term 19 | Term 34 | OUT-16 | OUT-31 | DO | 16 | 0 | SV-40201, SV-40202, SV-40203, SV-40204, XV-40201A, XV-40201B, XV-40201C, XV-40201D, XV-40202E, XV-40202F, XV-40202G, XV-40202H, XV-40203B, XV-40203C, XV-40203D, XV-40203E
C1 | C1S9 | C1S9-OB32.dxf | 1756-OB32 | JB-401 | Term 1 | Term 36 | OUT-0 | DC-1(+) | DO | 8 | 10 | XV-40201E, XV-40201F, XV-40201G, XV-40201H, XV-40202A, XV-40202B, XV-40202C, XV-40202D
C1 | C1S9 | C1S9-OB32.dxf | 1756-OB32 | JB-601 | Term 19 | Term 34 | OUT-16 | OUT-31 | DO | 12 | 4 | SV-60201, SV-60202, SV-60203, SV-60230, SV-60231, SV-60240A, SV-60240B, SV-60240C, XV-60202, XV-60205A, XV-60240D, XV-60251
C1 | C1S10 | C1S10-IF16.dxf | 1756-IF16 | JB-401 | Term 1 | Term 36 | i RTN-0 | IN-15 | AI | 22 | 10 | FT-40201, FT-40202, LT-40201, LT-40202, LT-40203, PT-40201, PT-40202, PT-60202, pHT-40201, pHT-40202
C1 | C1S11 | C1S11-IF16.dxf | 1756-IF16 | JB-601 | Term 1 | Term 36 | i RTN-0 | IN-15 | AI | 16 | 16 | DPI-60240, DPT-60202, FT-60201, FT-60204, FT-61307, PT-60203, PT-60204, PT-60205
C1 | C1S12 | C1S12-N2.dxf | 1756-N2 | Unpopulated / Reserve | - | - | - | - | EMPTY | 0 | 0 | Unpopulated Slot Position