## 00_JB_Summary
KALASIN ENGINEERING xCIP-1545 — JUNCTION BOX & I/O MAPPING SUMMARY
Summary of I/O Channel Allocations and Destination Junction Boxes Extracted from CAD Drawings
Junction Box / Destination Area | Connected Slots | Active DI | Active DO | Active AI | Active AO | Comm / Diagnostic | Total Active Channels | Spare Channels | Total Channel Capacity
CA1 | C1S1, C1S2, C1S3, C1S4, C1S8, C2S11, C2S12 | 0 | 0 | 0 | 0 | 12 | 12 | 98 | 124
CA1 (Main Control Room) | C1S0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 5
CA1 / Field RIO (EtherNet/IP DLR Trunk) | C2S0, C3S0, C4S0, C5S0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 16
IS-JB-603 | C4S1, C4S5 | 15 | 0 | 14 | 0 | 0 | 29 | 3 | 40
IS-JB-608 | C4S1, C4S5 | 7 | 0 | 12 | 0 | 0 | 19 | 13 | 32
IS-JB-612 | C4S2, C4S6 | 15 | 0 | 4 | 0 | 0 | 19 | 17 | 44
IS-JB-618 | C4S6 | 0 | 0 | 18 | 0 | 0 | 18 | 10 | 28
JB-401 | C1S10, C1S4, C1S5, C1S6, C1S8, C1S9 | 50 | 24 | 22 | 0 | 0 | 96 | 34 | 144
JB-402 | C2S1, C2S6, C2S9, C3S12 | 24 | 10 | 14 | 0 | 0 | 48 | 35 | 105
JB-601 | C1S11, C1S6, C1S7, C1S9 | 33 | 12 | 16 | 0 | 0 | 61 | 35 | 104
JB-602 | C2S10, C2S2, C2S3, C2S6, C3S12, C3S6 | 23 | 5 | 58 | 0 | 0 | 86 | 27 | 129
JB-606 | C3S1, C3S4, C3S6 | 4 | 1 | 4 | 0 | 0 | 9 | 45 | 60
JB-607 | C2S3, C2S4, C2S5, C2S7, C2S8, C3S12, C3S7, C3S8 | 81 | 42 | 54 | 0 | 0 | 177 | 51 | 248
JB-608 | C3S8 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 2
JB-612 | C3S2, C3S4, C3S9 | 17 | 15 | 8 | 0 | 0 | 40 | 32 | 80
JB-618 | C3S3, C3S5, C3S9 | 12 | 9 | 8 | 0 | 0 | 29 | 45 | 80
RIO-200 | C5S1, C5S2, C5S3, C5S4 | 40 | 8 | 18 | 0 | 0 | 66 | 64 | 144

## IO_Allocation_By_Drawing
I/O ALLOCATION SUMMARY BY DRAWING & SLOT
Detailed mapping showing which Junction Box and I/O channels are supported by each drawing frame
Chassis | Slot Tag | Drawing DXF File | Hardware Module | Signal Family | Destination Junction Box | Terminal Pin Range | I/O Channel Range | Active Points | Spare Points | Total Points | Connected Instruments / Devices
C4 | C4S0 | C4S0-EN4TR.dxf | 1756-EN4TR | COMM | CA1 / Field RIO (EtherNet/IP DLR Trunk) | RJ45-1 .. DISP-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) .. 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | 4 | 0 | 4 | DIAG-LED, ETH-01, ETH-02, USB-CFG
C4 | C4S1 | C4S1-IB32-1.dxf | 1756-IB32 | DI | IS-JB-603 | Term 1 .. Term 36 | IN-0 .. GND1 | 15 | 1 | 20 | AT-40201, AT-40202, AT-40203, LSH-60230, LSH-60231, LSH-60240, PD-60202, RV-60204, ZS-60201C, ZS-60201D, ZS-60201E, ZS-60229, ZS-60230, ZS-60231A, ZS-60231B
C4 | C4S1 | C4S1-IB32-1.dxf | 1756-IB32 | DI | IS-JB-608 | Term 19 .. Term 34 | IN-16 .. IN-31 | 7 | 9 | 16 | ZS-60201A, ZS-60201B, ZS-60231C, ZS-60231D, ZS-60231E, ZS-60231F, ZS-60240
C4 | C4S2 | C4S2-IB32-1.dxf | 1756-IB32 | DI | IS-JB-612 | Term 1 .. Term 36 | IN-0 .. GND1 | 15 | 17 | 36 | ISV-61303, ISV-61304, LSH-61304, LSH-61305, LSH-61307, LSH-61312, PSE-61302, PSE-61303, RV-61301, RV-61304, RV-61305, SC-61301, SC-61302, ZS-61312, ZS-61313
C4 | C4S3 | C4S3-N2.dxf | 1756-N2 | EMPTY | Unpopulated / Reserve | - | - | 0 | 0 | 0 | -
C4 | C4S4 | C4S4-N2.dxf | 1756-N2 | EMPTY | Unpopulated / Reserve | - | - | 0 | 0 | 0 | -
C4 | C4S5 | C4S5-IF16.dxf | 1756-IF16 | AI | IS-JB-603 | Term 1 .. Term 28 | i RTN-0 .. RTN | 14 | 2 | 20 | PT-60230, PT-60231, TT-60224, TT-60225, TT-60226, TT-60227, TT-60230
C4 | C4S5 | C4S5-IF16.dxf | 1756-IF16 | AI | IS-JB-608 | Term 19 .. Term 36 | i RTN-8 .. IN-15 | 12 | 4 | 16 | PT-60220, TT-60220, TT-60221, TT-60222, TT-60223, XT-60201
C4 | C4S6 | C4S6-IF16.dxf | 1756-IF16 | AI | IS-JB-612 | Term 1 .. Term 28 | i RTN-0 .. RTN | 4 | 0 | 8 | DPT-61310, DPT-61312
C4 | C4S6 | C4S6-IF16.dxf | 1756-IF16 | AI | IS-JB-618 | Term 5 .. Term 36 | i RTN-2 .. IN-15 | 18 | 10 | 28 | DPT-61301, DPT-61302, LT-61301, PT-61301, PT-61303, PT-61304, PT-61305, TT-61301, TT-61302
C4 | C4S7 | C4S7-N2.dxf | 1756-N2 | EMPTY | Unpopulated / Reserve | - | - | 0 | 0 | 0 | -
C4 | C4S8 | C4S8-N2.dxf | 1756-N2 | EMPTY | Unpopulated / Reserve | - | - | 0 | 0 | 0 | -
C4 | C4S9 | C4S9-N2.dxf | 1756-N2 | EMPTY | Unpopulated / Reserve | - | - | 0 | 0 | 0 | -
C4 | C4S10 | C4S10-N2.dxf | 1756-N2 | EMPTY | Unpopulated / Reserve | - | - | 0 | 0 | 0 | -
C4 | C4S11 | C4S11-N2.dxf | 1756-N2 | EMPTY | Unpopulated / Reserve | - | - | 0 | 0 | 0 | -
C4 | C4S12 | C4S12-N2.dxf | 1756-N2 | EMPTY | Unpopulated / Reserve | - | - | 0 | 0 | 0 | -

## IO_Grouped_By_JunctionBox
I/O ALLOCATION SUMMARY GROUPED BY JUNCTION BOX
Grouped overview listing all slot drawings and I/O channels feeding into each Junction Box
Destination Junction Box | Chassis | Slot Tag | Drawing DXF File | Hardware Module | Signal Family | Terminal Pin Range | I/O Channel Range | Active Points | Connected Instruments / Devices
CA1 / Field RIO (EtherNet/IP DLR Trunk) | C4 | C4S0 | C4S0-EN4TR.dxf | 1756-EN4TR | COMM | RJ45-1 .. DISP-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) .. 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | 4 | DIAG-LED, ETH-01, ETH-02, USB-CFG
IS-JB-603 | C4 | C4S1 | C4S1-IB32-1.dxf | 1756-IB32 | DI | Term 1 .. Term 36 | IN-0 .. GND1 | 15 | AT-40201, AT-40202, AT-40203, LSH-60230, LSH-60231, LSH-60240, PD-60202, RV-60204, ZS-60201C, ZS-60201D, ZS-60201E, ZS-60229, ZS-60230, ZS-60231A, ZS-60231B
IS-JB-603 | C4 | C4S5 | C4S5-IF16.dxf | 1756-IF16 | AI | Term 1 .. Term 28 | i RTN-0 .. RTN | 14 | PT-60230, PT-60231, TT-60224, TT-60225, TT-60226, TT-60227, TT-60230
IS-JB-608 | C4 | C4S1 | C4S1-IB32-1.dxf | 1756-IB32 | DI | Term 19 .. Term 34 | IN-16 .. IN-31 | 7 | ZS-60201A, ZS-60201B, ZS-60231C, ZS-60231D, ZS-60231E, ZS-60231F, ZS-60240
IS-JB-608 | C4 | C4S5 | C4S5-IF16.dxf | 1756-IF16 | AI | Term 19 .. Term 36 | i RTN-8 .. IN-15 | 12 | PT-60220, TT-60220, TT-60221, TT-60222, TT-60223, XT-60201
IS-JB-612 | C4 | C4S2 | C4S2-IB32-1.dxf | 1756-IB32 | DI | Term 1 .. Term 36 | IN-0 .. GND1 | 15 | ISV-61303, ISV-61304, LSH-61304, LSH-61305, LSH-61307, LSH-61312, PSE-61302, PSE-61303, RV-61301, RV-61304, RV-61305, SC-61301, SC-61302, ZS-61312, ZS-61313
IS-JB-612 | C4 | C4S6 | C4S6-IF16.dxf | 1756-IF16 | AI | Term 1 .. Term 28 | i RTN-0 .. RTN | 4 | DPT-61310, DPT-61312
IS-JB-618 | C4 | C4S6 | C4S6-IF16.dxf | 1756-IF16 | AI | Term 5 .. Term 36 | i RTN-2 .. IN-15 | 18 | DPT-61301, DPT-61302, LT-61301, PT-61301, PT-61303, PT-61304, PT-61305, TT-61301, TT-61302
Unpopulated / Reserve | C4 | C4S10 | C4S10-N2.dxf | 1756-N2 | EMPTY | - | - | 0 | -
Unpopulated / Reserve | C4 | C4S11 | C4S11-N2.dxf | 1756-N2 | EMPTY | - | - | 0 | -
Unpopulated / Reserve | C4 | C4S12 | C4S12-N2.dxf | 1756-N2 | EMPTY | - | - | 0 | -
Unpopulated / Reserve | C4 | C4S3 | C4S3-N2.dxf | 1756-N2 | EMPTY | - | - | 0 | -
Unpopulated / Reserve | C4 | C4S4 | C4S4-N2.dxf | 1756-N2 | EMPTY | - | - | 0 | -
Unpopulated / Reserve | C4 | C4S7 | C4S7-N2.dxf | 1756-N2 | EMPTY | - | - | 0 | -
Unpopulated / Reserve | C4 | C4S8 | C4S8-N2.dxf | 1756-N2 | EMPTY | - | - | 0 | -
Unpopulated / Reserve | C4 | C4S9 | C4S9-N2.dxf | 1756-N2 | EMPTY | - | - | 0 | -

## Junction_Box_List_By_Slot
KALASIN ENGINEERING xCIP-1545 — JUNCTION BOX LIST BY SLOT
Detailed breakdown per Chassis & Slot drawing showing Junction Boxes, Terminal Pin Ranges (From..To), and I/O Point Ranges (From..To)
Chassis | Slot Tag | Drawing DXF File | Hardware Module | Destination Junction Box | Terminal Pin From | Terminal Pin To | I/O Point From | I/O Point To | Signal Family | Active Points | Spare Points | Connected Devices / Channel Notes
C4 | C4S0 | C4S0-EN4TR.dxf | 1756-EN4TR | CA1 / Field RIO (EtherNet/IP DLR Trunk) | RJ45-1 | DISP-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | COMM | 4 | 0 | DIAG-LED, ETH-01, ETH-02, USB-CFG
C4 | C4S1 | C4S1-IB32-1.dxf | 1756-IB32 | IS-JB-603 | Term 1 | Term 36 | IN-0 | GND1 | DI | 15 | 1 | AT-40201, AT-40202, AT-40203, LSH-60230, LSH-60231, LSH-60240, PD-60202, RV-60204, ZS-60201C, ZS-60201D, ZS-60201E, ZS-60229, ZS-60230, ZS-60231A, ZS-60231B
C4 | C4S1 | C4S1-IB32-1.dxf | 1756-IB32 | IS-JB-608 | Term 19 | Term 34 | IN-16 | IN-31 | DI | 7 | 9 | ZS-60201A, ZS-60201B, ZS-60231C, ZS-60231D, ZS-60231E, ZS-60231F, ZS-60240
C4 | C4S2 | C4S2-IB32-1.dxf | 1756-IB32 | IS-JB-612 | Term 1 | Term 36 | IN-0 | GND1 | DI | 15 | 17 | ISV-61303, ISV-61304, LSH-61304, LSH-61305, LSH-61307, LSH-61312, PSE-61302, PSE-61303, RV-61301, RV-61304, RV-61305, SC-61301, SC-61302, ZS-61312, ZS-61313
C4 | C4S3 | C4S3-N2.dxf | 1756-N2 | Unpopulated / Reserve | - | - | - | - | EMPTY | 0 | 0 | Unpopulated Slot Position
C4 | C4S4 | C4S4-N2.dxf | 1756-N2 | Unpopulated / Reserve | - | - | - | - | EMPTY | 0 | 0 | Unpopulated Slot Position
C4 | C4S5 | C4S5-IF16.dxf | 1756-IF16 | IS-JB-603 | Term 1 | Term 28 | i RTN-0 | RTN | AI | 14 | 2 | PT-60230, PT-60231, TT-60224, TT-60225, TT-60226, TT-60227, TT-60230
C4 | C4S5 | C4S5-IF16.dxf | 1756-IF16 | IS-JB-608 | Term 19 | Term 36 | i RTN-8 | IN-15 | AI | 12 | 4 | PT-60220, TT-60220, TT-60221, TT-60222, TT-60223, XT-60201
C4 | C4S6 | C4S6-IF16.dxf | 1756-IF16 | IS-JB-612 | Term 1 | Term 28 | i RTN-0 | RTN | AI | 4 | 0 | DPT-61310, DPT-61312
C4 | C4S6 | C4S6-IF16.dxf | 1756-IF16 | IS-JB-618 | Term 5 | Term 36 | i RTN-2 | IN-15 | AI | 18 | 10 | DPT-61301, DPT-61302, LT-61301, PT-61301, PT-61303, PT-61304, PT-61305, TT-61301, TT-61302
C4 | C4S7 | C4S7-N2.dxf | 1756-N2 | Unpopulated / Reserve | - | - | - | - | EMPTY | 0 | 0 | Unpopulated Slot Position
C4 | C4S8 | C4S8-N2.dxf | 1756-N2 | Unpopulated / Reserve | - | - | - | - | EMPTY | 0 | 0 | Unpopulated Slot Position
C4 | C4S9 | C4S9-N2.dxf | 1756-N2 | Unpopulated / Reserve | - | - | - | - | EMPTY | 0 | 0 | Unpopulated Slot Position
C4 | C4S10 | C4S10-N2.dxf | 1756-N2 | Unpopulated / Reserve | - | - | - | - | EMPTY | 0 | 0 | Unpopulated Slot Position
C4 | C4S11 | C4S11-N2.dxf | 1756-N2 | Unpopulated / Reserve | - | - | - | - | EMPTY | 0 | 0 | Unpopulated Slot Position
C4 | C4S12 | C4S12-N2.dxf | 1756-N2 | Unpopulated / Reserve | - | - | - | - | EMPTY | 0 | 0 | Unpopulated Slot Position