## 00_Conflict_Summary
KALASIN ENGINEERING xCIP-1545 — I/O LIST AUDIT & CONFLICT REPORT
Comparison between DWG Schematic Extractions and IO_List-By_SlotConfig_rev02.xlsx Specification
Metric | Value
Total Slot Sheets Analyzed | 57
Total Discrepancies Found | 813
High Severity Conflicts (Tags / Terminals) | 790
Medium Severity Conflicts (Areas / Descriptions) | 23
Chassis | Slot Sheet | DWG Active Points | REF Active Points | Conflict Count | Audit Status
C1 | C1S0 | 5 | 5 | 0 | PASSED
C1 | C1S1 | 4 | 4 | 2 | CONFLICT DETECTED
C1 | C1S2 | 4 | 4 | 2 | CONFLICT DETECTED
C1 | C1S3 | 4 | 4 | 2 | CONFLICT DETECTED
C1 | C1S4 | 16 | 16 | 18 | CONFLICT DETECTED
C1 | C1S5 | 32 | 32 | 18 | CONFLICT DETECTED
C1 | C1S6 | 12 | 12 | 20 | CONFLICT DETECTED
C1 | C1S7 | 23 | 23 | 15 | CONFLICT DETECTED
C1 | C1S8 | 16 | 16 | 18 | CONFLICT DETECTED
C1 | C1S9 | 20 | 20 | 22 | CONFLICT DETECTED
C1 | C1S10 | 22 | 22 | 32 | CONFLICT DETECTED
C1 | C1S11 | 16 | 16 | 26 | CONFLICT DETECTED
C1 | C1S12 | 0 | 0 | 2 | CONFLICT DETECTED
C2 | C2S0 | 4 | 4 | 2 | CONFLICT DETECTED
C2 | C2S1 | 24 | 24 | 18 | CONFLICT DETECTED
C2 | C2S2 | 23 | 23 | 17 | CONFLICT DETECTED
C2 | C2S3 | 29 | 29 | 20 | CONFLICT DETECTED
C2 | C2S4 | 32 | 32 | 18 | CONFLICT DETECTED
C2 | C2S5 | 20 | 20 | 14 | CONFLICT DETECTED
C2 | C2S6 | 12 | 12 | 15 | CONFLICT DETECTED
C2 | C2S7 | 31 | 31 | 18 | CONFLICT DETECTED
C2 | C2S8 | 9 | 9 | 6 | CONFLICT DETECTED
C2 | C2S9 | 14 | 14 | 24 | CONFLICT DETECTED
C2 | C2S10 | 32 | 32 | 28 | CONFLICT DETECTED
C2 | C2S11 | 0 | 0 | 32 | CONFLICT DETECTED
C2 | C2S12 | 0 | 0 | 32 | CONFLICT DETECTED
C3 | C3S0 | 4 | 4 | 2 | CONFLICT DETECTED
C3 | C3S1 | 4 | 4 | 14 | CONFLICT DETECTED
C3 | C3S2 | 17 | 17 | 10 | CONFLICT DETECTED
C3 | C3S3 | 12 | 12 | 8 | CONFLICT DETECTED
C3 | C3S4 | 16 | 16 | 20 | CONFLICT DETECTED
C3 | C3S5 | 9 | 9 | 6 | CONFLICT DETECTED
C3 | C3S6 | 30 | 30 | 30 | CONFLICT DETECTED
C3 | C3S7 | 32 | 32 | 28 | CONFLICT DETECTED
C3 | C3S8 | 24 | 24 | 30 | CONFLICT DETECTED
C3 | C3S9 | 16 | 16 | 30 | CONFLICT DETECTED
C3 | C3S10 | 0 | 0 | 2 | CONFLICT DETECTED
C3 | C3S11 | 0 | 0 | 2 | CONFLICT DETECTED
C3 | C3S12 | 5 | 5 | 2 | CONFLICT DETECTED
C4 | C4S0 | 4 | 4 | 2 | CONFLICT DETECTED
C4 | C4S1 | 22 | 22 | 48 | CONFLICT DETECTED
C4 | C4S2 | 15 | 15 | 8 | CONFLICT DETECTED
C4 | C4S3 | 13 | 13 | 2 | CONFLICT DETECTED
C4 | C4S4 | 1 | 1 | 2 | CONFLICT DETECTED
C4 | C4S5 | 26 | 26 | 38 | CONFLICT DETECTED
C4 | C4S6 | 22 | 22 | 34 | CONFLICT DETECTED
C4 | C4S7 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S8 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S9 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S10 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S11 | 0 | 0 | 2 | CONFLICT DETECTED
C4 | C4S12 | 0 | 0 | 2 | CONFLICT DETECTED
C5 | C5S0 | 4 | 4 | 2 | CONFLICT DETECTED
C5 | C5S1 | 32 | 32 | 18 | CONFLICT DETECTED
C5 | C5S2 | 8 | 8 | 8 | CONFLICT DETECTED
C5 | C5S3 | 8 | 8 | 6 | CONFLICT DETECTED
C5 | C5S4 | 18 | 18 | 28 | CONFLICT DETECTED

## Channel_Level_Conflicts
CHANNEL-LEVEL CONFLICT AUDIT LOG
Conflict ID | Chassis | Sheet | Terminal No | Discrepancy Field | DWG Drawing Value | Excel Reference Value | Severity | Recommended Action
CONF-0001 | C1 | C1S1 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0002 | C1 | C1S1 | RJ45-1 | Terminal Row | Missing in DWG | Terminal RJ45-1 | HIGH | Add Terminal to DWG Schematic
CONF-0003 | C1 | C1S2 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0004 | C1 | C1S2 | RJ45-1 | Terminal Row | Missing in DWG | Terminal RJ45-1 | HIGH | Add Terminal to DWG Schematic
CONF-0005 | C1 | C1S3 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0006 | C1 | C1S3 | RJ45-1 | Terminal Row | Missing in DWG | Terminal RJ45-1 | HIGH | Add Terminal to DWG Schematic
CONF-0007 | C1 | C1S4 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0008 | C1 | C1S4 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0009 | C1 | C1S4 | 19 | PLC_Tag | Internal Power Common | FSL-40201_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0010 | C1 | C1S4 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0011 | C1 | C1S4 | 20 | PLC_Tag | Internal Power Common | FSL-40202_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0012 | C1 | C1S4 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0013 | C1 | C1S4 | 21 | PLC_Tag | FSL-40201_DI_1 | FT-40201_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0014 | C1 | C1S4 | 22 | PLC_Tag | FSL-40202_DI_1 | FT-40202_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0015 | C1 | C1S4 | 23 | PLC_Tag | FT-40201_DI_1 | HV-40201_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0016 | C1 | C1S4 | 24 | PLC_Tag | FT-40202_DI_1 | HV-40202_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0017 | C1 | C1S4 | 25 | PLC_Tag | HV-40201_DI_1 | HV-40203_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0018 | C1 | C1S4 | 26 | PLC_Tag | HV-40202_DI_1 | HV-40204_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0019 | C1 | C1S4 | 27 | PLC_Tag | HV-40203_DI_1 | HV-40205_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0020 | C1 | C1S4 | 28 | PLC_Tag | HV-40204_DI_1 | HV-40206_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0021 | C1 | C1S4 | 29 | PLC_Tag | HV-40205_DI_1 | XV-40201A_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0022 | C1 | C1S4 | 30 | PLC_Tag | HV-40206_DI_1 | XV-40201A_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0023 | C1 | C1S4 | 31 | PLC_Tag | XV-40201A_DI_1 | XV-40201B_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0024 | C1 | C1S4 | 32 | PLC_Tag | XV-40201A_DI_2 | XV-40201B_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0025 | C1 | C1S5 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0026 | C1 | C1S5 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0027 | C1 | C1S5 | 19 | PLC_Tag | Internal Power Common | XV-40202D_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0028 | C1 | C1S5 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0029 | C1 | C1S5 | 20 | PLC_Tag | Internal Power Common | XV-40202E_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0030 | C1 | C1S5 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0031 | C1 | C1S5 | 21 | PLC_Tag | XV-40202D_DI_2 | XV-40202A_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0032 | C1 | C1S5 | 22 | PLC_Tag | XV-40202E_DI_1 | XV-40202E_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0033 | C1 | C1S5 | 23 | PLC_Tag | XV-40202A_DI_1 | XV-40202F_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0034 | C1 | C1S5 | 24 | PLC_Tag | XV-40202E_DI_2 | XV-40202F_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0035 | C1 | C1S5 | 25 | PLC_Tag | XV-40202F_DI_1 | XV-40202G_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0036 | C1 | C1S5 | 26 | PLC_Tag | XV-40202F_DI_2 | XV-40202G_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0037 | C1 | C1S5 | 27 | PLC_Tag | XV-40202G_DI_1 | XV-40202H_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0038 | C1 | C1S5 | 28 | PLC_Tag | XV-40202G_DI_2 | XV-40202H_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0039 | C1 | C1S5 | 29 | PLC_Tag | XV-40202H_DI_1 | XV-40203B_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0040 | C1 | C1S5 | 30 | PLC_Tag | XV-40202H_DI_2 | XV-40203B_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0041 | C1 | C1S5 | 31 | PLC_Tag | XV-40203B_DI_1 | XV-40203C_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0042 | C1 | C1S5 | 32 | PLC_Tag | XV-40203B_DI_2 | XV-40203C_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0043 | C1 | C1S6 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0044 | C1 | C1S6 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0045 | C1 | C1S6 | 19 | PLC_Tag | Internal Power Common | ES-60202_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0046 | C1 | C1S6 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0047 | C1 | C1S6 | 20 | PLC_Tag | Internal Power Common | FS-60205_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0048 | C1 | C1S6 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0049 | C1 | C1S6 | 21 | PLC_Tag | ES-60202_DI_1 | LSL-60201_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0050 | C1 | C1S6 | 22 | PLC_Tag | FS-60205_DI_1 | SV-60201_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0051 | C1 | C1S6 | 23 | PLC_Tag | LSL-60201_DI_1 | SV-60201_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0052 | C1 | C1S6 | 24 | PLC_Tag | SV-60201_DI_1 | SV-60202_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0053 | C1 | C1S6 | 25 | PLC_Tag | SV-60201_DI_2 | SV-60202_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0054 | C1 | C1S6 | 26 | PLC_Tag | SV-60202_DI_1 | SV-60203_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0055 | C1 | C1S6 | 27 | PLC_Tag | SV-60202_DI_2 | SV-60203_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0056 | C1 | C1S6 | 28 | PLC_Tag | SV-60203_DI_1 | VS-60205_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0057 | C1 | C1S6 | 29 | PLC_Tag | SV-60203_DI_2 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0058 | C1 | C1S6 | 29 | Instrument_Tag | SV-60203 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0059 | C1 | C1S6 | 29 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0060 | C1 | C1S6 | 30 | PLC_Tag | VS-60205_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0061 | C1 | C1S6 | 30 | Instrument_Tag | VS-60205 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0062 | C1 | C1S6 | 30 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0063 | C1 | C1S7 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0064 | C1 | C1S7 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0065 | C1 | C1S7 | 19 | PLC_Tag | Internal Power Common | XV-60205A_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0066 | C1 | C1S7 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0067 | C1 | C1S7 | 20 | PLC_Tag | Internal Power Common | XV-60240D_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0068 | C1 | C1S7 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0069 | C1 | C1S7 | 21 | PLC_Tag | XV-60205A_DI_2 | XV-60240D_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0070 | C1 | C1S7 | 24 | PLC_Tag | XV-60240D_DI_1 | YA-60205_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0071 | C1 | C1S7 | 25 | PLC_Tag | XV-60240D_DI_2 | YI-60205_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0072 | C1 | C1S7 | 26 | PLC_Tag | YA-60205_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0073 | C1 | C1S7 | 26 | Instrument_Tag | YA-60205 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0074 | C1 | C1S7 | 26 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0075 | C1 | C1S7 | 27 | PLC_Tag | YI-60205_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0076 | C1 | C1S7 | 27 | Instrument_Tag | YI-60205 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0077 | C1 | C1S7 | 27 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0078 | C1 | C1S8 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0079 | C1 | C1S8 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0080 | C1 | C1S8 | 19 | PLC_Tag | Spare_DO_17 | XV-40202E_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0081 | C1 | C1S8 | 19 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0082 | C1 | C1S8 | 20 | PLC_Tag | Internal Power Common | XV-40202F_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0083 | C1 | C1S8 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0084 | C1 | C1S8 | 21 | PLC_Tag | XV-40202E_DO_1 | XV-40202G_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0085 | C1 | C1S8 | 22 | PLC_Tag | XV-40202F_DO_1 | XV-40202H_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0086 | C1 | C1S8 | 23 | PLC_Tag | XV-40202G_DO_1 | XV-40203B_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0087 | C1 | C1S8 | 24 | PLC_Tag | XV-40202H_DO_1 | XV-40203C_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0088 | C1 | C1S8 | 25 | PLC_Tag | XV-40203B_DO_1 | XV-40203D_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0089 | C1 | C1S8 | 26 | PLC_Tag | XV-40203C_DO_1 | XV-40203E_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0090 | C1 | C1S8 | 27 | PLC_Tag | XV-40203D_DO_1 | SV-40201_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0091 | C1 | C1S8 | 28 | PLC_Tag | XV-40203E_DO_1 | SV-40202_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0092 | C1 | C1S8 | 29 | PLC_Tag | SV-40201_DO_1 | SV-40203_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0093 | C1 | C1S8 | 30 | PLC_Tag | SV-40202_DO_1 | SV-40204_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0094 | C1 | C1S8 | 31 | PLC_Tag | SV-40203_DO_1 | XV-40201A_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0095 | C1 | C1S8 | 32 | PLC_Tag | SV-40204_DO_1 | XV-40201B_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0096 | C1 | C1S9 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0097 | C1 | C1S9 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0098 | C1 | C1S9 | 19 | PLC_Tag | Spare_DO_17 | SV-60201_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0099 | C1 | C1S9 | 19 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0100 | C1 | C1S9 | 20 | PLC_Tag | Internal Power Common | SV-60202_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0101 | C1 | C1S9 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0102 | C1 | C1S9 | 21 | PLC_Tag | SV-60201_DO_1 | SV-60230_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0103 | C1 | C1S9 | 22 | PLC_Tag | SV-60202_DO_1 | SV-60203_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0104 | C1 | C1S9 | 23 | PLC_Tag | SV-60230_DO_1 | SV-60240A_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0105 | C1 | C1S9 | 24 | PLC_Tag | SV-60203_DO_1 | SV-60231_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0106 | C1 | C1S9 | 25 | PLC_Tag | SV-60240A_DO_1 | SV-60240B_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0107 | C1 | C1S9 | 26 | PLC_Tag | SV-60231_DO_1 | SV-60240C_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0108 | C1 | C1S9 | 27 | PLC_Tag | SV-60240B_DO_1 | XV-60240D_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0109 | C1 | C1S9 | 28 | PLC_Tag | SV-60240C_DO_1 | XV-60251_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0110 | C1 | C1S9 | 29 | PLC_Tag | XV-60240D_DO_1 | XV-60202_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0111 | C1 | C1S9 | 30 | PLC_Tag | XV-60251_DO_1 | XV-60205A_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0112 | C1 | C1S9 | 31 | PLC_Tag | XV-60202_DO_1 | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0113 | C1 | C1S9 | 31 | Instrument_Tag | XV-60202 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0114 | C1 | C1S9 | 31 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0115 | C1 | C1S9 | 32 | PLC_Tag | XV-60205A_DO_1 | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0116 | C1 | C1S9 | 32 | Instrument_Tag | XV-60205A | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0117 | C1 | C1S9 | 32 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0118 | C1 | C1S10 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0119 | C1 | C1S10 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0120 | C1 | C1S10 | 11 | PLC_Tag | Internal Power Common | LT-40201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0121 | C1 | C1S10 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0122 | C1 | C1S10 | 12 | PLC_Tag | Internal Power Common | LT-40201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0123 | C1 | C1S10 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0124 | C1 | C1S10 | 13 | PLC_Tag | LT-40201_AI_1 | LT-40202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0125 | C1 | C1S10 | 14 | PLC_Tag | LT-40201_AI_1 | LT-40202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0126 | C1 | C1S10 | 15 | PLC_Tag | LT-40202_AI_1 | pHT-40201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0127 | C1 | C1S10 | 16 | PLC_Tag | LT-40202_AI_1 | pHT-40201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0128 | C1 | C1S10 | 17 | PLC_Tag | pHT-40201_AI_1 | pHT-40202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0129 | C1 | C1S10 | 18 | PLC_Tag | pHT-40201_AI_1 | pHT-40202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0130 | C1 | C1S10 | 19 | PLC_Tag | pHT-40202_AI_1 | PT-40201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0131 | C1 | C1S10 | 20 | PLC_Tag | pHT-40202_AI_1 | PT-40201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0132 | C1 | C1S10 | 21 | PLC_Tag | PT-40201_AI_1 | PT-40202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0133 | C1 | C1S10 | 22 | PLC_Tag | PT-40201_AI_1 | PT-40202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0134 | C1 | C1S10 | 23 | PLC_Tag | PT-40202_AI_1 | PT-60202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0135 | C1 | C1S10 | 24 | PLC_Tag | PT-40202_AI_1 | PT-60202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0136 | C1 | C1S10 | 25 | PLC_Tag | PT-60202_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0137 | C1 | C1S10 | 25 | Instrument_Tag | PT-60202 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0138 | C1 | C1S10 | 25 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0139 | C1 | C1S10 | 26 | PLC_Tag | PT-60202_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0140 | C1 | C1S10 | 26 | Instrument_Tag | PT-60202 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0141 | C1 | C1S10 | 26 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0142 | C1 | C1S10 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0143 | C1 | C1S10 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0144 | C1 | C1S10 | 31 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0145 | C1 | C1S10 | 31 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0146 | C1 | C1S10 | 31 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0147 | C1 | C1S10 | 32 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0148 | C1 | C1S10 | 32 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0149 | C1 | C1S10 | 32 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0150 | C1 | C1S11 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0151 | C1 | C1S11 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0152 | C1 | C1S11 | 11 | PLC_Tag | Internal Power Common | FT-61307_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0153 | C1 | C1S11 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0154 | C1 | C1S11 | 12 | PLC_Tag | Internal Power Common | FT-61307_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0155 | C1 | C1S11 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0156 | C1 | C1S11 | 13 | PLC_Tag | FT-61307_AI_1 | PT-60203_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0157 | C1 | C1S11 | 14 | PLC_Tag | FT-61307_AI_1 | PT-60203_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0158 | C1 | C1S11 | 15 | PLC_Tag | PT-60203_AI_1 | PT-60204_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0159 | C1 | C1S11 | 16 | PLC_Tag | PT-60203_AI_1 | PT-60204_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0160 | C1 | C1S11 | 17 | PLC_Tag | PT-60204_AI_1 | PT-60205_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0161 | C1 | C1S11 | 18 | PLC_Tag | PT-60204_AI_1 | PT-60205_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0162 | C1 | C1S11 | 19 | PLC_Tag | PT-60205_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0163 | C1 | C1S11 | 19 | Instrument_Tag | PT-60205 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0164 | C1 | C1S11 | 19 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0165 | C1 | C1S11 | 20 | PLC_Tag | PT-60205_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0166 | C1 | C1S11 | 20 | Instrument_Tag | PT-60205 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0167 | C1 | C1S11 | 20 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0168 | C1 | C1S11 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0169 | C1 | C1S11 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0170 | C1 | C1S11 | 31 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0171 | C1 | C1S11 | 31 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0172 | C1 | C1S11 | 31 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0173 | C1 | C1S11 | 32 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0174 | C1 | C1S11 | 32 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0175 | C1 | C1S11 | 32 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0176 | C1 | C1S12 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0177 | C1 | C1S12 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0178 | C2 | C2S0 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0179 | C2 | C2S0 | RJ45-1 | Terminal Row | Missing in DWG | Terminal RJ45-1 | HIGH | Add Terminal to DWG Schematic
CONF-0180 | C2 | C2S1 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0181 | C2 | C2S1 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0182 | C2 | C2S1 | 19 | PLC_Tag | Internal Power Common | XV-40205C_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0183 | C2 | C2S1 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0184 | C2 | C2S1 | 20 | PLC_Tag | Internal Power Common | XV-40205C_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0185 | C2 | C2S1 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0186 | C2 | C2S1 | 21 | PLC_Tag | XV-40205C_DI_1 | XV-40205D_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0187 | C2 | C2S1 | 22 | PLC_Tag | XV-40205C_DI_2 | XV-40205D_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0188 | C2 | C2S1 | 23 | PLC_Tag | XV-40205D_DI_1 | XV-40205F_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0189 | C2 | C2S1 | 24 | PLC_Tag | XV-40205D_DI_2 | XV-40205F_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0190 | C2 | C2S1 | 25 | PLC_Tag | XV-40205F_DI_1 | XV-40222_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0191 | C2 | C2S1 | 26 | PLC_Tag | XV-40205F_DI_2 | XV-40222_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0192 | C2 | C2S1 | 27 | PLC_Tag | XV-40222_DI_1 | Spare_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0193 | C2 | C2S1 | 27 | Instrument_Tag | XV-40222 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0194 | C2 | C2S1 | 27 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0195 | C2 | C2S1 | 28 | PLC_Tag | XV-40222_DI_2 | Spare_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0196 | C2 | C2S1 | 28 | Instrument_Tag | XV-40222 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0197 | C2 | C2S1 | 28 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0198 | C2 | C2S2 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0199 | C2 | C2S2 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0200 | C2 | C2S2 | 19 | PLC_Tag | Internal Power Common | XA-60242B_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0201 | C2 | C2S2 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0202 | C2 | C2S2 | 20 | PLC_Tag | Internal Power Common | XA-60243A_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0203 | C2 | C2S2 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0204 | C2 | C2S2 | 21 | PLC_Tag | XA-60242B_DI_1 | XA-60243B_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0205 | C2 | C2S2 | 22 | PLC_Tag | XA-60243A_DI_1 | XV-60214_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0206 | C2 | C2S2 | 23 | PLC_Tag | XA-60243B_DI_1 | XV-60214_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0207 | C2 | C2S2 | 24 | PLC_Tag | XV-60214_DI_1 | XV-60241_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0208 | C2 | C2S2 | 25 | PLC_Tag | XV-60214_DI_2 | XV-60241_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0209 | C2 | C2S2 | 26 | PLC_Tag | XV-60241_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0210 | C2 | C2S2 | 26 | Instrument_Tag | XV-60241 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0211 | C2 | C2S2 | 26 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0212 | C2 | C2S2 | 27 | PLC_Tag | XV-60241_DI_2 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0213 | C2 | C2S2 | 27 | Instrument_Tag | XV-60241 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0214 | C2 | C2S2 | 27 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0215 | C2 | C2S3 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0216 | C2 | C2S3 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0217 | C2 | C2S3 | 19 | Destination_Area | JB-602 | JB-607 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0218 | C2 | C2S3 | 19 | PLC_Tag | Internal Power Common | XV-60201_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0219 | C2 | C2S3 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0220 | C2 | C2S3 | 20 | Destination_Area | JB-602 | JB-607 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0221 | C2 | C2S3 | 20 | PLC_Tag | Internal Power Common | XV-60201_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0222 | C2 | C2S3 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0223 | C2 | C2S3 | 21 | PLC_Tag | XV-60201_DI_1 | XV-60264FQ_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0224 | C2 | C2S3 | 22 | PLC_Tag | XV-60201_DI_2 | XV-60264FQ_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0225 | C2 | C2S3 | 23 | PLC_Tag | XV-60264FQ_DI_1 | XV-60261_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0226 | C2 | C2S3 | 24 | PLC_Tag | XV-60264FQ_DI_2 | XV-60261_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0227 | C2 | C2S3 | 25 | PLC_Tag | XV-60261_DI_1 | XV-60264FR_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0228 | C2 | C2S3 | 26 | PLC_Tag | XV-60261_DI_2 | XV-60264FR_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0229 | C2 | C2S3 | 27 | PLC_Tag | XV-60264FR_DI_1 | XV-60261FA_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0230 | C2 | C2S3 | 28 | PLC_Tag | XV-60264FR_DI_2 | XV-60261FA_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0231 | C2 | C2S3 | 29 | PLC_Tag | XV-60261FA_DI_1 | XV-60264SN_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0232 | C2 | C2S3 | 30 | PLC_Tag | XV-60261FA_DI_2 | XV-60264SN_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0233 | C2 | C2S3 | 31 | PLC_Tag | XV-60264SN_DI_1 | XV-60261FB_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0234 | C2 | C2S3 | 32 | PLC_Tag | XV-60264SN_DI_2 | XV-60261FB_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0235 | C2 | C2S4 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0236 | C2 | C2S4 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0237 | C2 | C2S4 | 19 | PLC_Tag | Internal Power Common | XV-60262_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0238 | C2 | C2S4 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0239 | C2 | C2S4 | 20 | PLC_Tag | Internal Power Common | XV-60262_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0240 | C2 | C2S4 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0241 | C2 | C2S4 | 21 | PLC_Tag | XV-60262_DI_1 | XV-60262FE_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0242 | C2 | C2S4 | 22 | PLC_Tag | XV-60262_DI_2 | XV-60262FE_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0243 | C2 | C2S4 | 23 | PLC_Tag | XV-60262FE_DI_1 | XV-60262FF_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0244 | C2 | C2S4 | 24 | PLC_Tag | XV-60262FE_DI_2 | XV-60262FF_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0245 | C2 | C2S4 | 25 | PLC_Tag | XV-60262FF_DI_1 | XV-60262FG_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0246 | C2 | C2S4 | 26 | PLC_Tag | XV-60262FF_DI_2 | XV-60262FG_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0247 | C2 | C2S4 | 27 | PLC_Tag | XV-60262FG_DI_1 | XV-60262FH_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0248 | C2 | C2S4 | 28 | PLC_Tag | XV-60262FG_DI_2 | XV-60262FH_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0249 | C2 | C2S4 | 29 | PLC_Tag | XV-60262FH_DI_1 | XV-60262SE_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0250 | C2 | C2S4 | 30 | PLC_Tag | XV-60262FH_DI_2 | XV-60262SE_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0251 | C2 | C2S4 | 31 | PLC_Tag | XV-60262SE_DI_1 | XV-60262SF_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0252 | C2 | C2S4 | 32 | PLC_Tag | XV-60262SE_DI_2 | XV-60262SF_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0253 | C2 | C2S5 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0254 | C2 | C2S5 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0255 | C2 | C2S5 | 19 | PLC_Tag | Internal Power Common | XV-60263SL_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0256 | C2 | C2S5 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0257 | C2 | C2S5 | 20 | PLC_Tag | Internal Power Common | XV-60263SL_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0258 | C2 | C2S5 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0259 | C2 | C2S5 | 21 | PLC_Tag | XV-60263SL_DI_1 | XV-60263SM_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0260 | C2 | C2S5 | 22 | PLC_Tag | XV-60263SL_DI_2 | XV-60263SM_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0261 | C2 | C2S5 | 23 | PLC_Tag | XV-60263SM_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0262 | C2 | C2S5 | 23 | Instrument_Tag | XV-60263SM | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0263 | C2 | C2S5 | 23 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0264 | C2 | C2S5 | 24 | PLC_Tag | XV-60263SM_DI_2 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0265 | C2 | C2S5 | 24 | Instrument_Tag | XV-60263SM | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0266 | C2 | C2S5 | 24 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0267 | C2 | C2S6 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0268 | C2 | C2S6 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0269 | C2 | C2S6 | 19 | Destination_Area | JB-402 | JB-602 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0270 | C2 | C2S6 | 19 | PLC_Tag | Spare_DO_17 | XS-60240B_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0271 | C2 | C2S6 | 19 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0272 | C2 | C2S6 | 20 | Destination_Area | JB-402 | JB-602 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0273 | C2 | C2S6 | 20 | PLC_Tag | Internal Power Common | XV-60214_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0274 | C2 | C2S6 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0275 | C2 | C2S6 | 21 | PLC_Tag | XS-60240B_DO_1 | XV-60241_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0276 | C2 | C2S6 | 22 | PLC_Tag | XV-60214_DO_1 | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0277 | C2 | C2S6 | 22 | Instrument_Tag | XV-60214 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0278 | C2 | C2S6 | 22 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0279 | C2 | C2S6 | 23 | PLC_Tag | XV-60241_DO_1 | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0280 | C2 | C2S6 | 23 | Instrument_Tag | XV-60241 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0281 | C2 | C2S6 | 23 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0282 | C2 | C2S7 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0283 | C2 | C2S7 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0284 | C2 | C2S7 | 19 | PLC_Tag | Spare_DO_17 | XV-60262FG_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0285 | C2 | C2S7 | 19 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0286 | C2 | C2S7 | 20 | PLC_Tag | Internal Power Common | XV-60262FH_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0287 | C2 | C2S7 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0288 | C2 | C2S7 | 21 | PLC_Tag | XV-60262FG_DO_1 | XV-60262SE_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0289 | C2 | C2S7 | 22 | PLC_Tag | XV-60262FH_DO_1 | XV-60262SF_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0290 | C2 | C2S7 | 23 | PLC_Tag | XV-60262SE_DO_1 | XV-60262SG_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0291 | C2 | C2S7 | 24 | PLC_Tag | XV-60262SF_DO_1 | XV-60262SH_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0292 | C2 | C2S7 | 25 | PLC_Tag | XV-60262SG_DO_1 | XV-60263_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0293 | C2 | C2S7 | 26 | PLC_Tag | XV-60262SH_DO_1 | XV-60263FJ_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0294 | C2 | C2S7 | 27 | PLC_Tag | XV-60263_DO_1 | XV-60263FK_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0295 | C2 | C2S7 | 28 | PLC_Tag | XV-60263FJ_DO_1 | XV-60263FL_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0296 | C2 | C2S7 | 29 | PLC_Tag | XV-60263FK_DO_1 | XV-60263FM_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0297 | C2 | C2S7 | 30 | PLC_Tag | XV-60263FL_DO_1 | XV-60263SJ_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0298 | C2 | C2S7 | 31 | PLC_Tag | XV-60263FM_DO_1 | XV-60263SK_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0299 | C2 | C2S7 | 32 | PLC_Tag | XV-60263SJ_DO_1 | XV-60263SL_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0300 | C2 | C2S8 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0301 | C2 | C2S8 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0302 | C2 | C2S8 | 19 | PLC_Tag | Spare_DO_17 | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0303 | C2 | C2S8 | 20 | PLC_Tag | Internal Power Common | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0304 | C2 | C2S8 | 20 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0305 | C2 | C2S8 | 20 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0306 | C2 | C2S9 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0307 | C2 | C2S9 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0308 | C2 | C2S9 | 11 | PLC_Tag | Internal Power Common | PT-40222_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0309 | C2 | C2S9 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0310 | C2 | C2S9 | 12 | PLC_Tag | Internal Power Common | PT-40222_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0311 | C2 | C2S9 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0312 | C2 | C2S9 | 13 | PLC_Tag | PT-40222_AI_1 | TT-40221_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0313 | C2 | C2S9 | 14 | PLC_Tag | PT-40222_AI_1 | TT-40221_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0314 | C2 | C2S9 | 15 | PLC_Tag | TT-40221_AI_1 | TT-40222_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0315 | C2 | C2S9 | 16 | PLC_Tag | TT-40221_AI_1 | TT-40222_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0316 | C2 | C2S9 | 17 | PLC_Tag | TT-40222_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0317 | C2 | C2S9 | 17 | Instrument_Tag | TT-40222 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0318 | C2 | C2S9 | 17 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0319 | C2 | C2S9 | 18 | PLC_Tag | TT-40222_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0320 | C2 | C2S9 | 18 | Instrument_Tag | TT-40222 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0321 | C2 | C2S9 | 18 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0322 | C2 | C2S9 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0323 | C2 | C2S9 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0324 | C2 | C2S9 | 31 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0325 | C2 | C2S9 | 31 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0326 | C2 | C2S9 | 31 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0327 | C2 | C2S9 | 32 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0328 | C2 | C2S9 | 32 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0329 | C2 | C2S9 | 32 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0330 | C2 | C2S10 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0331 | C2 | C2S10 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0332 | C2 | C2S10 | 11 | PLC_Tag | Internal Power Common | PT-60215_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0333 | C2 | C2S10 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0334 | C2 | C2S10 | 12 | PLC_Tag | Internal Power Common | PT-60215_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0335 | C2 | C2S10 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0336 | C2 | C2S10 | 13 | PLC_Tag | PT-60215_AI_1 | PT-60216_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0337 | C2 | C2S10 | 14 | PLC_Tag | PT-60215_AI_1 | PT-60216_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0338 | C2 | C2S10 | 15 | PLC_Tag | PT-60216_AI_1 | PT-60240_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0339 | C2 | C2S10 | 16 | PLC_Tag | PT-60216_AI_1 | PT-60240_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0340 | C2 | C2S10 | 17 | PLC_Tag | PT-60240_AI_1 | PT-60241_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0341 | C2 | C2S10 | 18 | PLC_Tag | PT-60240_AI_1 | PT-60241_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0342 | C2 | C2S10 | 19 | PLC_Tag | PT-60241_AI_1 | TT-60210_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0343 | C2 | C2S10 | 20 | PLC_Tag | PT-60241_AI_1 | TT-60210_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0344 | C2 | C2S10 | 21 | PLC_Tag | TT-60210_AI_1 | TT-60210A_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0345 | C2 | C2S10 | 22 | PLC_Tag | TT-60210_AI_1 | TT-60210A_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0346 | C2 | C2S10 | 23 | PLC_Tag | TT-60210A_AI_1 | TT-60210B_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0347 | C2 | C2S10 | 24 | PLC_Tag | TT-60210A_AI_1 | TT-60210B_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0348 | C2 | C2S10 | 25 | PLC_Tag | TT-60210B_AI_1 | TT-60211_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0349 | C2 | C2S10 | 26 | PLC_Tag | TT-60210B_AI_1 | TT-60211_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0350 | C2 | C2S10 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0351 | C2 | C2S10 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0352 | C2 | C2S10 | 29 | PLC_Tag | TT-60211_AI_1 | TT-60212A_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0353 | C2 | C2S10 | 30 | PLC_Tag | TT-60211_AI_1 | TT-60212A_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0354 | C2 | C2S10 | 31 | PLC_Tag | Internal Power Common | TT-60212B_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0355 | C2 | C2S10 | 31 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0356 | C2 | C2S10 | 32 | PLC_Tag | Internal Power Common | TT-60212B_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0357 | C2 | C2S10 | 32 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0358 | C2 | C2S11 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0359 | C2 | C2S11 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0360 | C2 | C2S11 | 11 | PLC_Tag | Internal Power Common | Spare_AI_5 | HIGH | Align Excel PLC_Tag with DWG
CONF-0361 | C2 | C2S11 | 11 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0362 | C2 | C2S11 | 11 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0363 | C2 | C2S11 | 12 | PLC_Tag | Internal Power Common | Spare_AI_5 | HIGH | Align Excel PLC_Tag with DWG
CONF-0364 | C2 | C2S11 | 12 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0365 | C2 | C2S11 | 12 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0366 | C2 | C2S11 | 13 | PLC_Tag | Spare_AI_5 | Spare_AI_6 | HIGH | Align Excel PLC_Tag with DWG
CONF-0367 | C2 | C2S11 | 14 | PLC_Tag | Spare_AI_5 | Spare_AI_6 | HIGH | Align Excel PLC_Tag with DWG
CONF-0368 | C2 | C2S11 | 15 | PLC_Tag | Spare_AI_6 | Spare_AI_7 | HIGH | Align Excel PLC_Tag with DWG
CONF-0369 | C2 | C2S11 | 16 | PLC_Tag | Spare_AI_6 | Spare_AI_7 | HIGH | Align Excel PLC_Tag with DWG
CONF-0370 | C2 | C2S11 | 17 | PLC_Tag | Spare_AI_7 | Spare_AI_8 | HIGH | Align Excel PLC_Tag with DWG
CONF-0371 | C2 | C2S11 | 18 | PLC_Tag | Spare_AI_7 | Spare_AI_8 | HIGH | Align Excel PLC_Tag with DWG
CONF-0372 | C2 | C2S11 | 19 | PLC_Tag | Spare_AI_8 | Spare_AI_9 | HIGH | Align Excel PLC_Tag with DWG
CONF-0373 | C2 | C2S11 | 20 | PLC_Tag | Spare_AI_8 | Spare_AI_9 | HIGH | Align Excel PLC_Tag with DWG
CONF-0374 | C2 | C2S11 | 21 | PLC_Tag | Spare_AI_9 | Spare_AI_10 | HIGH | Align Excel PLC_Tag with DWG
CONF-0375 | C2 | C2S11 | 22 | PLC_Tag | Spare_AI_9 | Spare_AI_10 | HIGH | Align Excel PLC_Tag with DWG
CONF-0376 | C2 | C2S11 | 23 | PLC_Tag | Spare_AI_10 | Spare_AI_11 | HIGH | Align Excel PLC_Tag with DWG
CONF-0377 | C2 | C2S11 | 24 | PLC_Tag | Spare_AI_10 | Spare_AI_11 | HIGH | Align Excel PLC_Tag with DWG
CONF-0378 | C2 | C2S11 | 25 | PLC_Tag | Spare_AI_11 | Spare_AI_12 | HIGH | Align Excel PLC_Tag with DWG
CONF-0379 | C2 | C2S11 | 26 | PLC_Tag | Spare_AI_11 | Spare_AI_12 | HIGH | Align Excel PLC_Tag with DWG
CONF-0380 | C2 | C2S11 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0381 | C2 | C2S11 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0382 | C2 | C2S11 | 29 | PLC_Tag | Spare_AI_12 | Spare_AI_13 | HIGH | Align Excel PLC_Tag with DWG
CONF-0383 | C2 | C2S11 | 30 | PLC_Tag | Spare_AI_12 | Spare_AI_13 | HIGH | Align Excel PLC_Tag with DWG
CONF-0384 | C2 | C2S11 | 31 | PLC_Tag | Internal Power Common | Spare_AI_14 | HIGH | Align Excel PLC_Tag with DWG
CONF-0385 | C2 | C2S11 | 31 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0386 | C2 | C2S11 | 31 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0387 | C2 | C2S11 | 32 | PLC_Tag | Internal Power Common | Spare_AI_14 | HIGH | Align Excel PLC_Tag with DWG
CONF-0388 | C2 | C2S11 | 32 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0389 | C2 | C2S11 | 32 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0390 | C2 | C2S12 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0391 | C2 | C2S12 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0392 | C2 | C2S12 | 11 | PLC_Tag | Internal Power Common | Spare_AI_5 | HIGH | Align Excel PLC_Tag with DWG
CONF-0393 | C2 | C2S12 | 11 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0394 | C2 | C2S12 | 11 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0395 | C2 | C2S12 | 12 | PLC_Tag | Internal Power Common | Spare_AI_5 | HIGH | Align Excel PLC_Tag with DWG
CONF-0396 | C2 | C2S12 | 12 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0397 | C2 | C2S12 | 12 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0398 | C2 | C2S12 | 13 | PLC_Tag | Spare_AI_5 | Spare_AI_6 | HIGH | Align Excel PLC_Tag with DWG
CONF-0399 | C2 | C2S12 | 14 | PLC_Tag | Spare_AI_5 | Spare_AI_6 | HIGH | Align Excel PLC_Tag with DWG
CONF-0400 | C2 | C2S12 | 15 | PLC_Tag | Spare_AI_6 | Spare_AI_7 | HIGH | Align Excel PLC_Tag with DWG
CONF-0401 | C2 | C2S12 | 16 | PLC_Tag | Spare_AI_6 | Spare_AI_7 | HIGH | Align Excel PLC_Tag with DWG
CONF-0402 | C2 | C2S12 | 17 | PLC_Tag | Spare_AI_7 | Spare_AI_8 | HIGH | Align Excel PLC_Tag with DWG
CONF-0403 | C2 | C2S12 | 18 | PLC_Tag | Spare_AI_7 | Spare_AI_8 | HIGH | Align Excel PLC_Tag with DWG
CONF-0404 | C2 | C2S12 | 19 | PLC_Tag | Spare_AI_8 | Spare_AI_9 | HIGH | Align Excel PLC_Tag with DWG
CONF-0405 | C2 | C2S12 | 20 | PLC_Tag | Spare_AI_8 | Spare_AI_9 | HIGH | Align Excel PLC_Tag with DWG
CONF-0406 | C2 | C2S12 | 21 | PLC_Tag | Spare_AI_9 | Spare_AI_10 | HIGH | Align Excel PLC_Tag with DWG
CONF-0407 | C2 | C2S12 | 22 | PLC_Tag | Spare_AI_9 | Spare_AI_10 | HIGH | Align Excel PLC_Tag with DWG
CONF-0408 | C2 | C2S12 | 23 | PLC_Tag | Spare_AI_10 | Spare_AI_11 | HIGH | Align Excel PLC_Tag with DWG
CONF-0409 | C2 | C2S12 | 24 | PLC_Tag | Spare_AI_10 | Spare_AI_11 | HIGH | Align Excel PLC_Tag with DWG
CONF-0410 | C2 | C2S12 | 25 | PLC_Tag | Spare_AI_11 | Spare_AI_12 | HIGH | Align Excel PLC_Tag with DWG
CONF-0411 | C2 | C2S12 | 26 | PLC_Tag | Spare_AI_11 | Spare_AI_12 | HIGH | Align Excel PLC_Tag with DWG
CONF-0412 | C2 | C2S12 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0413 | C2 | C2S12 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0414 | C2 | C2S12 | 29 | PLC_Tag | Spare_AI_12 | Spare_AI_13 | HIGH | Align Excel PLC_Tag with DWG
CONF-0415 | C2 | C2S12 | 30 | PLC_Tag | Spare_AI_12 | Spare_AI_13 | HIGH | Align Excel PLC_Tag with DWG
CONF-0416 | C2 | C2S12 | 31 | PLC_Tag | Internal Power Common | Spare_AI_14 | HIGH | Align Excel PLC_Tag with DWG
CONF-0417 | C2 | C2S12 | 31 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0418 | C2 | C2S12 | 31 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0419 | C2 | C2S12 | 32 | PLC_Tag | Internal Power Common | Spare_AI_14 | HIGH | Align Excel PLC_Tag with DWG
CONF-0420 | C2 | C2S12 | 32 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0421 | C2 | C2S12 | 32 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0422 | C3 | C3S0 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0423 | C3 | C3S0 | RJ45-1 | Terminal Row | Missing in DWG | Terminal RJ45-1 | HIGH | Add Terminal to DWG Schematic
CONF-0424 | C3 | C3S1 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0425 | C3 | C3S1 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0426 | C3 | C3S1 | 19 | PLC_Tag | Internal Power Common | FT-60203_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0427 | C3 | C3S1 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0428 | C3 | C3S1 | 20 | PLC_Tag | Internal Power Common | LSH-60250_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0429 | C3 | C3S1 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0430 | C3 | C3S1 | 21 | PLC_Tag | FT-60203_DI_1 | XA-60261_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0431 | C3 | C3S1 | 22 | PLC_Tag | LSH-60250_DI_1 | XA-60262_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0432 | C3 | C3S1 | 23 | PLC_Tag | XA-60261_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0433 | C3 | C3S1 | 23 | Instrument_Tag | XA-60261 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0434 | C3 | C3S1 | 23 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0435 | C3 | C3S1 | 24 | PLC_Tag | XA-60262_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0436 | C3 | C3S1 | 24 | Instrument_Tag | XA-60262 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0437 | C3 | C3S1 | 24 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0438 | C3 | C3S2 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0439 | C3 | C3S2 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0440 | C3 | C3S2 | 19 | PLC_Tag | Internal Power Common | XV-61303_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0441 | C3 | C3S2 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0442 | C3 | C3S2 | 20 | PLC_Tag | Internal Power Common | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0443 | C3 | C3S2 | 20 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0444 | C3 | C3S2 | 20 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0445 | C3 | C3S2 | 21 | PLC_Tag | XV-61303_DI_2 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0446 | C3 | C3S2 | 21 | Instrument_Tag | XV-61303 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0447 | C3 | C3S2 | 21 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0448 | C3 | C3S3 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0449 | C3 | C3S3 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0450 | C3 | C3S3 | 19 | PLC_Tag | Internal Power Common | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0451 | C3 | C3S3 | 19 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0452 | C3 | C3S3 | 19 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0453 | C3 | C3S3 | 20 | PLC_Tag | Internal Power Common | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0454 | C3 | C3S3 | 20 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0455 | C3 | C3S3 | 20 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0456 | C3 | C3S4 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0457 | C3 | C3S4 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0458 | C3 | C3S4 | 19 | Destination_Area | JB-606 | JB-612 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0459 | C3 | C3S4 | 19 | PLC_Tag | Spare_DO_17 | PVM-61301_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0460 | C3 | C3S4 | 19 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0461 | C3 | C3S4 | 20 | Destination_Area | JB-606 | JB-612 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0462 | C3 | C3S4 | 20 | PLC_Tag | Internal Power Common | PVM-61301_DO_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0463 | C3 | C3S4 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0464 | C3 | C3S4 | 21 | PLC_Tag | PVM-61301_DO_1 | SV-61307_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0465 | C3 | C3S4 | 22 | PLC_Tag | PVM-61301_DO_2 | SV-61308_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0466 | C3 | C3S4 | 23 | PLC_Tag | SV-61307_DO_1 | SV-61309_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0467 | C3 | C3S4 | 24 | PLC_Tag | SV-61308_DO_1 | SV-61310_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0468 | C3 | C3S4 | 25 | PLC_Tag | SV-61309_DO_1 | SV-61311_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0469 | C3 | C3S4 | 26 | PLC_Tag | SV-61310_DO_1 | XS-61301A_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0470 | C3 | C3S4 | 27 | PLC_Tag | SV-61311_DO_1 | XS-61301B_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0471 | C3 | C3S4 | 28 | PLC_Tag | XS-61301A_DO_1 | XS-61301C_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0472 | C3 | C3S4 | 29 | PLC_Tag | XS-61301B_DO_1 | XS-61301D_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0473 | C3 | C3S4 | 30 | PLC_Tag | XS-61301C_DO_1 | XS-61301E_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0474 | C3 | C3S4 | 31 | PLC_Tag | XS-61301D_DO_1 | XS-61301F_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0475 | C3 | C3S4 | 32 | PLC_Tag | XS-61301E_DO_1 | XV-61302_DO_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0476 | C3 | C3S5 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0477 | C3 | C3S5 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0478 | C3 | C3S5 | 19 | PLC_Tag | Spare_DO_17 | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0479 | C3 | C3S5 | 20 | PLC_Tag | Internal Power Common | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0480 | C3 | C3S5 | 20 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0481 | C3 | C3S5 | 20 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0482 | C3 | C3S6 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0483 | C3 | C3S6 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0484 | C3 | C3S6 | 11 | PLC_Tag | Internal Power Common | TT-60241B_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0485 | C3 | C3S6 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0486 | C3 | C3S6 | 12 | PLC_Tag | Internal Power Common | TT-60241B_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0487 | C3 | C3S6 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0488 | C3 | C3S6 | 13 | PLC_Tag | TT-60241B_AI_1 | VT-60210A_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0489 | C3 | C3S6 | 14 | PLC_Tag | TT-60241B_AI_1 | VT-60210A_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0490 | C3 | C3S6 | 15 | PLC_Tag | VT-60210A_AI_1 | VT-60210B_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0491 | C3 | C3S6 | 16 | PLC_Tag | VT-60210A_AI_1 | VT-60210B_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0492 | C3 | C3S6 | 17 | PLC_Tag | VT-60210B_AI_1 | VT-60241A_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0493 | C3 | C3S6 | 18 | PLC_Tag | VT-60210B_AI_1 | VT-60241A_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0494 | C3 | C3S6 | 19 | PLC_Tag | VT-60241A_AI_1 | VT-60241B_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0495 | C3 | C3S6 | 20 | PLC_Tag | VT-60241A_AI_1 | VT-60241B_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0496 | C3 | C3S6 | 21 | PLC_Tag | VT-60241B_AI_1 | FT-60210_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0497 | C3 | C3S6 | 22 | PLC_Tag | VT-60241B_AI_1 | FT-60210_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0498 | C3 | C3S6 | 23 | PLC_Tag | FT-60210_AI_1 | FT-60211_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0499 | C3 | C3S6 | 24 | PLC_Tag | FT-60210_AI_1 | FT-60211_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0500 | C3 | C3S6 | 25 | PLC_Tag | FT-60211_AI_1 | FT-60210_AI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0501 | C3 | C3S6 | 26 | PLC_Tag | FT-60211_AI_1 | FT-60210_AI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0502 | C3 | C3S6 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0503 | C3 | C3S6 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0504 | C3 | C3S6 | 29 | PLC_Tag | FT-60210_AI_2 | FT-60211_AI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0505 | C3 | C3S6 | 30 | PLC_Tag | FT-60210_AI_2 | FT-60211_AI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0506 | C3 | C3S6 | 31 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0507 | C3 | C3S6 | 31 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0508 | C3 | C3S6 | 31 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0509 | C3 | C3S6 | 32 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0510 | C3 | C3S6 | 32 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0511 | C3 | C3S6 | 32 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0512 | C3 | C3S7 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0513 | C3 | C3S7 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0514 | C3 | C3S7 | 11 | PLC_Tag | Internal Power Common | FT-60261FC_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0515 | C3 | C3S7 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0516 | C3 | C3S7 | 12 | PLC_Tag | Internal Power Common | FT-60261FC_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0517 | C3 | C3S7 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0518 | C3 | C3S7 | 13 | PLC_Tag | FT-60261FC_AI_1 | FT-60261FD_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0519 | C3 | C3S7 | 14 | PLC_Tag | FT-60261FC_AI_1 | FT-60261FD_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0520 | C3 | C3S7 | 15 | PLC_Tag | FT-60261FD_AI_1 | FT-60262FE_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0521 | C3 | C3S7 | 16 | PLC_Tag | FT-60261FD_AI_1 | FT-60262FE_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0522 | C3 | C3S7 | 17 | PLC_Tag | FT-60262FE_AI_1 | FT-60262FF_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0523 | C3 | C3S7 | 18 | PLC_Tag | FT-60262FE_AI_1 | FT-60262FF_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0524 | C3 | C3S7 | 19 | PLC_Tag | FT-60262FF_AI_1 | FT-60262FG_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0525 | C3 | C3S7 | 20 | PLC_Tag | FT-60262FF_AI_1 | FT-60262FG_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0526 | C3 | C3S7 | 21 | PLC_Tag | FT-60262FG_AI_1 | FT-60262FH_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0527 | C3 | C3S7 | 22 | PLC_Tag | FT-60262FG_AI_1 | FT-60262FH_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0528 | C3 | C3S7 | 23 | PLC_Tag | FT-60262FH_AI_1 | FT-60263FJ_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0529 | C3 | C3S7 | 24 | PLC_Tag | FT-60262FH_AI_1 | FT-60263FJ_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0530 | C3 | C3S7 | 25 | PLC_Tag | FT-60263FJ_AI_1 | FT-60263FK_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0531 | C3 | C3S7 | 26 | PLC_Tag | FT-60263FJ_AI_1 | FT-60263FK_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0532 | C3 | C3S7 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0533 | C3 | C3S7 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0534 | C3 | C3S7 | 29 | PLC_Tag | FT-60263FK_AI_1 | FT-60263FL_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0535 | C3 | C3S7 | 30 | PLC_Tag | FT-60263FK_AI_1 | FT-60263FL_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0536 | C3 | C3S7 | 31 | PLC_Tag | Internal Power Common | FT-60263FM_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0537 | C3 | C3S7 | 31 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0538 | C3 | C3S7 | 32 | PLC_Tag | Internal Power Common | FT-60263FM_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0539 | C3 | C3S7 | 32 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0540 | C3 | C3S8 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0541 | C3 | C3S8 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0542 | C3 | C3S8 | 11 | PLC_Tag | Internal Power Common | PT-60221_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0543 | C3 | C3S8 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0544 | C3 | C3S8 | 12 | PLC_Tag | Internal Power Common | PT-60221_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0545 | C3 | C3S8 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0546 | C3 | C3S8 | 15 | PLC_Tag | PT-60221_AI_1 | TI-FH-60210_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0547 | C3 | C3S8 | 16 | PLC_Tag | PT-60221_AI_1 | TI-FH-60210_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0548 | C3 | C3S8 | 17 | PLC_Tag | TI-FH-60210_AI_1 | TT-60201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0549 | C3 | C3S8 | 18 | PLC_Tag | TI-FH-60210_AI_1 | TT-60201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0550 | C3 | C3S8 | 19 | PLC_Tag | TT-60201_AI_1 | TT-60202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0551 | C3 | C3S8 | 20 | PLC_Tag | TT-60201_AI_1 | TT-60202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0552 | C3 | C3S8 | 21 | PLC_Tag | TT-60202_AI_1 | TT-60207_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0553 | C3 | C3S8 | 22 | PLC_Tag | TT-60202_AI_1 | TT-60207_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0554 | C3 | C3S8 | 23 | PLC_Tag | TT-60207_AI_1 | UY-FH-60210A_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0555 | C3 | C3S8 | 24 | PLC_Tag | TT-60207_AI_1 | UY-FH-60210A_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0556 | C3 | C3S8 | 25 | PLC_Tag | UY-FH-60210A_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0557 | C3 | C3S8 | 25 | Instrument_Tag | UY-FH-60210A | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0558 | C3 | C3S8 | 25 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0559 | C3 | C3S8 | 26 | PLC_Tag | UY-FH-60210A_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0560 | C3 | C3S8 | 26 | Instrument_Tag | UY-FH-60210A | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0561 | C3 | C3S8 | 26 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0562 | C3 | C3S8 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0563 | C3 | C3S8 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0564 | C3 | C3S8 | 31 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0565 | C3 | C3S8 | 31 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0566 | C3 | C3S8 | 31 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0567 | C3 | C3S8 | 32 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0568 | C3 | C3S8 | 32 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0569 | C3 | C3S8 | 32 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0570 | C3 | C3S9 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0571 | C3 | C3S9 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0572 | C3 | C3S9 | 11 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0573 | C3 | C3S9 | 11 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0574 | C3 | C3S9 | 11 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0575 | C3 | C3S9 | 12 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0576 | C3 | C3S9 | 12 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0577 | C3 | C3S9 | 12 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0578 | C3 | C3S9 | 19 | PLC_Tag | Spare_AI_0 | PT-61302_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0579 | C3 | C3S9 | 19 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0580 | C3 | C3S9 | 20 | PLC_Tag | Spare_AI_0 | PT-61302_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0581 | C3 | C3S9 | 20 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0582 | C3 | C3S9 | 21 | PLC_Tag | PT-61302_AI_1 | PT-61309_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0583 | C3 | C3S9 | 22 | PLC_Tag | PT-61302_AI_1 | PT-61309_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0584 | C3 | C3S9 | 23 | PLC_Tag | PT-61309_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0585 | C3 | C3S9 | 23 | Instrument_Tag | PT-61309 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0586 | C3 | C3S9 | 23 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0587 | C3 | C3S9 | 24 | PLC_Tag | PT-61309_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0588 | C3 | C3S9 | 24 | Instrument_Tag | PT-61309 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0589 | C3 | C3S9 | 24 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0590 | C3 | C3S9 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0591 | C3 | C3S9 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0592 | C3 | C3S9 | 29 | PLC_Tag | Spare_AI_0 | PT-61302_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0593 | C3 | C3S9 | 29 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0594 | C3 | C3S9 | 30 | PLC_Tag | Spare_AI_0 | PT-61302_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0595 | C3 | C3S9 | 30 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0596 | C3 | C3S9 | 31 | PLC_Tag | Internal Power Common | PT-61309_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0597 | C3 | C3S9 | 31 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0598 | C3 | C3S9 | 32 | PLC_Tag | Internal Power Common | PT-61309_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0599 | C3 | C3S9 | 32 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0600 | C3 | C3S10 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0601 | C3 | C3S10 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0602 | C3 | C3S11 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0603 | C3 | C3S11 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0604 | C3 | C3S12 | 1 | Terminal Row | Missing in DWG | Terminal 1 | HIGH | Add Terminal to DWG Schematic
CONF-0605 | C3 | C3S12 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0606 | C4 | C4S0 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0607 | C4 | C4S0 | RJ45-1 | Terminal Row | Missing in DWG | Terminal RJ45-1 | HIGH | Add Terminal to DWG Schematic
CONF-0608 | C4 | C4S1 | 1 | Instrument_Tag | ISV-61303 | AT-40201 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0609 | C4 | C4S1 | 2 | Instrument_Tag | ISV-61304 | AT-40202 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0610 | C4 | C4S1 | 3 | Instrument_Tag | LSH-61304 | AT-40203 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0611 | C4 | C4S1 | 4 | Instrument_Tag | LSH-61305 | LSH-60230 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0612 | C4 | C4S1 | 5 | Instrument_Tag | LSH-61307 | LSH-60231 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0613 | C4 | C4S1 | 6 | Instrument_Tag | LSH-61312 | LSH-60240 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0614 | C4 | C4S1 | 7 | Instrument_Tag | PSE-61302 | PD-60202 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0615 | C4 | C4S1 | 8 | Instrument_Tag | PSE-61303 | RV-60204 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0616 | C4 | C4S1 | 9 | Instrument_Tag | RV-61301 | ZS-60201C | HIGH | Align Excel Instrument_Tag with DWG
CONF-0617 | C4 | C4S1 | 10 | Instrument_Tag | RV-61304 | ZS-60201D | HIGH | Align Excel Instrument_Tag with DWG
CONF-0618 | C4 | C4S1 | 11 | Instrument_Tag | RV-61305 | ZS-60201E | HIGH | Align Excel Instrument_Tag with DWG
CONF-0619 | C4 | C4S1 | 12 | Instrument_Tag | SC-61301 | ZS-60229 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0620 | C4 | C4S1 | 13 | Instrument_Tag | SC-61302 | ZS-60230 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0621 | C4 | C4S1 | 14 | Instrument_Tag | ZS-61312 | ZS-60231A | HIGH | Align Excel Instrument_Tag with DWG
CONF-0622 | C4 | C4S1 | 15 | Instrument_Tag | ZS-61313 | ZS-60231B | HIGH | Align Excel Instrument_Tag with DWG
CONF-0623 | C4 | C4S1 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0624 | C4 | C4S1 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0625 | C4 | C4S1 | 19 | Destination_Area | IS-JB-603 | IS-JB-608 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0626 | C4 | C4S1 | 19 | PLC_Tag | Internal Power Common | ZS-60201A_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0627 | C4 | C4S1 | 19 | Instrument_Tag |  | ZS-60201A | HIGH | Verify DWG Instrument_Tag
CONF-0628 | C4 | C4S1 | 19 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0629 | C4 | C4S1 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0630 | C4 | C4S1 | 20 | Destination_Area | IS-JB-603 | IS-JB-608 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0631 | C4 | C4S1 | 20 | PLC_Tag | Internal Power Common | ZS-60201B_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0632 | C4 | C4S1 | 20 | Instrument_Tag |  | ZS-60201B | HIGH | Verify DWG Instrument_Tag
CONF-0633 | C4 | C4S1 | 20 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0634 | C4 | C4S1 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0635 | C4 | C4S1 | 21 | PLC_Tag | ZS-60201A_DI_1 | ZS-60231C_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0636 | C4 | C4S1 | 21 | Instrument_Tag | ZS-60201A | ZS-60231C | HIGH | Align Excel Instrument_Tag with DWG
CONF-0637 | C4 | C4S1 | 21 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0638 | C4 | C4S1 | 22 | PLC_Tag | ZS-60201B_DI_1 | ZS-60231D_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0639 | C4 | C4S1 | 22 | Instrument_Tag | ZS-60201B | ZS-60231D | HIGH | Align Excel Instrument_Tag with DWG
CONF-0640 | C4 | C4S1 | 22 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0641 | C4 | C4S1 | 23 | PLC_Tag | ZS-60231C_DI_1 | ZS-60231E_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0642 | C4 | C4S1 | 23 | Instrument_Tag | ZS-60231C | ZS-60231E | HIGH | Align Excel Instrument_Tag with DWG
CONF-0643 | C4 | C4S1 | 23 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0644 | C4 | C4S1 | 24 | PLC_Tag | ZS-60231D_DI_1 | ZS-60231F_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0645 | C4 | C4S1 | 24 | Instrument_Tag | ZS-60231D | ZS-60231F | HIGH | Align Excel Instrument_Tag with DWG
CONF-0646 | C4 | C4S1 | 24 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0647 | C4 | C4S1 | 25 | PLC_Tag | ZS-60231E_DI_1 | ZS-60240_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0648 | C4 | C4S1 | 25 | Instrument_Tag | ZS-60231E | ZS-60240 | HIGH | Align Excel Instrument_Tag with DWG
CONF-0649 | C4 | C4S1 | 25 | Instrument_Description | Spare Reserve Channel | Process Instrument | MEDIUM | Align Excel Instrument_Description with DWG
CONF-0650 | C4 | C4S1 | 26 | PLC_Tag | ZS-60231F_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0651 | C4 | C4S1 | 26 | Instrument_Tag | ZS-60231F | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0652 | C4 | C4S1 | 26 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0653 | C4 | C4S1 | 27 | PLC_Tag | ZS-60240_DI_1 | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0654 | C4 | C4S1 | 27 | Instrument_Tag | ZS-60240 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0655 | C4 | C4S1 | 27 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0656 | C4 | C4S2 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0657 | C4 | C4S2 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0658 | C4 | C4S2 | 19 | PLC_Tag | Internal Power Common | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0659 | C4 | C4S2 | 19 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0660 | C4 | C4S2 | 19 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0661 | C4 | C4S2 | 20 | PLC_Tag | Internal Power Common | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0662 | C4 | C4S2 | 20 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0663 | C4 | C4S2 | 20 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0664 | C4 | C4S3 | 1 | Terminal Row | Missing in DWG | Terminal 1 | HIGH | Add Terminal to DWG Schematic
CONF-0665 | C4 | C4S3 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0666 | C4 | C4S4 | 1 | Terminal Row | Missing in DWG | Terminal 1 | HIGH | Add Terminal to DWG Schematic
CONF-0667 | C4 | C4S4 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0668 | C4 | C4S5 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0669 | C4 | C4S5 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0670 | C4 | C4S5 | 11 | PLC_Tag | Internal Power Common | TT-60226_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0671 | C4 | C4S5 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0672 | C4 | C4S5 | 12 | PLC_Tag | Internal Power Common | TT-60226_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0673 | C4 | C4S5 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0674 | C4 | C4S5 | 13 | PLC_Tag | TT-60226_AI_1 | TT-60227_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0675 | C4 | C4S5 | 14 | PLC_Tag | TT-60226_AI_1 | TT-60227_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0676 | C4 | C4S5 | 15 | PLC_Tag | TT-60227_AI_1 | TT-60230_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0677 | C4 | C4S5 | 16 | PLC_Tag | TT-60227_AI_1 | TT-60230_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0678 | C4 | C4S5 | 17 | PLC_Tag | TT-60230_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0679 | C4 | C4S5 | 17 | Instrument_Tag | TT-60230 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0680 | C4 | C4S5 | 17 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0681 | C4 | C4S5 | 18 | PLC_Tag | TT-60230_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0682 | C4 | C4S5 | 18 | Instrument_Tag | TT-60230 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0683 | C4 | C4S5 | 18 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0684 | C4 | C4S5 | 19 | Destination_Area | IS-JB-603 | IS-JB-608 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0685 | C4 | C4S5 | 19 | PLC_Tag | Spare_AI_0 | PT-60220_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0686 | C4 | C4S5 | 19 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0687 | C4 | C4S5 | 20 | Destination_Area | IS-JB-603 | IS-JB-608 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0688 | C4 | C4S5 | 20 | PLC_Tag | Spare_AI_0 | PT-60220_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0689 | C4 | C4S5 | 20 | Channel_Status | SPARE | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0690 | C4 | C4S5 | 21 | PLC_Tag | PT-60220_AI_1 | TT-60220_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0691 | C4 | C4S5 | 22 | PLC_Tag | PT-60220_AI_1 | TT-60220_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0692 | C4 | C4S5 | 23 | PLC_Tag | TT-60220_AI_1 | TT-60221_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0693 | C4 | C4S5 | 24 | PLC_Tag | TT-60220_AI_1 | TT-60221_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0694 | C4 | C4S5 | 25 | PLC_Tag | TT-60221_AI_1 | TT-60222_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0695 | C4 | C4S5 | 26 | PLC_Tag | TT-60221_AI_1 | TT-60222_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0696 | C4 | C4S5 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0697 | C4 | C4S5 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0698 | C4 | C4S5 | 29 | PLC_Tag | TT-60222_AI_1 | TT-60223_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0699 | C4 | C4S5 | 30 | PLC_Tag | TT-60222_AI_1 | TT-60223_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0700 | C4 | C4S5 | 31 | Destination_Area | IS-JB-603 | IS-JB-608 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0701 | C4 | C4S5 | 31 | PLC_Tag | Internal Power Common | XT-60201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0702 | C4 | C4S5 | 31 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0703 | C4 | C4S5 | 32 | Destination_Area | IS-JB-603 | IS-JB-608 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0704 | C4 | C4S5 | 32 | PLC_Tag | Internal Power Common | XT-60201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0705 | C4 | C4S5 | 32 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0706 | C4 | C4S6 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0707 | C4 | C4S6 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0708 | C4 | C4S6 | 11 | Destination_Area | IS-JB-612 | IS-JB-618 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0709 | C4 | C4S6 | 11 | PLC_Tag | Internal Power Common | DPT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0710 | C4 | C4S6 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0711 | C4 | C4S6 | 12 | Destination_Area | IS-JB-612 | IS-JB-618 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0712 | C4 | C4S6 | 12 | PLC_Tag | Internal Power Common | DPT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0713 | C4 | C4S6 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0714 | C4 | C4S6 | 13 | PLC_Tag | DPT-61301_AI_1 | DPT-61302_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0715 | C4 | C4S6 | 14 | PLC_Tag | DPT-61301_AI_1 | DPT-61302_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0716 | C4 | C4S6 | 15 | PLC_Tag | DPT-61302_AI_1 | LT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0717 | C4 | C4S6 | 16 | PLC_Tag | DPT-61302_AI_1 | LT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0718 | C4 | C4S6 | 17 | PLC_Tag | LT-61301_AI_1 | PT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0719 | C4 | C4S6 | 18 | PLC_Tag | LT-61301_AI_1 | PT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0720 | C4 | C4S6 | 19 | PLC_Tag | PT-61301_AI_1 | PT-61303_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0721 | C4 | C4S6 | 20 | PLC_Tag | PT-61301_AI_1 | PT-61303_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0722 | C4 | C4S6 | 21 | PLC_Tag | PT-61303_AI_1 | PT-61304_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0723 | C4 | C4S6 | 22 | PLC_Tag | PT-61303_AI_1 | PT-61304_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0724 | C4 | C4S6 | 23 | PLC_Tag | PT-61304_AI_1 | PT-61305_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0725 | C4 | C4S6 | 24 | PLC_Tag | PT-61304_AI_1 | PT-61305_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0726 | C4 | C4S6 | 25 | PLC_Tag | PT-61305_AI_1 | TT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0727 | C4 | C4S6 | 26 | PLC_Tag | PT-61305_AI_1 | TT-61301_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0728 | C4 | C4S6 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0729 | C4 | C4S6 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0730 | C4 | C4S6 | 29 | PLC_Tag | TT-61301_AI_1 | TT-61302_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0731 | C4 | C4S6 | 30 | PLC_Tag | TT-61301_AI_1 | TT-61302_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0732 | C4 | C4S6 | 31 | Destination_Area | IS-JB-612 | IS-JB-618 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0733 | C4 | C4S6 | 31 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0734 | C4 | C4S6 | 31 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0735 | C4 | C4S6 | 31 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0736 | C4 | C4S6 | 32 | Destination_Area | IS-JB-612 | IS-JB-618 | MEDIUM | Align Excel Destination_Area with DWG
CONF-0737 | C4 | C4S6 | 32 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0738 | C4 | C4S6 | 32 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0739 | C4 | C4S6 | 32 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0740 | C4 | C4S7 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0741 | C4 | C4S7 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0742 | C4 | C4S8 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0743 | C4 | C4S8 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0744 | C4 | C4S9 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0745 | C4 | C4S9 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0746 | C4 | C4S10 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0747 | C4 | C4S10 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0748 | C4 | C4S11 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0749 | C4 | C4S11 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0750 | C4 | C4S12 | - | Terminal Row | Missing in DWG | Terminal - | HIGH | Add Terminal to DWG Schematic
CONF-0751 | C4 | C4S12 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0752 | C5 | C5S0 | I/O List | Terminal Row | Terminal I/O List | Missing in Ref Excel | HIGH | Update Excel to include Terminal
CONF-0753 | C5 | C5S0 | RJ45-1 | Terminal Row | Missing in DWG | Terminal RJ45-1 | HIGH | Add Terminal to DWG Schematic
CONF-0754 | C5 | C5S1 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0755 | C5 | C5S1 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0756 | C5 | C5S1 | 19 | PLC_Tag | Internal Power Common | XA-80305C_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0757 | C5 | C5S1 | 19 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0758 | C5 | C5S1 | 20 | PLC_Tag | Internal Power Common | XA-80305D_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0759 | C5 | C5S1 | 20 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0760 | C5 | C5S1 | 21 | PLC_Tag | XA-80305C_DI_1 | XA-80305E_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0761 | C5 | C5S1 | 22 | PLC_Tag | XA-80305D_DI_1 | XA-80305F_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0762 | C5 | C5S1 | 23 | PLC_Tag | XA-80305E_DI_1 | XA-80306A_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0763 | C5 | C5S1 | 24 | PLC_Tag | XA-80305F_DI_1 | XA-80306B_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0764 | C5 | C5S1 | 25 | PLC_Tag | XA-80306A_DI_1 | XA-80306C_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0765 | C5 | C5S1 | 26 | PLC_Tag | XA-80306B_DI_1 | XA-80306D_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0766 | C5 | C5S1 | 27 | PLC_Tag | XA-80306C_DI_1 | XA-80306E_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0767 | C5 | C5S1 | 28 | PLC_Tag | XA-80306D_DI_1 | XA-80306F_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0768 | C5 | C5S1 | 29 | PLC_Tag | XA-80306E_DI_1 | XV-20201_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0769 | C5 | C5S1 | 30 | PLC_Tag | XA-80306F_DI_1 | XV-20201_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0770 | C5 | C5S1 | 31 | PLC_Tag | XV-20201_DI_1 | XV-20202_DI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0771 | C5 | C5S1 | 32 | PLC_Tag | XV-20201_DI_2 | XV-20202_DI_2 | HIGH | Align Excel PLC_Tag with DWG
CONF-0772 | C5 | C5S2 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0773 | C5 | C5S2 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0774 | C5 | C5S2 | 19 | PLC_Tag | Internal Power Common | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0775 | C5 | C5S2 | 19 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0776 | C5 | C5S2 | 19 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0777 | C5 | C5S2 | 20 | PLC_Tag | Internal Power Common | Spare_DI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0778 | C5 | C5S2 | 20 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0779 | C5 | C5S2 | 20 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0780 | C5 | C5S3 | 17 | Terminal Row | Missing in DWG | Terminal 17 | HIGH | Add Terminal to DWG Schematic
CONF-0781 | C5 | C5S3 | 18 | Terminal Row | Missing in DWG | Terminal 18 | HIGH | Add Terminal to DWG Schematic
CONF-0782 | C5 | C5S3 | 19 | PLC_Tag | Spare_DO_17 | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0783 | C5 | C5S3 | 20 | PLC_Tag | Internal Power Common | Spare_DO_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0784 | C5 | C5S3 | 20 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0785 | C5 | C5S3 | 20 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0786 | C5 | C5S4 | 9 | Terminal Row | Missing in DWG | Terminal 9 | HIGH | Add Terminal to DWG Schematic
CONF-0787 | C5 | C5S4 | 10 | Terminal Row | Missing in DWG | Terminal 10 | HIGH | Add Terminal to DWG Schematic
CONF-0788 | C5 | C5S4 | 11 | PLC_Tag | Internal Power Common | FT-936202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0789 | C5 | C5S4 | 11 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0790 | C5 | C5S4 | 12 | PLC_Tag | Internal Power Common | FT-936202_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0791 | C5 | C5S4 | 12 | Channel_Status | COMMON | ACTIVE | HIGH | Align Excel Channel_Status with DWG
CONF-0792 | C5 | C5S4 | 13 | PLC_Tag | FT-936202_AI_1 | LT-913201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0793 | C5 | C5S4 | 14 | PLC_Tag | FT-936202_AI_1 | LT-913201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0794 | C5 | C5S4 | 15 | PLC_Tag | LT-913201_AI_1 | PT-913201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0795 | C5 | C5S4 | 16 | PLC_Tag | LT-913201_AI_1 | PT-913201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0796 | C5 | C5S4 | 17 | PLC_Tag | PT-913201_AI_1 | XT-92201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0797 | C5 | C5S4 | 18 | PLC_Tag | PT-913201_AI_1 | XT-92201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0798 | C5 | C5S4 | 19 | PLC_Tag | XT-92201_AI_1 | XV-913201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0799 | C5 | C5S4 | 20 | PLC_Tag | XT-92201_AI_1 | XV-913201_AI_1 | HIGH | Align Excel PLC_Tag with DWG
CONF-0800 | C5 | C5S4 | 21 | PLC_Tag | XV-913201_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0801 | C5 | C5S4 | 21 | Instrument_Tag | XV-913201 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0802 | C5 | C5S4 | 21 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0803 | C5 | C5S4 | 22 | PLC_Tag | XV-913201_AI_1 | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0804 | C5 | C5S4 | 22 | Instrument_Tag | XV-913201 | Spare | HIGH | Align Excel Instrument_Tag with DWG
CONF-0805 | C5 | C5S4 | 22 | Channel_Status | ACTIVE | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0806 | C5 | C5S4 | 27 | Terminal Row | Missing in DWG | Terminal 27 | HIGH | Add Terminal to DWG Schematic
CONF-0807 | C5 | C5S4 | 28 | Terminal Row | Missing in DWG | Terminal 28 | HIGH | Add Terminal to DWG Schematic
CONF-0808 | C5 | C5S4 | 31 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0809 | C5 | C5S4 | 31 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0810 | C5 | C5S4 | 31 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG
CONF-0811 | C5 | C5S4 | 32 | PLC_Tag | Internal Power Common | Spare_AI_0 | HIGH | Align Excel PLC_Tag with DWG
CONF-0812 | C5 | C5S4 | 32 | Instrument_Tag |  | Spare | HIGH | Verify DWG Instrument_Tag
CONF-0813 | C5 | C5S4 | 32 | Channel_Status | COMMON | SPARE | HIGH | Align Excel Channel_Status with DWG