## Slide 1
INGREDION (THAILAND) CO., LTD. - KALASIN PLANT
PROJECT JET COOKER
Interconnection Cable Schedule
Complete Multi-Core & Trunk Routing Between MCC / CA1 Suite and Field Junction Boxes
Document No: CA1-SCH-CBL-001 | Revision: 3.6 | Date: September 2026 Engineering Contractor: AEC Industrial Engineering Co., Ltd.

## Slide 2
SYSTEM ARCHITECTURE
Overall Cable Routing & Signal Segregation Architecture
Physical pathways from MCC Room to Infeed, Jet Cooker, Spray Dryer, Packing Tower, and Slurry Building
Project Jet Cooker | Ingredion (Thailand) Co., Ltd. | AEC Industrial Engineering | Slide 2 of 8
Substation to Process Spine (TR-01)
Main heavy-duty hot-dip galvanized ladder tray (600x100mm) running from MCC room basement trench across overhead pipe rack.
Spray Dryer Riser Shaft (TR-SD)
Vertical cable riser traversing 1st to 8th floors. Segregated trays for Non-IS Control, Analog Shielded, and Ex-i Intrinsically Safe.
Packing Tower Riser (TR-PT)
Heavy-duty ladder tray for 2nd and 8th floor junction boxes. Blue-coated Ex-i dedicated cable tray with 300mm air gap separation.
Slurry Building Fiber Trunk (TR-EXT)
Overhead pipe rack route to remote building housing RIO-200. 6-core steel wire armoured fiber optic DLR ring backbone.
ENGINEERING SEGREGATION & INSTALLATION RULES (IEC 60079-14 & IEEE 518)
1. Intrinsically Safe (Ex-i) Cables: Distinctive BLUE outer sheath (RAL 5015). Maintain >= 300 mm clearance or solid grounded divider from power/control. 2. Shield Grounding: All overall and individual pair screens grounded at MCC Cabinet single-point clean earth bar ONLY. Field ends insulated and floating. 3. Spare Capacity: All multicore control cables sized with 20% to 35% installed spare conductors for future process expansion. 4. Cable Glands: Nickel-plated brass double-compression EMC cable glands (IP66) on standard JBs; Ex-e/Ex-i certified blue-ring glands on Ex-i JBs.

## Slide 3
INTERCONNECTION SCHEDULE
Panel M1 Interconnection Cable Schedule
Master Controller Bay (=CA1+MCP-M1) serving Infeed (JB-401), Spray Dryer 1F (JB-601), and Slurry (RIO-200)
Project Jet Cooker | Ingredion (Thailand) Co., Ltd. | AEC Industrial Engineering | Slide 3 of 8
Cable Tag | From | To (JB) | Location | Signal Function | Cable Specification | Tray | Len (m)
CBL-M1-JB401-01 | Panel M1 | JB-401 | Infeed 2nd Flr | Digital Inputs (DI) | CVV-S 48C x 1.5 mm2 | TR-IN-01 | 55m
CBL-M1-JB401-02 | Panel M1 | JB-401 | Infeed 2nd Flr | DI Extension & Spares | CVV-S 30C x 1.5 mm2 | TR-IN-01 | 55m
CBL-M1-JB401-03 | Panel M1 | JB-401 | Infeed 2nd Flr | Digital Outputs (DO) | CVV-S 40C x 1.5 mm2 | TR-IN-01 | 55m
CBL-M1-JB401-04 | Panel M1 | JB-401 | Infeed 2nd Flr | Analog Inputs (AI) | IS/OS/PVC 16P x 1.0 mm2 | TR-IN-01 | 55m
CBL-M1-JB601-01 | Panel M1 | JB-601 | Spray Dryer 1st Flr | Digital Inputs (DI) | CVV-S 60C x 1.5 mm2 | TR-SD-01 | 70m
CBL-M1-JB601-02 | Panel M1 | JB-601 | Spray Dryer 1st Flr | Digital Outputs (DO) | CVV-S 24C x 1.5 mm2 | TR-SD-01 | 70m
CBL-M1-JB601-03 | Panel M1 | JB-601 | Spray Dryer 1st Flr | Analog Inputs (AI) | IS/OS/PVC 16P x 1.0 mm2 | TR-SD-01 | 70m
CBL-M1-RIO200-FO | Panel M1 | RIO-200 | Slurry Out Bldg 2F | Redundant DLR Ethernet | 6-Core Armoured SM Fiber (OS2) | TR-EXT-01 | 165m
CBL-M1-RIO200-PWR | Panel M1 | RIO-200 | Slurry Out Bldg 2F | 230VAC UPS Power | XLPE/SWA/PVC 3C x 4.0 mm2 | TR-EXT-01 | 165m

## Slide 4
INTERCONNECTION SCHEDULE
Panel M2 Interconnection Cable Schedule
High-Density I/O Bay (=CA1+MCP-M2) serving Jet Cooker (JB-402), Spray Dryer 3F (JB-602), and Spray Dryer 7F (JB-607)
Project Jet Cooker | Ingredion (Thailand) Co., Ltd. | AEC Industrial Engineering | Slide 4 of 8
Cable Tag | From | To (JB) | Location | Signal Function | Cable Specification | Tray | Len (m)
CBL-M2-JB402-01 | Panel M2 | JB-402 | Jet Cooker 2nd Flr | Digital Inputs (DI) | CVV-S 40C x 1.5 mm2 | TR-JC-01 | 45m
CBL-M2-JB402-02 | Panel M2 | JB-402 | Jet Cooker 2nd Flr | Digital Outputs (DO) | CVV-S 24C x 1.5 mm2 | TR-JC-01 | 45m
CBL-M2-JB402-03 | Panel M2 | JB-402 | Jet Cooker 2nd Flr | Analog Inputs & AO | IS/OS/PVC 20P x 1.0 mm2 | TR-JC-01 | 45m
CBL-M2-JB602-01 | Panel M2 | JB-602 | Spray Dryer 3rd Flr | Digital Inputs (DI) | CVV-S 40C x 1.5 mm2 | TR-SD-02 | 85m
CBL-M2-JB602-02 | Panel M2 | JB-602 | Spray Dryer 3rd Flr | Digital Outputs (DO) | CVV-S 24C x 1.5 mm2 | TR-SD-02 | 85m
CBL-M2-JB602-03 | Panel M2 | JB-602 | Spray Dryer 3rd Flr | Analog Inputs & AO | IS/OS/PVC 36P x 1.0 mm2 | TR-SD-02 | 85m
CBL-M2-JB607-01 | Panel M2 | JB-607 | Spray Dryer 7th Flr | Digital Inputs (DI) Pt 1 | CVV-S 60C x 1.5 mm2 | TR-SD-03 | 125m
CBL-M2-JB607-02 | Panel M2 | JB-607 | Spray Dryer 7th Flr | Digital Inputs (DI) Pt 2 | CVV-S 60C x 1.5 mm2 | TR-SD-03 | 125m
CBL-M2-JB607-03 | Panel M2 | JB-607 | Spray Dryer 7th Flr | Digital Outputs (DO) Pt 1 | CVV-S 48C x 1.5 mm2 | TR-SD-03 | 125m
CBL-M2-JB607-04 | Panel M2 | JB-607 | Spray Dryer 7th Flr | Digital Outputs (DO) Pt 2 | CVV-S 30C x 1.5 mm2 | TR-SD-03 | 125m
CBL-M2-JB607-05 | Panel M2 | JB-607 | Spray Dryer 7th Flr | Analog Inputs & AO | IS/OS/PVC 40P x 1.0 mm2 | TR-SD-03 | 125m

## Slide 5
INTERCONNECTION SCHEDULE
Panel M3 Intrinsically Safe (Ex-i) Cable Schedule
Ex-i Hazardous Area Bay 1 (=CA1+MCP-M3) with Pepperl+Fuchs Isolators serving IS-JB-603, IS-JB-618, and JB-618
Project Jet Cooker | Ingredion (Thailand) Co., Ltd. | AEC Industrial Engineering | Slide 5 of 8
Cable Tag | From | To (JB) | Location | Signal Function | Cable Specification | Tray | Len (m)
CBL-M3-ISJB603-01 | Panel M3 | IS-JB-603 | Spray Dryer 3rd Flr | Ex-i Digital Inputs (DI) | CVV-S (IS) 24C x 1.5 mm2 [BLUE] | TR-SD-IS | 85m
CBL-M3-ISJB603-02 | Panel M3 | IS-JB-603 | Spray Dryer 3rd Flr | Ex-i Analog Inputs (AI) | IS/OS/PVC (IS) 16P x 1.0 mm2 [BLUE] | TR-SD-IS | 85m
CBL-M3-ISJB618-01 | Panel M3 | IS-JB-618 | Packing Tower 8th Flr | Ex-i Digital Inputs (DI) | CVV-S (IS) 40C x 1.5 mm2 [BLUE] | TR-PT-IS | 140m
CBL-M3-ISJB618-02 | Panel M3 | IS-JB-618 | Packing Tower 8th Flr | Ex-i Analog Inputs (AI) | IS/OS/PVC (IS) 16P x 1.0 mm2 [BLUE] | TR-PT-IS | 140m
CBL-M3-JB618-01 | Panel M3 | JB-618 | Packing Tower 8th Flr | Non-IS DI & AI | CVV-S 24C x 1.5 mm2 | TR-PT-01 | 140m
CBL-M3-JB618-02 | Panel M3 | JB-618 | Packing Tower 8th Flr | Non-IS Digital Outputs | CVV-S 40C x 1.5 mm2 | TR-PT-01 | 140m

## Slide 6
INTERCONNECTION SCHEDULE
Panel M4 Intrinsically Safe (Ex-i) Cable Schedule
Ex-i Hazardous Area Bay 2 (=CA1+MCP-M4) serving IS-JB-608, IS-JB-612, JB-606, JB-608, and JB-612
Project Jet Cooker | Ingredion (Thailand) Co., Ltd. | AEC Industrial Engineering | Slide 6 of 8
Cable Tag | From | To (JB) | Location | Signal Function | Cable Specification | Tray | Len (m)
CBL-M4-ISJB608-01 | Panel M4 | IS-JB-608 | Spray Dryer 8th Flr | Ex-i DI & DO Signals | CVV-S (IS) 30C x 1.5 mm2 [BLUE] | TR-SD-IS | 135m
CBL-M4-ISJB608-02 | Panel M4 | IS-JB-608 | Spray Dryer 8th Flr | Ex-i Analog Inputs (AI) | IS/OS/PVC (IS) 10P x 1.0 mm2 [BLUE] | TR-SD-IS | 135m
CBL-M4-ISJB612-01 | Panel M4 | IS-JB-612 | Packing Tower 2nd Flr | Ex-i Digital Inputs (DI) | CVV-S (IS) 40C x 1.5 mm2 [BLUE] | TR-PT-IS | 65m
CBL-M4-ISJB612-02 | Panel M4 | IS-JB-612 | Packing Tower 2nd Flr | Ex-i Analog Inputs (AI) | IS/OS/PVC (IS) 12P x 1.0 mm2 [BLUE] | TR-PT-IS | 65m
CBL-M4-JB606-01 | Panel M4 | JB-606 | Spray Dryer 6th Flr | Non-IS DI, DO & AI | CVV-S 30C x 1.5 mm2 | TR-SD-02 | 115m
CBL-M4-JB608-01 | Panel M4 | JB-608 | Spray Dryer 8th Flr | Non-IS Analog Inputs | IS/OS/PVC 8P x 1.0 mm2 | TR-SD-03 | 135m
CBL-M4-JB612-01 | Panel M4 | JB-612 | Packing Tower 2nd Flr | Non-IS Digital Inputs | CVV-S 40C x 1.5 mm2 | TR-PT-01 | 65m
CBL-M4-JB612-02 | Panel M4 | JB-612 | Packing Tower 2nd Flr | Non-IS DO & AI | CVV-S 24C x 1.5 + 10P x 1.0 | TR-PT-01 | 65m

## Slide 7
INTERCONNECTION SCHEDULE
MCC Switchgear & Remote I/O Trunk Schedule
Hardwired control interlocks to Motor Control Center switchgear and Armoured Fiber link to RIO-200
Project Jet Cooker | Ingredion (Thailand) Co., Ltd. | AEC Industrial Engineering | Slide 7 of 8
Cable Tag | From | To (JB) | Location | Signal Function | Cable Specification | Tray | Len (m)
CBL-M1-RIO200-FO | Panel M1 | RIO-200 | Slurry Out Bldg 2F | Redundant DLR Ethernet | 6-Core Armoured SM Fiber (OS2) | TR-EXT-01 | 165m
CBL-M1-RIO200-PWR | Panel M1 | RIO-200 | Slurry Out Bldg 2F | 230VAC UPS Power | XLPE/SWA/PVC 3C x 4.0 mm2 | TR-EXT-01 | 165m
CBL-M1-MCC-01 | Panel M1 | MCC Lineup | MCC Room | Motor Feedback Signals | 2x CVV-S 48C + 36C x 1.5 mm2 | TR-MCC-01 | 25m
CBL-M1-MCC-02 | Panel M1 | MCC Lineup | MCC Room | Motor Command Signals | 2x CVV-S 48C + 24C x 1.5 mm2 | TR-MCC-01 | 25m
CBL-M1-MCC-NET | Panel M1 | MCC Lineup | MCC Room | Smart Overloads (E300) | Armoured Industrial Cat6A DLR | TR-MCC-01 | 30m

## Slide 8
PROCUREMENT SCHEDULE
Master Cable Bill of Quantities (BOQ) & Drum Schedule
Consolidated procurement quantities with 10% installation slack and drum packaging
Project Jet Cooker | Ingredion (Thailand) Co., Ltd. | AEC Industrial Engineering | Slide 8 of 8
Item No. | Cable Specification & Rating | Signal Category | No. of Runs | Total Length (m) | Drum Packaging
CBL-01 | CVV-S 48C x 1.5 mm2 | Control | 2 | 198 m | 1x 198m Drum
CBL-02 | CVV-S 30C x 1.5 mm2 | Control | 3 | 324 m | 1x 324m Drum
CBL-03 | CVV-S 40C x 1.5 mm2 | Control | 5 | 429 m | 1x 429m Drum
CBL-04 | IS/OS/PVC 16P x 1.0 mm2 | Analog Shielded | 2 | 137 m | 1x 137m Drum
CBL-05 | CVV-S 60C x 1.5 mm2 | Control | 3 | 352 m | 1x 352m Drum
CBL-06 | CVV-S 24C x 1.5 mm2 | Control | 4 | 374 m | 1x 374m Drum
CBL-07 | 6-Core Armoured SM Fiber (OS2) | Fiber Optic | 1 | 181 m | 1x 181m Drum
CBL-08 | XLPE/SWA/PVC 3C x 4.0 mm2 | Power | 1 | 181 m | 1x 181m Drum
CBL-09 | IS/OS/PVC 20P x 1.0 mm2 | Analog Shielded | 1 | 49 m | 1x 49m Drum
CBL-10 | IS/OS/PVC 36P x 1.0 mm2 | Analog Shielded | 1 | 93 m | 1x 93m Drum
CBL-11 | IS/OS/PVC 40P x 1.0 mm2 | Analog Shielded | 1 | 137 m | 1x 137m Drum
CBL-12 | CVV-S (IS) 24C x 1.5 mm2 [BLUE] | Ex-i Intrinsically Safe | 1 | 93 m | 1x 93m Drum
CBL-13 | IS/OS/PVC (IS) 16P x 1.0 mm2 [BLUE] | Ex-i Intrinsically Safe | 2 | 247 m | 1x 247m Drum
CBL-14 | CVV-S (IS) 40C x 1.5 mm2 [BLUE] | Ex-i Intrinsically Safe | 2 | 225 m | 1x 225m Drum
CBL-15 | CVV-S (IS) 30C x 1.5 mm2 [BLUE] | Ex-i Intrinsically Safe | 1 | 148 m | 1x 148m Drum
CBL-16 | IS/OS/PVC (IS) 10P x 1.0 mm2 [BLUE] | Ex-i Intrinsically Safe | 1 | 148 m | 1x 148m Drum
CBL-17 | IS/OS/PVC (IS) 12P x 1.0 mm2 [BLUE] | Ex-i Intrinsically Safe | 1 | 71 m | 1x 71m Drum
CBL-18 | IS/OS/PVC 8P x 1.0 mm2 | Analog Shielded | 1 | 148 m | 1x 148m Drum
CBL-19 | CVV-S 24C x 1.5 + 10P x 1.0 | Control & Analog | 1 | 71 m | 1x 71m Drum
CBL-20 | 2x CVV-S 48C + 36C x 1.5 mm2 | Control | 1 | 27 m | 1x 27m Drum
CBL-21 | 2x CVV-S 48C + 24C x 1.5 mm2 | Control | 1 | 27 m | 1x 27m Drum
CBL-22 | Armoured Industrial Cat6A DLR | Industrial Ethernet | 1 | 33 m | 1x 33m Drum