## IS-JB-608_IO_List
KALASIN ENGINEERING — DESTINATION: IS-JB-608 (SPRAY DRYER 8TH FLOOR INTRINSICALLY SAFE JB)
Location: Spray Dryer 8F (Roof Atomizer Deck) ¦ Enclosure: 300 x 200 x 150 mm (Intrinsically Safe (Ex i Blue Terminals)) ¦ Total I/O: 32 (AI: 8 ¦ DI: 16 ¦ DO: 8) ¦ Active: 14, Spare: 18 (56.2%) | [16 empty] | ⬅ Return to Destination Index
DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE) | [6 empty] | SIGNAL SPECIFICATION |  |  | SOURCE SPECIFICATION (PLC RACK / CHASSIS / SLOT / CARD PIN / ePLAN WIRE TAG)
Dest Enclosure | Location / Area | Floor / Zone | Field Terminal Block | Term Pin | Instrument Tag | Instrument Description | I/O Type | Signal Spec | Point Status | Point Ref ID | Chassis | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag
IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S01-X2 | - | ZS-60201A |  | DI | 24VDC Dry Contact | ACTIVE | C4-S01-P16 | C4 | 1 | 16 | 17 | 1756-IB32 | ZS-60201A_DI_1 | Pin 17 | C4S1:17/C4S01-X2:17
IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S01-X2 | - | ZS-60201B |  | DI | 24VDC Dry Contact | ACTIVE | C4-S01-P17 | C4 | 1 | 17 | 18 | 1756-IB32 | ZS-60201B_DI_1 | Pin 18 | C4S1:18/C4S01-X2:18
IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231C |  | DI | 24VDC Dry Contact | ACTIVE | C4-S01-P18 | C4 | 1 | 18 | 19 | 1756-IB32 | ZS-60231C_DI_1 | Pin 19 | C4S1:19/C4S01-X2:19
IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231D |  | DI | 24VDC Dry Contact | ACTIVE | C4-S01-P19 | C4 | 1 | 19 | 20 | 1756-IB32 | ZS-60231D_DI_1 | Pin 20 | C4S1:20/C4S01-X2:20
IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231E |  | DI | 24VDC Dry Contact | ACTIVE | C4-S01-P20 | C4 | 1 | 20 | 21 | 1756-IB32 | ZS-60231E_DI_1 | Pin 21 | C4S1:21/C4S01-X2:21
IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231F |  | DI | 24VDC Dry Contact | ACTIVE | C4-S01-P21 | C4 | 1 | 21 | 22 | 1756-IB32 | ZS-60231F_DI_1 | Pin 22 | C4S1:22/C4S01-X2:22
IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S01-X2 | - | ZS-60240 |  | DI | 24VDC Dry Contact | ACTIVE | C4-S01-P22 | C4 | 1 | 22 | 23 | 1756-IB32 | ZS-60240_DI_1 | Pin 23 | C4S1:23/C4S01-X2:23
IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C4-S01-P23 | C4 | 1 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C4S1:24/C4S01-X2:24
IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C4-S01-P24 | C4 | 1 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C4S1:25/C4S01-X2:25
IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C4-S01-P25 | C4 | 1 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C4S1:26/C4S01-X2:26
IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C4-S01-P26 | C4 | 1 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C4S1:27/C4S01-X2:27
IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C4-S01-P27 | C4 | 1 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C4S1:28/C4S01-X2:28
IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C4-S01-P28 | C4 | 1 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C4S1:29/C4S01-X2:29
IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C4-S01-P29 | C4 | 1 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C4S1:30/C4S01-X2:30
IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C4-S01-P30 | C4 | 1 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C4S1:31/C4S01-X2:31
IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C4-S01-P31 | C4 | 1 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C4S1:32/C4S01-X2:32
IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S04-X1 | - | XA-60201 |  | DO | 24VDC Sourcing | ACTIVE | C4-S04-P08 | C4 | 4 | 8 | 9 | 1756-OB32 | XA-60201_DO_1 | Pin 9 | C4S4:9/C4S04-X1:9
IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C4-S04-P09 | C4 | 4 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C4S4:10/C4S04-X1:10
IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C4-S04-P10 | C4 | 4 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C4S4:11/C4S04-X1:11
IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C4-S04-P11 | C4 | 4 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C4S4:12/C4S04-X1:12
IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C4-S04-P12 | C4 | 4 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C4S4:13/C4S04-X1:13
IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C4-S04-P13 | C4 | 4 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C4S4:14/C4S04-X1:14
IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C4-S04-P14 | C4 | 4 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C4S4:15/C4S04-X1:15
IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C4-S04-P15 | C4 | 4 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C4S4:16/C4S04-X1:16
IS-JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | AI | 4-20mA HART | SPARE | C4-S05-P06 | C4 | 5 | 6 | 7 | 1756-IF16 | Spare_AI_0 | Pin 7 | C4S5:7/C4S05-X1:7
IS-JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | AI | 4-20mA HART | SPARE | C4-S05-P07 | C4 | 5 | 7 | 8 | 1756-IF16 | Spare_AI_0 | Pin 8 | C4S5:8/C4S05-X1:8
IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S06-X1 | - | PT-60220 | Pressure Transmitter | AI | 4-20mA HART | ACTIVE | C4-S06-P00 | C4 | 6 | 0 | 1 | 1756-IF16 | PT-60220_AI_1 | Pin 1 | C4S6:1/C4S06-X1:1
IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S06-X1 | - | TT-60220 |  | AI | 4-20mA HART | ACTIVE | C4-S06-P01 | C4 | 6 | 1 | 2 | 1756-IF16 | TT-60220_AI_1 | Pin 2 | C4S6:2/C4S06-X1:2
IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S06-X1 | - | TT-60221 |  | AI | 4-20mA HART | ACTIVE | C4-S06-P02 | C4 | 6 | 2 | 3 | 1756-IF16 | TT-60221_AI_1 | Pin 3 | C4S6:3/C4S06-X1:3
IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S06-X1 | - | TT-60222 |  | AI | 4-20mA HART | ACTIVE | C4-S06-P03 | C4 | 6 | 3 | 4 | 1756-IF16 | TT-60222_AI_1 | Pin 4 | C4S6:4/C4S06-X1:4
IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S06-X1 | - | TT-60223 |  | AI | 4-20mA HART | ACTIVE | C4-S06-P04 | C4 | 6 | 4 | 5 | 1756-IF16 | TT-60223_AI_1 | Pin 5 | C4S6:5/C4S06-X1:5
IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S06-X1 | - | XT-60201 |  | AI | 4-20mA HART | ACTIVE | C4-S06-P05 | C4 | 6 | 5 | 6 | 1756-IF16 | XT-60201_AI_1 | Pin 6 | C4S6:6/C4S06-X1:6