## JB-602_IO_List
KALASIN ENGINEERING — DESTINATION: JB-602 (SPRAY DRYER 3RD FLOOR JUNCTION BOX)
Location: Spray Dryer Floor 3F ¦ Enclosure: 800 x 600 x 250 mm (Standard Industrial (IP66 / SS304)) ¦ Total I/O: 82 (AI: 32 ¦ AO: 2 ¦ DI: 32 ¦ DO: 16) ¦ Active: 57, Spare: 25 (30.5%) | [16 empty] | ⬅ Return to Destination Index
DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE) | [6 empty] | SIGNAL SPECIFICATION |  |  | SOURCE SPECIFICATION (PLC RACK / CHASSIS / SLOT / CARD PIN / ePLAN WIRE TAG)
Dest Enclosure | Location / Area | Floor / Zone | Field Terminal Block | Term Pin | Instrument Tag | Instrument Description | I/O Type | Signal Spec | Point Status | Point Ref ID | Chassis | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X1 | - | FT-60202 |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P00 | C2 | 2 | 0 | 1 | 1756-IB32 | FT-60202_DI_1 | Pin 1 | C2S2:1/TBDI2:1A
JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | LSH-60251 |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P01 | C2 | 2 | 1 | 2 | 1756-IB32 | LSH-60251_DI_1 | Pin 2 | C2S2:2/TBDI2:2A
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X1 | - | PSL-60220 |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P02 | C2 | 2 | 2 | 3 | 1756-IB32 | PSL-60220_DI_1 | Pin 3 | C2S2:3/TBDI2:3A
JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | TSH-60230 |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P03 | C2 | 2 | 3 | 4 | 1756-IB32 | TSH-60230_DI_1 | Pin 4 | C2S2:4/TBDI2:4A
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X1 | - | TSH-60240 |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P04 | C2 | 2 | 4 | 5 | 1756-IB32 | TSH-60240_DI_1 | Pin 5 | C2S2:5/TBDI2:5A
JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSH-60241A |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P05 | C2 | 2 | 5 | 6 | 1756-IB32 | TSH-60241A_DI_1 | Pin 6 | C2S2:6/TBDI2:6A
JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | TSH-60242A |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P06 | C2 | 2 | 6 | 7 | 1756-IB32 | TSH-60242A_DI_1 | Pin 7 | C2S2:7/TBDI2:7A
JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSH-60243A |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P07 | C2 | 2 | 7 | 8 | 1756-IB32 | TSH-60243A_DI_1 | Pin 8 | C2S2:8/TBDI2:8A
JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSL-60241B |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P08 | C2 | 2 | 8 | 9 | 1756-IB32 | TSL-60241B_DI_1 | Pin 9 | C2S2:9/TBDI2:9A
JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | TSL-60242B |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P09 | C2 | 2 | 9 | 10 | 1756-IB32 | TSL-60242B_DI_1 | Pin 10 | C2S2:10/TBDI2:10A
JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSL-60243B |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P10 | C2 | 2 | 10 | 11 | 1756-IB32 | TSL-60243B_DI_1 | Pin 11 | C2S2:11/TBDI2:11A
JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60240A |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P11 | C2 | 2 | 11 | 12 | 1756-IB32 | XA-60240A_DI_1 | Pin 12 | C2S2:12/TBDI2:12A
JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60240B |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P12 | C2 | 2 | 12 | 13 | 1756-IB32 | XA-60240B_DI_1 | Pin 13 | C2S2:13/TBDI2:13A
JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60241A |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P13 | C2 | 2 | 13 | 14 | 1756-IB32 | XA-60241A_DI_1 | Pin 14 | C2S2:14/TBDI2:14A
JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60241B |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P14 | C2 | 2 | 14 | 15 | 1756-IB32 | XA-60241B_DI_1 | Pin 15 | C2S2:15/TBDI2:15A
JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | XA-60242A |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P15 | C2 | 2 | 15 | 16 | 1756-IB32 | XA-60242A_DI_1 | Pin 16 | C2S2:16/TBDI2:16A
JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X2 | - | XA-60242B |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P16 | C2 | 2 | 16 | 17 | 1756-IB32 | XA-60242B_DI_1 | Pin 17 | C2S2:17/C2S02-X2:17
JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X2 | - | XA-60243A |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P17 | C2 | 2 | 17 | 18 | 1756-IB32 | XA-60243A_DI_1 | Pin 18 | C2S2:18/C2S02-X2:18
JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X2 | - | XA-60243B |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P18 | C2 | 2 | 18 | 19 | 1756-IB32 | XA-60243B_DI_1 | Pin 19 | C2S2:19/TBDI2:17A
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60214 |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P19 | C2 | 2 | 19 | 20 | 1756-IB32 | XV-60214_DI_1 | Pin 20 | C2S2:20/TBDI2:18A
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60214 |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P20 | C2 | 2 | 20 | 21 | 1756-IB32 | XV-60214_DI_2 | Pin 21 | C2S2:21/TBDI2:19A
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60241 |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P21 | C2 | 2 | 21 | 22 | 1756-IB32 | XV-60241_DI_1 | Pin 22 | C2S2:22/TBDI2:20A
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60241 |  | DI | 24VDC Dry Contact | ACTIVE | C2-S02-P22 | C2 | 2 | 22 | 23 | 1756-IB32 | XV-60241_DI_2 | Pin 23 | C2S2:23/TBDI2:21A
JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C2-S02-P23 | C2 | 2 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C2S2:24/TBDI2:22A
JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C2-S02-P24 | C2 | 2 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C2S2:25/TBDI2:23A
JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C2-S02-P25 | C2 | 2 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C2S2:26/TBDI2:24A
JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C2-S02-P26 | C2 | 2 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C2S2:27/TBDI2:25A
JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C2-S02-P27 | C2 | 2 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C2S2:28/TBDI2:26A
JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C2-S02-P28 | C2 | 2 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C2S2:29/TBDI2:27A
JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C2-S02-P29 | C2 | 2 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C2S2:30/TBDI2:28A
JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C2-S02-P30 | C2 | 2 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C2S2:31/TBDI2:29A
JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | DI | 24VDC Dry Contact | SPARE | C2-S02-P31 | C2 | 2 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C2S2:32/TBDI2:30A
JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S06-X2 | - | XS-60240B |  | DO | 24VDC Sourcing | ACTIVE | C2-S06-P16 | C2 | 6 | 16 | 17 | 1756-OB32 | XS-60240B_DO_1 | Pin 17 | C2S6:17/C2S06-X2:17
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S06-X2 | - | XV-60214 |  | DO | 24VDC Sourcing | ACTIVE | C2-S06-P17 | C2 | 6 | 17 | 18 | 1756-OB32 | XV-60214_DO_1 | Pin 18 | C2S6:18/C2S06-X2:18
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S06-X2 | - | XV-60241 |  | DO | 24VDC Sourcing | ACTIVE | C2-S06-P18 | C2 | 6 | 18 | 19 | 1756-OB32 | XV-60241_DO_1 | Pin 19 | C2S6:19/RL.49:A1
JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C2-S06-P19 | C2 | 6 | 19 | 20 | 1756-OB32 | Spare_DO_0 | Pin 20 | C2S6:20/RL.50:A1
JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C2-S06-P20 | C2 | 6 | 20 | 21 | 1756-OB32 | Spare_DO_0 | Pin 21 | C2S6:21/RL.51:A1
JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C2-S06-P21 | C2 | 6 | 21 | 22 | 1756-OB32 | Spare_DO_0 | Pin 22 | C2S6:22/RL.52:A1
JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C2-S06-P22 | C2 | 6 | 22 | 23 | 1756-OB32 | Spare_DO_0 | Pin 23 | C2S6:23/RL.53:A1
JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C2-S06-P23 | C2 | 6 | 23 | 24 | 1756-OB32 | Spare_DO_0 | Pin 24 | C2S6:24/RL.54:A1
JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C2-S06-P24 | C2 | 6 | 24 | 25 | 1756-OB32 | Spare_DO_0 | Pin 25 | C2S6:25/RL.55:A1
JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C2-S06-P25 | C2 | 6 | 25 | 26 | 1756-OB32 | Spare_DO_0 | Pin 26 | C2S6:26/RL.56:A1
JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C2-S06-P26 | C2 | 6 | 26 | 27 | 1756-OB32 | Spare_DO_0 | Pin 27 | C2S6:27/RL.57:A1
JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C2-S06-P27 | C2 | 6 | 27 | 28 | 1756-OB32 | Spare_DO_0 | Pin 28 | C2S6:28/RL.58:A1
JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C2-S06-P28 | C2 | 6 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C2S6:29/RL.59:A1
JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C2-S06-P29 | C2 | 6 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C2S6:30/RL.60:A1
JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C2-S06-P30 | C2 | 6 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C2S6:31/RL.61:A1
JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | DO | 24VDC Sourcing | SPARE | C2-S06-P31 | C2 | 6 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C2S6:32/RL.62:A1
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | AT-60241 | Dust Analyzer Transmitter | AI | 4-20mA HART | ACTIVE | C2-S10-P00 | C2 | 10 | 0 | 1 | 1756-IF16 | AT-60241_AI_1 | Pin 1 | C2S10:1/C2S10-X1:1
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | DPT-60203 | Differential Pressure Transmitte | AI | 4-20mA HART | ACTIVE | C2-S10-P01 | C2 | 10 | 1 | 2 | 1756-IF16 | DPT-60203_AI_1 | Pin 2 | C2S10:2/C2S10-X1:2
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | FT-60202 |  | AI | 4-20mA HART | ACTIVE | C2-S10-P02 | C2 | 10 | 2 | 3 | 1756-IF16 | FT-60202_AI_1 | Pin 3 | C2S10:3/C2S10-X1:3
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60210 | Pressure Transmitter | AI | 4-20mA HART | ACTIVE | C2-S10-P03 | C2 | 10 | 3 | 4 | 1756-IF16 | PT-60210_AI_1 | Pin 4 | C2S10:4/C2S10-X1:4
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60215 | Pressure Transmitter | AI | 4-20mA HART | ACTIVE | C2-S10-P04 | C2 | 10 | 4 | 5 | 1756-IF16 | PT-60215_AI_1 | Pin 5 | C2S10:5/C2S10-X1:5
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60216 | Pressure Transmitter | AI | 4-20mA HART | ACTIVE | C2-S10-P05 | C2 | 10 | 5 | 6 | 1756-IF16 | PT-60216_AI_1 | Pin 6 | C2S10:6/C2S10-X1:6
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60240 | Pressure Transmitter | AI | 4-20mA HART | ACTIVE | C2-S10-P06 | C2 | 10 | 6 | 7 | 1756-IF16 | PT-60240_AI_1 | Pin 7 | C2S10:7/C2S10-X1:7
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60241 | Pressure Transmitter | AI | 4-20mA HART | ACTIVE | C2-S10-P07 | C2 | 10 | 7 | 8 | 1756-IF16 | PT-60241_AI_1 | Pin 8 | C2S10:8/C2S10-X1:8
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60210 |  | AI | 4-20mA HART | ACTIVE | C2-S10-P08 | C2 | 10 | 8 | 9 | 1756-IF16 | TT-60210_AI_1 | Pin 9 | C2S10:9/C2S10-X1:9
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60210A |  | AI | 4-20mA HART | ACTIVE | C2-S10-P09 | C2 | 10 | 9 | 10 | 1756-IF16 | TT-60210A_AI_1 | Pin 10 | C2S10:10/C2S10-X1:10
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60210B |  | AI | 4-20mA HART | ACTIVE | C2-S10-P10 | C2 | 10 | 10 | 11 | 1756-IF16 | TT-60210B_AI_1 | Pin 11 | C2S10:11/C2S10-X1:11
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60211 |  | AI | 4-20mA HART | ACTIVE | C2-S10-P11 | C2 | 10 | 11 | 12 | 1756-IF16 | TT-60211_AI_1 | Pin 12 | C2S10:12/C2S10-X1:12
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60212A |  | AI | 4-20mA HART | ACTIVE | C2-S10-P12 | C2 | 10 | 12 | 13 | 1756-IF16 | TT-60212A_AI_1 | Pin 13 | C2S10:13/C2S10-X1:13
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60212B |  | AI | 4-20mA HART | ACTIVE | C2-S10-P13 | C2 | 10 | 13 | 14 | 1756-IF16 | TT-60212B_AI_1 | Pin 14 | C2S10:14/C2S10-X1:14
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60214 |  | AI | 4-20mA HART | ACTIVE | C2-S10-P14 | C2 | 10 | 14 | 15 | 1756-IF16 | TT-60214_AI_1 | Pin 15 | C2S10:15/C2S10-X1:15
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60215A |  | AI | 4-20mA HART | ACTIVE | C2-S10-P15 | C2 | 10 | 15 | 16 | 1756-IF16 | TT-60215A_AI_1 | Pin 16 | C2S10:16/C2S10-X1:16
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60215B |  | AI | 4-20mA HART | ACTIVE | C2-S11-P00 | C2 | 11 | 0 | 1 | 1756-IF16 | TT-60215B_AI_1 | Pin 1 | C2S11:1/C2S11-X1:1
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60216 |  | AI | 4-20mA HART | ACTIVE | C2-S11-P01 | C2 | 11 | 1 | 2 | 1756-IF16 | TT-60216_AI_1 | Pin 2 | C2S11:2/C2S11-X1:2
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60240 |  | AI | 4-20mA HART | ACTIVE | C2-S11-P02 | C2 | 11 | 2 | 3 | 1756-IF16 | TT-60240_AI_1 | Pin 3 | C2S11:3/C2S11-X1:3
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60241A |  | AI | 4-20mA HART | ACTIVE | C2-S11-P03 | C2 | 11 | 3 | 4 | 1756-IF16 | TT-60241A_AI_1 | Pin 4 | C2S11:4/C2S11-X1:4
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60241B |  | AI | 4-20mA HART | ACTIVE | C2-S11-P04 | C2 | 11 | 4 | 5 | 1756-IF16 | TT-60241B_AI_1 | Pin 5 | C2S11:5/C2S11-X1:5
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60210A |  | AI | 4-20mA HART | ACTIVE | C2-S11-P05 | C2 | 11 | 5 | 6 | 1756-IF16 | VT-60210A_AI_1 | Pin 6 | C2S11:6/C2S11-X1:6
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60210B |  | AI | 4-20mA HART | ACTIVE | C2-S11-P06 | C2 | 11 | 6 | 7 | 1756-IF16 | VT-60210B_AI_1 | Pin 7 | C2S11:7/C2S11-X1:7
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60241A |  | AI | 4-20mA HART | ACTIVE | C2-S11-P07 | C2 | 11 | 7 | 8 | 1756-IF16 | VT-60241A_AI_1 | Pin 8 | C2S11:8/C2S11-X1:8
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60241B |  | AI | 4-20mA HART | ACTIVE | C2-S11-P08 | C2 | 11 | 8 | 9 | 1756-IF16 | VT-60241B_AI_1 | Pin 9 | C2S11:9/C2S11-X1:9
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60210 |  | AI | 4-20mA HART | ACTIVE | C2-S11-P09 | C2 | 11 | 9 | 10 | 1756-IF16 | FT-60210_AI_1 | Pin 10 | C2S11:10/C2S11-X1:10
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60211 |  | AI | 4-20mA HART | ACTIVE | C2-S11-P10 | C2 | 11 | 10 | 11 | 1756-IF16 | FT-60211_AI_1 | Pin 11 | C2S11:11/C2S11-X1:11
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60210 |  | AI | 4-20mA HART | ACTIVE | C2-S11-P11 | C2 | 11 | 11 | 12 | 1756-IF16 | FT-60210_AI_2 | Pin 12 | C2S11:12/C2S11-X1:12
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60211 |  | AI | 4-20mA HART | ACTIVE | C2-S11-P12 | C2 | 11 | 12 | 13 | 1756-IF16 | FT-60211_AI_2 | Pin 13 | C2S11:13/C2S11-X1:13
JB-602 | Spray Dryer 3rd Floor | - | C2S11-X1 | - | Spare | Spare Channel | AI | 4-20mA HART | SPARE | C2-S11-P13 | C2 | 11 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C2S11:14/C2S11-X1:14
JB-602 | Spray Dryer 3rd Floor | - | C2S11-X1 | - | Spare | Spare Channel | AI | 4-20mA HART | SPARE | C2-S11-P14 | C2 | 11 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C2S11:15/C2S11-X1:15
JB-602 | Spray Dryer 3rd Floor | - | C2S11-X1 | - | Spare | Spare Channel | AI | 4-20mA HART | SPARE | C2-S11-P15 | C2 | 11 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C2S11:16/C2S11-X1:16
JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S13-X1 | - | TV-60202 |  | AO | 4-20mA HART | ACTIVE | C3-S13-P01 | C3 | 13 | 1 | 2 | 1756-OF8 | TV-60202_AO_1 | Pin 2 | C3S13:2/C3S13-X1:2
JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C3S13-X1 | - | TV-60214 |  | AO | 4-20mA HART | ACTIVE | C3-S13-P02 | C3 | 13 | 2 | 3 | 1756-OF8 | TV-60214_AO_1 | Pin 3 | C3S13:3/C3S13-X1:3