## Rev.3
[13 empty] | DATE |  | 13 AUG 2026 |  | REV.
[13 empty] | DOC.NO. |  | Instrument I/O List |  | 3.6
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Instruement Tag | Instruement Description | Tag | Tag_New | P&ID No. | Description | Instrument Name | Column1 | DO | DI | AO | AI | Bus | Signal type | Signal to | Range | Function | Cable Type | Type of Protection | Remark
| Dust Analyzer Transmitter | AT-60241 |  | 325-01-602-PD-05 | Dust Analyzer Transmitter for Exhaust Duct (DTEX-22) | Dust Analyzer Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 5000 mg | 0 - 100% | LiY-CY TP 2Px1.0 , CVV 3Cx1.5 | - | -
| Differential Pressure Transmitte | DPT-60901 | DPT-60201 | 325-01-602-PD-09 | Steam filter pressure | Differential Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0-1 barg | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
| Differential Pressure Transmitte | DPT-61301 |  | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 500 mBar./0 - 100% | LiY-CY TP 1P x1.0 | Ex t/d | Safety Barriers
| Differential Pressure Transmitte | DPT-61302 |  | 325-01-613-PD-01 | Vent filter pressure | Differential Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 500 mBar./0 - 100% | LiY-CY TP 1P x1.0 | Ex t/d | Safety Barriers
| Differential Pressure Transmitte | DPT-61310 |  | 325-01-613-PD-03 | Vent filter pressure | Differential Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 0-250 mbarg / 0 - 100% | LiY-CY TP 1P x1.0 | Ex t/d | Safety Barriers
| Differential Pressure Transmitte | DPT-60202 |  | 325-01-602-PD-08 | Gas Pressure Differential Transmitter for Air Filter (FICA-31) | Differential Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 500 mBar | 0 to1000 | LiY-CY TP 1P x1.0 | - | -
| Differential Pressure Transmitte | DPT-60203 |  | 325-01-602-PD-03 | Gas Pressure Differential Transmitter for Air Filter (FICA-21) | Differential Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 500 mBar | 0-100 mbarg / 0 - 100% | LiY-CY TP 1P x1.0 | - | -
| Flow Switch |  | FSL-20201 | 325-01-202-PD-01 | Slurry low flow | Flow Switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | n/a | CVV 4Cx1 | - | -
| Flow Switch |  | FSL-40201 | 325-01-402-PD-01 | Slurry low flow | Flow Switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | n/a | CVV 4Cx1 | - | -
| Flow Switch |  | FSL-40202 | 325-01-402-PD-01 | Slurry low flow | Flow Switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | n/a | CVV 4Cx1 | - | -
| Flow Switch |  | FS-40204 | 325-01-402-PD-01 | Jet Cooker | Flow Switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | n/a | CVV 4Cx1 | - | -
| Flow Switch |  | FS-40205 | 325-01-402-PD-02 | Jet Cooker | Flow Switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | n/a | CVV 4Cx1 | - | -
| Coriolis Flow Transmitter | FT-40201 |  | 325-01-402-PD-02 | Slurry flowrate & density check transfer line | Coriolis Flow Transmitter |  | - | 1 | - | 2 | - | 4 - 20 mA,Pulse | PLC | 0-15 m³/hr | Flow rate | LiY-CY TP 3Px1.0 , CVV 3Cx1.5 | - | -
| Magnetic Flow Transmitter | FT-40202 |  | 325-01-402-PD-02 | Feed Slurry Flow Transmitter for Pipe (PIPE) | Magnetic Flow Transmitter |  | - | 1 | - | 1 | - | 4 - 20 mA,Pulse | PLC | 0 to 8,000 m³/hr | 0 - 100% | LiY-CY TP 2Px1.0 , CVV 3Cx1.5 | - | -
| Coriolis Flow Transmitter |  | FT-40221 | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter |  | - | 1 | - | 2 | - | 4 - 20 mA,Pulse | PLC | 0-6 m³/hr | Flow rate | LiY-CY TP 3Px1.0 , CVV 3Cx1.5 | - | -
| Coriolis Flow Transmitter |  | FT-40222 | 325-01-402-PD-02 | Jet Cooker | Coriolis Flow Transmitter |  | - | 1 | - | 2 | - | 4 - 20 mA,Pulse | PLC | 0-850 kg/hr | Flow rate | LiY-CY TP 3Px1.0 , CVV 3Cx1.5 | - | -
|  | FT-60221 |  | 325-01-602-PD-04 | Cool air Flow | Thermal Mass Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 2500 m3/h | n/a | LiY-CY TP 1P x1.0 | - | -
|  | FT-60201 |  | 325-01-602-PD-08 | Gas Flow Transmitter for Cooling Conveying Cold Air Duct (DTCA-32) | Thermal Mass Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 70000 m3/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60210 |  | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21B) | Thermal Mass Flow Transmitter |  | - | - | - | 2 | - | 4 - 20 mA | PLC | 126000 m3/h | 0 - 100% | LiY-CY TP 2P x1.0 | - | -
|  | FT-60211 |  | 325-01-602-PD-03 | Gas Flow Element for Dryer Hot Air Duct (DTHA-21A) | Thermal Mass Flow Transmitter |  | - | - | - | 2 | - | 4 - 20 mA | PLC | 126000 m3/h | 0 - 100% | LiY-CY TP 2P x1.0 | - | -
|  | FT-60261FA |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #1 (AMTV-11A) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60261FB |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #2 (AMTV-11A) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60261FC |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #3 (AMTV-11A) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60261FD |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #4 (AMTV-11A) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60262FE |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #5 (AMTV-11B) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60262FF |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #6 (AMTV-11B) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60262FG |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #7 (AMTV-11B) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60262FH |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #8 (AMTV-11B) | Ultrasonic Flow Transmitter |  | - | - |  | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60263FJ |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #9 (AMTV-11C) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60263FK |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #10 (AMTV-11C) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60263FL |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #11 (AMTV-11C) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60263FM |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #12 (AMTV-11C) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60264FN |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #13 (AMTV-11D) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60264FP |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #14 (AMTV-11D) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60264FQ |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #15 (AMTV-11D) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60264FR |  | 325-01-602-PD-02 | Feed Slurry Flow Transmitter for Nozzle #16 (AMTV-11D) | Ultrasonic Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 to 100 l/h | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-61307 | FT-61307 | 325-01-613-PD-04 | Compressed air Flow | Thermal Mass Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 1000 m3/hr | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
|  | FT-60901 | FT-60203 | 325-01-602-PD-09 | Culinary steam feed to Spray dryer | Vortex Flow Transmitter |  | - | 1 | - | 1 | - | 4 - 20 mA | PLC | 0 - 7000 kg/hr | 0 - 100% | LiY-CY TP 2P x1.0 | - | -
|  | FT-60902 | FT-60202 | 325-01-602-PD-09 | Steam feed to Spray dryer | Vortex Flow Transmitter |  | - | 1 | - | 1 | - | 4 - 20 mA | PLC | 0 - 2000 kg/hr | 0 - 100% | LiY-CY TP 2P x1.0 | - | -
|  | FT-61101 | FT-60204 | 325-01-602-PD-10 | Compressed air Flow | Thermal Mass Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 1000 m3/hr | 0 - 100% | LiY-CY TP 2Px1.0 , CVV 3Cx1.5 | - | -
|  | FT-90301 | FT-936201 | 325-01-930-PD-01 | Process Water | Magnetic Flow Transmitter |  | - | 1 | - | 1 | - | 4 - 20 mA,Pulse | PLC | 0-1000kg/m³ | Flow rate | LiY-CY TP 2Px1.0 , CVV 3Cx1.5 | - | -
|  | FT-93001 | FT-936202 | 325-01-930-PD-02 | Process Water | Magnetic Flow Transmitter |  | - | 1 | - | 1 | - | 4 - 20 mA,Pulse | PLC | 0 - 20 m3/ hr | 0 - 100% | LiY-CY TP 2Px1.0 , CVV 3Cx1.5 | - | -
|  | HS-61307A |  | 325-01-613-PD-03 | Start/Stop | Hand Switch |  | - | 2 | - | - | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307B |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307C |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307D |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307E |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307F |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307G |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307H |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307I |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307J |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307K |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307L |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307M |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307N |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307O |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307P |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307Q |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
|  | HS-61307R |  | 325-01-613-PD-03 | Start/Stop | Hand Switch | [5 empty] | - | Dry Contact | PLC |  |  | CVV 4Cx1 | Ex d | -
| Manual Valve With Position Switch | HV-4106 | HV-40203 | 325-01-402-PD-01 | Slurry Drain tank TS-40201 | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
| Manual Valve With Position Switch | HV-4108 | HV-40201 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
| Manual Valve With Position Switch | HV-4126 | HV-40204 | 325-01-402-PD-01 | Slurry Drain tank TS-40202 | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
| Manual Valve With Position Switch | HV-4128 | HV-40202 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
| Manual Valve With Position Switch | HV-4208 | HV-40206 | 325-01-402-PD-01 | Slurry Drain tank TS-40203 | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
| Manual Valve With Position Switch | HV-4210 | HV-40205 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
| Manual Valve With Position Switch |  | HV-40207 | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
| Manual Valve With Position Switch |  | HV-40208 | 325-01-402-PD-01 | Jet Cooker | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
|  | LSH-60230 |  | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-21) | Level switch |  |  | 1 |  |  | - | Dry Contact | PLC |  | Detected " high" / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex t/d | Safety Barriers
|  | LSH-60231 |  | 325-01-602-PD-04 | Powder Level Switch High for Cyclone (CYCL-22) | Level switch |  |  | 1 |  |  | - | Dry Contact | PLC |  | Detected " high" / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex t/d | Safety Barriers
|  | LSH-60240 |  | 325-01-602-PD-05 | Powder Level Switch High for Bag House (BGHS-21) | Level switch |  |  | 1 |  |  | - | Dry Contact | PLC |  | Detected " high" / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex t/d | Safety Barriers
|  | LSH-60250 |  | 325-01-602-PD-05 | Water Level Switch High for Fire Deluge Pipe (FWDP-21) | Level switch |  |  | 1 |  |  | - | Dry Contact | PLC |  | Detected " high" / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | - | -
|  | LSH-60251 |  | 325-01-602-PD-04 | Water Level Switch High for Fire Deluge Pipe (FWDP-22) | Level switch |  |  | 1 |  |  | - | Dry Contact | PLC |  | Detected " high" / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | - | -
|  | LSL-61101 | LSL-60201 | 325-01-602-PD-11 | Level low switch | Level switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " Low " / Run dry protection | CVV 3Cx1.5 , CVV 4Cx1 | - | -
|  | LSH-61301 |  | 325-01-613-PD-01 | Level alarm high | Level switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " Full " / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex t/d | Safety Barriers
|  | LSL-61302 |  | 325-01-613-PD-01 | Level alarm low | Level switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " Low " / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex t/d | Safety Barriers
|  | LS-61303 |  | 325-01-613-PD-01 | Level switch | Level switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " high" / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex t/d | Safety Barriers
|  | LSH-61304 |  | 325-01-613-PD-03 | Big bag level alarm high | Level switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex t/d | Safety Barriers
|  | LSH-61305 |  | 325-01-613-PD-05 | Big bag level alarm high | Level switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex t/d | Safety Barriers
|  | LSH-61306 |  | 325-01-613-PD-01 | Level alarm high | Level switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex t/d | Safety Barriers
|  |  | LSH-61307 | 325-01-613-PD-01 | High Level alarm reject screen | Level switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex t/d | Safety Barriers
|  |  | LSH-61308 | 325-01-613-PD-01 | High Level alarm Cooling cyclone | Level switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex t/d | Safety Barriers
|  | LSH-61312 |  | 325-01-613-PD-05 | Level alarm high | Level switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | Nondetected " Empty " / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex t/d | Safety Barriers
|  | LSL-81001 | LSL-814201 | 325-01-814-PD-01 | Low Level alarm |  |  | - | 1 | - | - | - | Dry Contact | PLC |  | Detected " Low " / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex t/d | Safety Barriers
| Level Transmitter | LT-40101 | LT-40201 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 1 | Level transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 m. | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
| Level Transmitter | LT-40102 | LT-40202 | 325-01-402-PD-01 | Level transmitter in pH Adjustment tank 2 | Level transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 m. | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
| Level Transmitter | LT-40201 | LT-40203 | 325-01-402-PD-02 | Level transmitter in Spray dryer infeed tank | Level transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 m. | 0 - 100% | LiY-CY TP 1P x1.0 | - | -
| Level Transmitter | LT-61301 |  | 325-01-613-PD-01 | Level powder in silo | Level transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC |  | 0 - 100% | LiY-CY TP 1P x1.0 | Ex ia | Safety Barriers
| PH Transmitter | pHT-40101 | pHT-40201 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 1 | pH Analyzer |  | - | 1 | - | 1 | - | 4 - 20 mA | PLC | 0-14 | 0 - 100% | LiY-CY TP 2Px1.0 , CVV 3Cx1.5 | - | -
| PH Transmitter | pHT-40102 | pHT-40202 | 325-01-402-PD-01 | pH analyzer in pH Adjustment tank 2 | pH Analyzer |  | - | 1 | - | 1 | - | 4 - 20 mA | PLC | 0-14 | 0 - 100% | LiY-CY TP 2Px1.0 , CVV 3Cx1.5 | - | -
|  | PSL-60220 |  | 325-01-602-PD-04 | Gas Pressure Switch Low for Spray Chamber (CHAM-21) | Pressure switch |  |  | 1 |  |  | - | Dry Contact | Hard Wired to MCC FANE-21 | -0.01 mbar | 0 to (- 20,000) Pa | CVV 3Cx1.5 , CVV 4Cx1 | - | -
|  |  | PSL-61301 | 325-01-613-PD-01 | Pressure alarm low | Pressure switch |  | - | 1 | - | - | - | Dry Contact | PLC | 0.3-0.7barg | 1 barg / Under pressure | CVV 3Cx1.5 , CVV 4Cx1 | - | -
|  | PSL-61302 |  | 325-01-613-PD-01 | Pressure alarm low | Pressure switch |  | - | 1 | - | - | - | Dry Contact | PLC | 40 mbarg | 1 barg / Under pressure | CVV 3Cx1.5 , CVV 4Cx1 | - | -
|  | PSL-61305 |  | 325-01-613-PD-03 | Pressure alarm low | Pressure switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | 1 barg / Under pressure | CVV 3Cx1.5 , CVV 4Cx1 | - | -
|  | PSL-61306 |  | 325-01-613-PD-05 | Pressure alarm low | Pressure switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | 1 barg / Under pressure | CVV 3Cx1.5 , CVV 4Cx1 | - | -
|  | PSL-61311 |  | 325-01-613-PD-04 | Pressure alarm low | Pressure switch |  | - | 1 | - | - | - | Dry Contact | PLC |  | 1 barg / Under pressure | CVV 3Cx1.5 , CVV 4Cx1 | - | -
| Pressure Transmitter | PT-40201 |  | 325-01-402-PD-02 | Pressure Transmitter for Inlet Filter Strainer (FSTR-11) | Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 to 500 mBar | 0-250 mbarg / 0 - 100% | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter | PT-40202 |  | 325-01-402-PD-02 | Feed Slurry Pressure Transmitter for Pipe (PIPE) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 10'barg | 0 to 500 | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter |  | PT-40222 | 325-01-402-PD-02 | Jet Cooker | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 12'barg | 0 to 500 | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter | PT-60201 |  | 325-01-602-PD-02 | Steam feed to Spray dryer | Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 20 bar | Control Pressure | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter | PT-60202 |  | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 to 500 bar | 0-100% | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter | PT-60203 |  | 325-01-602-PD-08 | Gas Pressure Transmitter for Cool Air Duct (DTCA-32) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter | PT-60210 |  | 325-01-602-PD-03 | Gas Pressure Transmitter for Hot Air Duct (DTHA-21) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter | PT-60215 |  | 325-01-602-PD-03 | 15% Polypropylene Glycol Pressure Indicator Transmitter for Heat Recovery Pumping Skid (PUCF-21) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 6 bar | 0-100% | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter | PT-60216 |  | 325-01-602-PD-03 | Gas Pressure Transmitter for Combustion Air Burner Duct (DTCB-21) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 100 mbar | 0-100% | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter | PT-60220 |  | 325-01-602-PD-04 | Gas Pressure Transmitter for Chamber (CHAM-21) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | -100 - 100 mbar | 0-100% | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
| Pressure Transmitter | PT-60221 |  | 325-01-602-PD-04 | Gas Pressure Transmitter for Cooling Air Duct (DTCA-25) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter | PT-60230 |  | 325-01-602-PD-04 | Gas Pressure Transmitter for Conveying Duct (DTCO-21) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
| Pressure Transmitter | PT-60231 |  | 325-01-602-PD-04 | Gas Pressure Transmitter for Cyclone Exhaust Duct (DTCE-21) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
| Pressure Transmitter | PT-60240 |  | 325-01-602-PD-05 | Gas Pressure Transmitter for Bag House Exhaust Duct (DTEX-22) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter | PT-60241 |  | 325-01-602-PD-05 | Gas Pressure Transmitter for Exhaust Fan (FANE-21) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 0.1 mbar | 0-100% | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter | PT-61101 | PT-60204 | 325-01-602-PD-10 | Pressure transmitter | Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 barg | 0-100% | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter | PT-61301 |  | 325-01-613-PD-01 | Pressure in silo | Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 1 barg | 0-100% | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
| Pressure Transmitter | PT-61302 |  | 325-01-613-PD-03 | Pressure in vacuum line | Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | -100 - 100 mbarg | 0-100% | LiY-CY TP 1P x1.0 | - | -
| Pressure Transmitter | PT-61303 |  | 325-01-613-PD-01 | Powder Pressure Transmitter for Cooling / Conveyor Cyclone (CYCL-31) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
| Pressure Transmitter | PT-61304 |  | 325-01-613-PD-01 | Gas Pressure Transmitter for Storage Bin Cyclone Inlet Duct (CYCL-31) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
| Pressure Transmitter | PT-61305 |  | 325-01-613-PD-01 | Gas Pressure Transmitter for Exhaust Duct (DTEX-31) | Pressure Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | -100 to 200 mbar | 0-100% | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
| Pressure Transmitter | PT-61309 |  | 325-01-613-PD-04 | Pressure transmitter | Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 10 barg | 0 - 8 barg / 0-100% | LiY-CY TP 1P x1.0 | - | -
|  | PV-60201 | PCV-60201 | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic Control valve |  | - | - | 1 | - | - | 4 - 20 mA | PLC | 0 - 100% | Position O/C./0 - 100% | LiY-CY TP 2P x1.0 | - | -
|  | SV-40101 | SV-40201 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 1 | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-40102 | SV-40202 | 325-01-402-PD-01 | Water service pH analyzer in pH Adjustment tank 2 | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-40103 | SV-40203 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 1 | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-40104 | SV-40204 | 325-01-402-PD-01 | Air service pH analyzer in pH Adjustment tank 2 | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-60220 |  | 325-01-602-PD-04 | PA On/Off Valve for Chamber PSE purge air (CHAM-21) | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-60230 |  | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 27 (CYCL-21) | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-60231 |  | 325-01-602-PD-04 | PA On/Off Valve for Cyclone Air Hammer 28 (CYCL-22) | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-60240A |  | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29A (BGHS-21) | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-60240B |  | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29B (BGHS-21) | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-60240C |  | 325-01-602-PD-05 | PA On/Off Valve for Cyclone Air Hammer 29C (BGHS-21) | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-61301 |  | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-61302 |  | 325-01-613-PD-01 | Air service | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-61303 |  | 325-01-613-PD-01 | Timer compress air pluse solenoid valve | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-61305 |  | 325-01-613-PD-01 | Air service | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-61308 |  | 325-01-613-PD-03 | Timer compress air pluse solenoid valve | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-61309 |  | 325-01-613-PD-03 | Air service | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-61310 |  | 325-01-613-PD-05 | Timer compress air pluse solenoid valve | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | SV-61311 |  | 325-01-613-PD-05 | Air service | Solenoid valve |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 2Cx1 | - | -
|  | TSH-60230 |  | 325-01-602-PD-04 | Gas and Powder Temperature Switch High for Conveying Duct (DTCO-21) | Temperature Switch |  |  | 1 |  |  | - | Dry Contact | Fire Deluge Control Panel | 0 - 140 C | 140 | CVV 3Cx1.5 , CVV 4Cx1 | Ex d | -
|  | TSH-60240 |  | 325-01-602-PD-05 | Gas and Powder Temperature Switch High for Exhaust Duct (DTEX-22) | Temperature Switch |  |  | 1 |  |  | - | Dry Contact | Fire Deluge Control Panel | 0 - 140 C | 140 | CVV 3Cx1.5 , CVV 4Cx1 | Ex d | -
|  |  | TT-40221 | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 120 C | 0 - 300 C | LiY-CY TP 1P x1.0 | - | -
|  |  | TT-40222 | 325-01-402-PD-02 | Jet Cooker | Temperature Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 200 C | 0 - 300 C | LiY-CY TP 1P x1.0 | - | -
|  | TT-60201 |  | 325-01-602-PD-02 | Steam feed to Spray dryer | Temperature Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 300 C | 0 - 300 C | LiY-CY TP 1P x1.0 | - | -
|  | TT-60210 |  | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | - | -
|  | TT-60212A |  | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 100 C | 0 to 150 | LiY-CY TP 1P x1.0 | - | -
|  | TT-60212B |  | 325-01-602-PD-03 | Bearing Temperature Transmitter for Main Supply Air Fan (FANS-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 100 C | 0 to 150 | LiY-CY TP 1P x1.0 | - | -
|  | TT-60211 |  | 325-01-602-PD-03 | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | - | -
|  | TT-60214 |  | 325-01-602-PD-03 | Steam Temperature Transmitter for Cold Air Duct (DTCA-23) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | -10 to 250°C | -10 to 250 | LiY-CY TP 1P x1.0 | - | -
|  | TT-60215A |  | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | -10 to 150°C | -10 to 150 | LiY-CY TP 1P x1.0 | - | -
|  | TT-60215B |  | 325-01-602-PD-03 | Liquid Temperature Transmitter for Heat Recovery (HXCR-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | -10 to 150°C | -10 to 150 | LiY-CY TP 1P x1.0 | - | -
|  | TT-60216 |  | 325-01-602-PD-03 | Gas Temperature Transmitter for Combustion Air Burner Duct (DTCB-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 200'°C | 0 to 200 | LiY-CY TP 1P x1.0 | - | -
|  | TT-60220 |  | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
|  | TT-60221 |  | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
|  | TT-60222 |  | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
|  | TT-60223 |  | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
|  | TT-60224 |  | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
|  | TT-60225 |  | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
|  | TT-60226 |  | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
|  | TT-60227 |  | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Spray Chamber (CHAM-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
|  | TT-60230 |  | 325-01-602-PD-04 | Gas and Powder Temperature Transmitter for Conveying Duct (DTCO-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
|  | TT-60240 |  | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Fan (FANE-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | - | -
|  | TT-60241A |  | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 100 C | 0 to 150 | LiY-CY TP 1P x1.0 | - | -
|  | TT-60241B |  | 325-01-602-PD-05 | Bearing Temperature Transmitter for Main Exhaust Air Fan (FANE-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 100 C | 0 to 150 | LiY-CY TP 1P x1.0 | - | -
|  | TT-60245 |  | 325-01-602-PD-05 | Gas Temperature Transmitter for Exhaust Stack (DTXS-21) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | -10 to 150°C | -10 to 150 | LiY-CY TP 1P x1.0 | - | -
|  | TT-60702 | TT-60202 | 325-01-602-PD-07 | Compress air temp to camera | Temperature Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0 - 40 C | Control Temperature | LiY-CY TP 1P x1.0 | - | -
|  | TT-61301 |  | 325-01-613-PD-01 | Gas Temperature Transmitter for Cold Air Duct (DTCA-32) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
|  | TT-61302 |  | 325-01-613-PD-01 | Gas and Powder Temperature Transmitter for Cooling Cyclone (CYCL-31) | Temperature Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | 0 - 400'°C | 0 to 400 | LiY-CY TP 1P x1.0 | Ex ic | Safety Barriers
|  |  | TCV-40222 | 325-01-402-PD-02 | Jet Cooker | Automatic Control valve |  | - | - | 1 | - | - | 4 - 20 mA | PLC | 0 - 100% | Command | LiY-CY TP 1P x1.0 | - | -
|  | TV-60214 | TCV-60214 | 325-01-602-PD-03 | Steam Temperature Valve for Pre-Heat Steam Heat Exchanger (HXCH-21) | Automatic Control valve |  | - | - | 1 | - | - | 4 - 20 mA | PLC | 0 - 100% | Command | LiY-CY TP 1P x1.0 | - | -
|  | TV-60702 | TCV-60202 | 325-01-602-PD-07 | Chiller water control valve | 3-way Control valve |  | - | - | 1 |  | - | 4 - 20 mA | PLC | 0 - 100% | Position O/C./0 - 100% |  | - | -
|  | VT-60210A |  | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | mm/sec | 0 to 15 | LiY-CY TP 1P x1.0 | - | -
|  | VT-60210B |  | 325-01-602-PD-03 | Vibration Transmitter for Main Supply Air Fan (FANS-21) | Vibration Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | mm/sec | 0 to 15 | LiY-CY TP 1P x1.0 | - | -
|  | VT-60241A |  | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | mm/sec | 0 to 15 | LiY-CY TP 1P x1.0 | - | -
|  | VT-60241B |  | 325-01-602-PD-05 | Vibration Transmitter for Main Exhaust Air Fan (FANE-21) | Vibration Transmitter |  |  |  |  | 1 | - | 4 - 20 mA | PLC | mm/sec | 0 to 15 | LiY-CY TP 1P x1.0 | - | -
|  | XT-60301 | XT-60201 | 325-01-402-PD-03 | LEL gas analyzer | Gas detector |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% | LiY-CY TP 2Px1.0 , CVV 3Cx1.5 | Ex ic | Safety Barriers
|  | XA-60301 | XA-60201 | 325-01-402-PD-03 | LEL gas Buzzer Alarm | Gas detector |  | 1 | - | - |  | - | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% | LiY-CY TP 2Px1.0 , CVV 3Cx1.5 | Ex ic | Safety Barriers
|  | XT-92201 |  | 325-01-923-PD-03 | LEL gas analyzer | Gas detector |  | - | - | - | 1 | - | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% | LiY-CY TP 2Px1.0 , CVV 3Cx1.5 | Ex ic | Safety Barriers
|  | XA-92201 |  | 325-01-923-PD-03 | LEL gas Buzzer Alarm | Gas detector |  | 1 | - | - |  | - | 4 - 20 mA | PLC | 0-10%LEL | 0 - 100% | LiY-CY TP 2Px1.0 , CVV 3Cx1.5 | Ex ic | Safety Barriers
|  | XV-40101A | XV-40201A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 1 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40101B | XV-40201B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 1 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40101C | XV-40201C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 1 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40101D | XV-40201D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 1 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40101E | XV-40201E | 325-01-402-PD-01 | Slurry pH Adjustment tank 1 transfer to pH Adjustment tank 2 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40101F | XV-40201F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40101G | XV-40201G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 1 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40101H | XV-40201H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 1 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40102A | XV-40202A | 325-01-402-PD-01 | Slurry feed-in pH Adjustment tank 2 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40102B | XV-40202B | 325-01-402-PD-01 | Slurry feed-out pH Adjustment tank 2 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40102C | XV-40202C | 325-01-402-PD-01 | Water washing line outlet pH Adjustment tank 2 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40102D | XV-40202D | 325-01-402-PD-01 | Slurry circulation pH Adjustment tank 2 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40102E | XV-40202E | 325-01-402-PD-01 | Slurry pH Adjustment tank 2 transfer to pH Adjustment tank 1 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40102F | XV-40202F | 325-01-402-PD-01 | Slurry feed-to spray dry tank | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40102G | XV-40202G | 325-01-402-PD-01 | CIP water washing pH Adjustment tank 2 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40102H | XV-40202H | 325-01-402-PD-01 | CIP Hight pressure water washing pH Adjustment tank 2 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40201B | XV-40203B | 325-01-402-PD-02 | Slurry feed-out Spray dryer infeed tank | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40201C | XV-40203C | 325-01-402-PD-02 | Water washing line outlet Spray dryer infeed tank | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40201D | XV-40203D | 325-01-402-PD-02 | CIP water washing Spray dryer infeed tank | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-40201E | XV-40203E | 325-01-402-PD-02 | CIP hight pressure water washing Spray dryer infeed tank | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  |  | XV-40203F | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  |  | XV-40204B | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  |  | XV-40204C | 325-01-402-PD-01 | Jet Cooker | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  |  | XV-40205A | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  |  | XV-40205B | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  |  | XV-40205C | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  |  | XV-40205D | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  |  | XV-40205F | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  |  | XV-40222 | 325-01-402-PD-02 | Jet Cooker | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-60201 |  | 325-01-602-PD-02 | Steam feed to Spray dryer | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-60251 |  | 325-01-602-PD-01 | Liquid On/Off Valve for Drain Pipe (PIPE) | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-60301 | XV-60214 | 325-01-602-PD-03 | Steam feed to Spray dryer | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | XV-61101 | XV-60202 | 325-01-602-PD-11 | High Pressure Water On/Off Valve for Drain Pipe | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | - | -
|  | HV-61301 | XV-61301 | 325-01-613-PD-01 | Product feed-out Packing silo | Automatic on/off valve |  | - | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | Ex d | -
|  | XV-61302 |  | 325-01-613-PD-02 | Dust collector feed vent | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | Ex d | -
|  | XV-61303 |  | 325-01-613-PD-02 | Dust collector feed from packer | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | Ex d | -
|  |  | DV-61301 | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61301 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | Ex d | -
|  |  | DV-61302 | 325-01-613-PD-01 | On/Off Valve for Diverter Valve DV-61302 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | Ex d | -
|  | ZS-60201A |  | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-60201B |  | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-60201C |  | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-60201D |  | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-60201E |  | 325-01-602-PD-04 | Limit Switch for CHAM-21 (Spray Chamber) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  |  | ZS-60229 | 325-01-602-PD-04 | Limit Switch for CY-60230 (Door Service) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  |  | ZS-60230 | 325-01-602-PD-04 | Limit Switch for CY-60231 (Door Service) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-60231A |  | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Spectacle Inserted) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-60231B |  | 325-01-602-PD-05 | Gas Limit Switch for DTEX-21 (Bag House Face Blind Inserted) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-60231C |  | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Spool Inserted) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-60231D |  | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Inlet Blind Inserted) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-60231E |  | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Spool Inserted) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-60231F |  | 325-01-602-PD-05 | Gas Limit Switch for DTEX-23 (Bag House By-Pass Outlet Blind Inserted) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  |  | ZS-60240 | 325-01-602-PD-05 | Limit Switch for FA-60240 (Door Service) | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-61310 |  | 325-01-613-PD-01 | Position Magnet Door | Limit Switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | n/a | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-61311 |  | 325-01-613-PD-01 | Position Magnet Door | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-61312 |  | 325-01-613-PD-01 | Position Magnet Door | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ZS-61313 |  | 325-01-613-PD-01 | Position Magnet Door | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
[5 empty] | Lototo-01 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
[5 empty] | Lototo-02 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
[5 empty] | Lototo-03 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
[5 empty] | Lototo-04 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
[5 empty] | Lototo-05 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
[5 empty] | Lototo-06 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
[5 empty] | Lototo-07 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
[5 empty] | Lototo-08 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
[5 empty] | Lototo-09 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
[5 empty] | Lototo-10 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
[5 empty] | Lototo-11 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
[5 empty] | Lototo-12 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
Machine Equipment Supply
|  | PSE-61300 |  | 325-01-613-PD-01 | Explosion Vent PSE-61300 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
|  | PSE-61301 |  | 325-01-613-PD-01 | Explosion Vent PSE-61301 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ISV-61302 |  | 325-01-613-PD-01 | Explosion isolation flap valve ISV-61302 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
|  | PSE-61302 |  | 325-01-613-PD-03 | Explosion Vent PSE-61302 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
|  | PSE-61303 |  | 325-01-613-PD-05 | Explosion Vent PSE-61303 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
|  | PSE-61304 |  | 325-01-613-PD-01 | Explosion Vent PSE-61304 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
|  | PSV-61301A | ZS-61306 | 325-01-613-PD-01 | Position Brether Valve High Pressure PSV-61301 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
|  | PSV-61301B | ZS-61307 | 325-01-613-PD-01 | Position Brether Valve Vacuum Pressure PSV-61301 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ISV-61303 |  | 325-01-613-PD-03 | Explosion isolation flap valve ISV-61303 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
|  | ISV-61304 |  | 325-01-613-PD-05 | Explosion isolation flap valve ISV-61304 | Position switch |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off | Detected " Fail " / Active | CVV 4Cx1 | Ex ic | Safety Barriers
MCC ROOM
| Tank Agitator | ATY-40101 | ATY-40201 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40201 |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off |  | MULTICORE LINK TO MCC PANEL
| Tank Agitator | ATY-40102 | ATY-40202 | 325-01-402-PD-01 | Start / Stop Command for VSD AT-40202 |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
| Tank Agitator | ATY-40201 | ATY-40203 | 325-01-402-PD-02 | Start / Stop Command for VSD AT-40203 |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
|  | BFY-60210 |  | 325-01-602-PD-03 | Start / Stop Command for VSD FANS-21 (Main Supply Air Fan) |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
|  | BFY-60211 |  | 325-01-602-PD-03 | Start / Stop Command for VSD FANC-21 (Combustion Fan) |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
|  | BFY-60240 |  | 325-01-602-PD-05 | Start / Stop Command for VSD FANE-21 (Exhaust Fan) |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
|  | BFY-60220 |  | 325-01-602-PD-04 | Start / Stop Command for VSD FANS-22 (Cooling Fan) |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
|  | BFY-60206 |  | 325-01-602-PD-08 | Start / Stop Command for VSD FANS-31 (Cooling / Conveying Fan) |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
|  | BFY-61301 |  | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61301 (Packing silo vent fan ) |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
|  | BFY-61302 |  | 325-01-613-PD-05 | Start / Stop Command for VSD BF-61302 (LEV Blower fan ) |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
|  | BFY-61303 |  | 325-01-613-PD-01 | Start / Stop Command for VSD BF-61303 (Fugitive Dust Fan ) |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
|  | BLM-61302 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR BL-61301 ( Bin Actuator Blower ) |  |  | 2 | 2 | - | - | - | 24 VDC energized | PLC | On-Off
|  | PCM-60205-B | PDM-60202B | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Oil Pump ) |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | PCM-60205-C | PDM-60202C | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 1 ) |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | PCM-60205-D | PDM-60202D | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Machine Fan 2 ) |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | PCM-60205-E | PDM-60202E | 325-01-602-PD-01 | Start / Stop Command for FVNR PUPD-11 (Main motor Fan ) |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
| PUMP | PCY-40201 | PCY-40203 | 325-01-402-PD-02 | Start / Stop Command for VSD PUCF-11 (Centrifugal Feed Pump) |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
| PUMP | PCY-40101 | PCY-40201 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40201 |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
| PUMP | PCY-40102 | PCY-40202 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40202 |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
|  |  | PDY-40204 | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40204 |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
|  |  | PDY-40205 | 325-01-402-PD-01 | Start / Stop Command for VSD PD-40205 |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
|  | PCY-60205-A | PDY-60202A | 325-01-602-PD-01 | Start / Stop Command for VSD PUPD-11 (Positive Displacement Pump ) |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
| PUMP | PCY-60215 |  | 325-01-602-PD-03 | Start / Stop Command for VSD PUCF-21 (Heat Recovery Centrifugal Pump) |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | PLC | On-Off
|  | PVM-61301 | BLM-61301 | 325-01-613-PD-03 | Start / Stop Command for FVNR PV-61301 (Vacuum Cleaning Fan) |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | RVM-60201 |  | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-21 (Cyclone-21 Rotary Valve ) |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | RVM-60202 |  | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-22 (Cyclone-22 Rotary Valve ) |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | RVM-60203 |  | 325-01-602-PD-08 | Start / Stop Command for FVNR RVAL-23 (Bag House Rotary Valve) |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | RVM-60204 |  | 325-01-602-PD-08 | Start / Stop Command for FVNR RV-60204 (Recycle silo Rotary Valve) |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | RVM-61301 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61301 |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | RVM-61302 |  | 325-01-613-PD-03 | Start / Stop Command for FVNR RV-61302 |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | RVM-61303 |  | 325-01-613-PD-05 | Start / Stop Command for FVNR RV-61303 |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | RVM-61304 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61304 |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | RVM-61305 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR RV-61305 |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | SCM-61301 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61301 (Sifter ) |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
|  | SCM-61302 |  | 325-01-613-PD-01 | Start / Stop Command for FVNR SC-61302 (Sifter ) |  |  | 1 | 3 | - | - | - | 24 VDC energized | PLC | On-Off
DEDERT SUPPLY EQUIPMENT
|  | FT-60701 | FT-60207 | 325-01-602-PD-07 | Instr. Air Flow Transmitter for Camera #4 (ACAM-21) | Flow Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC |  |  | LiY-CY TP 1P x1.0
| Pressure Transmitter | PT-60701 | PT-60207 | 325-01-602-PD-07 | Instr. Air Pressure Transmitter for Camera #4 (ACAM-21) | Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC |  |  | LiY-CY TP 1P x1.0
|  | SV-60240D |  | 325-01-602-PD-05 | PA On/Off Valve for Bag House Tank Valve (BGHS-21) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off |  | CVV 3Cx1 / CVV 4Cx1
|  | SV-60701 | SV-60207 | 325-01-602-PD-07 | Instr. Air On/Off Valve for Camera #4 (ACAM-21) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off |  | CVV 3Cx1 / CVV 4Cx1
|  | SV-60201 |  | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-21 Rotary Valve (RVAL-21) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off |  | CVV 3Cx1 / CVV 4Cx1
|  | SV-60202 |  | 325-01-602-PD-08 | PA On/Off Valve for Cyclone-22 Rotary Valve (RVAL-22) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off |  | CVV 3Cx1 / CVV 4Cx1
|  | SV-60203 |  | 325-01-602-PD-08 | PA On/Off Valve for Bag House Rotary Valve (RVAL-23) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off |  | CVV 3Cx1 / CVV 4Cx1
|  | SV-61304 |  | 325-01-613-PD-01 | PA On/Off Valve for Conveying Cooler Cyclone-31 Rotary Valve (RV-61304) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off |  | CVV 3Cx1 / CVV 4Cx1
|  | TT-60701 | TT-60207 | 325-01-602-PD-07 | Instr. Air Temperature Transmitter for Air Manifold - Camera #4 (ACAM-21) | Temperature Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | PLC |  |  | LiY-CY TP 1P x1.0
|  | XV-60261FA |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60261FB |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60261FC |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60261FD |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60261SA |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #1 (ATVM-11A) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60261SB |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #2 (ATVM-11A) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60261SC |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #3 (ATVM-11A) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60261SD |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #4 (ATVM-11A) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60262FE |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60262FF |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60262FG |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60262FH |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60262SE |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #5 (ATVM-11B) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60262SF |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #6 (ATVM-11B) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60262SG |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #7 (ATVM-11B) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60262SH |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #8 (ATVM-11B) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60263FJ |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60263FK |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60263FL |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60263FM |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60263SJ |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #9 (ATVM-11C) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60263SK |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #10 (ATVM-11C) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60263SL |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #11 (ATVM-11C) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60263SM |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #12 (ATVM-11C) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60264FN |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60264FP |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60264FQ |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60264FR |  | 325-01-602-PD-02 | Feed Slurry On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60264SN |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #13 (ATVM-11D) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60264SP |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #14 (ATVM-11D) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60264SQ |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #15 (ATVM-11D) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60264SR |  | 325-01-602-PD-02 | Steam On/Off Valve for Nozzle #16 (ATVM-11D) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60261DA |  | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11A | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60262DE |  | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11B | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60263DN |  | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11C | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60264DJ |  | 325-01-602-PD-02 | Slurry Drain On/Off Valve for ATVM-11D | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | XV-60241 |  | 325-01-602-PD-05 | Gas On/Off Valve for Bag House Isolation Damper (DMPR-22) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized,Dry Contact | PLC | On-Off |  | CVV 3Cx1 / CVV 4Cx1
|  | XA-60202A |  | 325-01-602-PD-08 | General Alarm Emergency Stop Actuation for XSUP-5601 (Supression Panel) | General Alarm Emergency Stop Actuation |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XA-60202B |  | 325-01-602-PD-08 | General Fault Controlled Stop for XSUP-5601 (Supression Panel) | General Fault Controlled Stop |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XA-60202C |  | 325-01-602-PD-08 | General Armed Status Indicator for XSUP-5601 (Supression Panel) | General Armed Status Indicator |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XA-60202D |  | 325-01-602-PD-08 | Power Fault Status Indicator for XSUP-5601 (Supression Panel) | Power Fault Status Indicator |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XA-60202E |  | 325-01-602-PD-08 | Dryer CHAM-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | Dryer CHAM-21 Emergency Stop Actuation |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XA-60202F |  | 325-01-602-PD-08 | CHAM-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CHAM-21 Controlled Stop Trouble (No Protection) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XA-60202G |  | 325-01-602-PD-08 | CYCL-21/22 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-21/22 Emergency Stop Actuation |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XA-60202H |  | 325-01-602-PD-08 | CYCL-21/22 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-21/22 Controlled Stop Trouble (No Protection) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XA-60202J |  | 325-01-602-PD-08 | BGHS-21 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | BGHS-21 Emergency Stop Actuation |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XA-60202K |  | 325-01-602-PD-08 | BGHS-21 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | BGHS-21 Controlled Stop Trouble (No Protection) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XA-60202L |  | 325-01-602-PD-08 | CYCL-31 Emergency Stop Actuation for XSUP-5601 (Supression Panel) | CYCL-31 Emergency Stop Actuation |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XA-60202M |  | 325-01-602-PD-08 | CYCL-31 Controlled Stop Trouble (No Protection) for XSUP-5601 (Supression Panel) | CYCL-31 Controlled Stop Trouble (No Protection) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XA-60261 |  | 325-01-602-PD-05 | Fire Deluge Fault (No Protection) for FWDP-21 (Fire Deluge) | Fire Deluge Fault (No Protection) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XA-60262 |  | 325-01-602-PD-05 | Fire Deluge Alarm (Deluge Activated) for FWDP-21 (Fire Deluge) | Fire Deluge Alarm (Deluge Activated) |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 4Cx1
|  | XS-60260 |  | 325-01-602-PD-05 | Start / Stop Command for FWDP-21 (Fire Deluge) | Start / Stop Command |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  | CVV 3Cx1
|  | XV-60240 |  | 325-01-602-PD-08 | Powder On/Off Valve for Diverter Valve (DVTR-21) | On/Off Valve |  | 1 | 2 | - | - | - | 24 VDC energized | PLC | On-Off |  | CVV 3Cx1 / CVV 4Cx1
Haver & Boecker. EQUIPMENT
|  | XA-61301A |  | 325-01-613-PD-02 | Request filter plant | Request filter plant |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | MULTICORE LINK TO PLC | - | -
|  | XA-61301B |  | 325-01-613-PD-02 | Request material transport | Request material transport |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-61301C |  | 325-01-613-PD-02 | Request belt plant | Request belt plant |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-61301D |  | 325-01-613-PD-02 | Machine in operation | Machine in operation |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-61301E |  | 325-01-613-PD-02 | General Fault | General Fault |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-61301F |  | 325-01-613-PD-02 | Machine is ready | Machine is ready |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-61301G |  | 325-01-613-PD-02 | Emergency stop activated | Emergency stop activated |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-61301H |  | 325-01-613-PD-02 | Silo minimum | Silo minimum |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-61301J |  | 325-01-613-PD-02 | Silo maximum | Silo maximum |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XS-61301A |  | 325-01-613-PD-02 | Filter plant in operation | Filter plant in operation |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
|  | XS-61301B |  | 325-01-613-PD-02 | Material transport in operation | Material transport in operation |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
|  | XS-61301C |  | 325-01-613-PD-02 | Belt plant in operation | Belt plant in operation |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
|  | XS-61301D |  | 325-01-613-PD-02 | Sequence Stop | Sequence Stop |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
|  | XS-61301E |  | 325-01-613-PD-02 | Status from Customer Emergency stop | Status from Customer Emergency stop |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
|  | XS-61301F |  | 325-01-613-PD-02 | Operation Release | Operation Release |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
|  |  |  | 325-01-613-PD-02 | Spare |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  |  |  | 325-01-613-PD-02 | Spare |  |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
|  |  |  | 325-01-613-PD-02 | Spare |  |  | 1 | - | - | - | - | 24 VDC energized | PLC | On-Off |  |  | - | -
|  |  |  | 325-01-613-PD-02 | Communication Signal |  |  | - | - | - | - | 1 | 24 VDC energized | PLC | On-Off |  |  | - | -
BGHS-21 Filter Control Panel
|  | XS-60240A |  | 325-01-602-PD-05 | Start / Stop Command for BGHS-21 (Bag House Air Pulsing) |  |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  | MULTICORE LINK TO PLC | - | -
|  | XS-60240B |  | 325-01-602-PD-05 | Fan Command for BGHS-21 (Bag House Air Pulsing) |  |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-60240A |  | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-60240B |  | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | DPI-60240 |  | 325-01-602-PD-05 | Gas Pressure Differntial Pressure (Bag House Air Pulsing) |  |  | - | - | - | 1 | - | 4 - 20 mA | PLC |  |  |  | - | -
HTRE-21 Heater Control Panel (TRACING)
|  | XS-60241A |  | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  | MULTICORE LINK TO PLC | - | -
|  | XA-60241A |  | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-60241B |  | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | TSH-60241A |  | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch |  |  | 1 |  |  | - | Dry Contact | Heat Control Panel (HTRE-21) | 0 - 100 C | 140 | CVV 3Cx1.5 , CVV 4Cx1 | Ex d | -
|  | TSL-60241B |  | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch |  |  | 1 |  |  | - | Dry Contact | Heat Control Panel (HTRE-21) | 0 - 100 C | 140 | CVV 3Cx1.5 , CVV 4Cx1 | Ex d | -
HTRE-22 Heater Control Panel (TRACING)
|  | XS-60242A |  | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  | MULTICORE LINK TO PLC | - | -
|  | XA-60242A |  | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-60242B |  | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | TSH-60242A |  | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch |  |  | 1 |  |  | - | Dry Contact | Heat Control Panel (HTRE-22) | 0 - 100 C | 140 | CVV 3Cx1.5 , CVV 4Cx1 | Ex d | -
|  | TSL-60242B |  | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch |  |  | 1 |  |  | - | Dry Contact | Heat Control Panel (HTRE-22) | 0 - 100 C | 140 | CVV 3Cx1.5 , CVV 4Cx1 | Ex d | -
HTRE-23 Heater Control Panel (TRACING)
|  | XS-60243A |  | 325-01-602-PD-05 | Start / Stop Command for HTRE-21 (Heater Control Panel) |  |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  | MULTICORE LINK TO PLC | - | -
|  | XA-60243A |  | 325-01-602-PD-05 | Alarm 1 for BGHS-21 (Bag House Air Pulsing) |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-60243B |  | 325-01-602-PD-05 | Alarm 2 for BGHS-21 (Bag House Air Pulsing) |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | TSH-60243A |  | 325-01-602-PD-05 | Surface Heating Temperature switch high for bag house cone (BGHS-21) | Temperature Switch |  |  | 1 |  |  | - | Dry Contact | Heat Control Panel (HTRE-23) | 0 - 100 C | 140 | CVV 3Cx1.5 , CVV 4Cx1 | Ex d | -
|  | TSL-60243B |  | 325-01-602-PD-05 | Surface Heating Temperature switch low for bag house cone (BGHS-21) | Temperature Switch |  |  | 1 |  |  | - | Dry Contact | Heat Control Panel (HTRE-23) | 0 - 100 C | 140 | CVV 3Cx1.5 , CVV 4Cx1 | Ex d | -
AHTR-21 Air Heater Control Panel
|  | XA-FH-60210A |  | 325-01-602-PD-06 | BMS PANEL POWER ON for AHTR-21 |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  | CVV 20C x 1 | - | -
|  | XA-FH-60210B |  | 325-01-602-PD-06 | BMS Burner High Fire Purge for AHTR-21 |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-FH-60210C |  | 325-01-602-PD-06 | BMS Burner On for AHTR-21 |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-FH-60210D |  | 325-01-602-PD-06 | BMS BMS Lockout for AHTR-21 |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XA-FH-60210E |  | 325-01-602-PD-06 | BMS Remote Modet for AHTR-21 |  |  | - | 1 | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XS-FH-60210A |  | 325-01-602-PD-06 | Start / Stop Command Burner Remote Start for AHTR-21 |  |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XS-FH-60210B |  | 325-01-602-PD-06 | Start / Stop Command Dryer Interlocks for AHTR-21 |  |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XS-FH-60210C |  | 325-01-602-PD-06 | Command Remote Reset for AHTR-21 |  |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | XS-FH-60210D |  | 325-01-602-PD-06 | Spare |  |  | 1 | - | - | - | - | Dry Contact | PLC | On-Off |  |  | - | -
|  | TI-FH-60210 |  | 325-01-602-PD-06 | Gas Burner Firing Rate Temp Signal to AHTR-21 |  |  | - | - | - | 1 | - | 4 - 20 mA | PLC | On-Off |  | LiY-CY TP 3P x1.0 | - | -
|  | UY-FH-60210A |  | 325-01-602-PD-06 | Comb fan VFD Speed Control |  |  | - | - | - | 1 | - | 4 - 20 mA | PLC | On-Off |  |  | - | -
|  | UY-FH-60210B |  | 325-01-602-PD-06 | Demand Signal |  |  | - | - | 1 | - | - | 4 - 20 mA | PLC | On-Off |  |  | - | -
|  | COM-FH-60210B |  | 325-01-602-PD-06 | Communication Signal |  |  | - | - | - | - | 1 | Modbus RTU | PLC |  |  | CAT 5e | - | -
|  | TE-60212 |  |  | Gas Temperature Element for Hot Air Duct (DTHA-21) | Temperature Element | [6 empty] | T/C Type K | AHTR Control Panel(HCP) |  |  | LiY-CY TP 1P x1.0 | - | -
|  | DPHL-60230 |  |  | Gas Pressure Differntial Switch Low for Exhaust Fan (FANE-21) | Pressure Differntial Switch Low | [7 empty] | AHTR Control Panel(HCP) |  |  | CVV 3Cx1 | - | -
|  | DPSL-60211 |  |  | Gas Pressure Differential Switch Low for Combustion Fan (FANC-21) | Pressure Differential Switch Low | [7 empty] | AHTR Control Panel(HCP) |  |  | CVV 3Cx1 | - | -
|  | FCV-60211B |  |  | Gas Flow Control Damper (Valve) for Burner Combustion Air Duct (DTCB-21) | Flow Control Damper (Valve) | [7 empty] | AHTR Control Panel(HCP) |  |  | LiY-CY TP 2P x1.0 , CVV 8Cx1 | - | -
|  | ZT-60211B |  |  | Gas Position Transmitter for Combustion Air Damper Actuator (DTCB-21) | Position Transmitter | [7 empty] | AHTR Control Panel(HCP) |  |  |  | - | -
|  | ZSL-60211B |  |  | Gas Position Switch Low for Combustion Air Damper Actuator (DTCB-21) | Position Switch Low | [7 empty] | AHTR Control Panel(HCP) |  |  | CVV 4Cx1 | - | -
|  | ZSH-60211B |  |  | Gas Position Switch High for Combustion Air Damper Actuator (DTCB-21) | Position Switch High | [7 empty] | AHTR Control Panel(HCP) |  |  |  | - | -
|  | VJ-01 (24VDC) |  |  | Valve train J-BOX | Control Box | [7 empty] | AHTR Control Panel(HCP) |  |  | LiY-CY TP 2P x1.0 , CVV 17Cx1 | - | -
|  | VJ-01 (220VAC) |  |  | Valve train J-BOX | Control Box | [7 empty] | AHTR Control Panel(HCP) |  |  | CVV 3Cx1.5 | - | -
|  | UJ-01 (24VDC) |  |  | Valve train J-BOX | Control Box | [7 empty] | AHTR Control Panel(HCP) |  |  | LiY-CY TP 2P x1.0 , CVV 4Cx1 | - | -
|  | UJ-01 (220VAC) |  |  | Valve train J-BOX | Control Box | [7 empty] | AHTR Control Panel(HCP) |  |  | CVV 5Cx1.5 | - | -
|  | PV-60210A |  |  | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | [7 empty] | AHTR Control Panel |  |  | LiY-CY TP 1P x1.0
|  | PV-60210B |  |  | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | Pressure Valve | [7 empty] | AHTR Control Panel |  |  | LiY-CY TP 1P x1.0
| Differential Pressure Transmitte | DPT-60210 |  |  | Gas Pressure Differential Switch Low for Main Supply Air Fan (FANS-21) | Pressure Differential Switch Low | [7 empty] | AHTR Control Panel |  |  | LiY-CY TP 1P x1.0
|  | DPSL-60210B |  |  | Gas Pressure Differential Switch Low for Air Heater (AHTR-21) | Pressure Differential Switch Low | [7 empty] | AHTR Control Panel |  |  | CVV 4Cx1
|  | DPSH-60210C |  |  | Gas Pressure Differential Switch High for Air Heater (AHTR-21) | Pressure Differential Switch High | [7 empty] | AHTR Control Panel |  |  | CVV 4Cx1
|  | BE-60210A |  |  | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | [7 empty] | AHTR Control Panel |  |  | CVV 4Cx1
|  | BE-60210B |  |  | Gas Flame Detector for Air Heater (AHTR-21) | Flame Detector | [7 empty] | AHTR Control Panel |  |  | CVV 4Cx1
|  | IX-60210A |  |  | Gas Ignition Transformer for Air Heater (AHTR-21) | Ignition Transformer | [7 empty] | AHTR Control Panel |  |  | LiY-CY TP 1P x1.0
|  | FCV-60210A |  |  | Gas Flow Control Valve for Air Heater Gas Train (GTRN-21) | Flow Control Valve | [7 empty] | AHTR Control Panel |  |  | LiY-CY TP 2P x1.0 , CVV 8Cx1
|  | ZSL-60210A |  |  | Gas Position Switch Low for Air Heater Gas Train (GTRN-21) | Position Switch Low | [7 empty] | AHTR Control Panel |  |  | CVV 4Cx1
|  | ZT-60210A |  |  | Gas Position Transmitter for Air Heater Gas Train (GTRN-21) | Position Transmitter | [7 empty] | AHTR Control Panel |  |  | LiY-CY TP 1P x1.0
|  | PSH-60210 |  |  | Gas Pressure Switch High for Air Heater Gas Train (GTRN-21) | Pressure Switch High | [7 empty] | AHTR Control Panel |  |  | CVV 4Cx1
|  | BV-60210B |  |  | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | [7 empty] | AHTR Control Panel |  |  | CVV 3Cx1
|  | ZSO-60210B |  |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | [7 empty] | AHTR Control Panel |  |  | CVV 4Cx1
|  | ZSC-60210B |  |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | [7 empty] | AHTR Control Panel
|  | VV-60210 |  |  | Gas Venting Valve (main gas) for Air Heater Gas Train (GTRN-21) | Venting Valve (main gas) | [7 empty] | AHTR Control Panel |  |  | CVV 3Cx1
|  | ZSO-60210C |  |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | [7 empty] | AHTR Control Panel |  |  | CVV 4Cx1
|  | ZSC-60210C |  |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | [7 empty] | AHTR Control Panel
|  | PSL-60210 |  |  | Gas Pressure Switch Low for Air Heater Gas Train (GTRN-21) | Pressure Switch Low | [7 empty] | AHTR Control Panel |  |  | CVV 4Cx1
|  | BV-60210A |  |  | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | Blocking Valve (main gas) | [7 empty] | AHTR Control Panel |  |  | CVV 3Cx1
|  | ZSO-60210A |  |  | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | Position Switch Open | [7 empty] | AHTR Control Panel |  |  | CVV 4Cx1
|  | ZSC-60210A |  |  | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | Position Switch Close | [7 empty] | AHTR Control Panel
PUPD Pump Control Panel
|  | ES-60202 |  | 325-01-602-PD-01 | E-Stop for PUPD-11 (Positive Displacement Pump ) | E-Stop |  |  | 1 |  |  |  |  | PLC |  | n/a | CVV 4Cx1 | - | -
| Pressure Transmitter | PT-60205 |  | 325-01-602-PD-01 | Feed Slurry Pressure Transmitter for High Pressure Pump Outlet (PUPD-11) | Pressure Transmitter |  | - | - | - | - | - | 4 - 20 mA | PDPU-1 1 Panel |  |  | LiY-CY TP 1P x1.0
| Flow Switch | FS-60205 |  | 325-01-602-PD-01 | Cooling Water Return Flow Switch for Positive Displacement Pump (PUPD-11) | Flow Switch |  | - | - | - | - | - |  | PDPU-1 1 Panel |  |  | CVV 4Cx1 | - | -
|  | XS-60205 |  | 325-01-602-PD-01 | Start / Stop Command for PUPD-11 (Positive Displacement Pump ) | Start / Stop Command |  | 1 | - | - | - | - |  | PLC
| Vibration Switch | VS-60205 |  | 325-01-602-PD-01 | Vibration Gear Box Vibration Switch for Switch Vibration for PUPD-11 (PUPD-11) | Vibration Switch |  | - | - | - | - | - | Dry Contact | PDPU-1 1 Panel | On-Off |  | CVV 4Cx1
|  | XV-60205A |  | 325-01-602-PD-01 | Cooling Water On/Off Valve for Cooling Water Supply for PUPD-11 (PUPD-11) | On/Off Valve |  | - | - | - | - | - | 24 VDC energized,Dry Contact | PDPU-1 1 Panel | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1
|  | YA-60205 |  | 325-01-602-PD-01 | Fault Command |  |  |  | 1 |  |  |  |  | PLC
|  | YI-60205 |  | 325-01-602-PD-01 | Run Command |  |  |  | 1 |  |  |  |  | PLC
Suppression Panel
|  | PSH-61301 |  | 325-01-613-PD-01 | Gas and Powder Pressure Switch High for Storage Bin Cyclone Inlet Duct (####-##) | Pressure Switch High | [7 empty] | Suppression Sys. Panel |  |  | CVV 3Cx1.5 , CVV 4Cx1
|  | PSH-60220 |  | 325-01-602-PD-04 | Gas Pressure Switch High for Spray Chamber (CHAM-21) | Pressure Switch High | [7 empty] | Suppression Sys. Panel |  |  | CVV 3Cx1.5 , CVV 4Cx1
|  | PSH-60230 |  | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-21) | Pressure Switch High | [7 empty] | Suppression Sys. Panel |  |  | CVV 3Cx1.5 , CVV 4Cx1
|  | PSH-60231 |  | 325-01-602-PD-04 | Gas Pressure Switch High for Cyclone (CYCL-22) | Pressure Switch High | [7 empty] | Suppression Sys. Panel |  |  | CVV 3Cx1.5 , CVV 4Cx1
|  | PSH-60224 |  | 325-01-602-PD-05 | Gas and Powder Pressure Switch High for Bag House (BGHS-21) | Pressure Switch High | [7 empty] | Suppression Sys. Panel |  |  | CVV 3Cx1.5 , CVV 4Cx1
REMOTE I-O Area-200
| Manual Valve With Position Switch | HV-2022 | HV-20204 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
| Manual Valve With Position Switch | HV-2024 | HV-20205 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
| Manual Valve With Position Switch | HV-2026 | HV-20206 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
| Manual Valve With Position Switch | HV-2030 | HV-20207 | 325-01-202-PD-01 | Slurry Drain line | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
| Manual Valve With Position Switch | HV-2032 | HV-20208 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
| Manual Valve With Position Switch | HV-2035 | HV-20209 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
| Manual Valve With Position Switch | HV-2038 | HV-20210 | 325-01-202-PD-02 | Slurry Drain line | Valve With Position Switch |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Manual / Position Close | CVV 4Cx1 | - | -
|  | XV-20201 |  | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | Ex d | -
|  | XV-20202 |  | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | Ex d | -
|  | XV-20203 |  | 325-01-202-PD-01 | Slurry Preparation Tank 1 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | Ex d | -
|  | XV-20211 |  | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | Ex d | -
|  | XV-20212 |  | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | Ex d | -
|  | XV-20213 |  | 325-01-202-PD-01 | Slurry Preparation Tank 2 | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | Ex d | -
|  | LS-81001 | LS-814201 | 325-01-814-PD-01 | Level alarm low | Level switch |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off | Nondetected " Empty " / Overfill | CVV 3Cx1.5 , CVV 4Cx1 | Ex ic | Safety Barriers
|  | PCM-2030 | PCM-20201 | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2030 |  |  | 1 | 3 | - | - | - | 24 VDC energized | RIO-200 | On-Off |  | MULTICORE LINK TO MCC 200 PANEL |  | Preparation area
|  | PCM-2031 |  | 325-01-202-PD-01 | Start / Stop Command for FVNR PC-2031 |  |  | 2 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off |  |  |  | Preparation area
| PUMP | PCY-81001 | PCY-814201 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81001 |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | RIO-200 | On-Off |  | MULTICORE LINK TO MCC 810 PANEL
| PUMP | PCY-81002 | PCY-814202 | 325-01-814-PD-01 | Start / Stop Command to VSD PC-81002 |  |  | 1 | 3 | - | - | 1 | 24 VDC energized | RIO-200 | On-Off
LPG Station
|  | FT-80301 | FT-913201 | 325-01-913-PD-02 | Flow outlet LPG line | Coriolis Flow Transmitter |  | - | 1 | - | 2 | - | 4 - 20 mA,Pulse | RIO-200 | 0-1000kg/hr | Flow rate | LiY-CY TP 3Px1.0 , CVV 3Cx1.5 | Ex d | -
| Level Transmitter | LT-80301 | LT-913201 | 325-01-913-PD-01 | Level LPG in storage | Level transmitter |  | - | - | - | 1 | - | 4 - 20 mA | RIO-200 |  | 0 - 100% | LiY-CY TP 1P x1.0 | Ex ia | Safety Barriers
| Pressure Transmitter | PT-80302 | PT-913201 | 325-01-913-PD-02 | Pressure outlet LPG line | Pressure Transmitter |  | - | - | - | 1 | - | 4 - 20 mA | RIO-200 | 0 - 10 barg | 0 - 8 barg / 0-100% | LiY-CY TP 1P x1.0 | Ex d | -
|  |  | XV-913201 | 325-01-913-PD-02 | Outlet LPG line | Automatic on/off valve |  | 1 | 2 | - | - | - | 24 VDC energized | RIO-200 | On-Off | Energized " Open" / Position O/C | CVV 3Cx1 / CVV 4Cx1 | Ex d | -
Gas Vaporizer 5
|  | XA-80305A |  | 325-01-803-PD-02 | Gas Vaporizer 5 control status | Gas vaporizer Ready |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  | CVV 16Cx1.5 | - | -
|  | XA-80305B |  | 325-01-803-PD-02 | Gas Vaporizer 5 control status | Gas vaporizer Run |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
|  | XA-80305C |  | 325-01-803-PD-02 | Gas Vaporizer 5 control status | Gas vaporizer Failed |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
|  | XA-80305D |  | 325-01-803-PD-02 | Gas Vaporizer 5 control status | Gas vaporizer Overheated |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
|  | XA-80305E |  | 325-01-803-PD-02 | Gas Vaporizer 5 control status | Gas vaporizer Excessive flow tripped |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
|  | XA-80305F |  | 325-01-803-PD-02 | Gas Vaporizer 5 control status | Gas vaporizer low water level |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
|  | XS-80305 |  | 325-01-803-PD-02 | Start / Stop Command for Gas Vaporizer 5 | Start / Stop Command |  | 1 | - | - | - | - | 24 VDC energized | RIO-200 | On-Off |  |  | - | -
Gas Vaporizer 6
|  | XA-80306A |  | 325-01-803-PD-02 | Gas Vaporizer 6 control status | Gas vaporizer Ready |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  | CVV 16Cx1.5 | - | -
|  | XA-80306B |  | 325-01-803-PD-02 | Gas Vaporizer 6 control status | Gas vaporizer Run |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
|  | XA-80306C |  | 325-01-803-PD-02 | Gas Vaporizer 6 control status | Gas vaporizer Failed |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
|  | XA-80306D |  | 325-01-803-PD-02 | Gas Vaporizer 6 control status | Gas vaporizer Overheated |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
|  | XA-80306E |  | 325-01-803-PD-02 | Gas Vaporizer 6 control status | Gas vaporizer Excessive flow tripped |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
|  | XA-80306F |  | 325-01-803-PD-02 | Gas Vaporizer 6 control status | Gas vaporizer low water level |  | - | 1 | - | - | - | Dry Contact | RIO-200 | On-Off |  |  | - | -
| Pressure Transmitter | XS-80306 |  | 325-01-803-PD-02 | Start / Stop Command for Gas Vaporizer 6 | Start / Stop Command |  | 1 | - | - | - | - | 24 VDC energized | RIO-200 | On-Off |  |  | - | -
Note on D219: jaturong: เปลี่ยนชื่อจาก XV-61304
Note on E219: jaturong: เปลี่ยนชื่อจาก XV-61304
Note on J262: jaturong: Start/Stop
Note on K262: jaturong: RUN/Fault/Mode
Note on N262: jaturong: TCP/IP
Note on J289: jaturong: Start Stop
Note on K289: jaturong: Emer+Lototo Overload
Note on K290: jaturong: Emer+Lototo Overload
Note on K293: jaturong: Emer+Lototo Overload
Note on K294: jaturong: Emer+Lototo Overload

## Sheet4
Count of I/O Type | Column Labels
Row Labels | AI | AO | BUS | DI | DO | Grand Total | Rack | DI | Require Slot | DO | Require Slot | AI | Require Slot | AO | Require Slot | Sum Slot//Rack
JB-401 | 16 |  | 6 | 42 | 54 | 118 | 0 | 68 |  | 60 |  | 19 |  | 0
JB-601 | 16 |  | 2 | 81 | 48 | 147 | 1 | 35 |  | 63 |  | 59 |  | 5 | 1
JB-602 | 29 | 2 | 4 | 25 | 11 | 71 | 2 | 57 |  | 21 |  | 20 |  | 0
JB-603 | 7 |  |  | 15 |  | 22 | 3 | 66 |  | 29 |  | 13 |  | 0
JB-607 | 27 | 2 | 2 | 6 | 43 | 80 | 4 | 52 |  | 22 |  | 9 |  | 0
RIO-200 | 14 |  | 2 | 50 | 16 | 82
(blank) | 34 | 3 |  | 116 | 131 | 284
JB-612 | 4 |  | 2 | 55 | 26 | 87
JB-618 | 13 |  | 2 | 61 | 21 | 97
JB-606 | 2 |  |  | 4 | 2 | 8
JB-402 | 7 | 1 |  | 6 | 9 | 23
JB-608 | 7 |  |  | 7 | 1 | 15
CA1 |  |  |  | 16 |  | 16
MCC |  |  |  | 1 | 9 | 10
Grand Total | 176 | 8 | 20 | 485 | 371 | 1060

## Slot_Description
| Card | Slot Desc | IO_Type | Q'Ty
| 32DI | 1756-IB32 | IN | 20
| 32DO | 1756-OB32 | OUT | 10
| 16AI | 1756-IF16 | IN | 10
| 8AO | 1756-OF8 | IOUT | 10
| CPU | 1756-L950TPSXT | CPU
| Empty | 1756-N2 | EMPTY
| Reserve | Reserve
Column1 | Rack | Slot | Card | Card Description | Signal Type
| C1 | 1 | CPU |  |  | Row Labels | Count of Slot
| C1 | 2 | Reserve |  |  | 16AI | 11
| C1 | 3 | 32DI |  |  | 1756-IF16 | 11
| C1 | 4 | 32DI |  |  | 32DI | 17
| C1 | 5 | 32DI |  |  | 1756-IB32 | 17
| C1 | 6 | 32DI |  |  | 32DO | 13
| C1 | 7 | 32DO |  |  | 1756-OB32 | 13
| C1 | 8 | 32DO |  |  | 8AO | 1
| C1 | 9 | 16AI |  |  | 1756-OF8 | 1
| C1 | 10 | 16AI |  |  | CPU | 1
| C1 | 11 | Empty |  |  | 1756-L950TPSXT | 1
| C1 | 12 | Empty |  |  | Empty | 32
| C1 | 13 | Empty |  |  | 1756-N2 | 32
| C2 | 1 | 32DI |  |  | Reserve | 3
| C2 | 2 | 32DI |  |  | Reserve | 3
| C2 | 3 | 32DI |  |  | Grand Total | 78
| C2 | 4 | 32DI
| C2 | 5 | 32DI
| C2 | 6 | 32DO
| C2 | 7 | 32DO
| C2 | 8 | 32DO
| C2 | 9 | 16AI
| C2 | 10 | 16AI
| C2 | 11 | 16AI
| C2 | 12 | 16AI
| C2 | 13 | 16AI
| C3 | 1 | 32DI
| C3 | 2 | 32DI
| C3 | 3 | 32DO
| C3 | 4 | 16AI
| C3 | 5 | 16AI
| C3 | 6 | Empty
| C3 | 7 | Empty
| C3 | 8 | Empty
| C3 | 9 | Empty
| C3 | 10 | Empty
| C3 | 11 | Empty
| C3 | 12 | Empty
| C3 | 13 | 8AO
| C4 | 1 | 32DI
| C4 | 2 | 32DI
| C4 | 3 | 32DI
| C4 | 4 | 32DO
| C4 | 5 | 16AI
| C4 | 6 | 16AI
| C4 | 7 | Empty
| C4 | 8 | Empty
| C4 | 9 | Empty
| C4 | 10 | Empty
| C4 | 11 | Empty
| C4 | 12 | Empty
| C4 | 13 | Empty
| C5 | 1 | 32DI
| C5 | 2 | 32DI
| C5 | 3 | 32DO
| C5 | 4 | 16AI
| C5 | 5 | 32DO
| C5 | 6 | 32DI
| C5 | 7 | Empty
| C5 | 8 | Empty
| C5 | 9 | Empty
| C5 | 10 | Empty
| C5 | 11 | Empty
| C5 | 12 | Empty
| C5 | 13 | Empty
| Cx | 1 | 32DI
| Cx | 2 | 32DI
| Cx | 3 | 32DI
| Cx | 4 | 32DI
| Cx | 5 | 32DO
| Cx | 6 | 32DO
| Cx | 7 | 32DO
| Cx | 8 | Empty
| Cx | 9 | Empty
| Cx | 10 | Empty
| Cx | 11 | Empty
| Cx | 12 | Empty
| Cx | 13 | Empty

## IO List
Reference Designation | Destination | Column7 | Column5 | Column52 | Terminal | Column6 | Terminal Label | Junction Box Location | Master Zone | Zone | Instruement Tag | Instruement_Description | Floor | P&ID No. 3.3 | P&ID No. 3.5 | Control Description | Column1 | Require IO | Column2 | PLC_Tag | I/O Type | IO_ID | IO-Point (Instruement) | Column23 | Column22 | Column3 | Card | Signal Type | Column4 | Column332 | Chassis | Slot | Point | Terminal2 | DI | DO | AI | AO | Bus | Bus Address | Signal Type2
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | AT-40201 |  | 3rd | - | - | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 0 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | AT-40202 |  | 3rd | - | - | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 1 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | AT-40203 |  | 3rd | - | - | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 2 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | AT-60241 |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 0 |  | 0 | 0 | 1 | 0 | 0
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | ATY-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | ATY-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 1 | 8 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | ATY-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 2 | [7 empty] | C7 | 1 | 9 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | ATY-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 3 | [7 empty] | C7 | 1 | 10 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | ATY-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 8 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | ATY-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | ATY-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 1 | 11 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | ATY-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 2 | [7 empty] | C7 | 1 | 12 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | ATY-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 3 | [7 empty] | C7 | 1 | 13 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | ATY-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 9 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | Infeed Tank | ATY-40203 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-401 | Infeed Tank | ATY-40203 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 1 | 14 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | Infeed Tank | ATY-40203 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | [5 empty] | DI |  | 2 | [7 empty] | C7 | 1 | 15 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | Infeed Tank | ATY-40203 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | [5 empty] | DI |  | 3 | [7 empty] | C7 | 1 | 16 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | Infeed Tank | ATY-40203 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 10 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | BFY-60206 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | BFY-60206 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 1 | 26 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | BFY-60206 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 14 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | BFY-60210 |  | 5th | 325-01-600-PD-03 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | BFY-60210 |  | 5th | 325-01-600-PD-03 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 11 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | BFY-60210 |  | 5th | 325-01-600-PD-03 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 30 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | BFY-60211 |  | 5th | 325-01-600-PD-03 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | BFY-60211 |  | 5th | 325-01-600-PD-03 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 12 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | BFY-60211 |  | 5th | 325-01-600-PD-03 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 31 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-607 | Spray Dryer | BFY-60220 |  | 7th | 325-01-600-PD-04 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-607 | Spray Dryer | BFY-60220 |  | 7th | 325-01-600-PD-04 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 17 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-607 | Spray Dryer | BFY-60220 |  | 7th | 325-01-600-PD-04 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 7 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | BFY-60240 |  | 5th | 325-01-600-PD-05 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | BFY-60240 |  | 5th | 325-01-600-PD-05 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 13 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | BFY-60240 |  | 5th | 325-01-600-PD-05 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 0 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-618 | Packing Tower | BFY-61301 |  | 8th | 325-01-613-PD-01 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-618 | Packing Tower | BFY-61301 |  | 8th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 8 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-618 | Packing Tower | BFY-61301 |  | 8th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 19 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-612 | Packing Tower | BFY-61302 |  | 2nd | 325-01-613-PD-05 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-612 | Packing Tower | BFY-61302 |  | 2nd | 325-01-613-PD-05 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 18 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-612 | Packing Tower | BFY-61302 |  | 2nd | 325-01-613-PD-05 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 10 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-618 | Packing Tower | BFY-61303 |  | 9th | 325-01-613-PD-01 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 1 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-618 | Packing Tower | BFY-61303 |  | 9th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 9 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-618 | Packing Tower | BFY-61303 |  | 9th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 20 |  | 1 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-618 | Packing Tower | BLM-61302 |  | 5th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 10 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | BLM-61302 |  | 5th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 3 | 11 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | BLM-61302 |  | 5th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 21 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | BLM-61302 |  | 5th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 6 | 22 |  | 2 | 2 | 0 | 0 | 0
MCC | JB-607 | [7 empty] | JB-607 | Spray Dryer | COM-FH-60210B |  | 7th | 325-01-600-PD-06 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 0 | 0 | 0 | 0 | 1 |  | BUS
MCC | JB-612 | [7 empty] | JB-612 | Packing Tower | Communication Signal |  | 1st | 325-01-613-PD-02 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 0 | 0 | 0 | 0 | 1 |  | BUS
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | DPI-60240 |  | 1st | 325-01-600-PD-05 | - |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 10 | 0 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | DPT-60201 |  | 6th | 325-01-600-PD-09 | 3-25-01-602-PD-09 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 5 | 0 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | DPT-60202 |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 10 | 1 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | DPT-60203 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 1 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | DPT-61301 |  | 8th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 5 | 4 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | DPT-61302 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 5 | 5 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | DPT-61310 |  | 2nd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 6 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | DPT-61312 |  | 2nd | 325-01-613-PD-05 | 3-25-01-613-PD-05 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 6 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | DV-61301 |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C3 | 1 | 16 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | DV-61301 |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C3 | 1 | 17 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | DV-61301 |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C3 | 3 | 0 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | DV-61302 |  | 9th | - | 3-25-01-613-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C3 | 1 | 18 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | DV-61302 |  | 9th | - | 3-25-01-613-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C3 | 1 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | DV-61302 |  | 9th | - | 3-25-01-613-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C3 | 3 | 1 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | ES-60202 |  | 1st | 325-01-600-PD-01 | - |  | x |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 5 | 16 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Boiler System | EXT-BIILER |  | 1st |  | External Remote Setpoint | [5 empty] | AI |  | 1 | [7 empty] | C5 | 4 | 0 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | FS-20201 |  | 1st | - | 3-25-01-202-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 0 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | FS-40204 |  | 2nd | - | 325-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 0 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | FS-40205 |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 1 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | FS-60205 |  | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 |  | x |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 5 | 17 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | FSL-40201 |  | 1st | - | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 3 | 16 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | FSL-40202 |  | 1st | - | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 3 | 17 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | Infeed Tank | FT-40201 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 9 | 0 |  | 1 | 0 | 2 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | Infeed Tank | FT-40201 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | AI |  | 2 | [5 empty] | x |  | C1 | 9 | 1 |  | 1 | 0 | 2 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | FT-40201 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 3 | 18 |  | 1 | 0 | 2 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | Infeed Tank | FT-40202 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 9 | 2 |  | 1 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | FT-40202 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 3 | 19 |  | 1 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | FT-40221 |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 2 |  | 1 | 0 | 2 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | FT-40221 |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 9 | 0 |  | 1 | 0 | 2 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | FT-40221 |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | AI |  | 2 | [7 empty] | C2 | 9 | 1 |  | 1 | 0 | 2 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | FT-40222 |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 3 |  | 1 | 0 | 2 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | FT-40222 |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 9 | 2 |  | 1 | 0 | 2 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | FT-40222 |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | AI |  | 2 | [7 empty] | C2 | 9 | 3 |  | 1 | 0 | 2 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | FT-60201 |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 10 | 2 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | FT-60202 |  | 5th | 325-01-600-PD-09 | 3-25-01-602-PD-09 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 0 |  | 1 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | FT-60202 |  | 5th | 325-01-600-PD-09 | 3-25-01-602-PD-09 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 2 |  | 1 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | FT-60203 |  | 6th | 325-01-600-PD-09 | 3-25-01-602-PD-09 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 1 | 0 |  | 1 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | FT-60203 |  | 6th | 325-01-600-PD-09 | 3-25-01-602-PD-09 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 5 | 1 |  | 1 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | FT-60204 |  | 1st | 325-01-600-PD-10 | 3-25-01-602-PD-10 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 10 | 3 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60207 |  | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 0 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | FT-60210 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 11 | 9 |  | 0 | 0 | 2 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | FT-60210 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 2 | [7 empty] | C2 | 11 | 11 |  | 0 | 0 | 2 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | FT-60211 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 11 | 10 |  | 0 | 0 | 2 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | FT-60211 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 2 | [7 empty] | C2 | 11 | 12 |  | 0 | 0 | 2 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60221 |  | 7th | 325-01-600-PD-04 | 3-25-01-602-PD-04 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 1 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60261FA |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 2 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60261FB |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 3 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60261FC |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 4 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60261FD |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 5 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60262FE |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60262FF |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60262FG |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 8 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60262FH |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60263FJ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60263FK |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60263FL |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60263FM |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60264FN |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60264FP |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 12 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60264FQ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 13 | 0 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | FT-60264FR |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 13 | 1 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | FT-61307 |  | 1st | - | 3-25-01-613-PD-04 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 10 | 4 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | FT-913201 |  | 1st | 325-01-803-PD-02 | 3-25-01-913-PD-02 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 1 |  | 1 | 0 | 2 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | FT-913201 |  | 1st | 325-01-803-PD-02 | 3-25-01-913-PD-02 | [5 empty] | AI |  | 1 | [7 empty] | C5 | 4 | 1 |  | 1 | 0 | 2 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | FT-913201 |  | 1st | 325-01-803-PD-02 | 3-25-01-913-PD-02 | [5 empty] | AI |  | 2 | [7 empty] | C5 | 4 | 2 |  | 1 | 0 | 2 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Process Water | FT-936201 |  | 1st | 325-01-930-PD-01 | 3-25-01-930-PD-08 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 2 |  | 1 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Process Water | FT-936201 |  | 1st | 325-01-930-PD-01 | 3-25-01-930-PD-08 | [5 empty] | AI |  | 1 | [7 empty] | C5 | 4 | 3 |  | 1 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Process Water | FT-936202 |  | 1st | 325-01-930-PD-02 | 3-25-01-930-PD-07 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 3 |  | 1 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Process Water | FT-936202 |  | 1st | 325-01-930-PD-02 | 3-25-01-930-PD-07 | [5 empty] | AI |  | 1 | [7 empty] | C5 | 4 | 4 |  | 1 | 0 | 1 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | HS-61307A |  | 8th | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 12 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | HS-61307B |  | 8th | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 13 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | HS-61307C |  | 7th | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 14 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | HS-61307D |  | 5th | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 15 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | HS-61307E |  | 5th | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 16 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | HS-61307F |  | 4th | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 19 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | HS-61307G |  | 3rd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 20 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | HS-61307H |  | 3rd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 21 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | HS-61307I |  | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 22 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | HS-61307J |  | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 23 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | HS-61307K |  | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 24 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | HS-61307L |  | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 25 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | HS-61307M |  | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 26 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | HS-61307N |  | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 27 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | HS-61307O |  | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 28 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | HS-61307P |  | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 29 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | HS-61307Q |  | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 30 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | HS-61307R |  | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | HV-20204 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | HV-20205 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | HV-20206 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | HV-20207 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | HV-20208 |  | 1st | 325-01-200-PD-02 | 3-25-01-202-PD-02 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | HV-20209 |  | 1st | 325-01-200-PD-02 | 3-25-01-202-PD-02 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | HV-20210 |  | 1st | 325-01-200-PD-02 | 3-25-01-202-PD-02 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | HV-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 3 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | HV-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 3 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | HV-40203 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 3 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | HV-40204 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 3 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | HV-40205 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 3 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | HV-40206 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 3 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | HV-40207 |  | 2nd | - | 325-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | HV-40208 |  | 2nd | - | 325-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | ISV-61301 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 0 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | ISV-61303 |  | 2nd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 0 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | ISV-61304 |  | 2nd | 325-01-613-PD-05 | 3-25-01-613-PD-05 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 1 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | LS-61303 |  | 7th | - | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | LSH-60230 |  | 1st | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 3 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | LSH-60231 |  | 1st | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | LSH-60240 |  | 1st | 325-01-600-PD-05 | 3-25-01-602-PD-05 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | LSH-60250 |  | 6th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 1 | 1 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | LSH-60251 |  | 4th | 325-01-600-PD-04 | 3-25-01-602-PD-04 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 1 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | LSH-61301 |  | 7th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 1 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | LSH-61303 |  | 7th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 2 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | LSH-61304 |  | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 2 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | LSH-61305 |  | 1st | 325-01-613-PD-05 | 3-25-01-613-PD-05 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 3 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | LSH-61306 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 3 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | LSH-61307 |  | 1st | - | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | LSH-61308 |  | 8th | - | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | LSH-61312 |  | 2nd | 325-01-613-PD-05 | 3-25-01-613-PD-05 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | LSL-60201 |  | 1st | 325-01-600-PD-11 | 3-25-01-602-PD-11 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 5 | 18 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | LSL-61302 |  | 6th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | CIP Water System | LSL-814201 |  | 1st | - | 3-25-01-814-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | LT-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 9 | 4 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | LT-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 9 | 5 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | Infeed Tank | LT-40203 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 9 | 3 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | LT-61301 |  | 8th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 5 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | LT-913201 |  | 1st | 325-01-803-PD-01 | 3-25-01-913-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C5 | 4 | 5 |  | 0 | 0 | 1 | 0 | 0
MCC | MCC | [7 empty] | RIO-200 | Slurry - Out Building | PCM-2030 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C6 | 5 | 0 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | RIO-200 | Slurry - Out Building | PCM-2030 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DO |  | 2 | [7 empty] | C6 | 5 | 1 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | RIO-200 | Slurry - Out Building | PCM-2030 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C6 | 6 | 0 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | RIO-200 | Slurry - Out Building | PCM-2030 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C6 | 6 | 1 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | RIO-200 | Slurry - Out Building | PCM-2031 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C6 | 5 | 2 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | RIO-200 | Slurry - Out Building | PCM-2031 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DO |  | 2 | [7 empty] | C6 | 5 | 3 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | RIO-200 | Slurry - Out Building | PCM-2031 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C6 | 6 | 2 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | RIO-200 | Slurry - Out Building | PCM-2031 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C6 | 6 | 3 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-2 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 1 | 27 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-2 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 1 | 28 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-2 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 15 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-2 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 5 | 16 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-3 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 1 | 29 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-3 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 1 | 30 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-3 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 17 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-3 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 5 | 18 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-4 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 1 | 31 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-4 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 2 | 0 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-4 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 19 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-4 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 5 | 20 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-5 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 1 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-5 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 2 | 2 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-5 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 21 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | PCM-60205-5 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 5 | 22 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | PCY-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | PCY-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 1 | 17 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | PCY-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 2 | [7 empty] | C7 | 1 | 18 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | PCY-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 3 | [7 empty] | C7 | 1 | 19 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | PCY-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 11 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | PCY-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | PCY-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 1 | 20 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | PCY-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 2 | [7 empty] | C7 | 1 | 21 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | PCY-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 3 | [7 empty] | C7 | 1 | 22 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | PCY-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 12 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | Infeed Tank | PCY-40203 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-401 | Infeed Tank | PCY-40203 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | [5 empty] | DI |  | 1 | [7 empty] | C7 | 1 | 23 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | Infeed Tank | PCY-40203 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | [5 empty] | DI |  | 2 | [7 empty] | C7 | 1 | 24 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | Infeed Tank | PCY-40203 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | [5 empty] | DI |  | 3 | [7 empty] | C7 | 1 | 25 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-401 | Infeed Tank | PCY-40203 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 13 |  | 3 | 1 | 0 | 0 | 1
MCC | JB-601 | [7 empty] | JB-601 | Spray Dryer | PCY-60205 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | JB-601 | [7 empty] | JB-601 | Spray Dryer | PCY-60205 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 3 |  | 3 | 1 | 0 | 0 | 1
MCC | JB-601 | [7 empty] | JB-601 | Spray Dryer | PCY-60205 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 2 | 4 |  | 3 | 1 | 0 | 0 | 1
MCC | JB-601 | [7 empty] | MCC | Spray Dryer | PCY-60205 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DI |  | 3 | [7 empty] | C7 | 3 | 25 |  | 3 | 1 | 0 | 0 | 1
MCC | JB-601 | [7 empty] | MCC | Spray Dryer | PCY-60205 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 31 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | PCY-60215 |  | 5th | 325-01-600-PD-03 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | PCY-60215 |  | 5th | 325-01-600-PD-03 | - | [5 empty] | DI | [9 empty] | C7 | 2 | 14 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | PCY-60215 |  | 5th | 325-01-600-PD-03 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 2 | 15 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | PCY-60215 |  | 5th | 325-01-600-PD-03 | - | [5 empty] | DI |  | 3 | [7 empty] | C7 | 2 | 16 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | PCY-60215 |  | 5th | 325-01-600-PD-03 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 1 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | RIO-200 | CIP Water System | PCY-814201 |  | 2nd | 3-25-01-810-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C6 | 5 | 4 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | RIO-200 | CIP Water System | PCY-814201 |  | 2nd | 3-25-01-810-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C6 | 6 | 4 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | RIO-200 | CIP Water System | PCY-814201 |  | 2nd | 3-25-01-810-PD-01 | - | [5 empty] | DI |  | 2 | [7 empty] | C6 | 6 | 5 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | RIO-200 | CIP Water System | PCY-814201 |  | 2nd | 3-25-01-810-PD-01 | - | [5 empty] | DI |  | 3 | [7 empty] | C6 | 6 | 6 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | RIO-200 | CIP Water System | PCY-814201 |  | 2nd | 3-25-01-810-PD-01 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
MCC | MCC | [7 empty] | RIO-200 | CIP Water System | PCY-814202 |  | 2nd | 3-25-01-810-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C6 | 5 | 5 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | RIO-200 | CIP Water System | PCY-814202 |  | 2nd | 3-25-01-810-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C6 | 6 | 7 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | RIO-200 | CIP Water System | PCY-814202 |  | 2nd | 3-25-01-810-PD-01 | - | [5 empty] | DI |  | 2 | [7 empty] | C6 | 6 | 8 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | RIO-200 | CIP Water System | PCY-814202 |  | 2nd | 3-25-01-810-PD-01 | - | [5 empty] | DI |  | 3 | [7 empty] | C6 | 6 | 9 |  | 3 | 1 | 0 | 0 | 1
MCC | MCC | [7 empty] | RIO-200 | CIP Water System | PCY-814202 |  | 2nd | 3-25-01-810-PD-01 | - | [5 empty] | BUS |  | 1 | [7 empty] | C7 | 0 | 0 |  | 3 | 1 | 0 | 0 | 1 |  | BUS
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | PD-60202 |  | 3rd | - | - | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | pHT-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 9 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | pHT-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 9 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | PK-913201 |  | 1st | - | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | PK-913202 |  | 1st | - | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | PSE-61300 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | PSE-61301 |  | 8th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | PSE-61302 |  | 2nd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | PSE-61303 |  | 2nd | 325-01-613-PD-05 | 3-25-01-613-PD-05 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | PSE-61304 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | PSL-60220 |  | 5th | 325-01-600-PD-04 | 3-25-01-602-PD-04 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 2 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | PSL-61301 |  | 5th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | PSL-61302 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | PSL-61305 |  | 1st | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 2 | 0 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | PSL-61306 |  | 1st | 325-01-613-PD-05 | 3-25-01-613-PD-05 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 2 | 1 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | PSL-61311 |  | 8th | 325-01-613-PD-04 | 3-25-01-613-PD-04 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | PSV-61301A |  | 8th | 325-01-613-PD-01 | 325-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | PSV-61301B |  | 8th | 325-01-613-PD-01 | 325-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | Infeed Tank | PT-40201 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 9 | 8 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | Infeed Tank | PT-40202 |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 9 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | PT-40222 |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 9 | 4 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | PT-60201 |  | 7th | - | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 13 | 2 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | Infeed Tank | PT-60202 |  | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 9 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | PT-60203 |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 10 | 5 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | PT-60204 |  | 1st | 325-01-600-PD-10 | 3-25-01-602-PD-10 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 10 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | PT-60205 |  | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 |  | x |  | xx |  | AI |  | 1 | [5 empty] | x |  | C1 | 10 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | PT-60207 |  | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 13 | 3 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | PT-60210 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 3 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | PT-60215 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 4 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | PT-60216 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 5 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 |  |  |  |  | JB-608 | Spray Dryer | PT-60220 |  | 6th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 6 | 0 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | PT-60221 |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-04 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 13 | 4 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | PT-60221 |  | 7th | 325-01-600-PD-04 | 3-25-01-602-PD-04 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 13 | 5 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | PT-60230 |  | 4th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 4 | 0 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | PT-60231 |  | 4th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 4 | 1 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | PT-60240 |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | PT-60241 |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | PT-61301 |  | 8th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 5 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | PT-61302 |  | 2nd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 5 | 8 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | PT-61302 |  | 2nd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 5 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | PT-61303 |  | 8th | - | 3-25-01-613-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 5 | 0 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | PT-61303 |  | 8th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 5 | 8 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | PT-61304 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 5 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | PT-61305 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 5 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | PT-61306 |  | 8th | - | 3-25-01-613-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 5 | 1 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | PT-61309 |  | 1st | 325-01-613-PD-04 | 3-25-01-613-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 5 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | PT-61309 |  | 1st | 325-01-613-PD-04 | 3-25-01-613-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 5 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | PT-913201 |  | 1st | 325-01-803-PD-02 | 3-25-01-913-PD-02 | [5 empty] | AI |  | 1 | [7 empty] | C5 | 4 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | PV-60201 |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AO |  | 1 | [7 empty] | C3 | 13 | 3 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | PVM-61301 |  | 2nd | 325-01-613-PD-03 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C4 | 2 | 2 |  | 2 | 2 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | PVM-61301 |  | 2nd | 325-01-613-PD-03 | - |  |  |  | xx |  | DI |  | 2 | [7 empty] | C4 | 2 | 3 |  | 2 | 2 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | PVM-61301 |  | 2nd | 325-01-613-PD-03 | - |  |  |  | xx |  | DO |  | 1 | [7 empty] | C4 | 4 | 16 |  | 2 | 2 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | PVM-61301 |  | 2nd | 325-01-613-PD-03 | - |  |  |  | xx |  | DO |  | 2 | [7 empty] | C4 | 4 | 17 |  | 2 | 2 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | RV-60204 |  | 3rd | - | - | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | RV-61301 |  | 2nd | - | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | RV-61304 |  | 2nd | - | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | RV-61305 |  | 2nd | - | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 11 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | RVM-60201 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 5 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | RVM-60201 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 2 | 6 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | RVM-60201 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 23 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | RVM-60201 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 5 | 24 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | RVM-60202 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 7 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | RVM-60202 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 2 | 8 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | RVM-60202 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 25 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | RVM-60202 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 5 | 26 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | RVM-60203 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 2 | 9 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | RVM-60203 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 2 | 10 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | RVM-60203 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 27 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | RVM-60203 |  | 1st | 325-01-600-PD-08 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 5 | 28 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-60204 |  | 9th | 325-01-600-PD-08 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 17 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-60204 |  | 9th | 325-01-600-PD-08 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 3 | 18 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-60204 |  | 9th | 325-01-600-PD-08 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 23 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-60204 |  | 9th | 325-01-600-PD-08 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 6 | 24 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-61301 |  | 6th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 19 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-61301 |  | 6th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 3 | 20 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-61301 |  | 6th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 25 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-61301 |  | 6th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 6 | 26 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | RVM-61302 |  | 1st | 325-01-613-PD-03 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 0 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | RVM-61302 |  | 1st | 325-01-613-PD-03 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 3 | 1 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | RVM-61302 |  | 1st | 325-01-613-PD-03 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 11 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | RVM-61302 |  | 1st | 325-01-613-PD-03 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 6 | 12 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | RVM-61303 |  | 1st | 325-01-613-PD-05 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 2 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | RVM-61303 |  | 1st | 325-01-613-PD-05 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 3 | 3 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | RVM-61303 |  | 1st | 325-01-613-PD-05 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 13 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | RVM-61303 |  | 1st | 325-01-613-PD-05 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 6 | 14 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-61304 |  | 9th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 21 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-61304 |  | 9th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 3 | 22 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-61304 |  | 9th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 27 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-61304 |  | 9th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 6 | 28 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-61305 |  | 9th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 23 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-61305 |  | 9th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 3 | 24 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-61305 |  | 9th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 29 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-618 | Packing Tower | RVM-61305 |  | 9th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 6 | 30 |  | 2 | 2 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | SC-61301 |  | 2nd | - | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | SC-61302 |  | 2nd | - | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 13 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | SCM-61301 |  | 4th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 4 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | SCM-61301 |  | 4th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 3 | 5 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | SCM-61301 |  | 4th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 15 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | SCM-61301 |  | 4th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 6 | 16 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | SCM-61302 |  | 4th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 2 | [7 empty] | C7 | 3 | 6 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | SCM-61302 |  | 4th | 325-01-613-PD-01 | - | [5 empty] | DI |  | 1 | [7 empty] | C7 | 3 | 7 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | SCM-61302 |  | 4th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 17 |  | 2 | 2 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-612 | Packing Tower | SCM-61302 |  | 4th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 2 | [7 empty] | C7 | 6 | 18 |  | 2 | 2 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 0 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 1 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 2 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 3 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 |  |  |  |  | CA1 | Main Control Cabinet | Spare |  |  | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 3 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | AI |  | 0 | [5 empty] | x |  | C1 | 9 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | AI |  | 0 | [5 empty] | x |  | C1 | 9 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | AI |  | 0 | [5 empty] | x |  | C1 | 9 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | AI |  | 0 | [5 empty] | x |  | C1 | 9 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | AI |  | 0 | [5 empty] | x |  | C1 | 9 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 2 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 3 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 6 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 6 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 6 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 6 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 6 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 6 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 6 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 6 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | Spare |  | 1st | - | - |  |  |  | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 6 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 0 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 1 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 2 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 3 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 4 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 5 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 6 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 7 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 8 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 9 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 10 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 11 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 12 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 13 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 14 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | CA1 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 7 | 15 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [5 empty] | x |  | C1 | 5 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 8 | 8 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 8 | 9 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 8 | 10 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 8 | 28 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 8 | 29 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 8 | 30 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 8 | 31 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 8 | 11 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 8 | 12 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 8 | 13 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 8 | 14 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [5 empty] | x |  | C1 | 8 | 15 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | AI |  | 0 | [5 empty] | x |  | C1 | 10 | 8 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | AI |  | 0 | [5 empty] | x |  | C1 | 10 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | AI |  | 0 | [5 empty] | x |  | C1 | 10 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | AI |  | 0 | [5 empty] | x |  | C1 | 10 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | AI |  | 0 | [5 empty] | x |  | C1 | 10 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | AI |  | 0 | [5 empty] | x |  | C1 | 10 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | AI |  | 0 | [5 empty] | x |  | C1 | 10 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 |  | Spare | [7 empty] | xx |  | AI |  | 0 | [5 empty] | x |  | C1 | 10 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | Spare |  | 2nd | - | - | [5 empty] | DI |  | 2 | [7 empty] | C2 | 1 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | Spare |  | 2nd | - | - | [5 empty] | DI |  | 2 | [7 empty] | C2 | 1 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | Spare |  | 2nd | - | - | [5 empty] | DI |  | 2 | [7 empty] | C2 | 1 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | Spare |  | 2nd | - | - | [5 empty] | DI |  | 2 | [7 empty] | C2 | 1 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | Spare |  | 2nd | - | - | [5 empty] | DI |  | 2 | [7 empty] | C2 | 1 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | Spare |  | 2nd | - | - | [5 empty] | DI |  | 2 | [7 empty] | C2 | 1 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | Spare |  | 2nd | - | - | [5 empty] | DI |  | 2 | [7 empty] | C2 | 1 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | Spare |  | 2nd | - | - | [5 empty] | DI |  | 2 | [7 empty] | C2 | 1 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [7 empty] | C2 | 2 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [7 empty] | C2 | 2 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [7 empty] | C2 | 2 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [7 empty] | C2 | 2 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [7 empty] | C2 | 2 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [7 empty] | C2 | 2 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [7 empty] | C2 | 2 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [7 empty] | C2 | 2 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 |  | Spare | [7 empty] | xx |  | DI |  | 0 | [7 empty] | C2 | 2 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | Spare |  | - | - | - | [5 empty] | DI |  | 0 | [7 empty] | C2 | 5 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | Spare |  | - | - | - | [5 empty] | DI |  | 0 | [7 empty] | C2 | 5 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | Spare |  | - | - | - | [5 empty] | DI |  | 0 | [7 empty] | C2 | 5 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | Spare |  | - | - | - | [5 empty] | DI |  | 0 | [7 empty] | C2 | 5 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | Spare |  | - | - | - | [5 empty] | DI |  | 0 | [7 empty] | C2 | 5 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | Spare |  | - | - | - | [5 empty] | DI |  | 0 | [7 empty] | C2 | 5 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | Spare |  | - | - | - | [5 empty] | DI |  | 0 | [7 empty] | C2 | 5 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | Spare |  | - | - | - | [5 empty] | DI |  | 0 | [7 empty] | C2 | 5 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | Spare |  | - | - | - | [5 empty] | DI |  | 0 | [7 empty] | C2 | 5 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | Spare |  | - | - | - | [5 empty] | DI |  | 0 | [7 empty] | C2 | 5 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | Spare |  | - | - | - | [5 empty] | DI |  | 0 | [7 empty] | C2 | 5 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | Spare |  | - | - | - | [5 empty] | DI |  | 0 | [7 empty] | C2 | 5 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 9 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 10 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 11 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 12 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 13 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 14 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 |  | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 15 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 19 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 20 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 21 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 22 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 23 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 24 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 25 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 26 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 27 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 28 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 29 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 30 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 6 | 31 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 7 | 31 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 9 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 10 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 11 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 12 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 13 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 14 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 15 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 16 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 17 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 18 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 19 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 20 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 21 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 22 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 23 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 24 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 25 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 26 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 27 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 28 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 29 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 30 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 | [6 empty] | Spare | [7 empty] | xx |  | DO |  | 0 | [7 empty] | C2 | 8 | 31 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 9 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 9 | 8 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 9 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 9 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 9 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 9 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 9 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 9 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 9 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 11 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 11 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 11 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 13 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 13 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 13 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 13 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AI |  | 0 | [7 empty] | C2 | 13 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C3 | 1 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  |  | - | - | [5 empty] | DI |  | 0 | [7 empty] | C3 | 1 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  |  | - | - | [5 empty] | DI |  | 0 | [7 empty] | C3 | 1 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  |  | - | - | [5 empty] | DI |  | 0 | [7 empty] | C3 | 1 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  |  | - | - | [5 empty] | DI |  | 0 | [7 empty] | C3 | 1 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 16 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 17 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 18 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 19 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | Spare |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C3 | 2 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 9 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 10 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 11 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 12 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 13 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 14 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 15 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 16 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 17 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 18 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 19 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 20 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 21 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 22 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 23 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 24 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 25 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 26 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 27 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 28 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 29 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 30 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C3 | 3 | 31 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C3 | 4 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C3 | 4 | 8 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C3 | 4 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C3 | 4 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C3 | 4 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C3 | 4 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C3 | 4 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C3 | 4 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C3 | 4 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C3 | 5 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C3 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C3 | 5 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AO |  | 0 | [7 empty] | C3 | 13 | 5 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AO |  | 0 | [7 empty] | C3 | 13 | 6 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 | [6 empty] | Spare | [7 empty] | xx |  | AO |  | 0 | [7 empty] | C3 | 13 | 7 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 1 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 17 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 18 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 19 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 2 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 16 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 17 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 18 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 19 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C4 | 3 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 1
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 2
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 3
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 4
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 5
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 6
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 7
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 9
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 10
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 11
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 12
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 13
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 14
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 15
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | Spare | [9 empty] | DO |  | 0 | [7 empty] | C4 | 4 | 31
=CA1+MCP-M4 | JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 3 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 4 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 5 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C4 | 5 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 16 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 17 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 18 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 19 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 26 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 27 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 28 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 29 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 30 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C5 | 2 | 31 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 8 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 9 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 10 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 11 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 12 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 13 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 14 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 15 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 16 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 17 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 18 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 19 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 20 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 21 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 22 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 23 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 24 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 25 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 26 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 27 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 28 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 29 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 30 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 | [6 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C5 | 3 | 31 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | Spare |  | 1st | - | 3-25-01-913-PD-02 | [5 empty] | AI |  | 0 | [7 empty] | C5 | 4 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | Spare |  | 1st | - | 3-25-01-913-PD-02 | [5 empty] | AI |  | 0 | [7 empty] | C5 | 4 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | Spare |  | 1st | - | 3-25-01-913-PD-02 | [5 empty] | AI |  | 0 | [7 empty] | C5 | 4 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | Spare |  | 1st | - | 3-25-01-913-PD-02 | [5 empty] | AI |  | 0 | [7 empty] | C5 | 4 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | Spare |  | 1st | - | 3-25-01-913-PD-02 | [5 empty] | AI |  | 0 | [7 empty] | C5 | 4 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C5 | 4 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 | [6 empty] | Spare | [9 empty] | AI |  | 0 | [7 empty] | C5 | 4 | 15 |  | 0 | 0 | 1 | 0 | 0
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C7 | 1 | 0 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C7 | 1 | 1 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C7 | 1 | 2 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C7 | 1 | 3 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C7 | 1 | 4 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C7 | 1 | 5 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C7 | 1 | 6 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-401 | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DI |  | 0 | [7 empty] | C7 | 1 | 7 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 4 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 5 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 6 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 7 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 8 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 9 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 10 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 11 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 12 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 13 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 14 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 15 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 16 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 17 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 18 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 19 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 20 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 21 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 22 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 23 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 24 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 25 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 26 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 27 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 28 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 29 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 30 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DI |  | 0 | [7 empty] | C7 | 4 | 31 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DO |  | 0 | [7 empty] | C7 | 5 | 0 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DO |  | 0 | [7 empty] | C7 | 5 | 1 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DO |  | 0 | [7 empty] | C7 | 5 | 2 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DO |  | 0 | [7 empty] | C7 | 5 | 3 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DO |  | 0 | [7 empty] | C7 | 5 | 4 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DO |  | 0 | [7 empty] | C7 | 5 | 5 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DO |  | 0 | [7 empty] | C7 | 5 | 6 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | MCC | PH Adjustment | Spare |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DO |  | 0 | [7 empty] | C7 | 5 | 7 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 8 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 9 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 10 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 11 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 12 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 13 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 14 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 15 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 16 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 17 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 18 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 19 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 20 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 21 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 22 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 23 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 24 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 25 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 26 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 27 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 28 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 29 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 30 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [9 empty] | Spare | [9 empty] | DO |  | 0 | [7 empty] | C7 | 7 | 31 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | SV-40201 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 24 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | SV-40202 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 25 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | SV-40203 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 26 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | SV-40204 |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 27 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60201 |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 5 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60201 |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 5 | 20 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60201 |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 16 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60202 |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 5 | 21 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60202 |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 5 | 22 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60202 |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 17 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60203 |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 5 | 23 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60203 |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 5 | 24 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60203 |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-08 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | SV-60207 |  | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 8 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | SV-60207 |  | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 3 | 9 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | SV-60207 |  | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 0 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | SV-60220 |  | 6th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | DO |  | 1 | [7 empty] | C4 | 4 | 0 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60230 |  | 1st | 325-01-600-PD-04 | 3-25-01-602-PD-04 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 18 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60231 |  | 1st | 325-01-600-PD-04 | 3-25-01-602-PD-04 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 21 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60240A |  | 1st | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 20 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60240B |  | 1st | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 22 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | SV-60240C |  | 1st | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 23 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | SV-61301 |  | 8th | 325-01-613-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C3 | 3 | 2 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | SV-61302 |  | 7th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DO |  | 1 | [7 empty] | C3 | 3 | 3 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | SV-61303 |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DO |  | 1 | [7 empty] | C3 | 3 | 4 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | SV-61304 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C3 | 2 | 24 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | SV-61304 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C3 | 2 | 25 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | SV-61304 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C3 | 3 | 5 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | SV-61305 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DO |  | 1 | [7 empty] | C3 | 3 | 6 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | SV-61306 |  | 5th | - | 3-25-01-613-PD-01 | [5 empty] | DO |  | 1 | [7 empty] | C3 | 3 | 7 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | SV-61307 |  | 3rd | - | 3-25-01-613-PD-01 | [5 empty] | DO |  | 1 | [7 empty] | C4 | 4 | 18 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | SV-61308 |  | 2nd | 325-01-613-PD-03 | - | [5 empty] | DO |  | 1 | [7 empty] | C4 | 4 | 19 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | SV-61309 |  | 2nd | 325-01-613-PD-03 | 3-25-01-613-PD-03 | [5 empty] | DO |  | 1 | [7 empty] | C4 | 4 | 20 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | SV-61310 |  | 2nd | 325-01-613-PD-05 | - | [5 empty] | DO |  | 1 | [7 empty] | C4 | 4 | 21 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | SV-61311 |  | 1st | 325-01-613-PD-05 | 3-25-01-613-PD-05 | [5 empty] | DO |  | 1 | [7 empty] | C4 | 4 | 22 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | TCV-40222 |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | AO |  | 1 | [7 empty] | C3 | 13 | 0 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | TI-FH-60210 |  | 7th | 325-01-600-PD-06 | - |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 13 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TSH-60230 |  | 3rd | 325-01-600-PD-04 | 3-25-01-602-PD-04 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 3 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TSH-60240 |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TSH-60241A |  | 4th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TSH-60242A |  | 3rd | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TSH-60243A |  | 4th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TSL-60241B |  | 4th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TSL-60242B |  | 3rd | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TSL-60243B |  | 4th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | TT-40221 |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 9 | 5 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | TT-40222 |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 9 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | TT-60201 |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 13 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | TT-60202 |  | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 13 | 8 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | TT-60207 |  | 7th | 325-01-600-PD-07 | 3-25-01-602-PD-07 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 13 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TT-60210 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 8 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TT-60210A |  | 5th | 325-01-600-PD-03 | - |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 9 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TT-60210B |  | 5th | 325-01-600-PD-03 | - |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TT-60211 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TT-60212A |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TT-60212B |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 13 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TT-60214 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 14 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TT-60215A |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 10 | 15 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TT-60215B |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 11 | 0 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TT-60216 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 11 | 1 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 |  |  |  |  | JB-608 | Spray Dryer | TT-60220 |  | 6th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 6 | 1 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 |  |  |  |  | JB-608 | Spray Dryer | TT-60221 |  | 6th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 6 | 2 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 |  |  |  |  | JB-608 | Spray Dryer | TT-60222 |  | 5th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 6 | 3 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 |  |  |  |  | JB-608 | Spray Dryer | TT-60223 |  | 5th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 6 | 4 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | TT-60224 |  | 4th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 4 | 2 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | TT-60225 |  | 3rd | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 4 | 3 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | TT-60226 |  | 2nd | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 4 | 4 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | TT-60227 |  | 1st | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 4 | 5 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | TT-60230 |  | 3rd | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 4 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TT-60240 |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 11 | 2 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TT-60241A |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 11 | 3 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TT-60241B |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 11 | 4 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | JB-608 |  |  | X1 |  |  |  |  | JB-608 | Spray Dryer | TT-60245 |  | 8th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 5 | 2 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | TT-61301 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 5 | 11 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | TT-61302 |  | 9th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 5 | 12 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | TT-61303 |  | 8th | - | 3-25-01-613-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 5 | 2 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | TT-61304 |  | 8th | - | 3-25-01-613-PD-01 | [5 empty] | AI |  | 1 | [7 empty] | C3 | 5 | 3 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TV-60202 |  | 3rd | 325-01-600-PD-07 | 3-25-01-602-PD-07 |  |  |  | xx |  | AO |  | 1 | [7 empty] | C3 | 13 | 1 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | TV-60214 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AO |  | 1 | [7 empty] | C3 | 13 | 2 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | UY-FH-60210A |  | 7th | 325-01-600-PD-06 | - |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 13 | 10 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | UY-FH-60210B |  | 7th | 325-01-600-PD-06 | - |  |  |  | xx |  | AO |  | 1 | [7 empty] | C3 | 13 | 4 |  | 0 | 0 | 0 | 1 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | VS-60205 |  | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 5 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | VT-60210A |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 11 | 5 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | VT-60210B |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 11 | 6 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | VT-60241A |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 11 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | VT-60241B |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | AI |  | 1 | [7 empty] | C2 | 11 | 8 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 |  |  |  |  | JB-608 | Spray Dryer | XA-60201 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | [5 empty] | DO |  | 1 | [7 empty] | C4 | 4 | 8 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XA-60202A |  | 1st | 325-01-600-PD-08 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 0 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XA-60202B |  | 1st | 325-01-600-PD-08 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 1 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XA-60202C |  | 1st | 325-01-600-PD-08 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 2 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XA-60202D |  | 1st | 325-01-600-PD-08 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 3 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XA-60202E |  | 1st | 325-01-600-PD-08 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XA-60202F |  | 1st | 325-01-600-PD-08 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XA-60202G |  | 1st | 325-01-600-PD-08 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XA-60202H |  | 1st | 325-01-600-PD-08 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XA-60202I |  | 1st | 325-01-600-PD-08 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XA-60202J |  | 1st | 325-01-600-PD-08 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XA-60202K |  | 1st | 325-01-600-PD-08 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XA-60202L |  | 1st | 325-01-600-PD-08 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XA-60202M |  | 1st | 325-01-600-PD-08 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | XA-60240A |  | 4th | 325-01-600-PD-05 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | XA-60240B |  | 4th | 325-01-600-PD-05 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | XA-60241A |  | 4th | 325-01-600-PD-05 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | XA-60241B |  | 4th | 325-01-600-PD-05 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X1 |  |  |  |  | JB-602 | Spray Dryer | XA-60242A |  | 3rd | 325-01-600-PD-05 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | XA-60242B |  | 3rd | 325-01-600-PD-05 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 16 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | XA-60243A |  | 4th | 325-01-600-PD-05 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 17 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | XA-60243B |  | 4th | 325-01-600-PD-05 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 18 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | XA-60261 |  | 6th | 325-01-600-PD-05 | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 1 | 2 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-606 |  |  | X1 |  |  |  |  | JB-606 | Spray Dryer | XA-60262 |  | 6th | 325-01-600-PD-05 | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 1 | 3 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | XA-61301A |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 2 | 4 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | XA-61301B |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 2 | 5 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | XA-61301C |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 2 | 6 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | XA-61301D |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 2 | 7 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | XA-61301E |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 2 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | XA-61301F |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 2 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | XA-61301G |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 2 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | XA-61301H |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 2 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | XA-61301J |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C4 | 2 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | XA-80305A |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | XA-80305B |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 15 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | LPG System | XA-80305C |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 16 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | LPG System | XA-80305D |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 17 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | LPG System | XA-80305E |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 18 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | LPG System | XA-80305F |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 19 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | LPG System | XA-80306A |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | LPG System | XA-80306B |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | LPG System | XA-80306C |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | LPG System | XA-80306D |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 23 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | LPG System | XA-80306E |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 24 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | LPG System | XA-80306F |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DI |  | 1 | [7 empty] | C5 | 1 | 25 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Boiler System | XA-92201 |  | 1st | 325-01-923-PD-03 | 3-25-01-922-PD-03 | [5 empty] | DO |  | 1 | [7 empty] | C5 | 3 | 0 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XA-FH-60210A |  | 7th | 325-01-600-PD-06 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 0 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XA-FH-60210B |  | 7th | 325-01-600-PD-06 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 1 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XA-FH-60210C |  | 7th | 325-01-600-PD-06 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 2 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XA-FH-60210D |  | 7th | 325-01-600-PD-06 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 3 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XA-FH-60210E |  | 7th | 325-01-600-PD-06 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 4 |  | 1 | 0 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-601 | Spray Dryer | XS-60205 |  | 1st | 325-01-600-PD-01 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 5 | 29 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | XS-60240A |  | 4th | 325-01-600-PD-05 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 2 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | XS-60240B |  | 4th | 325-01-600-PD-05 | - |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 6 | 16 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | XS-60241A |  | 4th | 325-01-600-PD-05 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 3 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | XS-60242A |  | 3rd | 325-01-600-PD-05 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 4 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-602 | Spray Dryer | XS-60243A |  | 4th | 325-01-600-PD-05 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 4 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-606 | Spray Dryer | XS-60260 |  | 6th | 325-01-600-PD-05 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 6 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | XS-61301A |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DO |  | 1 | [7 empty] | C4 | 4 | 23 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | XS-61301B |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DO |  | 1 | [7 empty] | C4 | 4 | 24 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | XS-61301C |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DO |  | 1 | [7 empty] | C4 | 4 | 25 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | XS-61301D |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DO |  | 1 | [7 empty] | C4 | 4 | 26 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | XS-61301E |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DO |  | 1 | [7 empty] | C4 | 4 | 27 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | XS-61301F |  | 1st | 325-01-613-PD-02 | - | [5 empty] | DO |  | 1 | [7 empty] | C4 | 4 | 28 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | RIO-200 | LPG System | XS-80305 |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DO |  | 1 | [7 empty] | C6 | 5 | 6 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | RIO-200 | LPG System | XS-80306 |  | 1st | 325-01-803-PD-02 | - | [5 empty] | DO |  | 1 | [7 empty] | C6 | 5 | 7 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-607 | Spray Dryer | XS-FH-60210A |  | 7th | 325-01-600-PD-06 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 8 |  | 0 | 1 | 0 | 0 | 0
MCC | MCC | [7 empty] | JB-607 | Spray Dryer | XS-FH-60210B |  | 7th | 325-01-600-PD-06 | - | [5 empty] | DO |  | 1 | [7 empty] | C7 | 6 | 9 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XS-FH-60210C |  | 7th | 325-01-600-PD-06 | - |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 1 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XS-FH-60210D |  | 7th | 325-01-600-PD-06 | - |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 2 |  | 0 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X1 |  |  |  |  | JB-608 | Spray Dryer | XT-60201 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 | [5 empty] | AI |  | 1 | [7 empty] | C4 | 6 | 5 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Boiler System | XT-92201 |  | 1st | 325-01-923-PD-03 | 3-25-01-922-PD-03 | [5 empty] | AI |  | 1 | [7 empty] | C5 | 4 | 7 |  | 0 | 0 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20201 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C5 | 1 | 26 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20201 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C5 | 1 | 27 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20201 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C5 | 3 | 1 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20202 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C5 | 1 | 28 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20202 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C5 | 1 | 29 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20202 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C5 | 3 | 2 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20203 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C5 | 1 | 30 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X2 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20203 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C5 | 1 | 31 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20203 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C5 | 3 | 3 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20211 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C5 | 2 | 0 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20211 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C5 | 2 | 1 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20211 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C5 | 3 | 4 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20212 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C5 | 2 | 2 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20212 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C5 | 2 | 3 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20212 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C5 | 3 | 5 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20213 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C5 | 2 | 4 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20213 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C5 | 2 | 5 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | Slurry - Out Building | XV-20213 |  | 1st | 325-01-200-PD-01 | 3-25-01-202-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C5 | 3 | 6 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40201A |  | 1st | - | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 3 | 26 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40201A |  | 1st | - | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 3 | 27 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40201A |  | 1st | - | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 28 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40201B |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 3 | 28 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40201B |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 3 | 29 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40201B |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 29 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40201C |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 3 | 30 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40201C |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 3 | 31 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40201C |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 30 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201D |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 0 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201D |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 1 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40201D |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 31 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201E |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 2 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201E |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 3 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201E |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 0 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201F |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 4 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201F |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 5 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201F |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 1 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201G |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 6 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201G |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 7 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201G |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 2 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201H |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 8 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201H |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 9 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40201H |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 3 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202A |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40202A |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 11 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40202A |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 4 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40202B |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 12 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40202B |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 13 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40202B |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 5 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40202C |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 14 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40202C |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 15 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40202C |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 6 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202D |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 16 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202D |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 17 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | PH Adjustment | XV-40202D |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 7 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202E |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 18 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202E |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202E |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 | [5 empty] | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 16 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202F |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 20 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202F |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 21 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202F |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 17 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202G |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 22 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202G |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 23 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202G |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 18 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202H |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 24 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202H |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 25 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | PH Adjustment | XV-40202H |  | 1st | 325-01-400-PD-01 | 3-25-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | XV-40203B |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 26 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | XV-40203B |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 27 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | XV-40203B |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 20 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | XV-40203C |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 28 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | XV-40203C |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 29 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | XV-40203C |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 21 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | XV-40203D |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 4 | 30 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | XV-40203D |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 4 | 31 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | XV-40203D |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 22 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | Infeed Tank | XV-40203E |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 5 | 0 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X1 |  |  |  |  | JB-401 | Infeed Tank | XV-40203E |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 5 | 1 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-401 |  |  | X2 |  |  |  |  | JB-401 | Infeed Tank | XV-40203E |  | 1st | 325-01-400-PD-02 | 3-25-01-402-PD-02 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 7 | 23 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40203F |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 6 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40203F |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 1 | 7 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40203F |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 6 | 0 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40204B |  | 2nd | - | 325-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 8 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40204B |  | 2nd | - | 325-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 1 | 9 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40204B |  | 2nd | - | 325-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 6 | 1 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40204C |  | 2nd | - | 325-01-402-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 10 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40204C |  | 2nd | - | 325-01-402-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 1 | 11 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40204C |  | 2nd | - | 325-01-402-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 6 | 2 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40205A |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 12 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40205A |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 1 | 13 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40205A |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 6 | 3 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40205B |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 14 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40205B |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 1 | 15 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40205B |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 6 | 4 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | XV-40205C |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 16 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | XV-40205C |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 1 | 17 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40205C |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 6 | 5 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | XV-40205D |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 18 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | XV-40205D |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 1 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40205D |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 6 | 6 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | XV-40205F |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 20 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | XV-40205F |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 1 | 21 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40205F |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 6 | 7 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | XV-40222 |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 1 | 22 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X2 |  |  |  |  | JB-402 | Jet Cooker | XV-40222 |  | 2nd | - | - |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 1 | 23 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-402 |  |  | X1 |  |  |  |  | JB-402 | Jet Cooker | XV-40222 |  | 2nd | - | 325-01-402-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 6 | 8 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60201 |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 16 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60201 |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 3 | 17 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60201 |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 3 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XV-60202 |  | 1st | 325-01-600-PD-11 | 3-25-01-602-PD-11 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 13 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XV-60202 |  | 1st | 325-01-600-PD-11 | 3-25-01-602-PD-11 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 6 | 14 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | XV-60202 |  | 1st | 325-01-600-PD-11 | 3-25-01-602-PD-11 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 26 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X1 |  |  |  |  | JB-601 | Spray Dryer | XV-60205A |  | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 15 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | XV-60205A |  | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 6 | 16 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | XV-60205A |  | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 27 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | XV-60214 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | XV-60214 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 2 | 20 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | XV-60214 |  | 5th | 325-01-600-PD-03 | 3-25-01-602-PD-03 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 6 | 17 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | XV-60240D |  | 1st | 325-01-600-PD-05 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 17 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | XV-60240D |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-05 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 6 | 18 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | XV-60240D |  | 1st | 325-01-600-PD-05 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | XV-60240D |  | 1st | 325-01-600-PD-08 | 3-25-01-602-PD-05 |  |  |  | xx |  | DI |  | 2 | [5 empty] | x |  | C1 | 6 | 20 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | XV-60240D |  | 1st | 325-01-600-PD-05 | - |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 24 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | XV-60241 |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 2 | 21 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | XV-60241 |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 2 | 22 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-602 |  |  | X2 |  |  |  |  | JB-602 | Spray Dryer | XV-60241 |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 6 | 18 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Infeed Tank | XV-60251 |  | 1st | 325-01-600-PD-01 | 3-25-01-602-PD-01 |  |  |  | xx |  | DO |  | 1 | [5 empty] | x |  | C1 | 8 | 25 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60261 |  | 7th | 325-01-600-PD-02 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 20 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60261 |  | 7th | 325-01-600-PD-02 | - |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 3 | 21 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261 |  | 7th | 325-01-600-PD-02 | - |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 4 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60261FA |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 24 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60261FA |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 3 | 25 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261FA |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 5 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60261FB |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 28 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60261FB |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 3 | 29 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261FB |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 6 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261FC |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 0 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261FC |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 1 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261FC |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 7 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261FD |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 4 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261FD |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 5 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261FD |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 8 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261SA |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 8 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261SA |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 9 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261SA |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 9 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261SB |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 10 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261SB |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 11 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261SB |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 10 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261SC |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 12 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261SC |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 13 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261SC |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 11 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261SD |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 14 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261SD |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 15 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60261SD |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 12 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262 |  | 7th | 325-01-600-PD-02 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 16 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262 |  | 7th | 325-01-600-PD-02 | - |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 17 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60262 |  | 7th | 325-01-600-PD-02 | - |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 13 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262FE |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 18 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262FE |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60262FE |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 14 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262FF |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 20 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262FF |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 21 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60262FF |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 15 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262FG |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 22 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262FG |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 23 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262FG |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 16 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262FH |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 24 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262FH |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 25 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262FH |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 17 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262SE |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 26 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262SE |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 27 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262SE |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 18 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262SF |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 28 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262SF |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 29 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262SF |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262SG |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 30 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262SG |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 31 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262SG |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 20 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60262SH |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 5 | 0 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60262SH |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 5 | 1 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60262SH |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 21 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263 |  | 7th | 325-01-600-PD-02 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 5 | 2 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263 |  | 7th | 325-01-600-PD-02 | - |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 5 | 3 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60263 |  | 7th | 325-01-600-PD-02 | - |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 22 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263FJ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 5 | 4 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263FJ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 5 | 5 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60263FJ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 23 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263FK |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 5 | 6 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263FK |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 5 | 7 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60263FK |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 24 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263FL |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 5 | 8 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263FL |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 5 | 9 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60263FL |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 25 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263FM |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 5 | 10 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263FM |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 5 | 11 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60263FM |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 26 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263SJ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 5 | 12 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263SJ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 5 | 13 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60263SJ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 27 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263SK |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 5 | 14 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60263SK |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 5 | 15 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60263SK |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 28 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60263SL |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 5 | 16 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60263SL |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 5 | 17 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60263SL |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 29 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60263SM |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 5 | 18 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60263SM |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 5 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60263SM |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 7 | 30 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264 |  | 7th | 325-01-600-PD-02 | - |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 10 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264 |  | 7th | 325-01-600-PD-02 | - |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 3 | 11 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264 |  | 7th | 325-01-600-PD-02 | - |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 8 | 0 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264FN |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 12 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264FN |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 3 | 13 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264FN |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 8 | 1 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264FP |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 14 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264FP |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 3 | 15 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264FP |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 8 | 2 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60264FQ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 18 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60264FQ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 3 | 19 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264FQ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 8 | 3 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60264FR |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 22 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60264FR |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 3 | 23 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264FR |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 8 | 4 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60264SN |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 26 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60264SN |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 3 | 27 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264SN |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 8 | 5 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60264SP |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 3 | 30 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X2 |  |  |  |  | JB-607 | Spray Dryer | XV-60264SP |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 3 | 31 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264SP |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 8 | 6 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264SQ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 2 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264SQ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 3 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264SQ |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 8 | 7 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264SR |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C2 | 4 | 6 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264SR |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C2 | 4 | 7 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M2 | JB-607 |  |  | X1 |  |  |  |  | JB-607 | Spray Dryer | XV-60264SR |  | 7th | 325-01-600-PD-02 | 3-25-01-602-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C2 | 8 | 8 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | XV-61301 |  | 5th | - | 3-25-01-613-PD-01 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C3 | 2 | 26 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X2 |  |  |  |  | JB-618 | Packing Tower | XV-61301 |  | 5th | - | 3-25-01-613-PD-01 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C3 | 2 | 27 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M3 | JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | XV-61301 |  | 5th | - | 3-25-01-613-PD-01 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C3 | 3 | 8 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | XV-61302 |  | 2nd | 325-01-613-PD-02 | 3-25-01-613-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C4 | 2 | 13 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | XV-61302 |  | 2nd | 325-01-613-PD-02 | 3-25-01-613-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C4 | 2 | 14 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | XV-61302 |  | 2nd | 325-01-613-PD-02 | 3-25-01-613-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C4 | 4 | 29 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | XV-61303 |  | 2nd | 325-01-613-PD-02 | 3-25-01-613-PD-02 |  |  |  | xx |  | DI |  | 1 | [7 empty] | C4 | 2 | 15 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | XV-61303 |  | 2nd | 325-01-613-PD-02 | 3-25-01-613-PD-02 |  |  |  | xx |  | DI |  | 2 | [7 empty] | C4 | 2 | 16 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M4 | JB-612 |  |  | X2 |  |  |  |  | JB-612 | Packing Tower | XV-61303 |  | 2nd | 325-01-613-PD-02 | 3-25-01-613-PD-02 |  |  |  | xx |  | DO |  | 1 | [7 empty] | C4 | 4 | 30 |  | 2 | 1 | 0 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | XV-913201 |  | 1st | - | 3-25-01-913-PD-02 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 2 | 6 |  | 2 | 1 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | XV-913201 |  | 1st | - | 3-25-01-913-PD-02 | [5 empty] | DI |  | 1 | [7 empty] | C5 | 2 | 7 |  | 2 | 1 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | XV-913201 |  | 1st | - | 3-25-01-913-PD-02 | [5 empty] | DO |  | 1 | [7 empty] | C5 | 3 | 7 |  | 2 | 1 | 1 | 0 | 0
=CA1+MCP-M5 | RIO-200 |  |  | X1 |  |  |  |  | RIO-200 | LPG System | XV-913201 |  | 1st | - | 3-25-01-913-PD-02 | [5 empty] | AI |  | 1 | [7 empty] | C5 | 4 | 8 |  | 0 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | YA-60205 |  | 1st | 325-01-600-PD-01 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M1 | JB-601 |  |  | X2 |  |  |  |  | JB-601 | Spray Dryer | YI-60205 |  | 1st | 325-01-600-PD-01 | - |  |  |  | xx |  | DI |  | 1 | [5 empty] | x |  | C1 | 6 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 |  |  |  |  | JB-608 | Spray Dryer | ZS-60201A |  | 6th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 1 | 16 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 |  |  |  |  | JB-608 | Spray Dryer | ZS-60201B |  | 6th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 1 | 17 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | ZS-60201C |  | 4th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 8 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | ZS-60201D |  | 4th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 9 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | ZS-60201E |  | 1st | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 10 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | ZS-60229 |  | 4th | - | 3-25-01-602-PD-04 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | ZS-60230 |  | 4th | - | 3-25-01-602-PD-04 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | ZS-60231A |  | 4th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 13 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-603 |  |  | X1 |  |  |  |  | JB-603 | Spray Dryer | ZS-60231B |  | 4th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 1 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 |  |  |  |  | JB-608 | Spray Dryer | ZS-60231C |  | 5th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 1 | 18 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 |  |  |  |  | JB-608 | Spray Dryer | ZS-60231D |  | 5th | 325-01-600-PD-04 | 3-25-01-602-PD-04 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 1 | 19 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 |  |  |  |  | JB-608 | Spray Dryer | ZS-60231E |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 1 | 20 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 |  |  |  |  | JB-608 | Spray Dryer | ZS-60231F |  | 5th | 325-01-600-PD-05 | 3-25-01-602-PD-05 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 1 | 21 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-608 |  |  | X2 |  |  |  |  | JB-608 | Spray Dryer | ZS-60240 |  | 6th | - | 3-25-01-602-PD-05 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 1 | 22 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | ZS-61310 |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 11 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M3 | IS-JB-618 |  |  | X1 |  |  |  |  | JB-618 | Packing Tower | ZS-61311 |  | 5th | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C3 | 2 | 12 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | ZS-61312 |  | 3rd | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 14 |  | 1 | 0 | 0 | 0 | 0
=CA1+MCP-M4 | IS-JB-612 |  |  | X1 |  |  |  |  | JB-612 | Packing Tower | ZS-61313 |  | 3rd | 325-01-613-PD-01 | 3-25-01-613-PD-01 | [5 empty] | DI |  | 1 | [7 empty] | C4 | 3 | 15 |  | 1 | 0 | 0 | 0 | 0
Total | [37 empty] | 0

## Sheet2
Row Labels
C1
3
DI
4
DI
5
DI
6
DO
7
DO
8
DO
9
AI
10
AI
C2
1
DI
2
DI
3
DO
4
DO
5
DO
6
AI
7
AI
8
AI
9
AI
10
AI
11
AO
C3
1
DI
2
DI
3
DO
4
AI
5
AI
C4
1
DI
2
DI
3
DI
4
DO
5
AI
C5
1
DI
2
DI
3
DO
4
AI
5
DO
6
DI
C0
1
DI
2
DI
3
DI
4
DI
5
DO
6
DO
7
DO
0
BUS
Grand Total

## Junction Box Config
Junction Name | Junction Loc | Size | LS | JB | Rack 0
RIO-200 | Slurry - Out Building 2nd Floor | 800-1000-400 |  | Y |  | IB32
IS-JB-608 | Spray Dryer 8th Floor | 300-200-150 | Y
IS-JB-603 | Spray Dryer 3rd Floor | 300-200-150 | Y
IS-JB-618 | Packing Tower 8th Floor | 450-300-150 | Y
IS-JB-612 | Packing Tower 2th Floor | 300-200-150 | Y
JB-401 | Infeed 2nd Floor | 800-600-250 |  | Y
JB-402 | Jet Cooker 2nd Floor | 450-300-150 |  | Y
JB-601 | Spray Dryer 1st Floor | 500-400-200 |  | Y
JB-607 | Spray Dryer 7th Floor | 800-600-250 |  | Y
JB-602 | Spray Dryer 3rd Floor | 800-600-250 |  | Y
JB-606 | Spray Dryer 6th Floor | 300-200-150 |  | Y
JB-608 | Spray Dryer 8th Floor | 300-200-150 |  | Y
JB-618 | Packing Tower 8th Floor | 450-300-150 |  | Y
JB-612 | Packing Tower 2th Floor | 450-300-150 |  | Y
CA1 | Main Control Cabinet | 1600-2000-800
MCC | MCC Room
Total

## Sheet3
Column1 | Column2
I/O Type
DI | 1
DO | 2
AI | 3
AO | 4
BUS | 0
Rack | Chassis
0 | C1
1 | C2
2 | C3
3 | C4
4 | C5
5 | C6

## Sheet1
Part Number
1756-A13
1756-PA75

## Table 1
Ingredion (Thailand) Co., Ltd. |  |  | PROJECT JET COOKER | [8 empty] | AEC Industrial Engineering Co., Ltd.
INSTRUMENT I/O LIST
[12 empty] | DATE 29 JUNE 2026 |  |  | REV.
[12 empty] | DOC.NO. Instrument I/O List |  |  | 0
Item. | Tag. No. | P&ID No. | Description | Instrument | PLC Signal |  |  |  |  | Signal type | Signal to | Range | Cable Type | Type of Protection | Remark
|  |  |  | Name | DO | DI | AO | AI | Bus
MAIN PLC/ SCADA
1 | XV-40204B | 325-01-402-PD-01 | Slurry feed-out 2 pH Adjustment tank 1 | Automatic Valve on/off | 1 | 2 | - | - | - | 24VDC,Dry Contact | PLC |  | CVV 3Cx1.5 , CVV 4Cx1 | - | -
2 | XV-40204C | 325-01-402-PD-01 | Water washing line outlet 2 pH Adjustment tank 1 | Automatic Valve on/off | 1 | 2 | - | - | - | 24VDC,Dry Contact | PLC |  | CVV 3Cx1.5 , CVV 4Cx1 | - | -
3 | XV-40205A | 325-01-402-PD-02 | Slurry feed from jet to Feed Tank | Automatic Valve on/off | 1 | 2 | - | - | - | 24VDC,Dry Contact | PLC |  | CVV 3Cx1.5 , CVV 4Cx1 | - | -
4 | XV-40205B | 325-01-402-PD-02 | Slurry Feed Tank outlet 2 to PC-40205 | Automatic Valve on/off | 1 | 2 | - | - | - | 24VDC,Dry Contact | PLC |  | CVV 3Cx1.5 , CVV 4Cx1 | - | -
5 | XV-40205C | 325-01-402-PD-02 | Water washing line outlet 2 Feed Tank | Automatic Valve on/off | 1 | 2 | - | - | - | 24VDC,Dry Contact | PLC |  | CVV 3Cx1.5 , CVV 4Cx1 | - | -
6 | XV-40205D | 325-01-402-PD-02 | Slurry Feed CIP Spray ball | Automatic Valve on/off | 1 | 2 | - | - | - | 24VDC,Dry Contact | PLC |  | CVV 3Cx1.5 , CVV 4Cx1 | - | -
7 | XV-40205F | 325-01-402-PD-02 | Slurry from PC-40205 feed to high pressure pump | Automatic Valve on/off | 1 | 2 | - | - | - | 24VDC,Dry Contact | PLC |  | CVV 3Cx1.5 , CVV 4Cx1 | - | -
8 | XV-40203F | 325-01-402-PD-02 | Slurry from PC-40203 feed to high pressure pump | Automatic Valve on/off | 1 | 2 | - | - | - | 24VDC,Dry Contact | PLC |  | CVV 3Cx1.5 , CVV 4Cx1 | - | -
9 | XV-40222 | 325-01-402-PD-02 | Culinary steam feed to jet cooker | Automatic Valve on/off | 1 | 2 | - | - | - | 24VDC,Dry Contact | PLC |  | CVV 3Cx1.5 , CVV 4Cx1 | - | -
10 | HV-40207 | 325-01-402-PD-01 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC |  | CVV 4Cx1 | - | -
11 | HV-40208 | 325-01-402-PD-02 | Slurry Drain line | Valve With Position Switch | - | 1 | - | - | - | Dry Contact | PLC |  | CVV 4Cx1 | - | -
12 | PG-40204 | 325-01-402-PD-01 | Slurry feed | Pressure gauge | - | - | - | - | - |  |  |  |  | - | -
13 | PG-40205 | 325-01-402-PD-02 | Slurry feed | Pressure gauge | - | - | - | - | - |  |  |  |  | - | -
14 | PG-40222 | 325-01-402-PD-02 | Culinary steam feed to jet cooker | Pressure gauge | - | - | - | - | - |  |  |  |  | - | -
15 | PT-40222 | 325-01-402-PD-02 | Steam feed to Jet cooker | Pressure Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0-20 Bar | LiY-CY TP 1P x1.0 | - | -
16 | TG-40222 | 325-01-402-PD-02 | Culinary steam feed to jet cooker | Temperature gauge | - | - | - | - | - |  |  |  |  | - | -
17 | TT-40221 | 325-01-402-PD-02 | Slurry Temperature feed outlet fron jet cool | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0-120 C | LiY-CY TP 1P x1.0 | - | -
18 | TT-40222 | 325-01-402-PD-02 | Steam feed to Spray dryer | Temperature Transmitter | - | - | - | 1 | - | 4 - 20 mA | PLC | 0-200 C | LiY-CY TP 1P x1.0 | - | -
19 | TV-60221 | 325-01-402-PD-02 | Steam Temperature Control Valve for feed to jet cook | Control valve | - | - | 1 | 1 | - | 4 - 20 mA | PLC |  | LiY-CY TP 2P x1.0 | - | -
20 | FT-40221 | 325-01-402-PD-02 | Slurry feed to jet cooker | Flow transmitter (Coriolis Flow) | - | - | - | 2 | - | 4 - 20 mA | PLC | 0 to 9000 kg/h | LiY-CY TP 2Px1.0 , CVV 3Cx1.5 | - | -
21 | FT-40222 | 325-01-402-PD-02 | Culinary steam feed to jet cooker | Flow Transmitter (Vortex Flow) | - | 1 | - | 1 | - | 4 - 20 mA,Pulse | PLC | 0 to 500 m3/h | LiY-CY TP 2Px1.0 , CVV 3Cx1.5 | - | -
22 | FS-40204 | 325-01-402-PD-01 | Slurry relief flow | Flow Switch | - | 1 | - | - | - | Dry Contact | PLC |  | CVV 4Cx1 | - | -
23 | FS-40205 | 325-01-402-PD-02 | Slurry relief flow | Flow Switch | - | 1 | - | - | - | Dry Contact | PLC |  | CVV 4Cx1 | - | -
MCC ROOM
24 | ATY-40204 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40204 |  | 1 | 1 | - | - | 1 | 24 VDC energized | PLC | On-Off
25 | ATY-40205 | 325-01-402-PD-01 | Start / Stop Command for VSD PC-40205 |  | 1 | 1 | - | - | 1 | 24 VDC energized | PLC | On-Off

## Card_Terminal
Column1 | Card Model | IO-Symbol | Signal//Chanel | Terminal
| 1756-IB32 |  | GND-0 | 17
| 1756-IB32 |  | GND-0 | 18
| 1756-IB32 |  | GND1 | 35
| 1756-IB32 |  | GND1 | 36
| 1756-IB32 | IN | IN-0 | 1
| 1756-IB32 | IN | IN-1 | 2
| 1756-IB32 | IN | IN-10 | 11
| 1756-IB32 | IN | IN-11 | 12
| 1756-IB32 | IN | IN-12 | 13
| 1756-IB32 | IN | IN-13 | 14
| 1756-IB32 | IN | IN-14 | 15
| 1756-IB32 | IN | IN-15 | 16
| 1756-IB32 | IN | IN-16 | 19
| 1756-IB32 | IN | IN-17 | 20
| 1756-IB32 | IN | IN-18 | 21
| 1756-IB32 | IN | IN-19 | 22
| 1756-IB32 | IN | IN-2 | 3
| 1756-IB32 | IN | IN-20 | 23
| 1756-IB32 | IN | IN-21 | 24
| 1756-IB32 | IN | IN-22 | 25
| 1756-IB32 | IN | IN-23 | 26
| 1756-IB32 | IN | IN-24 | 27
| 1756-IB32 | IN | IN-25 | 28
| 1756-IB32 | IN | IN-26 | 29
| 1756-IB32 | IN | IN-27 | 30
| 1756-IB32 | IN | IN-28 | 31
| 1756-IB32 | IN | IN-29 | 32
| 1756-IB32 | IN | IN-3 | 4
| 1756-IB32 | IN | IN-30 | 33
| 1756-IB32 | IN | IN-31 | 34
| 1756-IB32 | IN | IN-4 | 5
| 1756-IB32 | IN | IN-5 | 6
| 1756-IB32 | IN | IN-6 | 7
| 1756-IB32 | IN | IN-7 | 8
| 1756-IB32 | IN | IN-8 | 9
| 1756-IB32 | IN | IN-9 | 10
| 1756-IF16 |  | i RTN-0 | 1
| 1756-IF16 |  | i RTN-1 | 3
| 1756-IF16 |  | i RTN-10 | 23
| 1756-IF16 |  | i RTN-11 | 25
| 1756-IF16 |  | i RTN-12 | 29
| 1756-IF16 |  | i RTN-13 | 31
| 1756-IF16 |  | i RTN-14 | 33
| 1756-IF16 |  | i RTN-15 | 35
| 1756-IF16 |  | i RTN-2 | 5
| 1756-IF16 |  | i RTN-3 | 7
| 1756-IF16 |  | i RTN-4 | 11
| 1756-IF16 |  | i RTN-5 | 13
| 1756-IF16 |  | i RTN-6 | 15
| 1756-IF16 |  | i RTN-7 | 17
| 1756-IF16 |  | i RTN-8 | 19
| 1756-IF16 |  | i RTN-9 | 21
| 1756-IF16 | IN | IN-0 | 2
| 1756-IF16 |  | IN-1 | 4
| 1756-IF16 |  | IN-10 | 24
| 1756-IF16 |  | IN-11 | 26
| 1756-IF16 |  | IN-12 | 30
| 1756-IF16 |  | IN-13 | 32
| 1756-IF16 |  | IN-14 | 34
| 1756-IF16 |  | IN-15 | 36
| 1756-IF16 |  | IN-2 | 6
| 1756-IF16 |  | IN-3 | 8
| 1756-IF16 |  | IN-4 | 12
| 1756-IF16 |  | IN-5 | 14
| 1756-IF16 |  | IN-6 | 16
| 1756-IF16 |  | IN-7 | 18
| 1756-IF16 |  | IN-8 | 20
| 1756-IF16 |  | IN-9 | 22
| 1756-IF16 |  | RTN | 9
| 1756-IF16 |  | RTN | 10
| 1756-IF16 |  | RTN | 27
| 1756-IF16 |  | RTN | 28
| 1756-OB32 |  | DC-0(+) | 18
| 1756-OB32 |  | DC-1(+) | 36
| 1756-OB32 |  | OUT-0 | 1
| 1756-OB32 |  | OUT-1 | 2
| 1756-OB32 |  | OUT-10 | 11
| 1756-OB32 |  | OUT-11 | 12
| 1756-OB32 |  | OUT-12 | 13
| 1756-OB32 |  | OUT-13 | 14
| 1756-OB32 |  | OUT-14 | 15
| 1756-OB32 |  | OUT-15 | 16
| 1756-OB32 |  | OUT-16 | 19
| 1756-OB32 |  | OUT-17 | 20
| 1756-OB32 |  | OUT-18 | 21
| 1756-OB32 |  | OUT-19 | 22
| 1756-OB32 |  | OUT-2 | 3
| 1756-OB32 |  | OUT-20 | 23
| 1756-OB32 |  | OUT-21 | 24
| 1756-OB32 |  | OUT-22 | 25
| 1756-OB32 |  | OUT-23 | 26
| 1756-OB32 |  | OUT-24 | 27
| 1756-OB32 |  | OUT-25 | 28
| 1756-OB32 |  | OUT-26 | 29
| 1756-OB32 |  | OUT-27 | 30
| 1756-OB32 |  | OUT-28 | 31
| 1756-OB32 |  | OUT-29 | 32
| 1756-OB32 |  | OUT-3 | 4
| 1756-OB32 |  | OUT-30 | 33
| 1756-OB32 |  | OUT-31 | 34
| 1756-OB32 |  | OUT-4 | 5
| 1756-OB32 |  | OUT-5 | 6
| 1756-OB32 |  | OUT-6 | 7
| 1756-OB32 |  | OUT-7 | 8
| 1756-OB32 |  | OUT-8 | 9
| 1756-OB32 |  | OUT-9 | 10
| 1756-OB32 |  | RTN OUT-0 | 17
| 1756-OB32 |  | RTN OUT-1 | 35
| 1756-OF8 |  | IOUT-0 | 3
| 1756-OF8 |  | IOUT-1 | 9
| 1756-OF8 |  | IOUT-2 | 13
| 1756-OF8 |  | IOUT-3 | 19
| 1756-OF8 |  | IOUT-4 | 4
| 1756-OF8 |  | IOUT-5 | 10
| 1756-OF8 |  | IOUT-6 | 14
| 1756-OF8 |  | IOUT-7 | 20
| 1756-OF8 |  | RTN | 5
| 1756-OF8 |  | RTN | 6
| 1756-OF8 |  | RTN | 15
| 1756-OF8 |  | RTN | 16
| 1756-OF8 |  | VOUT-0 | 1
| 1756-OF8 |  | VOUT-1 | 7
| 1756-OF8 |  | VOUT-2 | 11
| 1756-OF8 |  | VOUT-3 | 17
| 1756-OF8 |  | VOUT-4 | 2
| 1756-OF8 |  | VOUT-5 | 8
| 1756-OF8 |  | VOUT-6 | 12
| 1756-OF8 |  | VOUT-7 | 18

## Sheet1 (2)
Tag. No. 3.5 | Junction Box | Zone | Floor | P&ID No. 3.3 | Tag. No. 3.52 | P&ID No. 3.5 | DO | DI | AO | AI | Bus
LSH-60230 | IS-JB-603 | Spray Dryer | 1st | 325-01-600-PD-04 | LSH-60230 | 3-25-01-602-PD-04 | - | 1 | - | - | -
LSH-60231 | IS-JB-603 | Spray Dryer | 1st | 325-01-600-PD-04 | LSH-60231 | 3-25-01-602-PD-04 | - | 1 | - | - | -
LSH-60240 | IS-JB-603 | Spray Dryer | 1st | 325-01-600-PD-05 | LSH-60240 | 3-25-01-602-PD-05 | - | 1 | - | - | -
TT-60226 | IS-JB-603 | Spray Dryer | 2nd | 325-01-600-PD-04 | TT-60226 | 3-25-01-602-PD-04 | - | - | - | 1 | -
TT-60227 | IS-JB-603 | Spray Dryer | 1st | 325-01-600-PD-04 | TT-60227 | 3-25-01-602-PD-04 | - | - | - | 1 | -
ZS-60201E | IS-JB-603 | Spray Dryer | 1st | 325-01-600-PD-04 | ZS-60201E | 3-25-01-602-PD-04 | - | 1 | - | - | -
TT-60225 | IS-JB-603 | Spray Dryer | 3rd | 325-01-600-PD-04 | TT-60225 | 3-25-01-602-PD-04 | - | - | - | 1 | -
TT-60230 | IS-JB-603 | Spray Dryer | 3rd | 325-01-600-PD-04 | TT-60230 | 3-25-01-602-PD-04 | - | - | - | 1 | -
PT-60230 | IS-JB-603 | Spray Dryer | 4th | 325-01-600-PD-04 | PT-60230 | 3-25-01-602-PD-04 | - | - | - | 1 | -
PT-60231 | IS-JB-603 | Spray Dryer | 4th | 325-01-600-PD-04 | PT-60231 | 3-25-01-602-PD-04 | - | - | - | 1 | -
TT-60224 | IS-JB-603 | Spray Dryer | 4th | 325-01-600-PD-04 | TT-60224 | 3-25-01-602-PD-04 | - | - | - | 1 | -
ZS-60201C | IS-JB-603 | Spray Dryer | 4th | 325-01-600-PD-04 | ZS-60201C | 3-25-01-602-PD-04 | - | 1 | - | - | -
ZS-60201D | IS-JB-603 | Spray Dryer | 4th | 325-01-600-PD-04 | ZS-60201D | 3-25-01-602-PD-04 | - | 1 | - | - | -
ZS-60229 | IS-JB-603 | Spray Dryer | 4th | - | ZS-60229 | 3-25-01-602-PD-04 | - | 1 | - | - | -
ZS-60230 | IS-JB-603 | Spray Dryer | 4th | - | ZS-60230 | 3-25-01-602-PD-04 | - | 1 | - | - | -
ZS-60231A | IS-JB-603 | Spray Dryer | 4th | 325-01-600-PD-05 | ZS-60231A | 3-25-01-602-PD-05 | - | 1 | - | - | -
ZS-60231B | IS-JB-603 | Spray Dryer | 4th | 325-01-600-PD-05 | ZS-60231B | 3-25-01-602-PD-05 | - | 1 | - | - | -
AT-40201 | IS-JB-603 | Spray Dryer | 3rd | - | AT-40201 | - | - | 1 | - | - | -
AT-40202 | IS-JB-603 | Spray Dryer | 3rd | - | AT-40202 | - | - | 1 | - | - | -
AT-40203 | IS-JB-603 | Spray Dryer | 3rd | - | AT-40203 | - | - | 1 | - | - | -
RV-60204 | IS-JB-603 | Spray Dryer | 3rd | - | RV-60204 | - | - | 1 | - | - | -
PD-60202 | IS-JB-603 | Spray Dryer | 3rd | - | PD-60202 | - | - | 1 | - | - | -
TT-60222 | IS-JB-608 | Spray Dryer | 5th | 325-01-600-PD-04 | TT-60222 | 3-25-01-602-PD-04 | - | - | - | 1 | -
TT-60223 | IS-JB-608 | Spray Dryer | 5th | 325-01-600-PD-04 | TT-60223 | 3-25-01-602-PD-04 | - | - | - | 1 | -
XT-60201 | IS-JB-608 | Spray Dryer | 5th | 325-01-600-PD-03 | XT-60201 | 3-25-01-602-PD-03 | - | - | - | 1 | -
XA-60201 | IS-JB-608 | Spray Dryer | 5th | 325-01-600-PD-03 | XA-60201 | 3-25-01-602-PD-03 | 1 | - | - | - | -
ZS-60231C | IS-JB-608 | Spray Dryer | 5th | 325-01-600-PD-04 | ZS-60231C | 3-25-01-602-PD-04 | - | 1 | - | - | -
ZS-60231D | IS-JB-608 | Spray Dryer | 5th | 325-01-600-PD-04 | ZS-60231D | 3-25-01-602-PD-04 | - | 1 | - | - | -
ZS-60231E | IS-JB-608 | Spray Dryer | 5th | 325-01-600-PD-05 | ZS-60231E | 3-25-01-602-PD-05 | - | 1 | - | - | -
ZS-60231F | IS-JB-608 | Spray Dryer | 5th | 325-01-600-PD-05 | ZS-60231F | 3-25-01-602-PD-05 | - | 1 | - | - | -
PT-60220 | IS-JB-608 | Spray Dryer | 6th | 325-01-600-PD-04 | PT-60220 | 3-25-01-602-PD-04 | - | - | - | 1 | -
TT-60220 | IS-JB-608 | Spray Dryer | 6th | 325-01-600-PD-04 | TT-60220 | 3-25-01-602-PD-04 | - | - | - | 1 | -
TT-60221 | IS-JB-608 | Spray Dryer | 6th | 325-01-600-PD-04 | TT-60221 | 3-25-01-602-PD-04 | - | - | - | 1 | -
ZS-60201A | IS-JB-608 | Spray Dryer | 6th | 325-01-600-PD-04 | ZS-60201A | 3-25-01-602-PD-04 | - | 1 | - | - | -
ZS-60201B | IS-JB-608 | Spray Dryer | 6th | 325-01-600-PD-04 | ZS-60201B | 3-25-01-602-PD-04 | - | 1 | - | - | -
ZS-60240 | IS-JB-608 | Spray Dryer | 6th | - | ZS-60240 | 3-25-01-602-PD-05 | - | 1 | - | - | -
DPT-61310 | IS-JB-612 | Packing Tower | 2nd | 325-01-613-PD-03 | DPT-61310 | 3-25-01-613-PD-03 | - | - | - | 1 | -
DPT-61312 | IS-JB-612 | Packing Tower | 2nd | 325-01-613-PD-05 | DPT-61312 | 3-25-01-613-PD-05 | - | - | - | 1 | -
LSH-61304 | IS-JB-612 | Packing Tower | 1st | 325-01-613-PD-03 | LSH-61304 | 3-25-01-613-PD-03 | - | 1 | - | - | -
LSH-61305 | IS-JB-612 | Packing Tower | 1st | 325-01-613-PD-05 | LSH-61305 | 3-25-01-613-PD-05 | - | 1 | - | - | -
LSH-61307 | IS-JB-612 | Packing Tower | 1st | - | LSH-61307 | 3-25-01-613-PD-01 | - | 1 | - | - | -
LSH-61312 | IS-JB-612 | Packing Tower | 2nd | 325-01-613-PD-05 | LSH-61312 | 3-25-01-613-PD-05 | - | 1 | - | - | -
ZS-61312 | IS-JB-612 | Packing Tower | 3rd | 325-01-613-PD-01 | ZS-61312 | 3-25-01-613-PD-01 | - | 1 | - | - | -
ZS-61313 | IS-JB-612 | Packing Tower | 3rd | 325-01-613-PD-01 | ZS-61313 | 3-25-01-613-PD-01 | - | 1 | - | - | -
PSE-61302 | IS-JB-612 | Packing Tower | 2nd | 325-01-613-PD-03 | PSE-61302 | 3-25-01-613-PD-03 | - | 1 | - | - | -
PSE-61303 | IS-JB-612 | Packing Tower | 2nd | 325-01-613-PD-05 | PSE-61303 | 3-25-01-613-PD-05 | - | 1 | - | - | -
ISV-61303 | IS-JB-612 | Packing Tower | 2nd | 325-01-613-PD-03 | ISV-61303 | 3-25-01-613-PD-03 | - | 1 | - | - | -
ISV-61304 | IS-JB-612 | Packing Tower | 2nd | 325-01-613-PD-05 | ISV-61304 | 3-25-01-613-PD-05 | - | 1 | - | - | -
SC-61301 | IS-JB-612 | Packing Tower | 2nd | - | SC-61301 | - | - | 1 | - | - | -
SC-61302 | IS-JB-612 | Packing Tower | 2nd | - | SC-61302 | - | - | 1 | - | - | -
RV-61301 | IS-JB-612 | Packing Tower | 2nd | - | RV-61301 | - | - | 1 | - | - | -
RV-61305 | IS-JB-612 | Packing Tower | 2nd | - | RV-61305 | - | - | 1 | - | - | -
RV-61304 | IS-JB-612 | Packing Tower | 2nd | - | RV-61304 | - | - | 1 | - | - | -
DPT-61301 | IS-JB-618 | Packing Tower | 8th | 325-01-613-PD-01 | DPT-61301 | 3-25-01-613-PD-01 | - | - | - | 1 | -
DPT-61302 | IS-JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | DPT-61302 | 3-25-01-613-PD-01 | - | - | - | 1 | -
LSH-61301 | IS-JB-618 | Packing Tower | 7th | 325-01-613-PD-01 | LSH-61301 | 3-25-01-613-PD-01 | - | 1 | - | - | -
LSL-61302 | IS-JB-618 | Packing Tower | 6th | 325-01-613-PD-01 | LSL-61302 | 3-25-01-613-PD-01 | - | 1 | - | - | -
- | IS-JB-618 | Packing Tower | 7th | 325-01-613-PD-01 | - | - | - | 1 | - | - | -
LSH-61306 | IS-JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | LSH-61306 | 3-25-01-613-PD-01 | - | 1 | - | - | -
LSH-61308 | IS-JB-618 | Packing Tower | 8th | - | LSH-61308 | 3-25-01-613-PD-01 | - | 1 | - | - | -
LT-61301 | IS-JB-618 | Packing Tower | 8th | 325-01-613-PD-01 | LT-61301 | 3-25-01-613-PD-01 | - | - | - | 1 | -
PT-61301 | IS-JB-618 | Packing Tower | 8th | 325-01-613-PD-01 | PT-61301 | 3-25-01-613-PD-01 | - | - | - | 1 | -
- | IS-JB-618 | Packing Tower | 8th | 325-01-613-PD-01 | - | 3-25-01-613-PD-01 | - | - | - | 1 | -
PT-61304 | IS-JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | PT-61304 | 3-25-01-613-PD-01 | - | - | - | 1 | -
PT-61305 | IS-JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | PT-61305 | 3-25-01-613-PD-01 | - | - | - | 1 | -
TT-61301 | IS-JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | TT-61301 | 3-25-01-613-PD-01 | - | - | - | 1 | -
TT-61302 | IS-JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | TT-61302 | 3-25-01-613-PD-01 | - | - | - | 1 | -
ZS-61310 | IS-JB-618 | Packing Tower | 5th | 325-01-613-PD-01 | ZS-61310 | 3-25-01-613-PD-01 | - | 1 | - | - | -
ZS-61311 | IS-JB-618 | Packing Tower | 5th | 325-01-613-PD-01 | ZS-61311 | 3-25-01-613-PD-01 | - | 1 | - | - | -
PSE-61300 | IS-JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | PSE-61300 | 3-25-01-613-PD-01 | - | 1 | - | - | -
PSE-61301 | IS-JB-618 | Packing Tower | 8th | 325-01-613-PD-01 | PSE-61301 | 3-25-01-613-PD-01 | - | 1 | - | - | -
ISV-61301 | IS-JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | ISV-61301 | 3-25-01-613-PD-01 | - | 1 | - | - | -
PSE-61304 | IS-JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | PSE-61304 | 3-25-01-613-PD-01 | - | 1 | - | - | -
PSV-61301A | IS-JB-618 | Packing Tower | 8th | 325-01-613-PD-01 | PSV-61301A | 325-01-613-PD-01 | - | 1 | - | - | -
PSV-61301B | IS-JB-618 | Packing Tower | 8th | 325-01-613-PD-01 | PSV-61301B | 325-01-613-PD-01 | - | 1 | - | - | -
PT-40201 | JB-401 | Infeed Tank | 1st | 325-01-400-PD-02 | PT-40201 | 3-25-01-402-PD-02 | - | - | - | 1 | -
FT-40201 | JB-401 | Infeed Tank | 1st | 325-01-400-PD-02 | FT-40201 | 3-25-01-402-PD-02 | - | 1 | - | 2 | -
FT-40202 | JB-401 | Infeed Tank | 1st | 325-01-400-PD-02 | FT-40202 | 3-25-01-402-PD-02 | - | 1 | - | 1 | -
HV-40206 | JB-401 | Infeed Tank | 1st | 325-01-400-PD-01 | HV-40206 | 3-25-01-402-PD-02 | - | 1 | - | - | -
HV-40205 | JB-401 | Infeed Tank | 1st | 325-01-400-PD-01 | HV-40205 | 3-25-01-402-PD-02 | - | 1 | - | - | -
LT-40203 | JB-401 | Infeed Tank | 1st | 325-01-400-PD-02 | LT-40203 | 3-25-01-402-PD-02 | - | - | - | 1 | -
PT-40202 | JB-401 | Infeed Tank | 1st | 325-01-400-PD-02 | PT-40202 | 3-25-01-402-PD-02 | - | - | - | 1 | -
PT-60202 | JB-401 | Infeed Tank | 1st | 325-01-600-PD-01 | PT-60202 | 3-25-01-602-PD-01 | - | - | - | 1 | -
XV-40203B | JB-401 | Infeed Tank | 1st | 325-01-400-PD-02 | XV-40203B | 3-25-01-402-PD-02 | 1 | 2 | - | - | -
XV-40203C | JB-401 | Infeed Tank | 1st | 325-01-400-PD-02 | XV-40203C | 3-25-01-402-PD-02 | 1 | 2 | - | - | -
XV-40203D | JB-401 | Infeed Tank | 1st | 325-01-400-PD-02 | XV-40203D | 3-25-01-402-PD-02 | 1 | 2 | - | - | -
XV-40203E | JB-401 | Infeed Tank | 1st | 325-01-400-PD-02 | XV-40203E | 3-25-01-402-PD-02 | 1 | 2 | - | - | -
XV-60251 | JB-401 | Infeed Tank | 1st | 325-01-600-PD-01 | XV-60251 | 3-25-01-602-PD-01 | 1 | 2 | - | - | -
ATY-40203 | JB-401 | Infeed Tank | 1st | 325-01-400-PD-02 | ATY-40203 | 3-25-01-402-PD-02 | 1 | 1 | - | - | 1
PCY-40203 | JB-401 | Infeed Tank | 1st | 325-01-400-PD-02 | PCY-40203 | 3-25-01-402-PD-02 | 1 | 1 | - | - | 1
FS-40201 | JB-401 | PH Adjustment | 1st | - | FS-40201 | 3-25-01-402-PD-01 | - | - | - | 1 | -
FS-40202 | JB-401 | PH Adjustment | 1st | - | FS-40202 | 3-25-01-402-PD-01 | - | - | - | 1 | -
HV-40203 | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | HV-40203 | 3-25-01-402-PD-01 | - | 1 | - | - | -
HV-40201 | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | HV-40201 | 3-25-01-402-PD-01 | - | 1 | - | - | -
HV-40204 | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | HV-40204 | 3-25-01-402-PD-01 | - | 1 | - | - | -
HV-40202 | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | HV-40202 | 3-25-01-402-PD-01 | - | 1 | - | - | -
LT-40201 | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | LT-40201 | 3-25-01-402-PD-01 | - | 1 | - | - | -
LT-40202 | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | LT-40202 | 3-25-01-402-PD-01 | - | 1 | - | - | -
pHT-40201 | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | pHT-40201 | 3-25-01-402-PD-01 | - | 1 | - | 1 | -
pHT-40202 | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | pHT-40202 | 3-25-01-402-PD-01 | - | 1 | - | 1 | -
SV-40201 | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | SV-40201 | 3-25-01-402-PD-01 | 1 | - | - | - | -
SV-40202 | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | SV-40202 | 3-25-01-402-PD-01 | 1 | - | - | - | -
SV-40203 | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | SV-40203 | 3-25-01-402-PD-01 | 1 | - | - | - | -
SV-40204 | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | SV-40204 | 3-25-01-402-PD-01 | 1 | - | - | - | -
XV-40201A | JB-401 | PH Adjustment | 1st | - | XV-40201A | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40201B | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40201B | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40201C | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40201C | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40201D | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40201D | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40201E | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40201E | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40201F | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40201F | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40201G | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40201G | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40201H | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40201H | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40202A | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40202A | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40202B | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40202B | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40202C | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40202C | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40202D | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40202D | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40202E | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40202E | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40202F | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40202F | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40202G | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40202G | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
XV-40202H | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | XV-40202H | 3-25-01-402-PD-01 | 1 | 2 | - | - | -
- | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | - | 3-25-01-402-PD-01 | 1 | 1 | - | - | 1
- | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | - | 3-25-01-402-PD-01 | 1 | 1 | - | - | 1
- | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | - | 3-25-01-402-PD-01 | 1 | 1 | - | - | 1
- | JB-401 | PH Adjustment | 1st | 325-01-400-PD-01 | - | 3-25-01-402-PD-01 | 1 | 1 | - | - | 1
FS-40204 | JB-402 | Jet Cooker | 2nd | - | FS-40204 | 325-01-402-PD-01 | - | 1 | - | - | -
FS-40205 | JB-402 | Jet Cooker | 2nd | - | FS-40205 | 325-01-402-PD-02 | - | 1 | - | - | -
FT-40221 | JB-402 | Jet Cooker | 2nd | - | FT-40221 | 325-01-402-PD-02 | - | 1 | - | 2 | -
FT-40222 | JB-402 | Jet Cooker | 2nd | - | FT-40222 | 325-01-402-PD-02 | - | 1 | - | 2 | -
HV-40207 | JB-402 | Jet Cooker | 2nd | - | HV-40207 | 325-01-402-PD-01 | - | 1 | - | - | -
HV-40208 | JB-402 | Jet Cooker | 2nd | - | HV-40208 | 325-01-402-PD-01 | - | 1 | - | - | -
PT-40222 | JB-402 | Jet Cooker | 2nd | - | PT-40222 | 325-01-402-PD-02 |  |  |  | 1 | -
TT-40221 | JB-402 | Jet Cooker | 2nd | - | TT-40221 | 325-01-402-PD-02 | - | - | - | 1 | -
TT-40222 | JB-402 | Jet Cooker | 2nd | - | TT-40222 | 325-01-402-PD-02 | - | - | - | 1 | -
TCV-40222 | JB-402 | Jet Cooker | 2nd | - | TCV-40222 | 325-01-402-PD-02 | - | - | 1 | - | -
XV-40203F | JB-402 | Jet Cooker | 2nd | - | XV-40203F | 325-01-402-PD-02 | 1 | 2 | - | - | -
XV-40204B | JB-402 | Jet Cooker | 2nd | - | XV-40204B | 325-01-402-PD-01 | 1 | 2 | - | - | -
XV-40204C | JB-402 | Jet Cooker | 2nd | - | XV-40204C | 325-01-402-PD-01 | 1 | 2 | - | - | -
XV-40205A | JB-402 | Jet Cooker | 2nd | - | XV-40205A | 325-01-402-PD-02 | 1 | 2 | - | - | -
XV-40205B | JB-402 | Jet Cooker | 2nd | - | XV-40205B | 325-01-402-PD-02 | 1 | 2 | - | - | -
XV-40205C | JB-402 | Jet Cooker | 2nd | - | XV-40205C | 325-01-402-PD-02 | 1 | 2 | - | - | -
XV-40205D | JB-402 | Jet Cooker | 2nd | - | XV-40205D | 325-01-402-PD-02 | 1 | 2 | - | - | -
XV-40205F | JB-402 | Jet Cooker | 2nd | - | XV-40205F | 325-01-402-PD-02 | 1 | 2 | - | - | -
XV-40222 | JB-402 | Jet Cooker | 2nd | - | XV-40222 | 325-01-402-PD-02 | 1 | 2 | - | - | -
DPT-60202 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | DPT-60202 | 3-25-01-602-PD-08 | - | - | - | 1 | -
FT-60201 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | FT-60201 | 3-25-01-602-PD-08 | - | - | - | 1 | -
FT-61307 | JB-601 | Spray Dryer | 1st | - | FT-61307 | 3-25-01-613-PD-04 | - | - | - | 1 | -
- | JB-601 | Spray Dryer | 1st | 325-01-613-PD-04 | - | - | - | - | - | 1 | -
FT-60204 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-10 | FT-60204 | 3-25-01-602-PD-10 | - | - | - | 1 | -
LSL-60201 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-11 | LSL-60201 | 3-25-01-602-PD-11 | - | 1 | - | - | -
PT-60203 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | PT-60203 | 3-25-01-602-PD-08 | - | - | - | 1 | -
PT-60204 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-10 | PT-60204 | 3-25-01-602-PD-10 | - | - | - | 1 | -
SV-60230 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-04 | SV-60230 | 3-25-01-602-PD-04 | 1 | - | - | - | -
SV-60231 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-04 | SV-60231 | 3-25-01-602-PD-04 | 1 | - | - | - | -
SV-60240A | JB-601 | Spray Dryer | 1st | 325-01-600-PD-05 | SV-60240A | 3-25-01-602-PD-05 | 1 | - | - | - | -
SV-60240B | JB-601 | Spray Dryer | 1st | 325-01-600-PD-05 | SV-60240B | 3-25-01-602-PD-05 | 1 | - | - | - | -
SV-60240C | JB-601 | Spray Dryer | 1st | 325-01-600-PD-05 | SV-60240C | 3-25-01-602-PD-05 | 1 | - | - | - | -
XV-60202 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-11 | XV-60202 | 3-25-01-602-PD-11 | 1 | 2 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | 1 | 1 | - | - | 1
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-01 | - | - | 2 | 2 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-01 | - | - | 2 | 2 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-01 | - | - | 2 | 2 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-01 | - | - | 2 | 2 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-01 | - | - | 1 | 1 | - | - | 1
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | 2 | 2 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | 2 | 2 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | 2 | 2 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-05 | - | - | 1 | 2 | - | - | -
SV-60201 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | SV-60201 | 3-25-01-602-PD-08 | 1 | 2 | - | - | -
SV-60202 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | SV-60202 | 3-25-01-602-PD-08 | 1 | 2 | - | - | -
SV-60203 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | SV-60203 | 3-25-01-602-PD-08 | 1 | 2 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | - | 1 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | - | 1 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | - | 1 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | - | 1 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | - | 1 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | - | 1 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | - | 1 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | - | 1 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | - | 1 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | - | 1 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | - | 1 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | - | - | - | 1 | - | - | -
XV-60240D | JB-601 | Spray Dryer | 1st | 325-01-600-PD-08 | XV-60240D | 3-25-01-602-PD-05 | 1 | 2 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-05 | - | - | - | - | - | 1 | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-01 | - | - | - | 1 | - | - | -
PT-60205 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-01 | PT-60205 | 3-25-01-602-PD-01 | - | - | - | 1 | -
FS-60205 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-01 | FS-60205 | 3-25-01-602-PD-01 | - | 1 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-01 | - | - | 1 | - | - | - | -
VS-60205 | JB-601 | Spray Dryer | 1st | 325-01-600-PD-01 | VS-60205 | 3-25-01-602-PD-01 | - | 1 | - | - | -
XV-60205A | JB-601 | Spray Dryer | 1st | 325-01-600-PD-01 | XV-60205A | 3-25-01-602-PD-01 | 1 | 2 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-01 | - | - | - | 1 | - | - | -
- | JB-601 | Spray Dryer | 1st | 325-01-600-PD-01 | - | - | - | 1 | - | - | -
AT-60241 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-05 | AT-60241 | 3-25-01-602-PD-05 | - | - | - | 1 | -
DPT-60203 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | DPT-60203 | 3-25-01-602-PD-03 | - | - | - | 1 | -
FT-60210 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | FT-60210 | 3-25-01-602-PD-03 | - | - | - | 2 | -
FT-60211 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | FT-60211 | 3-25-01-602-PD-03 | - | - | - | 2 | -
FT-60202 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-09 | FT-60202 | 3-25-01-602-PD-09 | - | 1 | - | 1 | -
LSH-60251 | JB-602 | Spray Dryer | 4th | 325-01-600-PD-04 | LSH-60251 | 3-25-01-602-PD-04 | - | 1 | - | - | -
PSL-60220 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-04 | PSL-60220 | 3-25-01-602-PD-04 | - | 1 | - | - | -
PT-60210 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | PT-60210 | 3-25-01-602-PD-03 | - | - | - | 1 | -
PT-60215 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | PT-60215 | 3-25-01-602-PD-03 | - | - | - | 1 | -
PT-60216 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | PT-60216 | 3-25-01-602-PD-03 | - | - | - | 1 | -
PT-60240 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-05 | PT-60240 | 3-25-01-602-PD-05 | - | - | - | 1 | -
PT-60241 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-05 | PT-60241 | 3-25-01-602-PD-05 | - | - | - | 1 | -
TSH-60230 | JB-602 | Spray Dryer | 3rd | 325-01-600-PD-04 | TSH-60230 | 3-25-01-602-PD-04 | - | 1 | - | - | -
TSH-60240 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-05 | TSH-60240 | 3-25-01-602-PD-05 | - | 1 | - | - | -
TT-60210 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | TT-60210 | 3-25-01-602-PD-03 | - | - | - | 1 | -
- | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | - | - | - | - | - | 1 | -
- | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | - | - | - | - | - | 1 | -
TT-60211 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | TT-60211 | 3-25-01-602-PD-03 | - | - | - | 1 | -
TT-60214 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | TT-60214 | 3-25-01-602-PD-03 | - | - | - | 1 | -
TT-60215A | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | TT-60215A | 3-25-01-602-PD-03 | - | - | - | 1 | -
TT-60215B | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | TT-60215B | 3-25-01-602-PD-03 | - | - | - | 1 | -
TT-60216 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | TT-60216 | 3-25-01-602-PD-03 | - | - | - | 1 | -
TT-60240 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-05 | TT-60240 | 3-25-01-602-PD-05 | - | - | - | 1 | -
TT-60241A | JB-602 | Spray Dryer | 5th | 325-01-600-PD-05 | TT-60241A | 3-25-01-602-PD-05 | - | - | - | 1 | -
TT-60241B | JB-602 | Spray Dryer | 5th | 325-01-600-PD-05 | TT-60241B | 3-25-01-602-PD-05 | - | - | - | 1 | -
TV-60214 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | TV-60214 | 3-25-01-602-PD-03 | - | - | 1 | - | -
TV-60202 | JB-602 | Spray Dryer | 3rd | 325-01-600-PD-07 | TV-60202 | 3-25-01-602-PD-07 | - | - | 1 | - | -
TT-60212A | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | TT-60212A | 3-25-01-602-PD-03 | - | - | - | 1 | -
TT-60212B | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | TT-60212B | 3-25-01-602-PD-03 | - | - | - | 1 | -
VT-60210A | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | VT-60210A | 3-25-01-602-PD-03 | - | - | - | 1 | -
VT-60210B | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | VT-60210B | 3-25-01-602-PD-03 | - | - | - | 1 | -
VT-60241A | JB-602 | Spray Dryer | 5th | 325-01-600-PD-05 | VT-60241A | 3-25-01-602-PD-05 | - | - | - | 1 | -
VT-60241B | JB-602 | Spray Dryer | 5th | 325-01-600-PD-05 | VT-60241B | 3-25-01-602-PD-05 | - | - | - | 1 | -
XV-60214 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | XV-60214 | 3-25-01-602-PD-03 | 1 | 2 | - | - | -
- | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | - | - | 1 | 1 | - | - | 1
- | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | - | - | 1 | 1 | - | - | 1
- | JB-602 | Spray Dryer | 5th | 325-01-600-PD-05 | - | - | 1 | 1 | - | - | 1
- | JB-602 | Spray Dryer | 5th | 325-01-600-PD-03 | - | - | 1 | 1 | - | - | 1
XV-60241 | JB-602 | Spray Dryer | 5th | 325-01-600-PD-05 | XV-60241 | 3-25-01-602-PD-05 | 1 | 2 | - | - | -
- | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | - | - | 1 | - | - | - | -
- | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | - | - | 1 | - | - | - | -
- | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | - | - | - | 1 | - | - | -
- | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | - | - | - | 1 | - | - | -
- | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | - | - | 1 | - | - | - | -
- | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | - | - | - | 1 | - | - | -
- | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | - | - | - | 1 | - | - | -
TSH-60241A | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | TSH-60241A | 3-25-01-602-PD-05 | - | 1 | - | - | -
TSL-60241B | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | TSL-60241B | 3-25-01-602-PD-05 | - | 1 | - | - | -
- | JB-602 | Spray Dryer | 3rd | 325-01-600-PD-05 | - | - | 1 | - | - | - | -
- | JB-602 | Spray Dryer | 3rd | 325-01-600-PD-05 | - | - | - | 1 | - | - | -
- | JB-602 | Spray Dryer | 3rd | 325-01-600-PD-05 | - | - | - | 1 | - | - | -
TSH-60242A | JB-602 | Spray Dryer | 3rd | 325-01-600-PD-05 | TSH-60242A | 3-25-01-602-PD-05 | - | 1 | - | - | -
TSL-60242B | JB-602 | Spray Dryer | 3rd | 325-01-600-PD-05 | TSL-60242B | 3-25-01-602-PD-05 | - | 1 | - | - | -
- | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | - | - | 1 | - | - | - | -
- | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | - | - | - | 1 | - | - | -
- | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | - | - | - | 1 | - | - | -
TSH-60243A | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | TSH-60243A | 3-25-01-602-PD-05 | - | 1 | - | - | -
TSL-60243B | JB-602 | Spray Dryer | 4th | 325-01-600-PD-05 | TSL-60243B | 3-25-01-602-PD-05 | - | 1 | - | - | -
DPT-60201 | JB-606 | Spray Dryer | 6th | 325-01-600-PD-09 | DPT-60201 | 3-25-01-602-PD-09 | - | - | - | 1 | -
FT-60203 | JB-606 | Spray Dryer | 6th | 325-01-600-PD-09 | FT-60203 | 3-25-01-602-PD-09 | - | 1 | - | 1 | -
LSH-60250 | JB-606 | Spray Dryer | 6th | 325-01-600-PD-05 | LSH-60250 | 3-25-01-602-PD-05 | - | 1 | - | - | -
SV-60220 | JB-606 | Spray Dryer | 6th | 325-01-600-PD-04 | SV-60220 | 3-25-01-602-PD-04 | 1 | - | - | - | -
- | JB-606 | Spray Dryer | 6th | 325-01-600-PD-05 | - | - | - | 1 | - | - | -
- | JB-606 | Spray Dryer | 6th | 325-01-600-PD-05 | - | - | - | 1 | - | - | -
- | JB-606 | Spray Dryer | 6th | 325-01-600-PD-05 | - | - | 1 | - | - | - | -
FT-60221 | JB-607 | Spray Dryer | 7th | 325-01-600-PD-04 | FT-60221 | 3-25-01-602-PD-04 | - | - | - | 1 | -
FT-60261FA | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60261FA | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60261FB | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60261FB | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60261FC | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60261FC | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60261FD | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60261FD | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60262FE | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60262FE | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60262FF | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60262FF | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60262FG | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60262FG | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60262FH | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60262FH | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60263FJ | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60263FJ | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60263FK | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60263FK | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60263FL | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60263FL | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60263FM | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60263FM | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60264FN | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60264FN | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60264FP | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60264FP | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60264FQ | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60264FQ | 3-25-01-602-PD-02 | - | - | - | 1 | -
FT-60264FR | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | FT-60264FR | 3-25-01-602-PD-02 | - | - | - | 1 | -
PT-60201 | JB-607 | Spray Dryer | 7th | - | PT-60201 | 3-25-01-602-PD-02 | - | - | - | 1 | -
PT-60221 | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | PT-60221 | 3-25-01-602-PD-04 | - | - | - | 1 | -
PT-60221 | JB-607 | Spray Dryer | 7th | 325-01-600-PD-04 | PT-60221 | 3-25-01-602-PD-04 | - | - | - | 1 | -
PV-60201 | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | PV-60201 | 3-25-01-602-PD-02 | - | - | 1 | - | -
TT-60201 | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | TT-60201 | 3-25-01-602-PD-02 | - | - | - | 1 | -
TT-60202 | JB-607 | Spray Dryer | 7th | 325-01-600-PD-07 | TT-60202 | 3-25-01-602-PD-07 | - | - | - | 1 | -
XV-60201 | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60201 | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-04 | - | - | 1 | 1 | - | - | 1
FT-60207 | JB-607 | Spray Dryer | 7th | 325-01-600-PD-07 | FT-60207 | 3-25-01-602-PD-07 | - | - | - | 1 | -
PT-60207 | JB-607 | Spray Dryer | 7th | 325-01-600-PD-07 | PT-60207 | 3-25-01-602-PD-07 | - | - | - | 1 | -
SV-60207 | JB-607 | Spray Dryer | 7th | 325-01-600-PD-07 | SV-60207 | 3-25-01-602-PD-07 | 1 | 2 | - | - | -
TT-60207 | JB-607 | Spray Dryer | 7th | 325-01-600-PD-07 | TT-60207 | 3-25-01-602-PD-07 | - | - | - | 1 | -
XV-60261FA | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60261FA | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60261FB | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60261FB | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60261FC | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60261FC | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60261FD | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60261FD | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60261SA | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60261SA | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60261SB | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60261SB | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60261SC | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60261SC | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60261SD | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60261SD | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60262FE | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60262FE | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60262FF | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60262FF | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60262FG | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60262FG | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60262FH | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60262FH | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60262SE | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60262SE | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60262SF | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60262SF | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60262SG | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60262SG | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60262SH | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60262SH | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60263FJ | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60263FJ | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60263FK | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60263FK | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60263FL | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60263FL | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60263FM | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60263FM | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60263SJ | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60263SJ | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60263SK | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60263SK | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60263SL | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60263SL | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60263SM | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60263SM | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60264FN | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60264FN | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60264FP | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60264FP | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60264FQ | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60264FQ | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60264FR | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60264FR | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60264SN | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60264SN | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60264SP | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60264SP | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60264SQ | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60264SQ | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
XV-60264SR | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | XV-60264SR | 3-25-01-602-PD-02 | 1 | 2 | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | - | - | 1 | 2 | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | - | - | 1 | 2 | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | - | - | 1 | 2 | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-02 | - | - | 1 | 2 | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-06 | - | - | - | 1 | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-06 | - | - | - | 1 | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-06 | - | - | - | 1 | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-06 | - | - | - | 1 | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-06 | - | - | - | 1 | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-06 | - | - | 1 | - | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-06 | - | - | 1 | - | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-06 | - | - | 1 | - | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-06 | - | - | 1 | - | - | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-06 | - | - | - | - | - | 1 | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-06 | - | - | - | - | - | 1 | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-06 | - | - | - | - | 1 | - | -
- | JB-607 | Spray Dryer | 7th | 325-01-600-PD-06 | - | - | - | - | - | - | 1
TT-60245 | JB-608 | Spray Dryer | 8th | 325-01-600-PD-05 | TT-60245 | 3-25-01-602-PD-05 | - | - | - | 1 | -
HS-61307F | JB-612 | Packing Tower | 4th | 325-01-613-PD-03 | HS-61307F | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307G | JB-612 | Packing Tower | 3rd | 325-01-613-PD-03 | HS-61307G | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307H | JB-612 | Packing Tower | 3rd | 325-01-613-PD-03 | HS-61307H | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307I | JB-612 | Packing Tower | 1st | 325-01-613-PD-03 | HS-61307I | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307J | JB-612 | Packing Tower | 1st | 325-01-613-PD-03 | HS-61307J | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307K | JB-612 | Packing Tower | 1st | 325-01-613-PD-03 | HS-61307K | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307L | JB-612 | Packing Tower | 1st | 325-01-613-PD-03 | HS-61307L | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307M | JB-612 | Packing Tower | 1st | 325-01-613-PD-03 | HS-61307M | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307N | JB-612 | Packing Tower | 1st | 325-01-613-PD-03 | HS-61307N | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307O | JB-612 | Packing Tower | 1st | 325-01-613-PD-03 | HS-61307O | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307P | JB-612 | Packing Tower | 1st | 325-01-613-PD-03 | HS-61307P | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307Q | JB-612 | Packing Tower | 1st | 325-01-613-PD-03 | HS-61307Q | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307R | JB-612 | Packing Tower | 1st | 325-01-613-PD-03 | HS-61307R | 3-25-01-613-PD-03 | - | 1 | - | - | -
PSL-61305 | JB-612 | Packing Tower | 1st | 325-01-613-PD-03 | PSL-61305 | 3-25-01-613-PD-03 | - | 1 | - | - | -
PSL-61306 | JB-612 | Packing Tower | 1st | 325-01-613-PD-05 | PSL-61306 | 3-25-01-613-PD-05 | - | 1 | - | - | -
PT-61302 | JB-612 | Packing Tower | 2nd | 325-01-613-PD-03 | PT-61302 | 3-25-01-613-PD-03 | - | - | - | 1 | -
PT-61309 | JB-612 | Packing Tower | 1st | 325-01-613-PD-04 | PT-61309 | 3-25-01-613-PD-04 | - | - | - | 1 | -
SV-61307 | JB-612 | Packing Tower | 3rd | - | SV-61307 | 3-25-01-613-PD-01 | 1 | - | - | - | -
- | JB-612 | Packing Tower | 2nd | 325-01-613-PD-03 | - | - | 1 | - | - | - | -
SV-61309 | JB-612 | Packing Tower | 2nd | 325-01-613-PD-03 | SV-61309 | 3-25-01-613-PD-03 | 1 | - | - | - | -
- | JB-612 | Packing Tower | 2nd | 325-01-613-PD-05 | - | - | 1 | - | - | - | -
SV-61311 | JB-612 | Packing Tower | 1st | 325-01-613-PD-05 | SV-61311 | 3-25-01-613-PD-05 | 1 | - | - | - | -
XV-61302 | JB-612 | Packing Tower | 2nd | 325-01-613-PD-02 | XV-61302 | 3-25-01-613-PD-02 | 1 | 2 | - | - | -
XV-61303 | JB-612 | Packing Tower | 2nd | 325-01-613-PD-02 | XV-61303 | 3-25-01-613-PD-02 | 1 | 2 | - | - | -
- | JB-612 | Packing Tower | 2nd | 325-01-613-PD-05 | - | - | 1 | 1 | - | - | 1
- | JB-612 | Packing Tower | 2nd | 325-01-613-PD-03 | - | - | 2 | 2 | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-03 | - | - | 2 | 2 | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-05 | - | - | 2 | 2 | - | - | -
- | JB-612 | Packing Tower | 4th | 325-01-613-PD-01 | - | - | 2 | 2 | - | - | -
- | JB-612 | Packing Tower | 4th | 325-01-613-PD-01 | - | - | 2 | 2 | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | - | 1 | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | - | 1 | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | - | 1 | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | - | 1 | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | - | 1 | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | - | 1 | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | - | 1 | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | - | 1 | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | - | 1 | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | 1 | - | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | 1 | - | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | 1 | - | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | 1 | - | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | 1 | - | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | 1 | - | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | - | 1 | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | 1 | - | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | 1 | - | - | - | -
- | JB-612 | Packing Tower | 1st | 325-01-613-PD-02 | - | - | - | - | - | - | 1
HS-61307A | JB-618 | Packing Tower | 8th | 325-01-613-PD-03 | HS-61307A | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307B | JB-618 | Packing Tower | 8th | 325-01-613-PD-03 | HS-61307B | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307C | JB-618 | Packing Tower | 7th | 325-01-613-PD-03 | HS-61307C | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307D | JB-618 | Packing Tower | 5th | 325-01-613-PD-03 | HS-61307D | 3-25-01-613-PD-03 | - | 1 | - | - | -
HS-61307E | JB-618 | Packing Tower | 5th | 325-01-613-PD-03 | HS-61307E | 3-25-01-613-PD-03 | - | 1 | - | - | -
LS-61303 | JB-618 | Packing Tower | 7th | - | LS-61303 | 3-25-01-613-PD-01 | - | 1 | - | - | -
LSH-61308 | JB-618 | Packing Tower | 9th | - | LSH-61308 | 3-25-01-613-PD-01 | - | 1 | - | - | -
PSL-61301 | JB-618 | Packing Tower | 5th | - | PSL-61301 | 3-25-01-613-PD-01 | - | 1 | - | - | -
- | JB-618 | Packing Tower | 5th | 325-01-613-PD-01 | - | - | - | 1 | - | - | -
PSL-61302 | JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | PSL-61302 | 3-25-01-613-PD-01 | - | 1 | - | - | -
PSL-61311 | JB-618 | Packing Tower | 8th | 325-01-613-PD-04 | PSL-61311 | 3-25-01-613-PD-04 | - | 1 | - | - | -
PT-61303 | JB-618 | Packing Tower | 8th | - | PT-61303 | 3-25-01-613-PD-01 | - | - | - | 1 | -
PT-61306 | JB-618 | Packing Tower | 8th | - | PT-61306 | 3-25-01-613-PD-01 | - | - | - | 1 | -
TT-61303 | JB-618 | Packing Tower | 8th | - | TT-61303 | 3-25-01-613-PD-01 | - | - | - | 1 | -
TT-61304 | JB-618 | Packing Tower | 8th | - | TT-61304 | 3-25-01-613-PD-01 | - | - | - | 1 | -
- | JB-618 | Packing Tower | 8th | 325-01-613-PD-01 | - | - | 1 | - | - | - | -
SV-61302 | JB-618 | Packing Tower | 7th | 325-01-613-PD-01 | SV-61302 | 3-25-01-613-PD-01 | 1 | - | - | - | -
SV-61303 | JB-618 | Packing Tower | 5th | 325-01-613-PD-01 | SV-61303 | 3-25-01-613-PD-01 | 1 | - | - | - | -
SV-61305 | JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | SV-61305 | 3-25-01-613-PD-01 | 1 | - | - | - | -
SV-61306 | JB-618 | Packing Tower | 5th | - | SV-61306 | 3-25-01-613-PD-01 | 1 | - | - | - | -
XV61301 | JB-618 | Packing Tower | 5th | - | XV61301 | 3-25-01-613-PD-01 | 1 | 2 | - | - | -
DV-61301 | JB-618 | Packing Tower | 5th | 325-01-613-PD-01 | DV-61301 | 3-25-01-613-PD-01 | 1 | 2 | - | - | -
DV-61302 | JB-618 | Packing Tower | 9th | - | DV-61302 | 3-25-01-613-PD-01 | 1 | 2 | - | - | -
- | JB-618 | Packing Tower | 8th | 325-01-613-PD-01 | - | - | 1 | 1 | - | - | 1
- | JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | - | - | 1 | 1 | - | - | 1
- | JB-618 | Packing Tower | 5th | 325-01-613-PD-01 | - | - | 2 | 2 | - | - | -
- | JB-618 | Packing Tower | 9th | 325-01-600-PD-08 | - | - | 2 | 2 | - | - | -
- | JB-618 | Packing Tower | 6th | 325-01-613-PD-01 | - | - | 2 | 2 | - | - | -
- | JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | - | - | 2 | 2 | - | - | -
- | JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | - | - | 2 | 2 | - | - | -
SV-61304 | JB-618 | Packing Tower | 9th | 325-01-613-PD-01 | SV-61304 | 3-25-01-613-PD-01 | 1 | 2 | - | - | -
FS-20201 | RIO-200 | Slurry - Out Building | 1st | - | FS-20201 | 3-25-01-202-PD-01 | - | - | - | 1 | -
HV-20204 | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-01 | HV-20204 | 3-25-01-202-PD-01 | - | 1 | - | - | -
HV-20205 | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-01 | HV-20205 | 3-25-01-202-PD-01 | - | 1 | - | - | -
HV-20206 | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-01 | HV-20206 | 3-25-01-202-PD-01 | - | 1 | - | - | -
HV-20207 | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-01 | HV-20207 | 3-25-01-202-PD-01 | - | 1 | - | - | -
HV-20208 | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-02 | HV-20208 | 3-25-01-202-PD-02 | - | 1 | - | - | -
HV-20209 | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-02 | HV-20209 | 3-25-01-202-PD-02 | - | 1 | - | - | -
HV-20210 | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-02 | HV-20210 | 3-25-01-202-PD-02 | - | 1 | - | - | -
XV-20201 | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-01 | XV-20201 | 3-25-01-202-PD-01 | 1 | 2 | - | - | -
XV-20202 | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-01 | XV-20202 | 3-25-01-202-PD-01 | 1 | 2 | - | - | -
XV-20203 | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-01 | XV-20203 | 3-25-01-202-PD-01 | 1 | 2 | - | - | -
XV-20211 | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-01 | XV-20211 | 3-25-01-202-PD-01 | 1 | 2 | - | - | -
XV-20212 | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-01 | XV-20212 | 3-25-01-202-PD-01 | 1 | 2 | - | - | -
XV-20213 | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-01 | XV-20213 | 3-25-01-202-PD-01 | 1 | 2 | - | - | -
- | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-01 | - | 3-25-01-202-PD-01 | 2 | 2 | - | - | -
- | RIO-200 | Slurry - Out Building | 1st | 325-01-200-PD-01 | - | 3-25-01-202-PD-01 | 2 | 2 | - | - | -
| RIO-200 | CIP Water System | 2nd | 3-25-01-810-PD-01 |  |  | 1 | 1 | - | - | 1
| RIO-200 | CIP Water System | 2nd | 3-25-01-810-PD-01 |  |  | 1 | 1 | - | - | 1
FT-913201 | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | FT-913201 | 3-25-01-913-PD-02 | - | 1 | - | 2 | -
PT-913201 | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | PT-913201 | 3-25-01-913-PD-02 | - | - | - | 1 | -
XV-913201 | RIO-200 | LPG System | 1st | - | XV-913201 | 3-25-01-913-PD-02 | 1 | 2 | - | 1 | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | - | 1 | - | - | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | - | 1 | - | - | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | - | 1 | - | - | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | - | 1 | - | - | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | - | 1 | - | - | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | - | 1 | - | - | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | 1 | - | - | - | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | - | 1 | - | - | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | - | 1 | - | - | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | - | 1 | - | - | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | - | 1 | - | - | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | - | 1 | - | - | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | - | 1 | - | - | -
- | RIO-200 | LPG System | 1st | 325-01-803-PD-02 | - | - | 1 | - | - | - | -
| RIO-200 | Boiler System | 1st |  |  | External Remote Setpoint | - | - | - | 1 | -
| RIO-200 | Boiler System | 1st |  |  | Spare | - | 1 | - | - | -
| RIO-200 | Boiler System | 1st |  |  | Spare | - | 1 | - | - | -
| RIO-200 | Boiler System | 1st |  |  | Spare | - | 1 | - | - | -
| RIO-200 | Boiler System | 1st |  |  | Spare | - | 1 | - | - | -
| RIO-200 | Boiler System | 1st |  |  | Spare | - | 1 | - | - | -
| RIO-200 | Boiler System | 1st |  |  | Spare | - | 1 | - | - | -
| RIO-200 | Boiler System | 1st |  |  | Boiler Common Alarm | 1 | - | - | - | -
| RIO-200 | Boiler System | 1st |  |  | Boiler trip | 1 | - | - | - | -
| RIO-200 | Boiler System | 1st |  |  | Burner Trip | 1 | - | - | - | -
| RIO-200 | Boiler System | 1st |  |  | Boiler Operation | 1 | - | - | - | -
| RIO-200 | Boiler System | 1st |  |  | Remote Setpoint Activateed | 1 | - | - | - | -
| RIO-200 | Boiler System | 1st |  |  | Remote Setpoint Status | 1 | - | - | - | -
FT-936202 | RIO-200 | Process Water | 1st | 325-01-930-PD-02 | FT-936202 | 3-25-01-930-PD-07 | - | 1 | - | 1 | -
FT-936201 | RIO-200 | Process Water | 1st | 325-01-930-PD-01 | FT-936201 | 3-25-01-930-PD-08 | - | 1 | - | 1 | -
LSL-814201 | RIO-200 | CIP Water System | 1st | - | LSL-814201 | 3-25-01-814-PD-01 | - | 1 | - | - | -
LT-913201 | RIO-200 | LPG System | 1st | 325-01-803-PD-01 | LT-913201 | 3-25-01-913-PD-01 | - | - | - | 1 | -
XT-92201 | RIO-200 | Boiler System | 1st | 325-01-923-PD-03 | XT-92201 | 3-25-01-922-PD-03 | - | - | - | 1 | -
XA-92201 | RIO-200 | Boiler System | 1st | 325-01-923-PD-03 | XA-92201 | 3-25-01-922-PD-03 | 1 | - | - | - | -
PK-913201 | RIO-200 | LPG System | 1st | - | PK-913201 | - | - | 1 | - | - | -
PK-913202 | RIO-200 | LPG System | 1st | - | PK-913202 | - | - | 1 | - | - | -

## Summary Dashboard
I/O LIST RECONCILIATION & COMPARISON REPORT
Comparison between [IO Check List.xlsx] (Rev 3.5/3.3) and [IO_List_xDev-R01-Tag35-3.xlsx] (Rev 3.6)
1. Executive Summary KPI Table
Metric Category | Count / Value | % of Check List | Engineering Implication
Total Rows Analyzed in IO Check List | 472 | 100.0% | Total instruments / signals in engineering check list
Direct Match on Tag 3.5 (Tag No. 3.6) | 328 | 69.5% | Tags existing and identical in Rev 3.6
Fallback Match on Tag 3.3 | 121 | 25.6% | Tag 3.5 was unassigned; tag matched using Rev 3.3 name
Missing in Dev (No Have) | 10 | 2.1% | Tags in Check List absent from Dev (includes renames/typos/removed)
Empty Tag Entries in Check List | 13 | 2.8% | Boiler remote setpoints, trips & alarms without assigned tag
Extra Tags in Dev Rev 3.6 (Not in Check List) | 85 | - | Newly introduced tags, control panels, package equipment
Rows with Attribute Discrepancies (JB / P&ID / IO) | 59 | 12.5% | Tags match, but Junction Box, P&ID or DI/DO/AI/AO count differs
2. Key Discrepancy Categories & Action Items
Category | Occurrences | Root Cause / Example | Recommended Engineering Action
Tag Typo in Check List | 1 | Row 156: 'XV61301' missing hyphen vs Dev 'XV-61301' | Correct typo in Check List to include hyphen.
Instrument Renamed in Dev | 2 | Rows 34-35: 'FS-40201', 'FS-40202' renamed to 'FSL-40201', 'FSL-40202' | Confirm Flow Switch Low (FSL) designation with P&ID.
Decommissioned / Removed I/P | 7 | Rows 64-67 (ATY/PCY-40101/40102), Row 186, Rows 360-361 | Confirm whether these 4-20mA I/P converters were removed from design.
Junction Box Routing Mismatch | 59 | e.g. PCM-2030 in RIO-200 vs MCC; XV-60251 in JB-401 vs JB-601 | Review physical field JB vs Motor Control Center (MCC) marshalling.
Signal Type / Channel Mismatch | 20 | e.g. FS-20201 has AI in Check List, but DI in Dev IO List | Reconcile whether devices are dry contact switches or analog transmitters.
Boiler System Unassigned Signals | 13 | Rows 379-391: Boiler alarms, trips & setpoints without tag number | Assign standard PLC tags (e.g. XA-80101) in Rev 3.6.

## Row_by_Row_Comparison
Item | Match Status | Check: Tag 3.3 | Check: Tag 3.5 | Dev: Matched Tag | In Rev.3 | In IO List | Check: JB | Dev: JB | JB Status | Check: P&ID 3.5 | Dev: P&ID | P&ID Status | DO (Chk/Dev) | DI (Chk/Dev) | AO (Chk/Dev) | AI (Chk/Dev) | Bus (Chk/Dev) | Signals Status | Detailed Discrepancies & Engineering Remarks
1 | MATCH (Tag 3.5) | FS-20201 | FS-20201 | FS-20201 | NO | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-01 | 3-25-01-202-PD-01 | MATCH | 0 / 0 | 0 / 1 | 0 / 0 | 1 / 0 | 0 / 0 | DIFF | Signal Diff: DI: 0->1, AI: 1->0
2 | MATCH (Tag 3.5) | HV-2022 | HV-20204 | HV-20204 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-01 | 3-25-01-202-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
3 | MATCH (Tag 3.5) | HV-2024 | HV-20205 | HV-20205 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-01 | 3-25-01-202-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.5) | HV-2026 | HV-20206 | HV-20206 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-01 | 3-25-01-202-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
5 | MATCH (Tag 3.5) | HV-2030 | HV-20207 | HV-20207 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-01 | 3-25-01-202-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
6 | MATCH (Tag 3.5) | HV-2032 | HV-20208 | HV-20208 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-02 | 3-25-01-202-PD-02 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
7 | MATCH (Tag 3.5) | HV-2035 | HV-20209 | HV-20209 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-02 | 3-25-01-202-PD-02 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
8 | MATCH (Tag 3.5) | HV-2038 | HV-20210 | HV-20210 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-02 | 3-25-01-202-PD-02 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
9 | MATCH (Tag 3.5) | XV-20201 | XV-20201 | XV-20201 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-01 | 3-25-01-202-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
10 | MATCH (Tag 3.5) | XV-20202 | XV-20202 | XV-20202 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-01 | 3-25-01-202-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
11 | MATCH (Tag 3.5) | XV-20203 | XV-20203 | XV-20203 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-01 | 3-25-01-202-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
12 | MATCH (Tag 3.5) | XV-20211 | XV-20211 | XV-20211 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-01 | 3-25-01-202-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
13 | MATCH (Tag 3.5) | XV-20212 | XV-20212 | XV-20212 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-01 | 3-25-01-202-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
14 | MATCH (Tag 3.5) | XV-20213 | XV-20213 | XV-20213 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-202-PD-01 | 3-25-01-202-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
15 | MATCH (Tag 3.3) | PCM-2030 | - | PCM-2030 | NO | YES | RIO-200 | MCC | DIFF | 3-25-01-202-PD-01 | 3-25-01-202-PD-01 | MATCH | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="RIO-200" vs Dev="MCC"
16 | MATCH (Tag 3.3) | PCM-2031 | - | PCM-2031 | YES | YES | RIO-200 | MCC | DIFF | 3-25-01-202-PD-01 | 3-25-01-202-PD-01 | MATCH | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="RIO-200" vs Dev="MCC"
1 | MATCH (Tag 3.5) | PT-40201 | PT-40201 | PT-40201 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-02 | 3-25-01-402-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
2 | MATCH (Tag 3.5) | FT-40201 | FT-40201 | FT-40201 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-02 | 3-25-01-402-PD-02 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 2 / 2 | 0 / 0 | MATCH | OK (Identical)
3 | MATCH (Tag 3.5) | FT-40202 | FT-40202 | FT-40202 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-02 | 3-25-01-402-PD-02 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.5) | HV-4208 | HV-40206 | HV-40206 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-02 | 3-25-01-402-PD-02 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
5 | MATCH (Tag 3.5) | HV-4210 | HV-40205 | HV-40205 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-02 | 3-25-01-402-PD-02 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
6 | MATCH (Tag 3.5) | LT-40201 | LT-40203 | LT-40203 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-02 | 3-25-01-402-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
7 | MATCH (Tag 3.5) | PT-40202 | PT-40202 | PT-40202 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-02 | 3-25-01-402-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
8 | MATCH (Tag 3.5) | PT-60202 | PT-60202 | PT-60202 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-602-PD-01 | 3-25-01-602-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
9 | MATCH (Tag 3.5) | XV-40201B | XV-40203B | XV-40203B | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-02 | 3-25-01-402-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
10 | MATCH (Tag 3.5) | XV-40201C | XV-40203C | XV-40203C | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-02 | 3-25-01-402-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
11 | MATCH (Tag 3.5) | XV-40201D | XV-40203D | XV-40203D | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-02 | 3-25-01-402-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
12 | MATCH (Tag 3.5) | XV-40201E | XV-40203E | XV-40203E | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-02 | 3-25-01-402-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
13 | MATCH (Tag 3.5) | XV-60251 | XV-60251 | XV-60251 | YES | YES | JB-401 | JB-601 | DIFF | 3-25-01-602-PD-01 | 3-25-01-602-PD-01 | MATCH | 1 / 1 | 2 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | DIFF | JB Difference: Check="JB-401" vs Dev="JB-601"; Signal Diff: DI: 2->0
14 | MATCH (Tag 3.5) | ATY-40201 | ATY-40203 | ATY-40203 | YES | YES | JB-401 | MCC | DIFF | 3-25-01-402-PD-02 | 3-25-01-402-PD-02 | MATCH | 1 / 1 | 1 / 3 | 0 / 0 | 0 / 0 | 1 / 1 | DIFF | JB Difference: Check="JB-401" vs Dev="MCC"; Signal Diff: DI: 1->3
15 | MATCH (Tag 3.5) | PCY-40201 | PCY-40203 | PCY-40203 | YES | YES | JB-401 | MCC | DIFF | 3-25-01-402-PD-02 | 3-25-01-402-PD-02 | MATCH | 1 / 1 | 1 / 3 | 0 / 0 | 0 / 0 | 1 / 1 | DIFF | JB Difference: Check="JB-401" vs Dev="MCC"; Signal Diff: DI: 1->3
1 | MISSING IN DEV | FS-40101 | FS-40201 | - | NO | NO | JB-401 | - | N/A | 3-25-01-402-PD-01 | - | N/A | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 0 | 0 / 0 | N/A | Renamed in Dev to "FSL-40201"
2 | MISSING IN DEV | FS-40102 | FS-40202 | - | NO | NO | JB-401 | - | N/A | 3-25-01-402-PD-01 | - | N/A | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 0 | 0 / 0 | N/A | Renamed in Dev to "FSL-40202"
3 | MATCH (Tag 3.5) | HV-4106 | HV-40203 | HV-40203 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.5) | HV-4108 | HV-40201 | HV-40201 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
5 | MATCH (Tag 3.5) | HV-4126 | HV-40204 | HV-40204 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
6 | MATCH (Tag 3.5) | HV-4128 | HV-40202 | HV-40202 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
7 | MATCH (Tag 3.5) | LT-40101 | LT-40201 | LT-40201 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 0 / 0 | 1 / 0 | 0 / 0 | 0 / 1 | 0 / 0 | DIFF | Signal Diff: DI: 1->0, AI: 0->1
8 | MATCH (Tag 3.5) | LT-40102 | LT-40202 | LT-40202 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 0 / 0 | 1 / 0 | 0 / 0 | 0 / 1 | 0 / 0 | DIFF | Signal Diff: DI: 1->0, AI: 0->1
9 | MATCH (Tag 3.5) | pHT-40101 | pHT-40201 | pHT-40201 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 0 / 0 | 1 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | DIFF | Signal Diff: DI: 1->0
10 | MATCH (Tag 3.5) | pHT-40102 | pHT-40202 | pHT-40202 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 0 / 0 | 1 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | DIFF | Signal Diff: DI: 1->0
11 | MATCH (Tag 3.5) | SV-40101 | SV-40201 | SV-40201 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
12 | MATCH (Tag 3.5) | SV-40102 | SV-40202 | SV-40202 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
13 | MATCH (Tag 3.5) | SV-40103 | SV-40203 | SV-40203 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
14 | MATCH (Tag 3.5) | SV-40104 | SV-40204 | SV-40204 | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
15 | MATCH (Tag 3.5) | XV-40101A | XV-40201A | XV-40201A | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
16 | MATCH (Tag 3.5) | XV-40101B | XV-40201B | XV-40201B | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
17 | MATCH (Tag 3.5) | XV-40101C | XV-40201C | XV-40201C | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
18 | MATCH (Tag 3.5) | XV-40101D | XV-40201D | XV-40201D | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
19 | MATCH (Tag 3.5) | XV-40101E | XV-40201E | XV-40201E | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
20 | MATCH (Tag 3.5) | XV-40101F | XV-40201F | XV-40201F | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
21 | MATCH (Tag 3.5) | XV-40101G | XV-40201G | XV-40201G | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
22 | MATCH (Tag 3.5) | XV-40101H | XV-40201H | XV-40201H | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
23 | MATCH (Tag 3.5) | XV-40102A | XV-40202A | XV-40202A | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
24 | MATCH (Tag 3.5) | XV-40102B | XV-40202B | XV-40202B | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
25 | MATCH (Tag 3.5) | XV-40102C | XV-40202C | XV-40202C | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
26 | MATCH (Tag 3.5) | XV-40102D | XV-40202D | XV-40202D | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
27 | MATCH (Tag 3.5) | XV-40102E | XV-40202E | XV-40202E | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
28 | MATCH (Tag 3.5) | XV-40102F | XV-40202F | XV-40202F | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
29 | MATCH (Tag 3.5) | XV-40102G | XV-40202G | XV-40202G | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
30 | MATCH (Tag 3.5) | XV-40102H | XV-40202H | XV-40202H | YES | YES | JB-401 | JB-401 | MATCH | 3-25-01-402-PD-01 | 3-25-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
31 | MISSING IN DEV | ATY-40101 | - | - | NO | NO | JB-401 | - | N/A | 3-25-01-402-PD-01 | - | N/A | 1 / 0 | 1 / 0 | 0 / 0 | 0 / 0 | 1 / 0 | N/A | Tag 3.3 ("ATY-40101") not found in Dev (Tag 3.5 empty)
32 | MISSING IN DEV | ATY-40102 | - | - | NO | NO | JB-401 | - | N/A | 3-25-01-402-PD-01 | - | N/A | 1 / 0 | 1 / 0 | 0 / 0 | 0 / 0 | 1 / 0 | N/A | Tag 3.3 ("ATY-40102") not found in Dev (Tag 3.5 empty)
33 | MISSING IN DEV | PCY-40101 | - | - | NO | NO | JB-401 | - | N/A | 3-25-01-402-PD-01 | - | N/A | 1 / 0 | 1 / 0 | 0 / 0 | 0 / 0 | 1 / 0 | N/A | Tag 3.3 ("PCY-40101") not found in Dev (Tag 3.5 empty)
34 | MISSING IN DEV | PCY-40102 | - | - | NO | NO | JB-401 | - | N/A | 3-25-01-402-PD-01 | - | N/A | 1 / 0 | 1 / 0 | 0 / 0 | 0 / 0 | 1 / 0 | N/A | Tag 3.3 ("PCY-40102") not found in Dev (Tag 3.5 empty)
1 | MATCH (Tag 3.5) | - | FS-40204 | FS-40204 | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-01 | 325-01-402-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
2 | MATCH (Tag 3.5) | - | FS-40205 | FS-40205 | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | 325-01-402-PD-02 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
3 | MATCH (Tag 3.5) | - | FT-40221 | FT-40221 | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | 325-01-402-PD-02 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 2 / 2 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.5) | - | FT-40222 | FT-40222 | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | 325-01-402-PD-02 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 2 / 2 | 0 / 0 | MATCH | OK (Identical)
5 | MATCH (Tag 3.5) | - | HV-40207 | HV-40207 | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-01 | 325-01-402-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
6 | MATCH (Tag 3.5) | - | HV-40208 | HV-40208 | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-01 | 325-01-402-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
7 | MATCH (Tag 3.5) | - | PT-40222 | PT-40222 | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | 325-01-402-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
8 | MATCH (Tag 3.5) | - | TT-40221 | TT-40221 | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | 325-01-402-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
9 | MATCH (Tag 3.5) | - | TT-40222 | TT-40222 | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | 325-01-402-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
10 | MATCH (Tag 3.5) | - | TCV-40222 | TCV-40222 | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | 325-01-402-PD-02 | MATCH | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
11 | MATCH (Tag 3.5) | - | XV-40203F | XV-40203F | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | 325-01-402-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
12 | MATCH (Tag 3.5) | - | XV-40204B | XV-40204B | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-01 | 325-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
13 | MATCH (Tag 3.5) | - | XV-40204C | XV-40204C | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-01 | 325-01-402-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
14 | MATCH (Tag 3.5) | - | XV-40205A | XV-40205A | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | 325-01-402-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
15 | MATCH (Tag 3.5) | - | XV-40205B | XV-40205B | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | 325-01-402-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
16 | MATCH (Tag 3.5) | - | XV-40205C | XV-40205C | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | 325-01-402-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
17 | MATCH (Tag 3.5) | - | XV-40205D | XV-40205D | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | 325-01-402-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
18 | MATCH (Tag 3.5) | - | XV-40205F | XV-40205F | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | 325-01-402-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
19 | MATCH (Tag 3.5) | - | XV-40222 | XV-40222 | YES | YES | JB-402 | JB-402 | MATCH | 325-01-402-PD-02 | -, 325-01-402-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
1 | MATCH (Tag 3.5) | HS-61307F | HS-61307F | HS-61307F | YES | YES | JB-612 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-612" vs Dev="MCC"
2 | MATCH (Tag 3.5) | HS-61307G | HS-61307G | HS-61307G | YES | YES | JB-612 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-612" vs Dev="MCC"
3 | MATCH (Tag 3.5) | HS-61307H | HS-61307H | HS-61307H | YES | YES | JB-612 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-612" vs Dev="MCC"
4 | MATCH (Tag 3.5) | HS-61307I | HS-61307I | HS-61307I | YES | YES | JB-612 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-612" vs Dev="MCC"
5 | MATCH (Tag 3.5) | HS-61307J | HS-61307J | HS-61307J | YES | YES | JB-612 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-612" vs Dev="MCC"
6 | MATCH (Tag 3.5) | HS-61307K | HS-61307K | HS-61307K | YES | YES | JB-612 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-612" vs Dev="MCC"
7 | MATCH (Tag 3.5) | HS-61307L | HS-61307L | HS-61307L | YES | YES | JB-612 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-612" vs Dev="MCC"
8 | MATCH (Tag 3.5) | HS-61307M | HS-61307M | HS-61307M | YES | YES | JB-612 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-612" vs Dev="MCC"
9 | MATCH (Tag 3.5) | HS-61307N | HS-61307N | HS-61307N | YES | YES | JB-612 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-612" vs Dev="MCC"
10 | MATCH (Tag 3.5) | HS-61307O | HS-61307O | HS-61307O | YES | YES | JB-612 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-612" vs Dev="MCC"
11 | MATCH (Tag 3.5) | HS-61307P | HS-61307P | HS-61307P | YES | YES | JB-612 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-612" vs Dev="MCC"
12 | MATCH (Tag 3.5) | HS-61307Q | HS-61307Q | HS-61307Q | YES | YES | JB-612 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-612" vs Dev="MCC"
13 | MATCH (Tag 3.5) | HS-61307R | HS-61307R | HS-61307R | YES | YES | JB-612 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-612" vs Dev="MCC"
14 | MATCH (Tag 3.5) | PSL-61305 | PSL-61305 | PSL-61305 | YES | YES | JB-612 | JB-612 | MATCH | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
15 | MATCH (Tag 3.5) | PSL-61306 | PSL-61306 | PSL-61306 | YES | YES | JB-612 | JB-612 | MATCH | 3-25-01-613-PD-05 | 3-25-01-613-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
16 | MATCH (Tag 3.5) | PT-61302 | PT-61302 | PT-61302 | YES | YES | JB-612 | JB-612 | MATCH | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 2 | 0 / 0 | DIFF | Signal Diff: AI: 1->2
17 | MATCH (Tag 3.5) | PT-61309 | PT-61309 | PT-61309 | YES | YES | JB-612 | JB-612 | MATCH | 3-25-01-613-PD-04 | 3-25-01-613-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 2 | 0 / 0 | DIFF | Signal Diff: AI: 1->2
18 | MATCH (Tag 3.5) | SV-61307 | SV-61307 | SV-61307 | NO | YES | JB-612 | JB-612 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
19 | MATCH (Tag 3.3) | SV-61308 | - | SV-61308 | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
20 | MATCH (Tag 3.5) | SV-61309 | SV-61309 | SV-61309 | YES | YES | JB-612 | JB-612 | MATCH | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
21 | MATCH (Tag 3.3) | SV-61310 | - | SV-61310 | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
22 | MATCH (Tag 3.5) | SV-61311 | SV-61311 | SV-61311 | YES | YES | JB-612 | JB-612 | MATCH | 3-25-01-613-PD-05 | 3-25-01-613-PD-05 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
23 | MATCH (Tag 3.5) | XV-61302 | XV-61302 | XV-61302 | YES | YES | JB-612 | JB-612 | MATCH | 3-25-01-613-PD-02 | 3-25-01-613-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
24 | MATCH (Tag 3.5) | XV-61303 | XV-61303 | XV-61303 | YES | YES | JB-612 | JB-612 | MATCH | 3-25-01-613-PD-02 | 3-25-01-613-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
25 | MATCH (Tag 3.3) | BFY-61302 | - | BFY-61302 | YES | YES | JB-612 | MCC | DIFF | - | - | N/A | 1 / 1 | 1 / 1 | 0 / 0 | 0 / 0 | 1 / 1 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-612" vs Dev="MCC"
26 | MATCH (Tag 3.3) | PVM-61301 | - | PVM-61301 | NO | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
27 | MATCH (Tag 3.3) | RVM-61302 | - | RVM-61302 | YES | YES | JB-612 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-612" vs Dev="MCC"
28 | MATCH (Tag 3.3) | RVM-61303 | - | RVM-61303 | YES | YES | JB-612 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-612" vs Dev="MCC"
29 | MATCH (Tag 3.3) | SCM-61301 | - | SCM-61301 | YES | YES | JB-612 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-612" vs Dev="MCC"
30 | MATCH (Tag 3.3) | SCM-61302 | - | SCM-61302 | YES | YES | JB-612 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-612" vs Dev="MCC"
31 | MATCH (Tag 3.3) | XA-61301A | - | XA-61301A | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
32 | MATCH (Tag 3.3) | XA-61301B | - | XA-61301B | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
33 | MATCH (Tag 3.3) | XA-61301C | - | XA-61301C | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
34 | MATCH (Tag 3.3) | XA-61301D | - | XA-61301D | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
35 | MATCH (Tag 3.3) | XA-61301E | - | XA-61301E | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
36 | MATCH (Tag 3.3) | XA-61301F | - | XA-61301F | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
37 | MATCH (Tag 3.3) | XA-61301G | - | XA-61301G | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
38 | MATCH (Tag 3.3) | XA-61301H | - | XA-61301H | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
39 | MATCH (Tag 3.3) | XA-61301J | - | XA-61301J | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
40 | MATCH (Tag 3.3) | XS-61301A | - | XS-61301A | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
41 | MATCH (Tag 3.3) | XS-61301B | - | XS-61301B | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
42 | MATCH (Tag 3.3) | XS-61301C | - | XS-61301C | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
43 | MATCH (Tag 3.3) | XS-61301D | - | XS-61301D | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
44 | MATCH (Tag 3.3) | XS-61301E | - | XS-61301E | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
45 | MATCH (Tag 3.3) | XS-61301F | - | XS-61301F | YES | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
46 | MATCH (Tag 3.3) | Spare | - | Spare | NO | YES | JB-612 | CA1, IS-JB-603, IS-JB-608, IS-JB-612, IS-JB-618, JB-401, JB-402, JB-601, JB-602, JB-606, JB-607, JB-608, JB-612, JB-618, MCC, RIO-200 | MATCH | - | -, 3-25-01-402-PD-01, 3-25-01-613-PD-01, 3-25-01-913-PD-02 | N/A | 0 / 166 | 1 / 210 | 0 / 3 | 0 / 68 | 0 / 0 | N/A | Tag 3.5 was blank/hyphen; matched via Tag 3.3
47 | MATCH (Tag 3.3) | Spare | - | Spare | NO | YES | JB-612 | CA1, IS-JB-603, IS-JB-608, IS-JB-612, IS-JB-618, JB-401, JB-402, JB-601, JB-602, JB-606, JB-607, JB-608, JB-612, JB-618, MCC, RIO-200 | MATCH | - | -, 3-25-01-402-PD-01, 3-25-01-613-PD-01, 3-25-01-913-PD-02 | N/A | 1 / 166 | 0 / 210 | 0 / 3 | 0 / 68 | 0 / 0 | N/A | Tag 3.5 was blank/hyphen; matched via Tag 3.3
48 | MATCH (Tag 3.3) | Spare | - | Spare | NO | YES | JB-612 | CA1, IS-JB-603, IS-JB-608, IS-JB-612, IS-JB-618, JB-401, JB-402, JB-601, JB-602, JB-606, JB-607, JB-608, JB-612, JB-618, MCC, RIO-200 | MATCH | - | -, 3-25-01-402-PD-01, 3-25-01-613-PD-01, 3-25-01-913-PD-02 | N/A | 1 / 166 | 0 / 210 | 0 / 3 | 0 / 68 | 0 / 0 | N/A | Tag 3.5 was blank/hyphen; matched via Tag 3.3
49 | MATCH (Tag 3.3) | Communication Signal | - | Communication Signal | NO | YES | JB-612 | JB-612 | MATCH | - | - | N/A | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
1 | MATCH (Tag 3.5) | HS-61307A | HS-61307A | HS-61307A | YES | YES | JB-618 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-618" vs Dev="MCC"
2 | MATCH (Tag 3.5) | HS-61307B | HS-61307B | HS-61307B | YES | YES | JB-618 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-618" vs Dev="MCC"
3 | MATCH (Tag 3.5) | HS-61307C | HS-61307C | HS-61307C | YES | YES | JB-618 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-618" vs Dev="MCC"
4 | MATCH (Tag 3.5) | HS-61307D | HS-61307D | HS-61307D | YES | YES | JB-618 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-618" vs Dev="MCC"
5 | MATCH (Tag 3.5) | HS-61307E | HS-61307E | HS-61307E | YES | YES | JB-618 | MCC | DIFF | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-618" vs Dev="MCC"
6 | MATCH (Tag 3.5) | LS-61303 | LS-61303 | LS-61303 | YES | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
7 | MATCH (Tag 3.5) | NEW | LSH-61308 | LSH-61308 | YES | YES | JB-618 | IS-JB-618 | DIFF | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | JB Difference: Check="JB-618" vs Dev="IS-JB-618"
8 | MATCH (Tag 3.5) | NEW | PSL-61301 | PSL-61301 | YES | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-01 | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
9 | MATCH (Tag 3.3) | PSL-61301 | - | PSL-61301 | YES | YES | JB-618 | JB-618 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
10 | MATCH (Tag 3.5) | PSL-61302 | PSL-61302 | PSL-61302 | YES | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
11 | MATCH (Tag 3.5) | PSL-61311 | PSL-61311 | PSL-61311 | YES | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-04 | 3-25-01-613-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
12 | MATCH (Tag 3.5) | - | PT-61303 | PT-61303 | YES | YES | JB-618 | IS-JB-618, JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 2 | 0 / 0 | DIFF | Signal Diff: AI: 1->2
13 | MATCH (Tag 3.5) | - | PT-61306 | PT-61306 | NO | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
14 | MATCH (Tag 3.5) | - | TT-61303 | TT-61303 | NO | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
15 | MATCH (Tag 3.5) | - | TT-61304 | TT-61304 | NO | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
16 | MATCH (Tag 3.3) | SV-61301 | - | SV-61301 | YES | YES | JB-618 | JB-618 | MATCH | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
17 | MATCH (Tag 3.5) | SV-61302 | SV-61302 | SV-61302 | YES | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
18 | MATCH (Tag 3.5) | SV-61303 | SV-61303 | SV-61303 | YES | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
19 | MATCH (Tag 3.5) | SV-61305 | SV-61305 | SV-61305 | YES | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
20 | MATCH (Tag 3.5) | SV-61306 | SV-61306 | SV-61306 | NO | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
21 | MISSING IN DEV | HV-61301 | XV61301 | - | NO | NO | JB-618 | - | N/A | 3-25-01-613-PD-01 | - | N/A | 1 / 0 | 2 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | N/A | Typo in Check List (missing hyphen): Dev has "XV-61301"
22 | MATCH (Tag 3.5) | XV-61301 | DV-61301 | DV-61301 | YES | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
23 | MATCH (Tag 3.5) | XV-61302 | DV-61302 | DV-61302 | YES | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
24 | MATCH (Tag 3.3) | BFY-61301 | - | BFY-61301 | YES | YES | JB-618 | MCC | DIFF | - | - | N/A | 1 / 1 | 1 / 1 | 0 / 0 | 0 / 0 | 1 / 1 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-618" vs Dev="MCC"
25 | MATCH (Tag 3.3) | BFY-61303 | - | BFY-61303 | YES | YES | JB-618 | MCC | DIFF | - | - | N/A | 1 / 1 | 1 / 1 | 0 / 0 | 0 / 0 | 1 / 1 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-618" vs Dev="MCC"
26 | MATCH (Tag 3.3) | BLM-61302 | - | BLM-61302 | YES | YES | JB-618 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-618" vs Dev="MCC"
27 | MATCH (Tag 3.3) | RVM-60204 | - | RVM-60204 | YES | YES | JB-618 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-618" vs Dev="MCC"
28 | MATCH (Tag 3.3) | RVM-61301 | - | RVM-61301 | YES | YES | JB-618 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-618" vs Dev="MCC"
29 | MATCH (Tag 3.3) | RVM-61304 | - | RVM-61304 | YES | YES | JB-618 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-618" vs Dev="MCC"
30 | MATCH (Tag 3.3) | RVM-61305 | - | RVM-61305 | YES | YES | JB-618 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-618" vs Dev="MCC"
31 | MATCH (Tag 3.5) | SV-61304 | SV-61304 | SV-61304 | YES | YES | JB-618 | JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
1 | MATCH (Tag 3.5) | DPT-60202 | DPT-60202 | DPT-60202 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-08 | 3-25-01-602-PD-08 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
2 | MATCH (Tag 3.5) | FT-60201 | FT-60201 | FT-60201 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-08 | 3-25-01-602-PD-08 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
3 | MATCH (Tag 3.5) | FT-60307 | FT-61307 | FT-61307 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-613-PD-04 | 3-25-01-613-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.3) | FT-61307 | - | FT-61307 | YES | YES | JB-601 | JB-601 | MATCH | - | 3-25-01-613-PD-04 | N/A | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
5 | MATCH (Tag 3.5) | FT-61101 | FT-60204 | FT-60204 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-10 | 3-25-01-602-PD-10 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
6 | MATCH (Tag 3.5) | LSL-61101 | LSL-60201 | LSL-60201 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-11 | 3-25-01-602-PD-11 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
7 | MATCH (Tag 3.5) | PT-60203 | PT-60203 | PT-60203 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-08 | 3-25-01-602-PD-08 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
8 | MATCH (Tag 3.5) | PT-61101 | PT-60204 | PT-60204 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-10 | 3-25-01-602-PD-10 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
9 | MATCH (Tag 3.5) | SV-60230 | SV-60230 | SV-60230 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
10 | MATCH (Tag 3.5) | SV-60231 | SV-60231 | SV-60231 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
11 | MATCH (Tag 3.5) | SV-60240A | SV-60240A | SV-60240A | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
12 | MATCH (Tag 3.5) | SV-60240B | SV-60240B | SV-60240B | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
13 | MATCH (Tag 3.5) | SV-60240C | SV-60240C | SV-60240C | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
14 | MATCH (Tag 3.5) | XV-61101 | XV-60202 | XV-60202 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-11 | 3-25-01-602-PD-11 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
15 | MATCH (Tag 3.3) | BFY-60206 | - | BFY-60206 | YES | YES | JB-601 | MCC | DIFF | - | - | N/A | 1 / 1 | 1 / 1 | 0 / 0 | 0 / 0 | 1 / 1 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-601" vs Dev="MCC"
16 | MATCH (Tag 3.3) | PCM-60205-2 | - | PCM-60205-2 | NO | YES | JB-601 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-601" vs Dev="MCC"
17 | MATCH (Tag 3.3) | PCM-60205-3 | - | PCM-60205-3 | NO | YES | JB-601 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-601" vs Dev="MCC"
18 | MATCH (Tag 3.3) | PCM-60205-4 | - | PCM-60205-4 | NO | YES | JB-601 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-601" vs Dev="MCC"
19 | MATCH (Tag 3.3) | PCM-60205-5 | - | PCM-60205-5 | NO | YES | JB-601 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-601" vs Dev="MCC"
20 | MISSING IN DEV | PCY-60205-1 | - | - | NO | NO | JB-601 | - | N/A | - | - | N/A | 1 / 0 | 1 / 0 | 0 / 0 | 0 / 0 | 1 / 0 | N/A | Tag 3.3 ("PCY-60205-1") not found in Dev (Tag 3.5 empty)
21 | MATCH (Tag 3.3) | RVM-60201 | - | RVM-60201 | YES | YES | JB-601 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-601" vs Dev="MCC"
22 | MATCH (Tag 3.3) | RVM-60202 | - | RVM-60202 | YES | YES | JB-601 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-601" vs Dev="MCC"
23 | MATCH (Tag 3.3) | RVM-60203 | - | RVM-60203 | YES | YES | JB-601 | MCC | DIFF | - | - | N/A | 2 / 2 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-601" vs Dev="MCC"
24 | MATCH (Tag 3.3) | XV-60240D | - | XV-60240D | NO | YES | JB-601 | JB-601 | MATCH | - | -, 3-25-01-602-PD-05 | N/A | 1 / 1 | 2 / 4 | 0 / 0 | 0 / 0 | 0 / 0 | DIFF | Tag 3.5 was blank/hyphen; matched via Tag 3.3; Signal Diff: DI: 2->4
25 | MATCH (Tag 3.5) | SV-60201 | SV-60201 | SV-60201 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-08 | 3-25-01-602-PD-08 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
26 | MATCH (Tag 3.5) | SV-60202 | SV-60202 | SV-60202 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-08 | 3-25-01-602-PD-08 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
27 | MATCH (Tag 3.5) | SV-60203 | SV-60203 | SV-60203 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-08 | 3-25-01-602-PD-08 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
28 | MATCH (Tag 3.3) | XA-60202A | - | XA-60202A | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
29 | MATCH (Tag 3.3) | XA-60202B | - | XA-60202B | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
30 | MATCH (Tag 3.3) | XA-60202C | - | XA-60202C | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
31 | MATCH (Tag 3.3) | XA-60202D | - | XA-60202D | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
32 | MATCH (Tag 3.3) | XA-60202E | - | XA-60202E | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
33 | MATCH (Tag 3.3) | XA-60202F | - | XA-60202F | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
34 | MATCH (Tag 3.3) | XA-60202G | - | XA-60202G | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
35 | MATCH (Tag 3.3) | XA-60202H | - | XA-60202H | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
36 | MATCH (Tag 3.3) | XA-60202J | - | XA-60202J | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
37 | MATCH (Tag 3.3) | XA-60202K | - | XA-60202K | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
38 | MATCH (Tag 3.3) | XA-60202L | - | XA-60202L | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
39 | MATCH (Tag 3.3) | XA-60202M | - | XA-60202M | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
40 | MATCH (Tag 3.5) | XV-60240 | XV-60240D | XV-60240D | NO | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-05 | -, 3-25-01-602-PD-05 | MATCH | 1 / 1 | 2 / 4 | 0 / 0 | 0 / 0 | 0 / 0 | DIFF | Signal Diff: DI: 2->4
41 | MATCH (Tag 3.3) | DPI-60240 | - | DPI-60240 | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
42 | MATCH (Tag 3.3) | ES-60202 | - | ES-60202 | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
43 | MATCH (Tag 3.5) | PT-60205 | PT-60205 | PT-60205 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-01 | 3-25-01-602-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
44 | MATCH (Tag 3.5) | FS-60205 | FS-60205 | FS-60205 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-01 | 3-25-01-602-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
45 | MATCH (Tag 3.3) | XS-60205 | - | XS-60205 | YES | YES | JB-601 | MCC | DIFF | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-601" vs Dev="MCC"
46 | MATCH (Tag 3.5) | VS-60205 | VS-60205 | VS-60205 | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-01 | 3-25-01-602-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
47 | MATCH (Tag 3.5) | XV-60205A | XV-60205A | XV-60205A | YES | YES | JB-601 | JB-601 | MATCH | 3-25-01-602-PD-01 | 3-25-01-602-PD-01 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
48 | MATCH (Tag 3.3) | YA-60205 | - | YA-60205 | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
49 | MATCH (Tag 3.3) | YI-60205 | - | YI-60205 | YES | YES | JB-601 | JB-601 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
1 | MATCH (Tag 3.5) | AT-60241 | AT-60241 | AT-60241 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
2 | MATCH (Tag 3.5) | DPT-60203 | DPT-60203 | DPT-60203 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
3 | MATCH (Tag 3.5) | FT-60210 | FT-60210 | FT-60210 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 2 / 2 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.5) | FT-60211 | FT-60211 | FT-60211 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 2 / 2 | 0 / 0 | MATCH | OK (Identical)
5 | MATCH (Tag 3.5) | FT-60902 | FT-60202 | FT-60202 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-09 | 3-25-01-602-PD-09 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
6 | MATCH (Tag 3.5) | LSH-60251 | LSH-60251 | LSH-60251 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
7 | MATCH (Tag 3.5) | PSL-60220 | PSL-60220 | PSL-60220 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
8 | MATCH (Tag 3.5) | PT-60210 | PT-60210 | PT-60210 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
9 | MATCH (Tag 3.5) | PT-60215 | PT-60215 | PT-60215 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
10 | MATCH (Tag 3.5) | PT-60216 | PT-60216 | PT-60216 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
11 | MATCH (Tag 3.5) | PT-60240 | PT-60240 | PT-60240 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
12 | MATCH (Tag 3.5) | PT-60241 | PT-60241 | PT-60241 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
13 | MATCH (Tag 3.5) | TSH-60230 | TSH-60230 | TSH-60230 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
14 | MATCH (Tag 3.5) | TSH-60240 | TSH-60240 | TSH-60240 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
15 | MATCH (Tag 3.5) | TT-60210 | TT-60210 | TT-60210 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
16 | MATCH (Tag 3.3) | TT-60210A | - | TT-60210A | NO | YES | JB-602 | JB-602 | MATCH | - | - | N/A | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
17 | MATCH (Tag 3.3) | TT-60210B | - | TT-60210B | NO | YES | JB-602 | JB-602 | MATCH | - | - | N/A | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
18 | MATCH (Tag 3.5) | TT-60211 | TT-60211 | TT-60211 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
19 | MATCH (Tag 3.5) | TT-60214 | TT-60214 | TT-60214 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
20 | MATCH (Tag 3.5) | TT-60215A | TT-60215A | TT-60215A | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
21 | MATCH (Tag 3.5) | TT-60215B | TT-60215B | TT-60215B | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
22 | MATCH (Tag 3.5) | TT-60216 | TT-60216 | TT-60216 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
23 | MATCH (Tag 3.5) | TT-60240 | TT-60240 | TT-60240 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
24 | MATCH (Tag 3.5) | TT-60241A | TT-60241A | TT-60241A | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
25 | MATCH (Tag 3.5) | TT-60241B | TT-60241B | TT-60241B | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
26 | MATCH (Tag 3.5) | TV-60214 | TV-60214 | TV-60214 | NO | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
27 | MATCH (Tag 3.5) | TV-60702 | TV-60202 | TV-60202 | NO | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-07 | 3-25-01-602-PD-07 | MATCH | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
28 | MATCH (Tag 3.5) | TT-60212A | TT-60212A | TT-60212A | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
29 | MATCH (Tag 3.5) | TT-60212B | TT-60212B | TT-60212B | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
30 | MATCH (Tag 3.5) | VT-60210A | VT-60210A | VT-60210A | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
31 | MATCH (Tag 3.5) | VT-60210B | VT-60210B | VT-60210B | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
32 | MATCH (Tag 3.5) | VT-60241A | VT-60241A | VT-60241A | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
33 | MATCH (Tag 3.5) | VT-60241B | VT-60241B | VT-60241B | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
34 | MATCH (Tag 3.5) | XV-60301 | XV-60214 | XV-60214 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
35 | MATCH (Tag 3.3) | BFY-60210 | - | BFY-60210 | YES | YES | JB-602 | MCC | DIFF | - | - | N/A | 1 / 1 | 1 / 1 | 0 / 0 | 0 / 0 | 1 / 1 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-602" vs Dev="MCC"
36 | MATCH (Tag 3.3) | BFY-60211 | - | BFY-60211 | YES | YES | JB-602 | MCC | DIFF | - | - | N/A | 1 / 1 | 1 / 1 | 0 / 0 | 0 / 0 | 1 / 1 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-602" vs Dev="MCC"
37 | MATCH (Tag 3.3) | BFY-60240 | - | BFY-60240 | YES | YES | JB-602 | MCC | DIFF | - | - | N/A | 1 / 1 | 1 / 1 | 0 / 0 | 0 / 0 | 1 / 1 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-602" vs Dev="MCC"
38 | MATCH (Tag 3.3) | PCY-60215 | - | PCY-60215 | YES | YES | JB-602 | MCC | DIFF | - | - | N/A | 1 / 1 | 1 / 3 | 0 / 0 | 0 / 0 | 1 / 1 | DIFF | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-602" vs Dev="MCC"; Signal Diff: DI: 1->3
39 | MATCH (Tag 3.5) | XV-60241 | XV-60241 | XV-60241 | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
40 | MATCH (Tag 3.3) | XS-60240A | - | XS-60240A | YES | YES | JB-602 | MCC | DIFF | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-602" vs Dev="MCC"
41 | MATCH (Tag 3.3) | XS-60240B | - | XS-60240B | YES | YES | JB-602 | JB-602 | MATCH | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
42 | MATCH (Tag 3.3) | XA-60240A | - | XA-60240A | YES | YES | JB-602 | JB-602 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
43 | MATCH (Tag 3.3) | XA-60240B | - | XA-60240B | YES | YES | JB-602 | JB-602 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
44 | MATCH (Tag 3.3) | XS-60241A | - | XS-60241A | YES | YES | JB-602 | MCC | DIFF | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-602" vs Dev="MCC"
45 | MATCH (Tag 3.3) | XA-60241A | - | XA-60241A | YES | YES | JB-602 | JB-602 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
46 | MATCH (Tag 3.3) | XA-60241B | - | XA-60241B | YES | YES | JB-602 | JB-602 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
47 | MATCH (Tag 3.5) | TSH-60241A | TSH-60241A | TSH-60241A | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
48 | MATCH (Tag 3.5) | TSL-60241B | TSL-60241B | TSL-60241B | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
49 | MATCH (Tag 3.3) | XS-60242A | - | XS-60242A | YES | YES | JB-602 | MCC | DIFF | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-602" vs Dev="MCC"
50 | MATCH (Tag 3.3) | XA-60242A | - | XA-60242A | YES | YES | JB-602 | JB-602 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
51 | MATCH (Tag 3.3) | XA-60242B | - | XA-60242B | YES | YES | JB-602 | JB-602 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
52 | MATCH (Tag 3.5) | TSH-60242A | TSH-60242A | TSH-60242A | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
53 | MATCH (Tag 3.5) | TSL-60242B | TSL-60242B | TSL-60242B | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
54 | MATCH (Tag 3.3) | XS-60243A | - | XS-60243A | YES | YES | JB-602 | MCC | DIFF | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-602" vs Dev="MCC"
55 | MATCH (Tag 3.3) | XA-60243A | - | XA-60243A | YES | YES | JB-602 | JB-602 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
56 | MATCH (Tag 3.3) | XA-60243B | - | XA-60243B | YES | YES | JB-602 | JB-602 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
57 | MATCH (Tag 3.5) | TSH-60243A | TSH-60243A | TSH-60243A | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
58 | MATCH (Tag 3.5) | TSL-60243B | TSL-60243B | TSL-60243B | YES | YES | JB-602 | JB-602 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
1 | MATCH (Tag 3.5) | DPT-60901 | DPT-60201 | DPT-60201 | YES | YES | JB-606 | JB-606 | MATCH | 3-25-01-602-PD-09 | 3-25-01-602-PD-09 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
2 | MATCH (Tag 3.5) | FT-60901 | FT-60203 | FT-60203 | YES | YES | JB-606 | JB-606 | MATCH | 3-25-01-602-PD-09 | 3-25-01-602-PD-09 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
3 | MATCH (Tag 3.5) | LSH-60250 | LSH-60250 | LSH-60250 | YES | YES | JB-606 | JB-606 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.5) | SV-60220 | SV-60220 | SV-60220 | YES | YES | JB-606 | JB-606 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
5 | MATCH (Tag 3.3) | XA-60261 | - | XA-60261 | YES | YES | JB-606 | JB-606 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
6 | MATCH (Tag 3.3) | XA-60262 | - | XA-60262 | YES | YES | JB-606 | JB-606 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
7 | MATCH (Tag 3.3) | XS-60260 | - | XS-60260 | YES | YES | JB-606 | MCC | DIFF | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-606" vs Dev="MCC"
1 | MATCH (Tag 3.5) | FT-60221 | FT-60221 | FT-60221 | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
2 | MATCH (Tag 3.5) | FT-60261FA | FT-60261FA | FT-60261FA | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
3 | MATCH (Tag 3.5) | FT-60261FB | FT-60261FB | FT-60261FB | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.5) | FT-60261FC | FT-60261FC | FT-60261FC | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
5 | MATCH (Tag 3.5) | FT-60261FD | FT-60261FD | FT-60261FD | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
6 | MATCH (Tag 3.5) | FT-60262FE | FT-60262FE | FT-60262FE | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
7 | MATCH (Tag 3.5) | FT-60262FF | FT-60262FF | FT-60262FF | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
8 | MATCH (Tag 3.5) | FT-60262FG | FT-60262FG | FT-60262FG | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
9 | MATCH (Tag 3.5) | FT-60262FH | FT-60262FH | FT-60262FH | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
10 | MATCH (Tag 3.5) | FT-60263FJ | FT-60263FJ | FT-60263FJ | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
11 | MATCH (Tag 3.5) | FT-60263FK | FT-60263FK | FT-60263FK | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
12 | MATCH (Tag 3.5) | FT-60263FL | FT-60263FL | FT-60263FL | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
13 | MATCH (Tag 3.5) | FT-60263FM | FT-60263FM | FT-60263FM | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
14 | MATCH (Tag 3.5) | FT-60264FN | FT-60264FN | FT-60264FN | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
15 | MATCH (Tag 3.5) | FT-60264FP | FT-60264FP | FT-60264FP | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
16 | MATCH (Tag 3.5) | FT-60264FQ | FT-60264FQ | FT-60264FQ | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
17 | MATCH (Tag 3.5) | FT-60264FR | FT-60264FR | FT-60264FR | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
18 | MATCH (Tag 3.5) | PT-60201 | PT-60201 | PT-60201 | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
19 | MATCH (Tag 3.5) | PT-60221 | PT-60221 | PT-60221 | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 2 | 0 / 0 | DIFF | Signal Diff: AI: 1->2
20 | MATCH (Tag 3.5) | PT-60221 | PT-60221 | PT-60221 | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 2 | 0 / 0 | DIFF | Signal Diff: AI: 1->2
21 | MATCH (Tag 3.5) | PV-60201 | PV-60201 | PV-60201 | NO | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
22 | MATCH (Tag 3.5) | TT-60201 | TT-60201 | TT-60201 | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
23 | MATCH (Tag 3.5) | TT-60702 | TT-60202 | TT-60202 | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-07 | 3-25-01-602-PD-07 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
24 | MATCH (Tag 3.5) | XV-60201 | XV-60201 | XV-60201 | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
25 | MATCH (Tag 3.3) | BFY-60220 | - | BFY-60220 | YES | YES | JB-607 | MCC | DIFF | - | - | N/A | 1 / 1 | 1 / 1 | 0 / 0 | 0 / 0 | 1 / 1 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-607" vs Dev="MCC"
26 | MATCH (Tag 3.5) | FT-60701 | FT-60207 | FT-60207 | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-07 | 3-25-01-602-PD-07 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
27 | MATCH (Tag 3.5) | PT-60701 | PT-60207 | PT-60207 | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-07 | 3-25-01-602-PD-07 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
28 | MATCH (Tag 3.5) | SV-60701 | SV-60207 | SV-60207 | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-07 | 3-25-01-602-PD-07 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
29 | MATCH (Tag 3.5) | TT-60701 | TT-60207 | TT-60207 | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-07 | 3-25-01-602-PD-07 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
30 | MATCH (Tag 3.5) | XV-60261FA | XV-60261FA | XV-60261FA | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
31 | MATCH (Tag 3.5) | XV-60261FB | XV-60261FB | XV-60261FB | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
32 | MATCH (Tag 3.5) | XV-60261FC | XV-60261FC | XV-60261FC | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
33 | MATCH (Tag 3.5) | XV-60261FD | XV-60261FD | XV-60261FD | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
34 | MATCH (Tag 3.5) | XV-60261SA | XV-60261SA | XV-60261SA | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
35 | MATCH (Tag 3.5) | XV-60261SB | XV-60261SB | XV-60261SB | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
36 | MATCH (Tag 3.5) | XV-60261SC | XV-60261SC | XV-60261SC | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
37 | MATCH (Tag 3.5) | XV-60261SD | XV-60261SD | XV-60261SD | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
38 | MATCH (Tag 3.5) | XV-60262FE | XV-60262FE | XV-60262FE | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
39 | MATCH (Tag 3.5) | XV-60262FF | XV-60262FF | XV-60262FF | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
40 | MATCH (Tag 3.5) | XV-60262FG | XV-60262FG | XV-60262FG | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
41 | MATCH (Tag 3.5) | XV-60262FH | XV-60262FH | XV-60262FH | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
42 | MATCH (Tag 3.5) | XV-60262SE | XV-60262SE | XV-60262SE | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
43 | MATCH (Tag 3.5) | XV-60262SF | XV-60262SF | XV-60262SF | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
44 | MATCH (Tag 3.5) | XV-60262SG | XV-60262SG | XV-60262SG | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
45 | MATCH (Tag 3.5) | XV-60262SH | XV-60262SH | XV-60262SH | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
46 | MATCH (Tag 3.5) | XV-60263FJ | XV-60263FJ | XV-60263FJ | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
47 | MATCH (Tag 3.5) | XV-60263FK | XV-60263FK | XV-60263FK | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
48 | MATCH (Tag 3.5) | XV-60263FL | XV-60263FL | XV-60263FL | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
49 | MATCH (Tag 3.5) | XV-60263FM | XV-60263FM | XV-60263FM | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
50 | MATCH (Tag 3.5) | XV-60263SJ | XV-60263SJ | XV-60263SJ | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
51 | MATCH (Tag 3.5) | XV-60263SK | XV-60263SK | XV-60263SK | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
52 | MATCH (Tag 3.5) | XV-60263SL | XV-60263SL | XV-60263SL | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
53 | MATCH (Tag 3.5) | XV-60263SM | XV-60263SM | XV-60263SM | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
54 | MATCH (Tag 3.5) | XV-60264FN | XV-60264FN | XV-60264FN | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
55 | MATCH (Tag 3.5) | XV-60264FP | XV-60264FP | XV-60264FP | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
56 | MATCH (Tag 3.5) | XV-60264FQ | XV-60264FQ | XV-60264FQ | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
57 | MATCH (Tag 3.5) | XV-60264FR | XV-60264FR | XV-60264FR | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
58 | MATCH (Tag 3.5) | XV-60264SN | XV-60264SN | XV-60264SN | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
59 | MATCH (Tag 3.5) | XV-60264SP | XV-60264SP | XV-60264SP | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
60 | MATCH (Tag 3.5) | XV-60264SQ | XV-60264SQ | XV-60264SQ | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
61 | MATCH (Tag 3.5) | XV-60264SR | XV-60264SR | XV-60264SR | YES | YES | JB-607 | JB-607 | MATCH | 3-25-01-602-PD-02 | 3-25-01-602-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
62 | MATCH (Tag 3.3) | XV-60261 | - | XV-60261 | NO | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
63 | MATCH (Tag 3.3) | XV-60262 | - | XV-60262 | NO | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
64 | MATCH (Tag 3.3) | XV-60263 | - | XV-60263 | NO | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
65 | MATCH (Tag 3.3) | XV-60264 | - | XV-60264 | NO | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 1 / 1 | 2 / 2 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
66 | MATCH (Tag 3.3) | XA-FH-60210A | - | XA-FH-60210A | YES | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
67 | MATCH (Tag 3.3) | XA-FH-60210B | - | XA-FH-60210B | YES | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
68 | MATCH (Tag 3.3) | XA-FH-60210C | - | XA-FH-60210C | YES | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
69 | MATCH (Tag 3.3) | XA-FH-60210D | - | XA-FH-60210D | YES | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
70 | MATCH (Tag 3.3) | XA-FH-60210E | - | XA-FH-60210E | YES | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
71 | MATCH (Tag 3.3) | XS-FH-60210A | - | XS-FH-60210A | YES | YES | JB-607 | MCC | DIFF | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-607" vs Dev="MCC"
72 | MATCH (Tag 3.3) | XS-FH-60210B | - | XS-FH-60210B | YES | YES | JB-607 | MCC | DIFF | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="JB-607" vs Dev="MCC"
73 | MATCH (Tag 3.3) | XS-FH-60210C | - | XS-FH-60210C | YES | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
74 | MATCH (Tag 3.3) | XS-FH-60210D | - | XS-FH-60210D | YES | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
75 | MATCH (Tag 3.3) | TI-FH-60210 | - | TI-FH-60210 | YES | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
76 | MATCH (Tag 3.3) | UY-FH-60210A | - | UY-FH-60210A | YES | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
77 | MATCH (Tag 3.3) | UY-FH-60210B | - | UY-FH-60210B | YES | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
78 | MATCH (Tag 3.3) | COM-FH-60210B | - | COM-FH-60210B | YES | YES | JB-607 | JB-607 | MATCH | - | - | N/A | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
1 | MATCH (Tag 3.5) | TT-60245 | TT-60245 | TT-60245 | YES | YES | JB-608 | JB-608 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
1 | MISSING IN DEV | PCY-81001 | - | - | NO | NO | RIO-200 | - | N/A | - | - | N/A | 1 / 0 | 1 / 0 | 0 / 0 | 0 / 0 | 1 / 0 | N/A | Tag 3.3 ("PCY-81001") not found in Dev (Tag 3.5 empty)
2 | MISSING IN DEV | PCY-81002 | - | - | NO | NO | RIO-200 | - | N/A | - | - | N/A | 1 / 0 | 1 / 0 | 0 / 0 | 0 / 0 | 1 / 0 | N/A | Tag 3.3 ("PCY-81002") not found in Dev (Tag 3.5 empty)
1 | MATCH (Tag 3.5) | FT-80301 | FT-913201 | FT-913201 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-913-PD-02 | 3-25-01-913-PD-02 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 2 / 2 | 0 / 0 | MATCH | OK (Identical)
2 | MATCH (Tag 3.5) | PT-80302 | PT-913201 | PT-913201 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-913-PD-02 | 3-25-01-913-PD-02 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
3 | MATCH (Tag 3.5) | NEW | XV-913201 | XV-913201 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-913-PD-02 | 3-25-01-913-PD-02 | MATCH | 1 / 1 | 2 / 2 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.3) | XA-80305A | - | XA-80305A | YES | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
5 | MATCH (Tag 3.3) | XA-80305B | - | XA-80305B | YES | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
6 | MATCH (Tag 3.3) | XA-80305C | - | XA-80305C | YES | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
7 | MATCH (Tag 3.3) | XA-80305D | - | XA-80305D | YES | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
8 | MATCH (Tag 3.3) | XA-80305E | - | XA-80305E | YES | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
9 | MATCH (Tag 3.3) | XA-80305F | - | XA-80305F | YES | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
10 | MATCH (Tag 3.3) | XS-80305 | - | XS-80305 | YES | YES | RIO-200 | MCC | DIFF | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="RIO-200" vs Dev="MCC"
11 | MATCH (Tag 3.3) | XA-80306A | - | XA-80306A | YES | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
12 | MATCH (Tag 3.3) | XA-80306B | - | XA-80306B | YES | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
13 | MATCH (Tag 3.3) | XA-80306C | - | XA-80306C | YES | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
14 | MATCH (Tag 3.3) | XA-80306D | - | XA-80306D | YES | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
15 | MATCH (Tag 3.3) | XA-80306E | - | XA-80306E | YES | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
16 | MATCH (Tag 3.3) | XA-80306F | - | XA-80306F | YES | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
17 | MATCH (Tag 3.3) | XS-80306 | - | XS-80306 | YES | YES | RIO-200 | MCC | DIFF | - | - | N/A | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3; JB Difference: Check="RIO-200" vs Dev="MCC"
1 | EMPTY TAG IN CHECKLIST | - | - | - | NO | NO | RIO-200 | - | N/A | External Remote Setpoint | - | N/A | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 0 | 0 / 0 | N/A | No Tag number; Description in PID col: "External Remote Setpoint"
2 | EMPTY TAG IN CHECKLIST | - | - | - | NO | NO | RIO-200 | - | N/A | Spare | - | N/A | 0 / 0 | 1 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | N/A | No Tag number; Description in PID col: "Spare"
3 | EMPTY TAG IN CHECKLIST | - | - | - | NO | NO | RIO-200 | - | N/A | Spare | - | N/A | 0 / 0 | 1 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | N/A | No Tag number; Description in PID col: "Spare"
4 | EMPTY TAG IN CHECKLIST | - | - | - | NO | NO | RIO-200 | - | N/A | Spare | - | N/A | 0 / 0 | 1 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | N/A | No Tag number; Description in PID col: "Spare"
5 | EMPTY TAG IN CHECKLIST | - | - | - | NO | NO | RIO-200 | - | N/A | Spare | - | N/A | 0 / 0 | 1 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | N/A | No Tag number; Description in PID col: "Spare"
6 | EMPTY TAG IN CHECKLIST | - | - | - | NO | NO | RIO-200 | - | N/A | Spare | - | N/A | 0 / 0 | 1 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | N/A | No Tag number; Description in PID col: "Spare"
7 | EMPTY TAG IN CHECKLIST | - | - | - | NO | NO | RIO-200 | - | N/A | Spare | - | N/A | 0 / 0 | 1 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | N/A | No Tag number; Description in PID col: "Spare"
8 | EMPTY TAG IN CHECKLIST | - | - | - | NO | NO | RIO-200 | - | N/A | Boiler Common Alarm | - | N/A | 1 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | N/A | No Tag number; Description in PID col: "Boiler Common Alarm"
9 | EMPTY TAG IN CHECKLIST | - | - | - | NO | NO | RIO-200 | - | N/A | Boiler trip | - | N/A | 1 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | N/A | No Tag number; Description in PID col: "Boiler trip"
10 | EMPTY TAG IN CHECKLIST | - | - | - | NO | NO | RIO-200 | - | N/A | Burner Trip | - | N/A | 1 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | N/A | No Tag number; Description in PID col: "Burner Trip"
11 | EMPTY TAG IN CHECKLIST | - | - | - | NO | NO | RIO-200 | - | N/A | Boiler Operation | - | N/A | 1 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | N/A | No Tag number; Description in PID col: "Boiler Operation"
12 | EMPTY TAG IN CHECKLIST | - | - | - | NO | NO | RIO-200 | - | N/A | Remote Setpoint Activateed | - | N/A | 1 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | N/A | No Tag number; Description in PID col: "Remote Setpoint Activateed"
13 | EMPTY TAG IN CHECKLIST | - | - | - | NO | NO | RIO-200 | - | N/A | Remote Setpoint Status | - | N/A | 1 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | N/A | No Tag number; Description in PID col: "Remote Setpoint Status"
1 | MATCH (Tag 3.5) | FT-93001 | FT-936202 | FT-936202 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-930-PD-07 | 3-25-01-930-PD-07 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
2 | MATCH (Tag 3.5) | FT-90301 | FT-936201 | FT-936201 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-930-PD-08 | 3-25-01-930-PD-08 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
1 | MATCH (Tag 3.5) | DPT-61310 | DPT-61310 | DPT-61310 | YES | YES | IS-JB-612 | IS-JB-612 | MATCH | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
2 | MATCH (Tag 3.5) | DPT-61312 | DPT-61312 | DPT-61312 | NO | YES | IS-JB-612 | IS-JB-612 | MATCH | 3-25-01-613-PD-05 | 3-25-01-613-PD-05 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
3 | MATCH (Tag 3.5) | LSH-61304 | LSH-61304 | LSH-61304 | YES | YES | IS-JB-612 | IS-JB-612 | MATCH | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.5) | LSH-61305 | LSH-61305 | LSH-61305 | YES | YES | IS-JB-612 | IS-JB-612 | MATCH | 3-25-01-613-PD-05 | 3-25-01-613-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
5 | MATCH (Tag 3.5) | - | LSH-61307 | LSH-61307 | YES | YES | IS-JB-612 | IS-JB-612 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
6 | MATCH (Tag 3.5) | LSH-61312 | LSH-61312 | LSH-61312 | YES | YES | IS-JB-612 | IS-JB-612 | MATCH | 3-25-01-613-PD-05 | 3-25-01-613-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
7 | MATCH (Tag 3.5) | ZS-61312 | ZS-61312 | ZS-61312 | YES | YES | IS-JB-612 | IS-JB-612 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
8 | MATCH (Tag 3.5) | ZS-61313 | ZS-61313 | ZS-61313 | YES | YES | IS-JB-612 | IS-JB-612 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
9 | MATCH (Tag 3.5) | PSE-61302 | PSE-61302 | PSE-61302 | YES | YES | IS-JB-612 | IS-JB-612 | MATCH | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
10 | MATCH (Tag 3.5) | PSE-61303 | PSE-61303 | PSE-61303 | YES | YES | IS-JB-612 | IS-JB-612 | MATCH | 3-25-01-613-PD-05 | 3-25-01-613-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
11 | MATCH (Tag 3.5) | ISV-61303 | ISV-61303 | ISV-61303 | YES | YES | IS-JB-612 | IS-JB-612 | MATCH | 3-25-01-613-PD-03 | 3-25-01-613-PD-03 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
12 | MATCH (Tag 3.5) | ISV-61304 | ISV-61304 | ISV-61304 | YES | YES | IS-JB-612 | IS-JB-612 | MATCH | 3-25-01-613-PD-05 | 3-25-01-613-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
13 | MATCH (Tag 3.5) | - | SC-61301 | SC-61301 | NO | YES | IS-JB-612 | IS-JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
14 | MATCH (Tag 3.5) | - | SC-61302 | SC-61302 | NO | YES | IS-JB-612 | IS-JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
15 | MATCH (Tag 3.5) | - | RV-61301 | RV-61301 | NO | YES | IS-JB-612 | IS-JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
16 | MATCH (Tag 3.5) | - | RV-61305 | RV-61305 | NO | YES | IS-JB-612 | IS-JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
17 | MATCH (Tag 3.5) | - | RV-61304 | RV-61304 | NO | YES | IS-JB-612 | IS-JB-612 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
1 | MATCH (Tag 3.5) | DPT-61301 | DPT-61301 | DPT-61301 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
2 | MATCH (Tag 3.5) | DPT-61302 | DPT-61302 | DPT-61302 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
3 | MATCH (Tag 3.5) | LSH-61301 | LSH-61301 | LSH-61301 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.5) | LSL-61302 | LSL-61302 | LSL-61302 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
5 | MATCH (Tag 3.3) | LSH-61303 | - | LSH-61303 | NO | YES | IS-JB-618 | IS-JB-618 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | Tag 3.5 was blank/hyphen; matched via Tag 3.3
6 | MATCH (Tag 3.5) | LSH-61306 | LSH-61306 | LSH-61306 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
7 | MATCH (Tag 3.5) | - | LSH-61308 | LSH-61308 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
8 | MATCH (Tag 3.5) | LT-61301 | LT-61301 | LT-61301 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
9 | MATCH (Tag 3.5) | PT-61301 | PT-61301 | PT-61301 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
10 | MATCH (Tag 3.3) | PT-61303 | - | PT-61303 | YES | YES | IS-JB-618 | IS-JB-618, JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 2 | 0 / 0 | DIFF | Tag 3.5 was blank/hyphen; matched via Tag 3.3; Signal Diff: AI: 1->2
11 | MATCH (Tag 3.5) | PT-61304 | PT-61304 | PT-61304 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
12 | MATCH (Tag 3.5) | PT-61305 | PT-61305 | PT-61305 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
13 | MATCH (Tag 3.5) | TT-61301 | TT-61301 | TT-61301 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
14 | MATCH (Tag 3.5) | TT-61302 | TT-61302 | TT-61302 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
15 | MATCH (Tag 3.5) | ZS-61310 | ZS-61310 | ZS-61310 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
16 | MATCH (Tag 3.5) | ZS-61311 | ZS-61311 | ZS-61311 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
17 | MATCH (Tag 3.5) | PSE-61300 | PSE-61300 | PSE-61300 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
18 | MATCH (Tag 3.5) | PSE-61301 | PSE-61301 | PSE-61301 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
19 | MATCH (Tag 3.5) | ISV-61301 | ISV-61301 | ISV-61301 | NO | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
20 | MATCH (Tag 3.5) | PSE-61304 | PSE-61304 | PSE-61304 | YES | YES | IS-JB-618 | IS-JB-618 | MATCH | 3-25-01-613-PD-01 | 3-25-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
21 | MATCH (Tag 3.5) | PSV-61301A | PSV-61301A | PSV-61301A | NO | YES | IS-JB-618 | IS-JB-618 | MATCH | 325-01-613-PD-01 | 325-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
22 | MATCH (Tag 3.5) | PSV-61301B | PSV-61301B | PSV-61301B | NO | YES | IS-JB-618 | IS-JB-618 | MATCH | 325-01-613-PD-01 | 325-01-613-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
1 | MATCH (Tag 3.5) | LSH-60230 | LSH-60230 | LSH-60230 | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
2 | MATCH (Tag 3.5) | LSH-60231 | LSH-60231 | LSH-60231 | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
3 | MATCH (Tag 3.5) | LSH-60240 | LSH-60240 | LSH-60240 | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.5) | TT-60226 | TT-60226 | TT-60226 | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
5 | MATCH (Tag 3.5) | TT-60227 | TT-60227 | TT-60227 | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
6 | MATCH (Tag 3.5) | ZS-60201E | ZS-60201E | ZS-60201E | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
7 | MATCH (Tag 3.5) | TT-60225 | TT-60225 | TT-60225 | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
8 | MATCH (Tag 3.5) | TT-60230 | TT-60230 | TT-60230 | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
9 | MATCH (Tag 3.5) | PT-60230 | PT-60230 | PT-60230 | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
10 | MATCH (Tag 3.5) | PT-60231 | PT-60231 | PT-60231 | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
11 | MATCH (Tag 3.5) | TT-60224 | TT-60224 | TT-60224 | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
12 | MATCH (Tag 3.5) | ZS-60201C | ZS-60201C | ZS-60201C | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
13 | MATCH (Tag 3.5) | ZS-60201D | ZS-60201D | ZS-60201D | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
14 | MATCH (Tag 3.5) | - | ZS-60229 | ZS-60229 | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
15 | MATCH (Tag 3.5) | - | ZS-60230 | ZS-60230 | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
16 | MATCH (Tag 3.5) | ZS-60231A | ZS-60231A | ZS-60231A | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
17 | MATCH (Tag 3.5) | ZS-60231B | ZS-60231B | ZS-60231B | YES | YES | IS-JB-603 | IS-JB-603 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
18 | MATCH (Tag 3.5) | - | AT-40201 | AT-40201 | NO | YES | IS-JB-603 | IS-JB-603 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
19 | MATCH (Tag 3.5) | - | AT-40202 | AT-40202 | NO | YES | IS-JB-603 | IS-JB-603 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
20 | MATCH (Tag 3.5) | - | AT-40203 | AT-40203 | NO | YES | IS-JB-603 | IS-JB-603 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
21 | MATCH (Tag 3.5) | - | RV-60204 | RV-60204 | NO | YES | IS-JB-603 | IS-JB-603 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
22 | MATCH (Tag 3.5) | - | PD-60202 | PD-60202 | NO | YES | IS-JB-603 | IS-JB-603 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
1 | MATCH (Tag 3.5) | TT-60222 | TT-60222 | TT-60222 | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
2 | MATCH (Tag 3.5) | TT-60223 | TT-60223 | TT-60223 | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
3 | MATCH (Tag 3.5) | XT-60301 | XT-60201 | XT-60201 | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.5) | XA-60301 | XA-60201 | XA-60201 | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-03 | 3-25-01-602-PD-03 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
5 | MATCH (Tag 3.5) | ZS-60231C | ZS-60231C | ZS-60231C | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
6 | MATCH (Tag 3.5) | ZS-60231D | ZS-60231D | ZS-60231D | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
7 | MATCH (Tag 3.5) | ZS-60231E | ZS-60231E | ZS-60231E | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
8 | MATCH (Tag 3.5) | ZS-60231F | ZS-60231F | ZS-60231F | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
9 | MATCH (Tag 3.5) | PT-60220 | PT-60220 | PT-60220 | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
10 | MATCH (Tag 3.5) | TT-60220 | TT-60220 | TT-60220 | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
11 | MATCH (Tag 3.5) | TT-60221 | TT-60221 | TT-60221 | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
12 | MATCH (Tag 3.5) | ZS-60201A | ZS-60201A | ZS-60201A | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
13 | MATCH (Tag 3.5) | ZS-60201B | ZS-60201B | ZS-60201B | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-04 | 3-25-01-602-PD-04 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
14 | MATCH (Tag 3.5) | - | ZS-60240 | ZS-60240 | YES | YES | IS-JB-608 | IS-JB-608 | MATCH | 3-25-01-602-PD-05 | 3-25-01-602-PD-05 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
1 | MATCH (Tag 3.5) | LSL-81001 | LSL-814201 | LSL-814201 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-814-PD-01 | 3-25-01-814-PD-01 | MATCH | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
2 | MATCH (Tag 3.5) | LT-80301 | LT-913201 | LT-913201 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-913-PD-01 | 3-25-01-913-PD-01 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
3 | MATCH (Tag 3.5) | XT-92201 | XT-92201 | XT-92201 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-922-PD-03 | 3-25-01-922-PD-03 | MATCH | 0 / 0 | 0 / 0 | 0 / 0 | 1 / 1 | 0 / 0 | MATCH | OK (Identical)
4 | MATCH (Tag 3.5) | XA-92201 | XA-92201 | XA-92201 | YES | YES | RIO-200 | RIO-200 | MATCH | 3-25-01-922-PD-03 | 3-25-01-922-PD-03 | MATCH | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
5 | MATCH (Tag 3.5) | - | PK-913201 | PK-913201 | NO | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)
6 | MATCH (Tag 3.5) | - | PK-913202 | PK-913202 | NO | YES | RIO-200 | RIO-200 | MATCH | - | - | N/A | 0 / 0 | 1 / 1 | 0 / 0 | 0 / 0 | 0 / 0 | MATCH | OK (Identical)

## Missing_in_Dev (No Have)
Item | Check List Row | Tag No. 3.3 | Tag No. 3.5 | Junction Box | Zone | Floor | P&ID 3.5 / Description | DO | DI | AO | AI | Bus | Diagnostic Findings & Resolution
1 | 34 | FS-40101 | FS-40201 | JB-401 | PH Adjustment | 1st | 3-25-01-402-PD-01 | 0 | 0 | 0 | 1 | 0 | Renamed in Dev to "FSL-40201"
2 | 35 | FS-40102 | FS-40202 | JB-401 | PH Adjustment | 1st | 3-25-01-402-PD-01 | 0 | 0 | 0 | 1 | 0 | Renamed in Dev to "FSL-40202"
31 | 64 | ATY-40101 | - | JB-401 | PH Adjustment | 1st | 3-25-01-402-PD-01 | 1 | 1 | 0 | 0 | 1 | Tag 3.3 ("ATY-40101") not found in Dev (Tag 3.5 empty)
32 | 65 | ATY-40102 | - | JB-401 | PH Adjustment | 1st | 3-25-01-402-PD-01 | 1 | 1 | 0 | 0 | 1 | Tag 3.3 ("ATY-40102") not found in Dev (Tag 3.5 empty)
33 | 66 | PCY-40101 | - | JB-401 | PH Adjustment | 1st | 3-25-01-402-PD-01 | 1 | 1 | 0 | 0 | 1 | Tag 3.3 ("PCY-40101") not found in Dev (Tag 3.5 empty)
34 | 67 | PCY-40102 | - | JB-401 | PH Adjustment | 1st | 3-25-01-402-PD-01 | 1 | 1 | 0 | 0 | 1 | Tag 3.3 ("PCY-40102") not found in Dev (Tag 3.5 empty)
21 | 156 | HV-61301 | XV61301 | JB-618 | Packing Tower | 5th | 3-25-01-613-PD-01 | 1 | 2 | 0 | 0 | 0 | Typo in Check List (missing hyphen): Dev has "XV-61301"
20 | 186 | PCY-60205-1 | - | JB-601 | Spray Dryer | 1st | - | 1 | 1 | 0 | 0 | 1 | Tag 3.3 ("PCY-60205-1") not found in Dev (Tag 3.5 empty)
1 | 360 | PCY-81001 | - | RIO-200 | CIP Water System | 2nd | - | 1 | 1 | 0 | 0 | 1 | Tag 3.3 ("PCY-81001") not found in Dev (Tag 3.5 empty)
2 | 361 | PCY-81002 | - | RIO-200 | CIP Water System | 2nd | - | 1 | 1 | 0 | 0 | 1 | Tag 3.3 ("PCY-81002") not found in Dev (Tag 3.5 empty)
1 | 379 | - | - | RIO-200 | Boiler System | 1st | External Remote Setpoint | 0 | 0 | 0 | 1 | 0 | No Tag number; Description in PID col: "External Remote Setpoint"
2 | 380 | - | - | RIO-200 | Boiler System | 1st | Spare | 0 | 1 | 0 | 0 | 0 | No Tag number; Description in PID col: "Spare"
3 | 381 | - | - | RIO-200 | Boiler System | 1st | Spare | 0 | 1 | 0 | 0 | 0 | No Tag number; Description in PID col: "Spare"
4 | 382 | - | - | RIO-200 | Boiler System | 1st | Spare | 0 | 1 | 0 | 0 | 0 | No Tag number; Description in PID col: "Spare"
5 | 383 | - | - | RIO-200 | Boiler System | 1st | Spare | 0 | 1 | 0 | 0 | 0 | No Tag number; Description in PID col: "Spare"
6 | 384 | - | - | RIO-200 | Boiler System | 1st | Spare | 0 | 1 | 0 | 0 | 0 | No Tag number; Description in PID col: "Spare"
7 | 385 | - | - | RIO-200 | Boiler System | 1st | Spare | 0 | 1 | 0 | 0 | 0 | No Tag number; Description in PID col: "Spare"
8 | 386 | - | - | RIO-200 | Boiler System | 1st | Boiler Common Alarm | 1 | 0 | 0 | 0 | 0 | No Tag number; Description in PID col: "Boiler Common Alarm"
9 | 387 | - | - | RIO-200 | Boiler System | 1st | Boiler trip | 1 | 0 | 0 | 0 | 0 | No Tag number; Description in PID col: "Boiler trip"
10 | 388 | - | - | RIO-200 | Boiler System | 1st | Burner Trip | 1 | 0 | 0 | 0 | 0 | No Tag number; Description in PID col: "Burner Trip"
11 | 389 | - | - | RIO-200 | Boiler System | 1st | Boiler Operation | 1 | 0 | 0 | 0 | 0 | No Tag number; Description in PID col: "Boiler Operation"
12 | 390 | - | - | RIO-200 | Boiler System | 1st | Remote Setpoint Activateed | 1 | 0 | 0 | 0 | 0 | No Tag number; Description in PID col: "Remote Setpoint Activateed"
13 | 391 | - | - | RIO-200 | Boiler System | 1st | Remote Setpoint Status | 1 | 0 | 0 | 0 | 0 | No Tag number; Description in PID col: "Remote Setpoint Status"

## Extra_in_Dev (Not in Check)
Dev Tag | In Rev.3 Master | In IO List Wiring | Junction Box / Destination | Description | P&ID No. | DO | DI | AO | AI | Bus | Category / Equipment Type
112 | NO | YES | 112 | - | - | 0 | 0 | 0 | 0 | 0 | Instrument
AHTR-21 Air Heater Control Panel | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Control Panel Interface
ATY-40202 | YES | YES | MCC | Tank Agitator | 3-25-01-402-PD-01 | 1 | 3 | 0 | 0 | 1 | Instrument
BE-60210A | YES | NO | - | Gas Flame Detector for Air Heater (AHTR-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
BE-60210B | YES | NO | - | Gas Flame Detector for Air Heater (AHTR-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
BGHS-21 Filter Control Panel | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Control Panel Interface
BLM-61301 | YES | NO | - | Start / Stop Command for FVNR PV-61301 (Vacuum Cleaning Fan) | 325-01-613-PD-03 | 1 | 3 | 0 | 0 | 0 | Instrument
BV-60210A | YES | NO | - | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
BV-60210B | YES | NO | - | Gas Blocking Valve (main gas) for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
DEDERT SUPPLY EQUIPMENT | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Package Vendor Equipment
DPHL-60230 | YES | NO | - | Gas Pressure Differntial Switch Low for Exhaust Fan (FANE-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
DPSH-60210C | YES | NO | - | Gas Pressure Differential Switch High for Air Heater (AHTR-21) | - | 0 | 0 | 0 | 0 | 0 | New Rev 3.6 Instrument
DPSL-60210B | YES | NO | - | Gas Pressure Differential Switch Low for Air Heater (AHTR-21) | - | 0 | 0 | 0 | 0 | 0 | New Rev 3.6 Instrument
DPSL-60211 | YES | NO | - | Gas Pressure Differential Switch Low for Combustion Fan (FANC-21) | - | 0 | 0 | 0 | 0 | 0 | New Rev 3.6 Instrument
DPT-60210 | YES | NO | - | Differential Pressure Transmitte | - | 0 | 0 | 0 | 0 | 0 | Instrument
EXT-BIILER | NO | YES | RIO-200 | - | External Remote Setpoint | 0 | 0 | 0 | 1 | 0 | Instrument
FCV-60210A | YES | NO | - | Gas Flow Control Valve for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
FCV-60211B | YES | NO | - | Gas Flow Control Damper (Valve) for Burner Combustion Air Duct (DTCB-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
FSL-20201 | YES | NO | - | Flow Switch | 325-01-202-PD-01 | 0 | 1 | 0 | 0 | 0 | New Rev 3.6 Instrument
FSL-40201 | YES | YES | JB-401 | Flow Switch | 3-25-01-402-PD-01 | 0 | 1 | 0 | 0 | 0 | New Rev 3.6 Instrument
FSL-40202 | YES | YES | JB-401 | Flow Switch | 3-25-01-402-PD-01 | 0 | 1 | 0 | 0 | 0 | New Rev 3.6 Instrument
Gas Vaporizer 5 | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Heater / Vaporizer Package
Gas Vaporizer 6 | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Heater / Vaporizer Package
HTRE-21 Heater Control Panel (TRACING) | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Control Panel Interface
HTRE-22 Heater Control Panel (TRACING) | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Control Panel Interface
HTRE-23 Heater Control Panel (TRACING) | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Control Panel Interface
Haver & Boecker. EQUIPMENT | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Package Vendor Equipment
ISV-61302 | YES | NO | - | Explosion isolation flap valve ISV-61302 | 325-01-613-PD-01 | 0 | 1 | 0 | 0 | 0 | New Rev 3.6 Instrument
IX-60210A | YES | NO | - | Gas Ignition Transformer for Air Heater (AHTR-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
LPG Station | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Instrument
LS-814201 | YES | NO | - | Level alarm low | 325-01-814-PD-01 | 0 | 1 | 0 | 0 | 0 | Instrument
MCC ROOM | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Instrument
Machine Equipment Supply | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Instrument
PCM-20201 | YES | NO | - | Start / Stop Command for FVNR PC-2030 | 325-01-202-PD-01 | 1 | 3 | 0 | 0 | 0 | Instrument
PCV-60201 | YES | NO | - | Steam feed to Spray dryer | 325-01-602-PD-02 | 0 | 0 | 1 | 0 | 0 | Instrument
PCY-40202 | YES | YES | MCC | PUMP | 3-25-01-402-PD-01 | 1 | 3 | 0 | 0 | 1 | Instrument
PCY-60205 | NO | YES | JB-601 | - | - | 1 | 3 | 0 | 0 | 1 | Instrument
PCY-814201 | YES | YES | MCC | PUMP | 325-01-814-PD-01 | 1 | 3 | 0 | 0 | 1 | Instrument
PCY-814202 | YES | YES | MCC | PUMP | 325-01-814-PD-01 | 1 | 3 | 0 | 0 | 1 | Instrument
PDM-60202B | YES | NO | - | Start / Stop Command for FVNR PUPD-11 (Oil Pump ) | 325-01-602-PD-01 | 1 | 3 | 0 | 0 | 0 | Instrument
PDM-60202C | YES | NO | - | Start / Stop Command for FVNR PUPD-11 (Machine Fan 1 ) | 325-01-602-PD-01 | 1 | 3 | 0 | 0 | 0 | Instrument
PDM-60202D | YES | NO | - | Start / Stop Command for FVNR PUPD-11 (Machine Fan 2 ) | 325-01-602-PD-01 | 1 | 3 | 0 | 0 | 0 | Instrument
PDM-60202E | YES | NO | - | Start / Stop Command for FVNR PUPD-11 (Main motor Fan ) | 325-01-602-PD-01 | 1 | 3 | 0 | 0 | 0 | Instrument
PDY-40204 | YES | NO | - | Start / Stop Command for VSD PD-40204 | 325-01-402-PD-01 | 1 | 3 | 0 | 0 | 1 | Instrument
PDY-40205 | YES | NO | - | Start / Stop Command for VSD PD-40205 | 325-01-402-PD-01 | 1 | 3 | 0 | 0 | 1 | Instrument
PDY-60202A | YES | NO | - | Start / Stop Command for VSD PUPD-11 (Positive Displacement Pump ) | 325-01-602-PD-01 | 1 | 3 | 0 | 0 | 1 | Instrument
PSH-60210 | YES | NO | - | Gas Pressure Switch High for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
PSH-60220 | YES | NO | - | Gas Pressure Switch High for Spray Chamber (CHAM-21) | 325-01-602-PD-04 | 0 | 0 | 0 | 0 | 0 | Instrument
PSH-60224 | YES | NO | - | Gas and Powder Pressure Switch High for Bag House (BGHS-21) | 325-01-602-PD-05 | 0 | 0 | 0 | 0 | 0 | Instrument
PSH-60230 | YES | NO | - | Gas Pressure Switch High for Cyclone (CYCL-21) | 325-01-602-PD-04 | 0 | 0 | 0 | 0 | 0 | Instrument
PSH-60231 | YES | NO | - | Gas Pressure Switch High for Cyclone (CYCL-22) | 325-01-602-PD-04 | 0 | 0 | 0 | 0 | 0 | Instrument
PSH-61301 | YES | NO | - | Gas and Powder Pressure Switch High for Storage Bin Cyclone Inlet Duct (####-##) | 325-01-613-PD-01 | 0 | 0 | 0 | 0 | 0 | Instrument
PSL-60210 | YES | NO | - | Gas Pressure Switch Low for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
PUPD Pump Control Panel | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Control Panel Interface
PV-60210A | YES | NO | - | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
PV-60210B | YES | NO | - | Gas Pressure Valve for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
REMOTE I-O Area-200 | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Instrument
SV-60240D | YES | NO | - | PA On/Off Valve for Bag House Tank Valve (BGHS-21) | 325-01-602-PD-05 | 1 | 2 | 0 | 0 | 0 | Instrument
Suppression Panel | YES | NO | - | - | - | 0 | 0 | 0 | 0 | 0 | Control Panel Interface
TCV-60202 | YES | NO | - | Chiller water control valve | 325-01-602-PD-07 | 0 | 0 | 1 | 0 | 0 | Instrument
TCV-60214 | YES | NO | - | Steam Temperature Valve for Pre-Heat Steam Heat Exchanger (HXCH-21) | 325-01-602-PD-03 | 0 | 0 | 1 | 0 | 0 | Instrument
TE-60212 | YES | NO | - | Gas Temperature Element for Hot Air Duct (DTHA-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
UJ-01 (220VAC) | YES | NO | - | Valve train J-BOX | - | 0 | 0 | 0 | 0 | 0 | Instrument
UJ-01 (24VDC) | YES | NO | - | Valve train J-BOX | - | 0 | 0 | 0 | 0 | 0 | Instrument
VJ-01 (220VAC) | YES | NO | - | Valve train J-BOX | - | 0 | 0 | 0 | 0 | 0 | Instrument
VJ-01 (24VDC) | YES | NO | - | Valve train J-BOX | - | 0 | 0 | 0 | 0 | 0 | Instrument
VV-60210 | YES | NO | - | Gas Venting Valve (main gas) for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
XA-60202I | NO | YES | JB-601 | - | - | 0 | 1 | 0 | 0 | 0 | Instrument
XV-60261DA | YES | NO | - | Slurry Drain On/Off Valve for ATVM-11A | 325-01-602-PD-02 | 1 | 2 | 0 | 0 | 0 | Instrument
XV-60262DE | YES | NO | - | Slurry Drain On/Off Valve for ATVM-11B | 325-01-602-PD-02 | 1 | 2 | 0 | 0 | 0 | Instrument
XV-60263DN | YES | NO | - | Slurry Drain On/Off Valve for ATVM-11C | 325-01-602-PD-02 | 1 | 2 | 0 | 0 | 0 | Instrument
XV-60264DJ | YES | NO | - | Slurry Drain On/Off Valve for ATVM-11D | 325-01-602-PD-02 | 1 | 2 | 0 | 0 | 0 | Instrument
ZS-61306 | YES | NO | - | Position Brether Valve High Pressure PSV-61301 | 325-01-613-PD-01 | 0 | 1 | 0 | 0 | 0 | Instrument
ZS-61307 | YES | NO | - | Position Brether Valve Vacuum Pressure PSV-61301 | 325-01-613-PD-01 | 0 | 1 | 0 | 0 | 0 | Instrument
ZSC-60210A | YES | NO | - | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
ZSC-60210B | YES | NO | - | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
ZSC-60210C | YES | NO | - | Gas Position Switch Close for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
ZSH-60211B | YES | NO | - | Gas Position Switch High for Combustion Air Damper Actuator (DTCB-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
ZSL-60210A | YES | NO | - | Gas Position Switch Low for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
ZSL-60211B | YES | NO | - | Gas Position Switch Low for Combustion Air Damper Actuator (DTCB-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
ZSO-60210A | YES | NO | - | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
ZSO-60210B | YES | NO | - | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
ZSO-60210C | YES | NO | - | Gas Position Switch Open for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
ZT-60210A | YES | NO | - | Gas Position Transmitter for Air Heater Gas Train (GTRN-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument
ZT-60211B | YES | NO | - | Gas Position Transmitter for Combustion Air Damper Actuator (DTCB-21) | - | 0 | 0 | 0 | 0 | 0 | Instrument

## Attribute_Discrepancies
Item | Tag 3.5 / 3.6 | Matched Dev Tag | Discrepancy Type | Check List Value | Dev Value (Rev 3.6) | Detailed Impact
1 | FS-20201 | FS-20201 | Signal Channel Count Mismatch | DO:0 DI:0 AO:0 AI:1 Bus:0 | DO:0 DI:1 AO:0 AI:0 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch
15 | - | PCM-2030 | Junction Box Routing Mismatch | JB: RIO-200 | JB: MCC | Cables routed to different enclosure (RIO-200 vs MCC)
16 | - | PCM-2031 | Junction Box Routing Mismatch | JB: RIO-200 | JB: MCC | Cables routed to different enclosure (RIO-200 vs MCC)
13 | XV-60251 | XV-60251 | Junction Box Routing Mismatch | JB: JB-401 | JB: JB-601 | Cables routed to different enclosure (JB-401 vs JB-601)
13 | XV-60251 | XV-60251 | Signal Channel Count Mismatch | DO:1 DI:2 AO:0 AI:0 Bus:0 | DO:1 DI:0 AO:0 AI:0 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch
14 | ATY-40203 | ATY-40203 | Junction Box Routing Mismatch | JB: JB-401 | JB: MCC | Cables routed to different enclosure (JB-401 vs MCC)
14 | ATY-40203 | ATY-40203 | Signal Channel Count Mismatch | DO:1 DI:1 AO:0 AI:0 Bus:1 | DO:1 DI:3 AO:0 AI:0 Bus:1 | PLC hardware I/O card capacity and wiring point mismatch
15 | PCY-40203 | PCY-40203 | Junction Box Routing Mismatch | JB: JB-401 | JB: MCC | Cables routed to different enclosure (JB-401 vs MCC)
15 | PCY-40203 | PCY-40203 | Signal Channel Count Mismatch | DO:1 DI:1 AO:0 AI:0 Bus:1 | DO:1 DI:3 AO:0 AI:0 Bus:1 | PLC hardware I/O card capacity and wiring point mismatch
7 | LT-40201 | LT-40201 | Signal Channel Count Mismatch | DO:0 DI:1 AO:0 AI:0 Bus:0 | DO:0 DI:0 AO:0 AI:1 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch
8 | LT-40202 | LT-40202 | Signal Channel Count Mismatch | DO:0 DI:1 AO:0 AI:0 Bus:0 | DO:0 DI:0 AO:0 AI:1 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch
9 | pHT-40201 | pHT-40201 | Signal Channel Count Mismatch | DO:0 DI:1 AO:0 AI:1 Bus:0 | DO:0 DI:0 AO:0 AI:1 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch
10 | pHT-40202 | pHT-40202 | Signal Channel Count Mismatch | DO:0 DI:1 AO:0 AI:1 Bus:0 | DO:0 DI:0 AO:0 AI:1 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch
1 | HS-61307F | HS-61307F | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
2 | HS-61307G | HS-61307G | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
3 | HS-61307H | HS-61307H | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
4 | HS-61307I | HS-61307I | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
5 | HS-61307J | HS-61307J | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
6 | HS-61307K | HS-61307K | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
7 | HS-61307L | HS-61307L | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
8 | HS-61307M | HS-61307M | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
9 | HS-61307N | HS-61307N | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
10 | HS-61307O | HS-61307O | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
11 | HS-61307P | HS-61307P | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
12 | HS-61307Q | HS-61307Q | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
13 | HS-61307R | HS-61307R | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
16 | PT-61302 | PT-61302 | Signal Channel Count Mismatch | DO:0 DI:0 AO:0 AI:1 Bus:0 | DO:0 DI:0 AO:0 AI:2 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch
17 | PT-61309 | PT-61309 | Signal Channel Count Mismatch | DO:0 DI:0 AO:0 AI:1 Bus:0 | DO:0 DI:0 AO:0 AI:2 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch
25 | - | BFY-61302 | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
27 | - | RVM-61302 | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
28 | - | RVM-61303 | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
29 | - | SCM-61301 | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
30 | - | SCM-61302 | Junction Box Routing Mismatch | JB: JB-612 | JB: MCC | Cables routed to different enclosure (JB-612 vs MCC)
1 | HS-61307A | HS-61307A | Junction Box Routing Mismatch | JB: JB-618 | JB: MCC | Cables routed to different enclosure (JB-618 vs MCC)
2 | HS-61307B | HS-61307B | Junction Box Routing Mismatch | JB: JB-618 | JB: MCC | Cables routed to different enclosure (JB-618 vs MCC)
3 | HS-61307C | HS-61307C | Junction Box Routing Mismatch | JB: JB-618 | JB: MCC | Cables routed to different enclosure (JB-618 vs MCC)
4 | HS-61307D | HS-61307D | Junction Box Routing Mismatch | JB: JB-618 | JB: MCC | Cables routed to different enclosure (JB-618 vs MCC)
5 | HS-61307E | HS-61307E | Junction Box Routing Mismatch | JB: JB-618 | JB: MCC | Cables routed to different enclosure (JB-618 vs MCC)
7 | LSH-61308 | LSH-61308 | Junction Box Routing Mismatch | JB: JB-618 | JB: IS-JB-618 | Cables routed to different enclosure (JB-618 vs IS-JB-618)
12 | PT-61303 | PT-61303 | Signal Channel Count Mismatch | DO:0 DI:0 AO:0 AI:1 Bus:0 | DO:0 DI:0 AO:0 AI:2 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch
24 | - | BFY-61301 | Junction Box Routing Mismatch | JB: JB-618 | JB: MCC | Cables routed to different enclosure (JB-618 vs MCC)
25 | - | BFY-61303 | Junction Box Routing Mismatch | JB: JB-618 | JB: MCC | Cables routed to different enclosure (JB-618 vs MCC)
26 | - | BLM-61302 | Junction Box Routing Mismatch | JB: JB-618 | JB: MCC | Cables routed to different enclosure (JB-618 vs MCC)
27 | - | RVM-60204 | Junction Box Routing Mismatch | JB: JB-618 | JB: MCC | Cables routed to different enclosure (JB-618 vs MCC)
28 | - | RVM-61301 | Junction Box Routing Mismatch | JB: JB-618 | JB: MCC | Cables routed to different enclosure (JB-618 vs MCC)
29 | - | RVM-61304 | Junction Box Routing Mismatch | JB: JB-618 | JB: MCC | Cables routed to different enclosure (JB-618 vs MCC)
30 | - | RVM-61305 | Junction Box Routing Mismatch | JB: JB-618 | JB: MCC | Cables routed to different enclosure (JB-618 vs MCC)
15 | - | BFY-60206 | Junction Box Routing Mismatch | JB: JB-601 | JB: MCC | Cables routed to different enclosure (JB-601 vs MCC)
16 | - | PCM-60205-2 | Junction Box Routing Mismatch | JB: JB-601 | JB: MCC | Cables routed to different enclosure (JB-601 vs MCC)
17 | - | PCM-60205-3 | Junction Box Routing Mismatch | JB: JB-601 | JB: MCC | Cables routed to different enclosure (JB-601 vs MCC)
18 | - | PCM-60205-4 | Junction Box Routing Mismatch | JB: JB-601 | JB: MCC | Cables routed to different enclosure (JB-601 vs MCC)
19 | - | PCM-60205-5 | Junction Box Routing Mismatch | JB: JB-601 | JB: MCC | Cables routed to different enclosure (JB-601 vs MCC)
21 | - | RVM-60201 | Junction Box Routing Mismatch | JB: JB-601 | JB: MCC | Cables routed to different enclosure (JB-601 vs MCC)
22 | - | RVM-60202 | Junction Box Routing Mismatch | JB: JB-601 | JB: MCC | Cables routed to different enclosure (JB-601 vs MCC)
23 | - | RVM-60203 | Junction Box Routing Mismatch | JB: JB-601 | JB: MCC | Cables routed to different enclosure (JB-601 vs MCC)
24 | - | XV-60240D | Signal Channel Count Mismatch | DO:1 DI:2 AO:0 AI:0 Bus:0 | DO:1 DI:4 AO:0 AI:0 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch
40 | XV-60240D | XV-60240D | Signal Channel Count Mismatch | DO:1 DI:2 AO:0 AI:0 Bus:0 | DO:1 DI:4 AO:0 AI:0 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch
45 | - | XS-60205 | Junction Box Routing Mismatch | JB: JB-601 | JB: MCC | Cables routed to different enclosure (JB-601 vs MCC)
35 | - | BFY-60210 | Junction Box Routing Mismatch | JB: JB-602 | JB: MCC | Cables routed to different enclosure (JB-602 vs MCC)
36 | - | BFY-60211 | Junction Box Routing Mismatch | JB: JB-602 | JB: MCC | Cables routed to different enclosure (JB-602 vs MCC)
37 | - | BFY-60240 | Junction Box Routing Mismatch | JB: JB-602 | JB: MCC | Cables routed to different enclosure (JB-602 vs MCC)
38 | - | PCY-60215 | Junction Box Routing Mismatch | JB: JB-602 | JB: MCC | Cables routed to different enclosure (JB-602 vs MCC)
38 | - | PCY-60215 | Signal Channel Count Mismatch | DO:1 DI:1 AO:0 AI:0 Bus:1 | DO:1 DI:3 AO:0 AI:0 Bus:1 | PLC hardware I/O card capacity and wiring point mismatch
40 | - | XS-60240A | Junction Box Routing Mismatch | JB: JB-602 | JB: MCC | Cables routed to different enclosure (JB-602 vs MCC)
44 | - | XS-60241A | Junction Box Routing Mismatch | JB: JB-602 | JB: MCC | Cables routed to different enclosure (JB-602 vs MCC)
49 | - | XS-60242A | Junction Box Routing Mismatch | JB: JB-602 | JB: MCC | Cables routed to different enclosure (JB-602 vs MCC)
54 | - | XS-60243A | Junction Box Routing Mismatch | JB: JB-602 | JB: MCC | Cables routed to different enclosure (JB-602 vs MCC)
7 | - | XS-60260 | Junction Box Routing Mismatch | JB: JB-606 | JB: MCC | Cables routed to different enclosure (JB-606 vs MCC)
19 | PT-60221 | PT-60221 | Signal Channel Count Mismatch | DO:0 DI:0 AO:0 AI:1 Bus:0 | DO:0 DI:0 AO:0 AI:2 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch
20 | PT-60221 | PT-60221 | Signal Channel Count Mismatch | DO:0 DI:0 AO:0 AI:1 Bus:0 | DO:0 DI:0 AO:0 AI:2 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch
25 | - | BFY-60220 | Junction Box Routing Mismatch | JB: JB-607 | JB: MCC | Cables routed to different enclosure (JB-607 vs MCC)
71 | - | XS-FH-60210A | Junction Box Routing Mismatch | JB: JB-607 | JB: MCC | Cables routed to different enclosure (JB-607 vs MCC)
72 | - | XS-FH-60210B | Junction Box Routing Mismatch | JB: JB-607 | JB: MCC | Cables routed to different enclosure (JB-607 vs MCC)
10 | - | XS-80305 | Junction Box Routing Mismatch | JB: RIO-200 | JB: MCC | Cables routed to different enclosure (RIO-200 vs MCC)
17 | - | XS-80306 | Junction Box Routing Mismatch | JB: RIO-200 | JB: MCC | Cables routed to different enclosure (RIO-200 vs MCC)
10 | - | PT-61303 | Signal Channel Count Mismatch | DO:0 DI:0 AO:0 AI:1 Bus:0 | DO:0 DI:0 AO:0 AI:2 Bus:0 | PLC hardware I/O card capacity and wiring point mismatch