## C1_Slot_Summary
KALASIN ENGINEERING — C1 (MAIN CONTROLLER RACK (CHASSIS 1))
Location: Control Cabinet CA1 (Main Control Room) ¦ Net: Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) ¦ Total Active Slots: 8
Slot No. | Module Model | I/O Type | Capacity | Active Points | Spare Points | Spare % | Primary Destinations | Sheet Link
Slot 03 | 1756-IB32 | DI | 32 | 16 | 16 | 50.0% | CA1, JB-401 | Go to Slot 03 ➔
Slot 04 | 1756-IB32 | DI | 32 | 32 | 0 | 0.0% | JB-401 | Go to Slot 04 ➔
Slot 05 | 1756-IB32 | DI | 32 | 12 | 20 | 62.5% | JB-401, JB-601 | Go to Slot 05 ➔
Slot 06 | 1756-IB32 | DI | 32 | 23 | 9 | 28.1% | JB-601 | Go to Slot 06 ➔
Slot 07 | 1756-OB32 | DO | 32 | 16 | 16 | 50.0% | CA1, JB-401 | Go to Slot 07 ➔
Slot 08 | 1756-OB32 | DO | 32 | 20 | 12 | 37.5% | JB-401, JB-601 | Go to Slot 08 ➔
Slot 09 | 1756-IF16 | AI | 16 | 11 | 5 | 31.2% | JB-401 | Go to Slot 09 ➔
Slot 10 | 1756-IF16 | AI | 16 | 8 | 8 | 50.0% | JB-601 | Go to Slot 10 ➔

## Slot_03
KALASIN ENGINEERING — C1 SLOT 03 (1756-IB32 • DI)
Chassis: C1 (Main Controller Rack (Chassis 1)) ¦ Panel: Control Cabinet CA1 (Main Control Room) ¦ Net: Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) ¦ Total Points: 32 (Active: 16, Spare: 16 / 50.0%) | [16 empty] | Destination: CA1, JB-401
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C1-S03-P00 | 3 | 0 | 1 | 1756-IB32 | Spare_DI_0 | Pin 1 | C1S3:1/C1S03-X1:1 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P01 | 3 | 1 | 2 | 1756-IB32 | Spare_DI_0 | Pin 2 | C1S3:2/C1S03-X1:2 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P02 | 3 | 2 | 3 | 1756-IB32 | Spare_DI_0 | Pin 3 | C1S3:3/C1S03-X1:3 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P03 | 3 | 3 | 4 | 1756-IB32 | Spare_DI_0 | Pin 4 | C1S3:4/C1S03-X1:4 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P04 | 3 | 4 | 5 | 1756-IB32 | Spare_DI_0 | Pin 5 | C1S3:5/C1S03-X1:5 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P05 | 3 | 5 | 6 | 1756-IB32 | Spare_DI_0 | Pin 6 | C1S3:6/C1S03-X1:6 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P06 | 3 | 6 | 7 | 1756-IB32 | Spare_DI_0 | Pin 7 | C1S3:7/C1S03-X1:7 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P07 | 3 | 7 | 8 | 1756-IB32 | Spare_DI_0 | Pin 8 | C1S3:8/C1S03-X1:8 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P08 | 3 | 8 | 9 | 1756-IB32 | Spare_DI_0 | Pin 9 | C1S3:9/C1S03-X1:9 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P09 | 3 | 9 | 10 | 1756-IB32 | Spare_DI_0 | Pin 10 | C1S3:10/C1S03-X1:10 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P10 | 3 | 10 | 11 | 1756-IB32 | Spare_DI_0 | Pin 11 | C1S3:11/C1S03-X1:11 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P11 | 3 | 11 | 12 | 1756-IB32 | Spare_DI_0 | Pin 12 | C1S3:12/C1S03-X1:12 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P12 | 3 | 12 | 13 | 1756-IB32 | Spare_DI_0 | Pin 13 | C1S3:13/C1S03-X1:13 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P13 | 3 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C1S3:14/C1S03-X1:14 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P14 | 3 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C1S3:15/C1S03-X1:15 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P15 | 3 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C1S3:16/C1S03-X1:16 | DI | 24VDC Dry Contact | SPARE | CA1 | Main Control Cabinet | Main Control Cabinet | C1S03-X1 | - | Spare | Spare Channel | -
C1-S03-P16 | 3 | 16 | 17 | 1756-IB32 | FSL-40201_DI_1 | Pin 17 | C1S3:17/C1S03-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | FSL-40201 | Flow Switch | 3-25-01-402-PD-01
C1-S03-P17 | 3 | 17 | 18 | 1756-IB32 | FSL-40202_DI_1 | Pin 18 | C1S3:18/C1S03-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | FSL-40202 | Flow Switch | 3-25-01-402-PD-01
C1-S03-P18 | 3 | 18 | 19 | 1756-IB32 | FT-40201_DI_1 | Pin 19 | C1S3:19/C1S03-X2:19 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | FT-40201 | Coriolis Flow Transmitter | 3-25-01-402-PD-02
C1-S03-P19 | 3 | 19 | 20 | 1756-IB32 | FT-40202_DI_1 | Pin 20 | C1S3:20/C1S03-X2:20 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | FT-40202 | Magnetic Flow Transmitter | 3-25-01-402-PD-02
C1-S03-P20 | 3 | 20 | 21 | 1756-IB32 | HV-40201_DI_1 | Pin 21 | C1S3:21/C1S03-X2:21 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40201 | Manual Valve With Position Switch | 3-25-01-402-PD-01
C1-S03-P21 | 3 | 21 | 22 | 1756-IB32 | HV-40202_DI_1 | Pin 22 | C1S3:22/C1S03-X2:22 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40202 | Manual Valve With Position Switch | 3-25-01-402-PD-01
C1-S03-P22 | 3 | 22 | 23 | 1756-IB32 | HV-40203_DI_1 | Pin 23 | C1S3:23/C1S03-X2:23 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40203 | Manual Valve With Position Switch | 3-25-01-402-PD-01
C1-S03-P23 | 3 | 23 | 24 | 1756-IB32 | HV-40204_DI_1 | Pin 24 | C1S3:24/C1S03-X2:24 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | HV-40204 | Manual Valve With Position Switch | 3-25-01-402-PD-01
C1-S03-P24 | 3 | 24 | 25 | 1756-IB32 | HV-40205_DI_1 | Pin 25 | C1S3:25/C1S03-X2:25 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | HV-40205 | Manual Valve With Position Switch | 3-25-01-402-PD-02
C1-S03-P25 | 3 | 25 | 26 | 1756-IB32 | HV-40206_DI_1 | Pin 26 | C1S3:26/C1S03-X2:26 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S03-X2 | - | HV-40206 | Manual Valve With Position Switch | 3-25-01-402-PD-02
C1-S03-P26 | 3 | 26 | 27 | 1756-IB32 | XV-40201A_DI_1 | Pin 27 | C1S3:27/C1S03-X2:27 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201A |  | 3-25-01-402-PD-01
C1-S03-P27 | 3 | 27 | 28 | 1756-IB32 | XV-40201A_DI_2 | Pin 28 | C1S3:28/C1S03-X2:28 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201A |  | 3-25-01-402-PD-01
C1-S03-P28 | 3 | 28 | 29 | 1756-IB32 | XV-40201B_DI_1 | Pin 29 | C1S3:29/C1S03-X2:29 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201B |  | 3-25-01-402-PD-01
C1-S03-P29 | 3 | 29 | 30 | 1756-IB32 | XV-40201B_DI_2 | Pin 30 | C1S3:30/C1S03-X2:30 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201B |  | 3-25-01-402-PD-01
C1-S03-P30 | 3 | 30 | 31 | 1756-IB32 | XV-40201C_DI_1 | Pin 31 | C1S3:31/C1S03-X2:31 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201C |  | 3-25-01-402-PD-01
C1-S03-P31 | 3 | 31 | 32 | 1756-IB32 | XV-40201C_DI_2 | Pin 32 | C1S3:32/C1S03-X2:32 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S03-X2 | - | XV-40201C |  | 3-25-01-402-PD-01

## Slot_04
KALASIN ENGINEERING — C1 SLOT 04 (1756-IB32 • DI)
Chassis: C1 (Main Controller Rack (Chassis 1)) ¦ Panel: Control Cabinet CA1 (Main Control Room) ¦ Net: Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) ¦ Total Points: 32 (Active: 32, Spare: 0 / 0.0%) | [16 empty] | Destination: JB-401
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C1-S04-P00 | 4 | 0 | 1 | 1756-IB32 | XV-40201D_DI_1 | Pin 1 | C1S4:1/TBDI1:1A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201D |  | 3-25-01-402-PD-01
C1-S04-P01 | 4 | 1 | 2 | 1756-IB32 | XV-40201D_DI_2 | Pin 2 | C1S4:2/TBDI1:2A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201D |  | 3-25-01-402-PD-01
C1-S04-P02 | 4 | 2 | 3 | 1756-IB32 | XV-40201E_DI_1 | Pin 3 | C1S4:3/TBDI1:3A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201E |  | 3-25-01-402-PD-01
C1-S04-P03 | 4 | 3 | 4 | 1756-IB32 | XV-40201E_DI_2 | Pin 4 | C1S4:4/TBDI1:4A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201E |  | 3-25-01-402-PD-01
C1-S04-P04 | 4 | 4 | 5 | 1756-IB32 | XV-40201F_DI_1 | Pin 5 | C1S4:5/TBDI1:5A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201F |  | 3-25-01-402-PD-01
C1-S04-P05 | 4 | 5 | 6 | 1756-IB32 | XV-40201F_DI_2 | Pin 6 | C1S4:6/TBDI1:6A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201F |  | 3-25-01-402-PD-01
C1-S04-P06 | 4 | 6 | 7 | 1756-IB32 | XV-40201G_DI_1 | Pin 7 | C1S4:7/TBDI1:7A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201G |  | 3-25-01-402-PD-01
C1-S04-P07 | 4 | 7 | 8 | 1756-IB32 | XV-40201G_DI_2 | Pin 8 | C1S4:8/TBDI1:8A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201G |  | 3-25-01-402-PD-01
C1-S04-P08 | 4 | 8 | 9 | 1756-IB32 | XV-40201H_DI_1 | Pin 9 | C1S4:9/TBDI1:9A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201H |  | 3-25-01-402-PD-01
C1-S04-P09 | 4 | 9 | 10 | 1756-IB32 | XV-40201H_DI_2 | Pin 10 | C1S4:10/TBDI1:10A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40201H |  | 3-25-01-402-PD-01
C1-S04-P11 | 4 | 11 | 12 | 1756-IB32 | XV-40202A_DI_2 | Pin 12 | C1S4:12/TBDI1:12A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202A |  | 3-25-01-402-PD-01
C1-S04-P12 | 4 | 12 | 13 | 1756-IB32 | XV-40202B_DI_1 | Pin 13 | C1S4:13/TBDI1:13A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202B |  | 3-25-01-402-PD-01
C1-S04-P13 | 4 | 13 | 14 | 1756-IB32 | XV-40202B_DI_2 | Pin 14 | C1S4:14/TBDI1:14A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202B |  | 3-25-01-402-PD-01
C1-S04-P14 | 4 | 14 | 15 | 1756-IB32 | XV-40202C_DI_1 | Pin 15 | C1S4:15/TBDI1:15A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202C |  | 3-25-01-402-PD-01
C1-S04-P15 | 4 | 15 | 16 | 1756-IB32 | XV-40202C_DI_2 | Pin 16 | C1S4:16/TBDI1:16A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X1 | - | XV-40202C |  | 3-25-01-402-PD-01
C1-S04-P16 | 4 | 16 | 17 | 1756-IB32 | XV-40202D_DI_1 | Pin 17 | C1S4:17/C1S04-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202D |  | 3-25-01-402-PD-01
C1-S04-P17 | 4 | 17 | 18 | 1756-IB32 | XV-40202D_DI_2 | Pin 18 | C1S4:18/C1S04-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202D |  | 3-25-01-402-PD-01
C1-S04-P18 | 4 | 18 | 19 | 1756-IB32 | XV-40202E_DI_1 | Pin 19 | C1S4:19/TBDI1:17A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202E |  | 3-25-01-402-PD-01
C1-S04-P19 | 4 | 19 | 20 | 1756-IB32 | XV-40202A_DI_1 | Pin 20 | C1S4:20/TBDI1:18A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202A |  | 3-25-01-402-PD-01
C1-S04-P19 | 4 | 19 | 20 | 1756-IB32 | XV-40202E_DI_2 | Pin 20 | C1S4:20/TBDI1:18A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202E |  | 3-25-01-402-PD-01
C1-S04-P20 | 4 | 20 | 21 | 1756-IB32 | XV-40202F_DI_1 | Pin 21 | C1S4:21/TBDI1:19A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202F |  | 3-25-01-402-PD-01
C1-S04-P21 | 4 | 21 | 22 | 1756-IB32 | XV-40202F_DI_2 | Pin 22 | C1S4:22/TBDI1:20A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202F |  | 3-25-01-402-PD-01
C1-S04-P22 | 4 | 22 | 23 | 1756-IB32 | XV-40202G_DI_1 | Pin 23 | C1S4:23/TBDI1:21A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202G |  | 3-25-01-402-PD-01
C1-S04-P23 | 4 | 23 | 24 | 1756-IB32 | XV-40202G_DI_2 | Pin 24 | C1S4:24/TBDI1:22A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202G |  | 3-25-01-402-PD-01
C1-S04-P24 | 4 | 24 | 25 | 1756-IB32 | XV-40202H_DI_1 | Pin 25 | C1S4:25/TBDI1:23A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202H |  | 3-25-01-402-PD-01
C1-S04-P25 | 4 | 25 | 26 | 1756-IB32 | XV-40202H_DI_2 | Pin 26 | C1S4:26/TBDI1:24A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S04-X2 | - | XV-40202H |  | 3-25-01-402-PD-01
C1-S04-P26 | 4 | 26 | 27 | 1756-IB32 | XV-40203B_DI_1 | Pin 27 | C1S4:27/TBDI1:25A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203B |  | 3-25-01-402-PD-02
C1-S04-P27 | 4 | 27 | 28 | 1756-IB32 | XV-40203B_DI_2 | Pin 28 | C1S4:28/TBDI1:26A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203B |  | 3-25-01-402-PD-02
C1-S04-P28 | 4 | 28 | 29 | 1756-IB32 | XV-40203C_DI_1 | Pin 29 | C1S4:29/TBDI1:27A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203C |  | 3-25-01-402-PD-02
C1-S04-P29 | 4 | 29 | 30 | 1756-IB32 | XV-40203C_DI_2 | Pin 30 | C1S4:30/TBDI1:28A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203C |  | 3-25-01-402-PD-02
C1-S04-P30 | 4 | 30 | 31 | 1756-IB32 | XV-40203D_DI_1 | Pin 31 | C1S4:31/TBDI1:29A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203D |  | 3-25-01-402-PD-02
C1-S04-P31 | 4 | 31 | 32 | 1756-IB32 | XV-40203D_DI_2 | Pin 32 | C1S4:32/TBDI1:30A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S04-X2 | - | XV-40203D |  | 3-25-01-402-PD-02

## Slot_05
KALASIN ENGINEERING — C1 SLOT 05 (1756-IB32 • DI)
Chassis: C1 (Main Controller Rack (Chassis 1)) ¦ Panel: Control Cabinet CA1 (Main Control Room) ¦ Net: Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) ¦ Total Points: 32 (Active: 12, Spare: 20 / 62.5%) | [16 empty] | Destination: JB-401, JB-601
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C1-S05-P00 | 5 | 0 | 1 | 1756-IB32 | XV-40203E_DI_1 | Pin 1 | C1S5:1/TBDI2:1A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S05-X1 | - | XV-40203E |  | 3-25-01-402-PD-02
C1-S05-P01 | 5 | 1 | 2 | 1756-IB32 | XV-40203E_DI_2 | Pin 2 | C1S5:2/TBDI2:2A | DI | 24VDC Dry Contact | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S05-X1 | - | XV-40203E |  | 3-25-01-402-PD-02
C1-S05-P02 | 5 | 2 | 3 | 1756-IB32 | Spare_DI_0 | Pin 3 | C1S5:3/TBDI2:3A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P03 | 5 | 3 | 4 | 1756-IB32 | Spare_DI_0 | Pin 4 | C1S5:4/TBDI2:4A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P04 | 5 | 4 | 5 | 1756-IB32 | Spare_DI_0 | Pin 5 | C1S5:5/TBDI2:5A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P05 | 5 | 5 | 6 | 1756-IB32 | Spare_DI_0 | Pin 6 | C1S5:6/TBDI2:6A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P06 | 5 | 6 | 7 | 1756-IB32 | Spare_DI_0 | Pin 7 | C1S5:7/TBDI2:7A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P07 | 5 | 7 | 8 | 1756-IB32 | Spare_DI_0 | Pin 8 | C1S5:8/TBDI2:8A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P08 | 5 | 8 | 9 | 1756-IB32 | Spare_DI_0 | Pin 9 | C1S5:9/TBDI2:9A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P09 | 5 | 9 | 10 | 1756-IB32 | Spare_DI_0 | Pin 10 | C1S5:10/TBDI2:10A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P10 | 5 | 10 | 11 | 1756-IB32 | Spare_DI_0 | Pin 11 | C1S5:11/TBDI2:11A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P11 | 5 | 11 | 12 | 1756-IB32 | Spare_DI_0 | Pin 12 | C1S5:12/TBDI2:12A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P12 | 5 | 12 | 13 | 1756-IB32 | Spare_DI_0 | Pin 13 | C1S5:13/TBDI2:13A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P13 | 5 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C1S5:14/TBDI2:14A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P14 | 5 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C1S5:15/TBDI2:15A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P15 | 5 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C1S5:16/TBDI2:16A | DI | 24VDC Dry Contact | SPARE | JB-401 | Infeed 2nd Floor | - | C1S05-X1 | - | Spare | Spare Channel | -
C1-S05-P16 | 5 | 16 | 17 | 1756-IB32 | ES-60202_DI_1 | Pin 17 | C1S5:17/C1S05-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | ES-60202 |  | -
C1-S05-P17 | 5 | 17 | 18 | 1756-IB32 | FS-60205_DI_1 | Pin 18 | C1S5:18/C1S05-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | FS-60205 | Flow Switch | 3-25-01-602-PD-01
C1-S05-P18 | 5 | 18 | 19 | 1756-IB32 | LSL-60201_DI_1 | Pin 19 | C1S5:19/TBDI2:17A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | LSL-60201 |  | 3-25-01-602-PD-11
C1-S05-P19 | 5 | 19 | 20 | 1756-IB32 | SV-60201_DI_1 | Pin 20 | C1S5:20/TBDI2:18A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60201 |  | 3-25-01-602-PD-08
C1-S05-P20 | 5 | 20 | 21 | 1756-IB32 | SV-60201_DI_2 | Pin 21 | C1S5:21/TBDI2:19A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60201 |  | 3-25-01-602-PD-08
C1-S05-P21 | 5 | 21 | 22 | 1756-IB32 | SV-60202_DI_1 | Pin 22 | C1S5:22/TBDI2:20A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60202 |  | 3-25-01-602-PD-08
C1-S05-P22 | 5 | 22 | 23 | 1756-IB32 | SV-60202_DI_2 | Pin 23 | C1S5:23/TBDI2:21A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60202 |  | 3-25-01-602-PD-08
C1-S05-P23 | 5 | 23 | 24 | 1756-IB32 | SV-60203_DI_1 | Pin 24 | C1S5:24/TBDI2:22A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60203 |  | 3-25-01-602-PD-08
C1-S05-P24 | 5 | 24 | 25 | 1756-IB32 | SV-60203_DI_2 | Pin 25 | C1S5:25/TBDI2:23A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | SV-60203 |  | 3-25-01-602-PD-08
C1-S05-P25 | 5 | 25 | 26 | 1756-IB32 | VS-60205_DI_1 | Pin 26 | C1S5:26/TBDI2:24A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S05-X2 | - | VS-60205 | Vibration Switch | 3-25-01-602-PD-01
C1-S05-P26 | 5 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C1S5:27/TBDI2:25A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | -
C1-S05-P27 | 5 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C1S5:28/TBDI2:26A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | -
C1-S05-P28 | 5 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C1S5:29/TBDI2:27A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | -
C1-S05-P29 | 5 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C1S5:30/TBDI2:28A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | -
C1-S05-P30 | 5 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C1S5:31/TBDI2:29A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | -
C1-S05-P31 | 5 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C1S5:32/TBDI2:30A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S05-X2 | - | Spare | Spare Channel | -

## Slot_06
KALASIN ENGINEERING — C1 SLOT 06 (1756-IB32 • DI)
Chassis: C1 (Main Controller Rack (Chassis 1)) ¦ Panel: Control Cabinet CA1 (Main Control Room) ¦ Net: Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) ¦ Total Points: 32 (Active: 23, Spare: 9 / 28.1%) | [16 empty] | Destination: JB-601
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C1-S06-P00 | 6 | 0 | 1 | 1756-IB32 | XA-60202A_DI_1 | Pin 1 | C1S6:1/TBDI3:1A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202A |  | -
C1-S06-P01 | 6 | 1 | 2 | 1756-IB32 | XA-60202B_DI_1 | Pin 2 | C1S6:2/TBDI3:2A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202B |  | -
C1-S06-P02 | 6 | 2 | 3 | 1756-IB32 | XA-60202C_DI_1 | Pin 3 | C1S6:3/TBDI3:3A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202C |  | -
C1-S06-P03 | 6 | 3 | 4 | 1756-IB32 | XA-60202D_DI_1 | Pin 4 | C1S6:4/TBDI3:4A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202D |  | -
C1-S06-P04 | 6 | 4 | 5 | 1756-IB32 | XA-60202E_DI_1 | Pin 5 | C1S6:5/TBDI3:5A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202E |  | -
C1-S06-P05 | 6 | 5 | 6 | 1756-IB32 | XA-60202F_DI_1 | Pin 6 | C1S6:6/TBDI3:6A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202F |  | -
C1-S06-P06 | 6 | 6 | 7 | 1756-IB32 | XA-60202G_DI_1 | Pin 7 | C1S6:7/TBDI3:7A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202G |  | -
C1-S06-P07 | 6 | 7 | 8 | 1756-IB32 | XA-60202H_DI_1 | Pin 8 | C1S6:8/TBDI3:8A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202H |  | -
C1-S06-P08 | 6 | 8 | 9 | 1756-IB32 | XA-60202I_DI_1 | Pin 9 | C1S6:9/TBDI3:9A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202I |  | -
C1-S06-P09 | 6 | 9 | 10 | 1756-IB32 | XA-60202J_DI_1 | Pin 10 | C1S6:10/TBDI3:10A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202J |  | -
C1-S06-P10 | 6 | 10 | 11 | 1756-IB32 | XA-60202K_DI_1 | Pin 11 | C1S6:11/TBDI3:11A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202K |  | -
C1-S06-P11 | 6 | 11 | 12 | 1756-IB32 | XA-60202L_DI_1 | Pin 12 | C1S6:12/TBDI3:12A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202L |  | -
C1-S06-P12 | 6 | 12 | 13 | 1756-IB32 | XA-60202M_DI_1 | Pin 13 | C1S6:13/TBDI3:13A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XA-60202M |  | -
C1-S06-P13 | 6 | 13 | 14 | 1756-IB32 | XV-60202_DI_1 | Pin 14 | C1S6:14/TBDI3:14A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XV-60202 |  | 3-25-01-602-PD-11
C1-S06-P14 | 6 | 14 | 15 | 1756-IB32 | XV-60202_DI_2 | Pin 15 | C1S6:15/TBDI3:15A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XV-60202 |  | 3-25-01-602-PD-11
C1-S06-P15 | 6 | 15 | 16 | 1756-IB32 | XV-60205A_DI_1 | Pin 16 | C1S6:16/TBDI3:16A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X1 | - | XV-60205A |  | 3-25-01-602-PD-01
C1-S06-P16 | 6 | 16 | 17 | 1756-IB32 | XV-60205A_DI_2 | Pin 17 | C1S6:17/C1S06-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60205A |  | 3-25-01-602-PD-01
C1-S06-P17 | 6 | 17 | 18 | 1756-IB32 | XV-60240D_DI_1 | Pin 18 | C1S6:18/C1S06-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60240D |  | -
C1-S06-P18 | 6 | 18 | 19 | 1756-IB32 | XV-60240D_DI_2 | Pin 19 | C1S6:19/TBDI3:17A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60240D |  | 3-25-01-602-PD-05
C1-S06-P19 | 6 | 19 | 20 | 1756-IB32 | XV-60240D_DI_1 | Pin 20 | C1S6:20/TBDI3:18A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60240D |  | -
C1-S06-P20 | 6 | 20 | 21 | 1756-IB32 | XV-60240D_DI_2 | Pin 21 | C1S6:21/TBDI3:19A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | XV-60240D |  | 3-25-01-602-PD-05
C1-S06-P21 | 6 | 21 | 22 | 1756-IB32 | YA-60205_DI_1 | Pin 22 | C1S6:22/TBDI3:20A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | YA-60205 |  | -
C1-S06-P22 | 6 | 22 | 23 | 1756-IB32 | YI-60205_DI_1 | Pin 23 | C1S6:23/TBDI3:21A | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | YI-60205 |  | -
C1-S06-P23 | 6 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C1S6:24/TBDI3:22A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P24 | 6 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C1S6:25/TBDI3:23A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P25 | 6 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C1S6:26/TBDI3:24A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P26 | 6 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C1S6:27/TBDI3:25A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P27 | 6 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C1S6:28/TBDI3:26A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P28 | 6 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C1S6:29/TBDI3:27A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P29 | 6 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C1S6:30/TBDI3:28A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P30 | 6 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C1S6:31/TBDI3:29A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -
C1-S06-P31 | 6 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C1S6:32/TBDI3:30A | DI | 24VDC Dry Contact | SPARE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S06-X2 | - | Spare | Spare Channel | -

## Slot_07
KALASIN ENGINEERING — C1 SLOT 07 (1756-OB32 • DO)
Chassis: C1 (Main Controller Rack (Chassis 1)) ¦ Panel: Control Cabinet CA1 (Main Control Room) ¦ Net: Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) ¦ Total Points: 32 (Active: 16, Spare: 16 / 50.0%) | [16 empty] | Destination: CA1, JB-401
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C1-S07-P00 | 7 | 0 | 1 | 1756-OB32 | Spare_DO_0 | Pin 1 | C1S7:1/TBDI4:1A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P01 | 7 | 1 | 2 | 1756-OB32 | Spare_DO_0 | Pin 2 | C1S7:2/TBDI4:2A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P02 | 7 | 2 | 3 | 1756-OB32 | Spare_DO_0 | Pin 3 | C1S7:3/TBDI4:3A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P03 | 7 | 3 | 4 | 1756-OB32 | Spare_DO_0 | Pin 4 | C1S7:4/TBDI4:4A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P04 | 7 | 4 | 5 | 1756-OB32 | Spare_DO_0 | Pin 5 | C1S7:5/TBDI4:5A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P05 | 7 | 5 | 6 | 1756-OB32 | Spare_DO_0 | Pin 6 | C1S7:6/TBDI4:6A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P06 | 7 | 6 | 7 | 1756-OB32 | Spare_DO_0 | Pin 7 | C1S7:7/TBDI4:7A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P07 | 7 | 7 | 8 | 1756-OB32 | Spare_DO_0 | Pin 8 | C1S7:8/TBDI4:8A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P08 | 7 | 8 | 9 | 1756-OB32 | Spare_DO_0 | Pin 9 | C1S7:9/TBDI4:9A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P09 | 7 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C1S7:10/TBDI4:10A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P10 | 7 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C1S7:11/TBDI4:11A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P11 | 7 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C1S7:12/TBDI4:12A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P12 | 7 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C1S7:13/TBDI4:13A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P13 | 7 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C1S7:14/TBDI4:14A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P14 | 7 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C1S7:15/TBDI4:15A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P15 | 7 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C1S7:16/TBDI4:16A | DO | 24VDC Sourcing | SPARE | CA1 | Main Control Cabinet | - | C1S07-X1 | - | Spare | Spare Channel | -
C1-S07-P16 | 7 | 16 | 17 | 1756-OB32 | XV-40202E_DO_1 | Pin 17 | C1S7:17/C1S07-X2:17 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202E |  | 3-25-01-402-PD-01
C1-S07-P17 | 7 | 17 | 18 | 1756-OB32 | XV-40202F_DO_1 | Pin 18 | C1S7:18/C1S07-X2:18 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202F |  | 3-25-01-402-PD-01
C1-S07-P18 | 7 | 18 | 19 | 1756-OB32 | XV-40202G_DO_1 | Pin 19 | C1S7:19/TBDI4:17A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202G |  | 3-25-01-402-PD-01
C1-S07-P19 | 7 | 19 | 20 | 1756-OB32 | XV-40202H_DO_1 | Pin 20 | C1S7:20/TBDI4:18A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40202H |  | 3-25-01-402-PD-01
C1-S07-P20 | 7 | 20 | 21 | 1756-OB32 | XV-40203B_DO_1 | Pin 21 | C1S7:21/TBDI4:19A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203B |  | 3-25-01-402-PD-02
C1-S07-P21 | 7 | 21 | 22 | 1756-OB32 | XV-40203C_DO_1 | Pin 22 | C1S7:22/TBDI4:20A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203C |  | 3-25-01-402-PD-02
C1-S07-P22 | 7 | 22 | 23 | 1756-OB32 | XV-40203D_DO_1 | Pin 23 | C1S7:23/TBDI4:21A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203D |  | 3-25-01-402-PD-02
C1-S07-P23 | 7 | 23 | 24 | 1756-OB32 | XV-40203E_DO_1 | Pin 24 | C1S7:24/TBDI4:22A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S07-X2 | - | XV-40203E |  | 3-25-01-402-PD-02
C1-S07-P24 | 7 | 24 | 25 | 1756-OB32 | SV-40201_DO_1 | Pin 25 | C1S7:25/TBDI4:23A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40201 |  | 3-25-01-402-PD-01
C1-S07-P25 | 7 | 25 | 26 | 1756-OB32 | SV-40202_DO_1 | Pin 26 | C1S7:26/TBDI4:24A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40202 |  | 3-25-01-402-PD-01
C1-S07-P26 | 7 | 26 | 27 | 1756-OB32 | SV-40203_DO_1 | Pin 27 | C1S7:27/TBDI4:25A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40203 |  | 3-25-01-402-PD-01
C1-S07-P27 | 7 | 27 | 28 | 1756-OB32 | SV-40204_DO_1 | Pin 28 | C1S7:28/TBDI4:26A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | SV-40204 |  | 3-25-01-402-PD-01
C1-S07-P28 | 7 | 28 | 29 | 1756-OB32 | XV-40201A_DO_1 | Pin 29 | C1S7:29/TBDI4:27A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201A |  | 3-25-01-402-PD-01
C1-S07-P29 | 7 | 29 | 30 | 1756-OB32 | XV-40201B_DO_1 | Pin 30 | C1S7:30/TBDI4:28A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201B |  | 3-25-01-402-PD-01
C1-S07-P30 | 7 | 30 | 31 | 1756-OB32 | XV-40201C_DO_1 | Pin 31 | C1S7:31/TBDI4:29A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201C |  | 3-25-01-402-PD-01
C1-S07-P31 | 7 | 31 | 32 | 1756-OB32 | XV-40201D_DO_1 | Pin 32 | C1S7:32/TBDI4:30A | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S07-X2 | - | XV-40201D |  | 3-25-01-402-PD-01

## Slot_08
KALASIN ENGINEERING — C1 SLOT 08 (1756-OB32 • DO)
Chassis: C1 (Main Controller Rack (Chassis 1)) ¦ Panel: Control Cabinet CA1 (Main Control Room) ¦ Net: Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) ¦ Total Points: 32 (Active: 20, Spare: 12 / 37.5%) | [16 empty] | Destination: JB-401, JB-601
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C1-S08-P00 | 8 | 0 | 1 | 1756-OB32 | XV-40201E_DO_1 | Pin 1 | C1S8:1/RL.1:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201E |  | 3-25-01-402-PD-01
C1-S08-P01 | 8 | 1 | 2 | 1756-OB32 | XV-40201F_DO_1 | Pin 2 | C1S8:2/RL.2:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201F |  | 3-25-01-402-PD-01
C1-S08-P02 | 8 | 2 | 3 | 1756-OB32 | XV-40201G_DO_1 | Pin 3 | C1S8:3/RL.3:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201G |  | 3-25-01-402-PD-01
C1-S08-P03 | 8 | 3 | 4 | 1756-OB32 | XV-40201H_DO_1 | Pin 4 | C1S8:4/RL.4:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40201H |  | 3-25-01-402-PD-01
C1-S08-P04 | 8 | 4 | 5 | 1756-OB32 | XV-40202A_DO_1 | Pin 5 | C1S8:5/RL.5:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202A |  | 3-25-01-402-PD-01
C1-S08-P05 | 8 | 5 | 6 | 1756-OB32 | XV-40202B_DO_1 | Pin 6 | C1S8:6/RL.6:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202B |  | 3-25-01-402-PD-01
C1-S08-P06 | 8 | 6 | 7 | 1756-OB32 | XV-40202C_DO_1 | Pin 7 | C1S8:7/RL.7:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202C |  | 3-25-01-402-PD-01
C1-S08-P07 | 8 | 7 | 8 | 1756-OB32 | XV-40202D_DO_1 | Pin 8 | C1S8:8/RL.8:A1 | DO | 24VDC Sourcing | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S08-X1 | - | XV-40202D |  | 3-25-01-402-PD-01
C1-S08-P08 | 8 | 8 | 9 | 1756-OB32 | Spare_DO_0 | Pin 9 | C1S8:9/RL.9:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P09 | 8 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C1S8:10/RL.10:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P10 | 8 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C1S8:11/RL.11:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P11 | 8 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C1S8:12/RL.12:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P12 | 8 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C1S8:13/RL.13:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P13 | 8 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C1S8:14/RL.14:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P14 | 8 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C1S8:15/RL.15:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P15 | 8 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C1S8:16/RL.16:A1 | DO | 24VDC Sourcing | SPARE | JB-401 | Infeed 2nd Floor | - | C1S08-X1 | - | Spare | Spare Channel | -
C1-S08-P16 | 8 | 16 | 17 | 1756-OB32 | SV-60201_DO_1 | Pin 17 | C1S8:17/C1S08-X2:17 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60201 |  | 3-25-01-602-PD-08
C1-S08-P17 | 8 | 17 | 18 | 1756-OB32 | SV-60202_DO_1 | Pin 18 | C1S8:18/C1S08-X2:18 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60202 |  | 3-25-01-602-PD-08
C1-S08-P18 | 8 | 18 | 19 | 1756-OB32 | SV-60230_DO_1 | Pin 19 | C1S8:19/RL.17:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60230 |  | 3-25-01-602-PD-04
C1-S08-P19 | 8 | 19 | 20 | 1756-OB32 | SV-60203_DO_1 | Pin 20 | C1S8:20/RL.18:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60203 |  | 3-25-01-602-PD-08
C1-S08-P20 | 8 | 20 | 21 | 1756-OB32 | SV-60240A_DO_1 | Pin 21 | C1S8:21/RL.19:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60240A |  | 3-25-01-602-PD-05
C1-S08-P21 | 8 | 21 | 22 | 1756-OB32 | SV-60231_DO_1 | Pin 22 | C1S8:22/RL.20:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60231 |  | 3-25-01-602-PD-04
C1-S08-P22 | 8 | 22 | 23 | 1756-OB32 | SV-60240B_DO_1 | Pin 23 | C1S8:23/RL.21:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60240B |  | 3-25-01-602-PD-05
C1-S08-P23 | 8 | 23 | 24 | 1756-OB32 | SV-60240C_DO_1 | Pin 24 | C1S8:24/RL.22:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | SV-60240C |  | 3-25-01-602-PD-05
C1-S08-P24 | 8 | 24 | 25 | 1756-OB32 | XV-60240D_DO_1 | Pin 25 | C1S8:25/RL.23:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | XV-60240D |  | -
C1-S08-P25 | 8 | 25 | 26 | 1756-OB32 | XV-60251_DO_1 | Pin 26 | C1S8:26/RL.24:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Infeed Tank | C1S08-X2 | - | XV-60251 |  | 3-25-01-602-PD-01
C1-S08-P26 | 8 | 26 | 27 | 1756-OB32 | XV-60202_DO_1 | Pin 27 | C1S8:27/RL.25:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | XV-60202 |  | 3-25-01-602-PD-11
C1-S08-P27 | 8 | 27 | 28 | 1756-OB32 | XV-60205A_DO_1 | Pin 28 | C1S8:28/RL.26:A1 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S08-X2 | - | XV-60205A |  | 3-25-01-602-PD-01
C1-S08-P28 | 8 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C1S8:29/RL.27:A1 | DO | 24VDC Sourcing | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S08-X2 | - | Spare | Spare Channel | -
C1-S08-P29 | 8 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C1S8:30/RL.28:A1 | DO | 24VDC Sourcing | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S08-X2 | - | Spare | Spare Channel | -
C1-S08-P30 | 8 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C1S8:31/RL.29:A1 | DO | 24VDC Sourcing | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S08-X2 | - | Spare | Spare Channel | -
C1-S08-P31 | 8 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C1S8:32/RL.30:A1 | DO | 24VDC Sourcing | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S08-X2 | - | Spare | Spare Channel | -

## Slot_09
KALASIN ENGINEERING — C1 SLOT 09 (1756-IF16 • AI)
Chassis: C1 (Main Controller Rack (Chassis 1)) ¦ Panel: Control Cabinet CA1 (Main Control Room) ¦ Net: Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) ¦ Total Points: 16 (Active: 11, Spare: 5 / 31.2%) | [16 empty] | Destination: JB-401
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C1-S09-P00 | 9 | 0 | 1 | 1756-IF16 | FT-40201_AI_1 | Pin 1 | C1S9:1/RL.33:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | FT-40201 | Coriolis Flow Transmitter | 3-25-01-402-PD-02
C1-S09-P01 | 9 | 1 | 2 | 1756-IF16 | FT-40201_AI_2 | Pin 2 | C1S9:2/RL.34:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | FT-40201 | Coriolis Flow Transmitter | 3-25-01-402-PD-02
C1-S09-P02 | 9 | 2 | 3 | 1756-IF16 | FT-40202_AI_1 | Pin 3 | C1S9:3/RL.35:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | FT-40202 | Magnetic Flow Transmitter | 3-25-01-402-PD-02
C1-S09-P03 | 9 | 3 | 4 | 1756-IF16 | LT-40203_AI_1 | Pin 4 | C1S9:4/RL.36:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | LT-40203 | Level Transmitter | 3-25-01-402-PD-02
C1-S09-P04 | 9 | 4 | 5 | 1756-IF16 | LT-40201_AI_1 | Pin 5 | C1S9:5/RL.37:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | LT-40201 | Level Transmitter | 3-25-01-402-PD-01
C1-S09-P05 | 9 | 5 | 6 | 1756-IF16 | LT-40202_AI_1 | Pin 6 | C1S9:6/RL.38:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | LT-40202 | Level Transmitter | 3-25-01-402-PD-01
C1-S09-P06 | 9 | 6 | 7 | 1756-IF16 | pHT-40201_AI_1 | Pin 7 | C1S9:7/RL.39:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | pHT-40201 | PH Transmitter | 3-25-01-402-PD-01
C1-S09-P07 | 9 | 7 | 8 | 1756-IF16 | pHT-40202_AI_1 | Pin 8 | C1S9:8/RL.40:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / PH Adjustment | C1S09-X1 | - | pHT-40202 | PH Transmitter | 3-25-01-402-PD-01
C1-S09-P08 | 9 | 8 | 9 | 1756-IF16 | PT-40201_AI_1 | Pin 9 | C1S9:9/RL.41:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | PT-40201 | Pressure Transmitter | 3-25-01-402-PD-02
C1-S09-P09 | 9 | 9 | 10 | 1756-IF16 | PT-40202_AI_1 | Pin 10 | C1S9:10/RL.42:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | PT-40202 | Pressure Transmitter | 3-25-01-402-PD-02
C1-S09-P10 | 9 | 10 | 11 | 1756-IF16 | PT-60202_AI_1 | Pin 11 | C1S9:11/RL.43:A1 | AI | 4-20mA HART | ACTIVE | JB-401 | Infeed 2nd Floor | 1st / Infeed Tank | C1S09-X1 | - | PT-60202 | Pressure Transmitter | 3-25-01-602-PD-01
C1-S09-P11 | 9 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C1S9:12/RL.44:A1 | AI | 4-20mA HART | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | -
C1-S09-P12 | 9 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C1S9:13/RL.45:A1 | AI | 4-20mA HART | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | -
C1-S09-P13 | 9 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C1S9:14/RL.46:A1 | AI | 4-20mA HART | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | -
C1-S09-P14 | 9 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C1S9:15/RL.47:A1 | AI | 4-20mA HART | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | -
C1-S09-P15 | 9 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C1S9:16/RL.48:A1 | AI | 4-20mA HART | SPARE | JB-401 | Infeed 2nd Floor | - | C1S09-X1 | - | Spare | Spare Channel | -

## Slot_10
KALASIN ENGINEERING — C1 SLOT 10 (1756-IF16 • AI)
Chassis: C1 (Main Controller Rack (Chassis 1)) ¦ Panel: Control Cabinet CA1 (Main Control Room) ¦ Net: Stratix 5400 / EN4TR Ring Node 1 (192.168.1.10) ¦ Total Points: 16 (Active: 8, Spare: 8 / 50.0%) | [16 empty] | Destination: JB-601
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C1-S10-P00 | 10 | 0 | 1 | 1756-IF16 | DPI-60240_AI_1 | Pin 1 | C1S10:1/C1S10-X1:1 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | DPI-60240 |  | -
C1-S10-P01 | 10 | 1 | 2 | 1756-IF16 | DPT-60202_AI_1 | Pin 2 | C1S10:2/C1S10-X1:2 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | DPT-60202 | Differential Pressure Transmitte | 3-25-01-602-PD-08
C1-S10-P02 | 10 | 2 | 3 | 1756-IF16 | FT-60201_AI_1 | Pin 3 | C1S10:3/C1S10-X1:3 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | FT-60201 |  | 3-25-01-602-PD-08
C1-S10-P03 | 10 | 3 | 4 | 1756-IF16 | FT-60204_AI_1 | Pin 4 | C1S10:4/C1S10-X1:4 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | FT-60204 |  | 3-25-01-602-PD-10
C1-S10-P04 | 10 | 4 | 5 | 1756-IF16 | FT-61307_AI_1 | Pin 5 | C1S10:5/C1S10-X1:5 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | FT-61307 |  | 3-25-01-613-PD-04
C1-S10-P05 | 10 | 5 | 6 | 1756-IF16 | PT-60203_AI_1 | Pin 6 | C1S10:6/C1S10-X1:6 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | PT-60203 | Pressure Transmitter | 3-25-01-602-PD-08
C1-S10-P06 | 10 | 6 | 7 | 1756-IF16 | PT-60204_AI_1 | Pin 7 | C1S10:7/C1S10-X1:7 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | PT-60204 | Pressure Transmitter | 3-25-01-602-PD-10
C1-S10-P07 | 10 | 7 | 8 | 1756-IF16 | PT-60205_AI_1 | Pin 8 | C1S10:8/C1S10-X1:8 | AI | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C1S10-X1 | - | PT-60205 | Pressure Transmitter | 3-25-01-602-PD-01
C1-S10-P08 | 10 | 8 | 9 | 1756-IF16 | Spare_AI_0 | Pin 9 | C1S10:9/C1S10-X1:9 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P09 | 10 | 9 | 10 | 1756-IF16 | Spare_AI_0 | Pin 10 | C1S10:10/C1S10-X1:10 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P10 | 10 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C1S10:11/C1S10-X1:11 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P11 | 10 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C1S10:12/C1S10-X1:12 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P12 | 10 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C1S10:13/C1S10-X1:13 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P13 | 10 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C1S10:14/C1S10-X1:14 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P14 | 10 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C1S10:15/C1S10-X1:15 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -
C1-S10-P15 | 10 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C1S10:16/C1S10-X1:16 | AI | 4-20mA HART | SPARE | JB-601 | Spray Dryer 1st Floor | - | C1S10-X1 | - | Spare | Spare Channel | -