## C2_Slot_Summary
KALASIN ENGINEERING — C2 (I/O EXPANSION RACK 1 (CHASSIS 2))
Location: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Active Slots: 13
Slot No. | Module Model | I/O Type | Capacity | Active Points | Spare Points | Spare % | Primary Destinations | Sheet Link
Slot 01 | 1756-IB32 | DI | 32 | 24 | 8 | 25.0% | JB-402 | Go to Slot 01 ➔
Slot 02 | 1756-IB32 | DI | 32 | 23 | 9 | 28.1% | JB-602 | Go to Slot 02 ➔
Slot 03 | 1756-IB32 | DI | 29 | 29 | 0 | 0.0% | JB-607 | Go to Slot 03 ➔
Slot 04 | 1756-IB32 | DI | 32 | 32 | 0 | 0.0% | JB-607 | Go to Slot 04 ➔
Slot 05 | 1756-IB32 | DI | 32 | 20 | 12 | 37.5% | JB-607 | Go to Slot 05 ➔
Slot 06 | 1756-OB32 | DO | 32 | 12 | 20 | 62.5% | JB-402, JB-602 | Go to Slot 06 ➔
Slot 07 | 1756-OB32 | DO | 32 | 31 | 1 | 3.1% | JB-607 | Go to Slot 07 ➔
Slot 08 | 1756-OB32 | DO | 32 | 9 | 23 | 71.9% | JB-607 | Go to Slot 08 ➔
Slot 09 | 1756-IF16 | AI | 16 | 7 | 9 | 56.2% | JB-402 | Go to Slot 09 ➔
Slot 10 | 1756-IF16 | AI | 16 | 16 | 0 | 0.0% | JB-602 | Go to Slot 10 ➔
Slot 11 | 1756-IF16 | AI | 16 | 13 | 3 | 18.8% | JB-602 | Go to Slot 11 ➔
Slot 12 | 1756-IF16 | AI | 16 | 16 | 0 | 0.0% | JB-607 | Go to Slot 12 ➔
Slot 13 | 1756-IF16 | AI | 16 | 11 | 5 | 31.2% | JB-607 | Go to Slot 13 ➔

## Slot_01
KALASIN ENGINEERING — C2 SLOT 01 (1756-IB32 • DI)
Chassis: C2 (I/O Expansion Rack 1 (Chassis 2)) ¦ Panel: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 32 (Active: 24, Spare: 8 / 25.0%) | [16 empty] | Destination: JB-402
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C2-S01-P00 | 1 | 0 | 1 | 1756-IB32 | FS-40204_DI_1 | Pin 1 | C2S1:1/TBDI1:1A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | FS-40204 | Flow Switch | 325-01-402-PD-01
C2-S01-P01 | 1 | 1 | 2 | 1756-IB32 | FS-40205_DI_1 | Pin 2 | C2S1:2/TBDI1:2A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | FS-40205 | Flow Switch | 325-01-402-PD-02
C2-S01-P02 | 1 | 2 | 3 | 1756-IB32 | FT-40221_DI_1 | Pin 3 | C2S1:3/TBDI1:3A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | FT-40221 | Coriolis Flow Transmitter | 325-01-402-PD-02
C2-S01-P03 | 1 | 3 | 4 | 1756-IB32 | FT-40222_DI_1 | Pin 4 | C2S1:4/TBDI1:4A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | FT-40222 | Coriolis Flow Transmitter | 325-01-402-PD-02
C2-S01-P04 | 1 | 4 | 5 | 1756-IB32 | HV-40207_DI_1 | Pin 5 | C2S1:5/TBDI1:5A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | HV-40207 | Manual Valve With Position Switch | 325-01-402-PD-01
C2-S01-P05 | 1 | 5 | 6 | 1756-IB32 | HV-40208_DI_1 | Pin 6 | C2S1:6/TBDI1:6A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | HV-40208 | Manual Valve With Position Switch | 325-01-402-PD-01
C2-S01-P06 | 1 | 6 | 7 | 1756-IB32 | XV-40203F_DI_1 | Pin 7 | C2S1:7/TBDI1:7A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40203F |  | 325-01-402-PD-02
C2-S01-P07 | 1 | 7 | 8 | 1756-IB32 | XV-40203F_DI_2 | Pin 8 | C2S1:8/TBDI1:8A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40203F |  | 325-01-402-PD-02
C2-S01-P08 | 1 | 8 | 9 | 1756-IB32 | XV-40204B_DI_1 | Pin 9 | C2S1:9/TBDI1:9A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40204B |  | 325-01-402-PD-01
C2-S01-P09 | 1 | 9 | 10 | 1756-IB32 | XV-40204B_DI_2 | Pin 10 | C2S1:10/TBDI1:10A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40204B |  | 325-01-402-PD-01
C2-S01-P10 | 1 | 10 | 11 | 1756-IB32 | XV-40204C_DI_1 | Pin 11 | C2S1:11/TBDI1:11A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40204C |  | 325-01-402-PD-01
C2-S01-P11 | 1 | 11 | 12 | 1756-IB32 | XV-40204C_DI_2 | Pin 12 | C2S1:12/TBDI1:12A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40204C |  | 325-01-402-PD-01
C2-S01-P12 | 1 | 12 | 13 | 1756-IB32 | XV-40205A_DI_1 | Pin 13 | C2S1:13/TBDI1:13A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40205A |  | 325-01-402-PD-02
C2-S01-P13 | 1 | 13 | 14 | 1756-IB32 | XV-40205A_DI_2 | Pin 14 | C2S1:14/TBDI1:14A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40205A |  | 325-01-402-PD-02
C2-S01-P14 | 1 | 14 | 15 | 1756-IB32 | XV-40205B_DI_1 | Pin 15 | C2S1:15/TBDI1:15A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40205B |  | 325-01-402-PD-02
C2-S01-P15 | 1 | 15 | 16 | 1756-IB32 | XV-40205B_DI_2 | Pin 16 | C2S1:16/TBDI1:16A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X1 | - | XV-40205B |  | 325-01-402-PD-02
C2-S01-P16 | 1 | 16 | 17 | 1756-IB32 | XV-40205C_DI_1 | Pin 17 | C2S1:17/C2S01-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205C |  | 325-01-402-PD-02
C2-S01-P17 | 1 | 17 | 18 | 1756-IB32 | XV-40205C_DI_2 | Pin 18 | C2S1:18/C2S01-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205C |  | 325-01-402-PD-02
C2-S01-P18 | 1 | 18 | 19 | 1756-IB32 | XV-40205D_DI_1 | Pin 19 | C2S1:19/TBDI1:17A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205D |  | 325-01-402-PD-02
C2-S01-P19 | 1 | 19 | 20 | 1756-IB32 | XV-40205D_DI_2 | Pin 20 | C2S1:20/TBDI1:18A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205D |  | 325-01-402-PD-02
C2-S01-P20 | 1 | 20 | 21 | 1756-IB32 | XV-40205F_DI_1 | Pin 21 | C2S1:21/TBDI1:19A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205F |  | 325-01-402-PD-02
C2-S01-P21 | 1 | 21 | 22 | 1756-IB32 | XV-40205F_DI_2 | Pin 22 | C2S1:22/TBDI1:20A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40205F |  | 325-01-402-PD-02
C2-S01-P22 | 1 | 22 | 23 | 1756-IB32 | XV-40222_DI_1 | Pin 23 | C2S1:23/TBDI1:21A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40222 |  | 325-01-402-PD-02
C2-S01-P23 | 1 | 23 | 24 | 1756-IB32 | XV-40222_DI_2 | Pin 24 | C2S1:24/TBDI1:22A | DI | 24VDC Dry Contact | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | XV-40222 |  | -
C2-S01-P24 | 1 | 24 | 25 | 1756-IB32 | Spare_DI_2 | Pin 25 | C2S1:25/TBDI1:23A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P25 | 1 | 25 | 26 | 1756-IB32 | Spare_DI_2 | Pin 26 | C2S1:26/TBDI1:24A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P26 | 1 | 26 | 27 | 1756-IB32 | Spare_DI_2 | Pin 27 | C2S1:27/TBDI1:25A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P27 | 1 | 27 | 28 | 1756-IB32 | Spare_DI_2 | Pin 28 | C2S1:28/TBDI1:26A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P28 | 1 | 28 | 29 | 1756-IB32 | Spare_DI_2 | Pin 29 | C2S1:29/TBDI1:27A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P29 | 1 | 29 | 30 | 1756-IB32 | Spare_DI_2 | Pin 30 | C2S1:30/TBDI1:28A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P30 | 1 | 30 | 31 | 1756-IB32 | Spare_DI_2 | Pin 31 | C2S1:31/TBDI1:29A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -
C2-S01-P31 | 1 | 31 | 32 | 1756-IB32 | Spare_DI_2 | Pin 32 | C2S1:32/TBDI1:30A | DI | 24VDC Dry Contact | SPARE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S01-X2 | - | Spare | Spare Channel | -

## Slot_02
KALASIN ENGINEERING — C2 SLOT 02 (1756-IB32 • DI)
Chassis: C2 (I/O Expansion Rack 1 (Chassis 2)) ¦ Panel: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 32 (Active: 23, Spare: 9 / 28.1%) | [16 empty] | Destination: JB-602
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C2-S02-P00 | 2 | 0 | 1 | 1756-IB32 | FT-60202_DI_1 | Pin 1 | C2S2:1/TBDI2:1A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X1 | - | FT-60202 |  | 3-25-01-602-PD-09
C2-S02-P01 | 2 | 1 | 2 | 1756-IB32 | LSH-60251_DI_1 | Pin 2 | C2S2:2/TBDI2:2A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | LSH-60251 |  | 3-25-01-602-PD-04
C2-S02-P02 | 2 | 2 | 3 | 1756-IB32 | PSL-60220_DI_1 | Pin 3 | C2S2:3/TBDI2:3A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X1 | - | PSL-60220 |  | 3-25-01-602-PD-04
C2-S02-P03 | 2 | 3 | 4 | 1756-IB32 | TSH-60230_DI_1 | Pin 4 | C2S2:4/TBDI2:4A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | TSH-60230 |  | 3-25-01-602-PD-04
C2-S02-P04 | 2 | 4 | 5 | 1756-IB32 | TSH-60240_DI_1 | Pin 5 | C2S2:5/TBDI2:5A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X1 | - | TSH-60240 |  | 3-25-01-602-PD-05
C2-S02-P05 | 2 | 5 | 6 | 1756-IB32 | TSH-60241A_DI_1 | Pin 6 | C2S2:6/TBDI2:6A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSH-60241A |  | 3-25-01-602-PD-05
C2-S02-P06 | 2 | 6 | 7 | 1756-IB32 | TSH-60242A_DI_1 | Pin 7 | C2S2:7/TBDI2:7A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | TSH-60242A |  | 3-25-01-602-PD-05
C2-S02-P07 | 2 | 7 | 8 | 1756-IB32 | TSH-60243A_DI_1 | Pin 8 | C2S2:8/TBDI2:8A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSH-60243A |  | 3-25-01-602-PD-05
C2-S02-P08 | 2 | 8 | 9 | 1756-IB32 | TSL-60241B_DI_1 | Pin 9 | C2S2:9/TBDI2:9A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSL-60241B |  | 3-25-01-602-PD-05
C2-S02-P09 | 2 | 9 | 10 | 1756-IB32 | TSL-60242B_DI_1 | Pin 10 | C2S2:10/TBDI2:10A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | TSL-60242B |  | 3-25-01-602-PD-05
C2-S02-P10 | 2 | 10 | 11 | 1756-IB32 | TSL-60243B_DI_1 | Pin 11 | C2S2:11/TBDI2:11A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | TSL-60243B |  | 3-25-01-602-PD-05
C2-S02-P11 | 2 | 11 | 12 | 1756-IB32 | XA-60240A_DI_1 | Pin 12 | C2S2:12/TBDI2:12A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60240A |  | -
C2-S02-P12 | 2 | 12 | 13 | 1756-IB32 | XA-60240B_DI_1 | Pin 13 | C2S2:13/TBDI2:13A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60240B |  | -
C2-S02-P13 | 2 | 13 | 14 | 1756-IB32 | XA-60241A_DI_1 | Pin 14 | C2S2:14/TBDI2:14A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60241A |  | -
C2-S02-P14 | 2 | 14 | 15 | 1756-IB32 | XA-60241B_DI_1 | Pin 15 | C2S2:15/TBDI2:15A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X1 | - | XA-60241B |  | -
C2-S02-P15 | 2 | 15 | 16 | 1756-IB32 | XA-60242A_DI_1 | Pin 16 | C2S2:16/TBDI2:16A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X1 | - | XA-60242A |  | -
C2-S02-P16 | 2 | 16 | 17 | 1756-IB32 | XA-60242B_DI_1 | Pin 17 | C2S2:17/C2S02-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C2S02-X2 | - | XA-60242B |  | -
C2-S02-P17 | 2 | 17 | 18 | 1756-IB32 | XA-60243A_DI_1 | Pin 18 | C2S2:18/C2S02-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X2 | - | XA-60243A |  | -
C2-S02-P18 | 2 | 18 | 19 | 1756-IB32 | XA-60243B_DI_1 | Pin 19 | C2S2:19/TBDI2:17A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S02-X2 | - | XA-60243B |  | -
C2-S02-P19 | 2 | 19 | 20 | 1756-IB32 | XV-60214_DI_1 | Pin 20 | C2S2:20/TBDI2:18A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60214 |  | 3-25-01-602-PD-03
C2-S02-P20 | 2 | 20 | 21 | 1756-IB32 | XV-60214_DI_2 | Pin 21 | C2S2:21/TBDI2:19A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60214 |  | 3-25-01-602-PD-03
C2-S02-P21 | 2 | 21 | 22 | 1756-IB32 | XV-60241_DI_1 | Pin 22 | C2S2:22/TBDI2:20A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60241 |  | 3-25-01-602-PD-05
C2-S02-P22 | 2 | 22 | 23 | 1756-IB32 | XV-60241_DI_2 | Pin 23 | C2S2:23/TBDI2:21A | DI | 24VDC Dry Contact | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S02-X2 | - | XV-60241 |  | 3-25-01-602-PD-05
C2-S02-P23 | 2 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C2S2:24/TBDI2:22A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P24 | 2 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C2S2:25/TBDI2:23A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P25 | 2 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C2S2:26/TBDI2:24A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P26 | 2 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C2S2:27/TBDI2:25A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P27 | 2 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C2S2:28/TBDI2:26A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P28 | 2 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C2S2:29/TBDI2:27A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P29 | 2 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C2S2:30/TBDI2:28A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P30 | 2 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C2S2:31/TBDI2:29A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -
C2-S02-P31 | 2 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C2S2:32/TBDI2:30A | DI | 24VDC Dry Contact | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S02-X2 | - | Spare | Spare Channel | -

## Slot_03
KALASIN ENGINEERING — C2 SLOT 03 (1756-IB32 • DI)
Chassis: C2 (I/O Expansion Rack 1 (Chassis 2)) ¦ Panel: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 29 (Active: 29, Spare: 0 / 0.0%) | [16 empty] | Destination: JB-607
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C2-S03-P00 | 3 | 0 | 1 | 1756-IB32 | XA-FH-60210A_DI_1 | Pin 1 | C2S3:1/TBDI3:1A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210A |  | -
C2-S03-P01 | 3 | 1 | 2 | 1756-IB32 | XA-FH-60210B_DI_1 | Pin 2 | C2S3:2/TBDI3:2A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210B |  | -
C2-S03-P02 | 3 | 2 | 3 | 1756-IB32 | XA-FH-60210C_DI_1 | Pin 3 | C2S3:3/TBDI3:3A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210C |  | -
C2-S03-P03 | 3 | 3 | 4 | 1756-IB32 | XA-FH-60210D_DI_1 | Pin 4 | C2S3:4/TBDI3:4A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210D |  | -
C2-S03-P04 | 3 | 4 | 5 | 1756-IB32 | XA-FH-60210E_DI_1 | Pin 5 | C2S3:5/TBDI3:5A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XA-FH-60210E |  | -
C2-S03-P08 | 3 | 8 | 9 | 1756-IB32 | SV-60207_DI_1 | Pin 9 | C2S3:9/TBDI3:9A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | SV-60207 |  | 3-25-01-602-PD-07
C2-S03-P09 | 3 | 9 | 10 | 1756-IB32 | SV-60207_DI_2 | Pin 10 | C2S3:10/TBDI3:10A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | SV-60207 |  | 3-25-01-602-PD-07
C2-S03-P10 | 3 | 10 | 11 | 1756-IB32 | XV-60264_DI_1 | Pin 11 | C2S3:11/TBDI3:11A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264 |  | -
C2-S03-P11 | 3 | 11 | 12 | 1756-IB32 | XV-60264_DI_2 | Pin 12 | C2S3:12/TBDI3:12A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264 |  | -
C2-S03-P12 | 3 | 12 | 13 | 1756-IB32 | XV-60264FN_DI_1 | Pin 13 | C2S3:13/TBDI3:13A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264FN |  | 3-25-01-602-PD-02
C2-S03-P13 | 3 | 13 | 14 | 1756-IB32 | XV-60264FN_DI_2 | Pin 14 | C2S3:14/TBDI3:14A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264FN |  | 3-25-01-602-PD-02
C2-S03-P14 | 3 | 14 | 15 | 1756-IB32 | XV-60264FP_DI_1 | Pin 15 | C2S3:15/TBDI3:15A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264FP |  | 3-25-01-602-PD-02
C2-S03-P15 | 3 | 15 | 16 | 1756-IB32 | XV-60264FP_DI_2 | Pin 16 | C2S3:16/TBDI3:16A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X1 | - | XV-60264FP |  | 3-25-01-602-PD-02
C2-S03-P16 | 3 | 16 | 17 | 1756-IB32 | XV-60201_DI_1 | Pin 17 | C2S3:17/C2S03-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60201 |  | 3-25-01-602-PD-02
C2-S03-P17 | 3 | 17 | 18 | 1756-IB32 | XV-60201_DI_2 | Pin 18 | C2S3:18/C2S03-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60201 |  | 3-25-01-602-PD-02
C2-S03-P18 | 3 | 18 | 19 | 1756-IB32 | XV-60264FQ_DI_1 | Pin 19 | C2S3:19/TBDI3:17A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264FQ |  | 3-25-01-602-PD-02
C2-S03-P19 | 3 | 19 | 20 | 1756-IB32 | XV-60264FQ_DI_2 | Pin 20 | C2S3:20/TBDI3:18A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264FQ |  | 3-25-01-602-PD-02
C2-S03-P20 | 3 | 20 | 21 | 1756-IB32 | XV-60261_DI_1 | Pin 21 | C2S3:21/TBDI3:19A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261 |  | -
C2-S03-P21 | 3 | 21 | 22 | 1756-IB32 | XV-60261_DI_2 | Pin 22 | C2S3:22/TBDI3:20A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261 |  | -
C2-S03-P22 | 3 | 22 | 23 | 1756-IB32 | XV-60264FR_DI_1 | Pin 23 | C2S3:23/TBDI3:21A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264FR |  | 3-25-01-602-PD-02
C2-S03-P23 | 3 | 23 | 24 | 1756-IB32 | XV-60264FR_DI_2 | Pin 24 | C2S3:24/TBDI3:22A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264FR |  | 3-25-01-602-PD-02
C2-S03-P24 | 3 | 24 | 25 | 1756-IB32 | XV-60261FA_DI_1 | Pin 25 | C2S3:25/TBDI3:23A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261FA |  | 3-25-01-602-PD-02
C2-S03-P25 | 3 | 25 | 26 | 1756-IB32 | XV-60261FA_DI_2 | Pin 26 | C2S3:26/TBDI3:24A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261FA |  | 3-25-01-602-PD-02
C2-S03-P26 | 3 | 26 | 27 | 1756-IB32 | XV-60264SN_DI_1 | Pin 27 | C2S3:27/TBDI3:25A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264SN |  | 3-25-01-602-PD-02
C2-S03-P27 | 3 | 27 | 28 | 1756-IB32 | XV-60264SN_DI_2 | Pin 28 | C2S3:28/TBDI3:26A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264SN |  | 3-25-01-602-PD-02
C2-S03-P28 | 3 | 28 | 29 | 1756-IB32 | XV-60261FB_DI_1 | Pin 29 | C2S3:29/TBDI3:27A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261FB |  | 3-25-01-602-PD-02
C2-S03-P29 | 3 | 29 | 30 | 1756-IB32 | XV-60261FB_DI_2 | Pin 30 | C2S3:30/TBDI3:28A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60261FB |  | 3-25-01-602-PD-02
C2-S03-P30 | 3 | 30 | 31 | 1756-IB32 | XV-60264SP_DI_1 | Pin 31 | C2S3:31/TBDI3:29A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264SP |  | 3-25-01-602-PD-02
C2-S03-P31 | 3 | 31 | 32 | 1756-IB32 | XV-60264SP_DI_2 | Pin 32 | C2S3:32/TBDI3:30A | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S03-X2 | - | XV-60264SP |  | 3-25-01-602-PD-02

## Slot_04
KALASIN ENGINEERING — C2 SLOT 04 (1756-IB32 • DI)
Chassis: C2 (I/O Expansion Rack 1 (Chassis 2)) ¦ Panel: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 32 (Active: 32, Spare: 0 / 0.0%) | [16 empty] | Destination: JB-607
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C2-S04-P00 | 4 | 0 | 1 | 1756-IB32 | XV-60261FC_DI_1 | Pin 1 | C2S4:1/RL.1:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261FC |  | 3-25-01-602-PD-02
C2-S04-P01 | 4 | 1 | 2 | 1756-IB32 | XV-60261FC_DI_2 | Pin 2 | C2S4:2/RL.2:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261FC |  | 3-25-01-602-PD-02
C2-S04-P02 | 4 | 2 | 3 | 1756-IB32 | XV-60264SQ_DI_1 | Pin 3 | C2S4:3/RL.3:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60264SQ |  | 3-25-01-602-PD-02
C2-S04-P03 | 4 | 3 | 4 | 1756-IB32 | XV-60264SQ_DI_2 | Pin 4 | C2S4:4/RL.4:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60264SQ |  | 3-25-01-602-PD-02
C2-S04-P04 | 4 | 4 | 5 | 1756-IB32 | XV-60261FD_DI_1 | Pin 5 | C2S4:5/RL.5:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261FD |  | 3-25-01-602-PD-02
C2-S04-P05 | 4 | 5 | 6 | 1756-IB32 | XV-60261FD_DI_2 | Pin 6 | C2S4:6/RL.6:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261FD |  | 3-25-01-602-PD-02
C2-S04-P06 | 4 | 6 | 7 | 1756-IB32 | XV-60264SR_DI_1 | Pin 7 | C2S4:7/RL.7:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60264SR |  | 3-25-01-602-PD-02
C2-S04-P07 | 4 | 7 | 8 | 1756-IB32 | XV-60264SR_DI_2 | Pin 8 | C2S4:8/RL.8:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60264SR |  | 3-25-01-602-PD-02
C2-S04-P08 | 4 | 8 | 9 | 1756-IB32 | XV-60261SA_DI_1 | Pin 9 | C2S4:9/RL.9:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SA |  | 3-25-01-602-PD-02
C2-S04-P09 | 4 | 9 | 10 | 1756-IB32 | XV-60261SA_DI_2 | Pin 10 | C2S4:10/RL.10:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SA |  | 3-25-01-602-PD-02
C2-S04-P10 | 4 | 10 | 11 | 1756-IB32 | XV-60261SB_DI_1 | Pin 11 | C2S4:11/RL.11:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SB |  | 3-25-01-602-PD-02
C2-S04-P11 | 4 | 11 | 12 | 1756-IB32 | XV-60261SB_DI_2 | Pin 12 | C2S4:12/RL.12:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SB |  | 3-25-01-602-PD-02
C2-S04-P12 | 4 | 12 | 13 | 1756-IB32 | XV-60261SC_DI_1 | Pin 13 | C2S4:13/RL.13:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SC |  | 3-25-01-602-PD-02
C2-S04-P13 | 4 | 13 | 14 | 1756-IB32 | XV-60261SC_DI_2 | Pin 14 | C2S4:14/RL.14:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SC |  | 3-25-01-602-PD-02
C2-S04-P14 | 4 | 14 | 15 | 1756-IB32 | XV-60261SD_DI_1 | Pin 15 | C2S4:15/RL.15:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SD |  | 3-25-01-602-PD-02
C2-S04-P15 | 4 | 15 | 16 | 1756-IB32 | XV-60261SD_DI_2 | Pin 16 | C2S4:16/RL.16:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X1 | - | XV-60261SD |  | 3-25-01-602-PD-02
C2-S04-P16 | 4 | 16 | 17 | 1756-IB32 | XV-60262_DI_1 | Pin 17 | C2S4:17/C2S04-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262 |  | -
C2-S04-P17 | 4 | 17 | 18 | 1756-IB32 | XV-60262_DI_2 | Pin 18 | C2S4:18/C2S04-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262 |  | -
C2-S04-P18 | 4 | 18 | 19 | 1756-IB32 | XV-60262FE_DI_1 | Pin 19 | C2S4:19/RL.17:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FE |  | 3-25-01-602-PD-02
C2-S04-P19 | 4 | 19 | 20 | 1756-IB32 | XV-60262FE_DI_2 | Pin 20 | C2S4:20/RL.18:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FE |  | 3-25-01-602-PD-02
C2-S04-P20 | 4 | 20 | 21 | 1756-IB32 | XV-60262FF_DI_1 | Pin 21 | C2S4:21/RL.19:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FF |  | 3-25-01-602-PD-02
C2-S04-P21 | 4 | 21 | 22 | 1756-IB32 | XV-60262FF_DI_2 | Pin 22 | C2S4:22/RL.20:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FF |  | 3-25-01-602-PD-02
C2-S04-P22 | 4 | 22 | 23 | 1756-IB32 | XV-60262FG_DI_1 | Pin 23 | C2S4:23/RL.21:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FG |  | 3-25-01-602-PD-02
C2-S04-P23 | 4 | 23 | 24 | 1756-IB32 | XV-60262FG_DI_2 | Pin 24 | C2S4:24/RL.22:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FG |  | 3-25-01-602-PD-02
C2-S04-P24 | 4 | 24 | 25 | 1756-IB32 | XV-60262FH_DI_1 | Pin 25 | C2S4:25/RL.23:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FH |  | 3-25-01-602-PD-02
C2-S04-P25 | 4 | 25 | 26 | 1756-IB32 | XV-60262FH_DI_2 | Pin 26 | C2S4:26/RL.24:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262FH |  | 3-25-01-602-PD-02
C2-S04-P26 | 4 | 26 | 27 | 1756-IB32 | XV-60262SE_DI_1 | Pin 27 | C2S4:27/RL.25:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SE |  | 3-25-01-602-PD-02
C2-S04-P27 | 4 | 27 | 28 | 1756-IB32 | XV-60262SE_DI_2 | Pin 28 | C2S4:28/RL.26:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SE |  | 3-25-01-602-PD-02
C2-S04-P28 | 4 | 28 | 29 | 1756-IB32 | XV-60262SF_DI_1 | Pin 29 | C2S4:29/RL.27:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SF |  | 3-25-01-602-PD-02
C2-S04-P29 | 4 | 29 | 30 | 1756-IB32 | XV-60262SF_DI_2 | Pin 30 | C2S4:30/RL.28:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SF |  | 3-25-01-602-PD-02
C2-S04-P30 | 4 | 30 | 31 | 1756-IB32 | XV-60262SG_DI_1 | Pin 31 | C2S4:31/RL.29:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SG |  | 3-25-01-602-PD-02
C2-S04-P31 | 4 | 31 | 32 | 1756-IB32 | XV-60262SG_DI_2 | Pin 32 | C2S4:32/RL.30:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S04-X2 | - | XV-60262SG |  | 3-25-01-602-PD-02

## Slot_05
KALASIN ENGINEERING — C2 SLOT 05 (1756-IB32 • DI)
Chassis: C2 (I/O Expansion Rack 1 (Chassis 2)) ¦ Panel: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 32 (Active: 20, Spare: 12 / 37.5%) | [16 empty] | Destination: JB-607
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C2-S05-P00 | 5 | 0 | 1 | 1756-IB32 | XV-60262SH_DI_1 | Pin 1 | C2S5:1/RL.33:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60262SH |  | 3-25-01-602-PD-02
C2-S05-P01 | 5 | 1 | 2 | 1756-IB32 | XV-60262SH_DI_2 | Pin 2 | C2S5:2/RL.34:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60262SH |  | 3-25-01-602-PD-02
C2-S05-P02 | 5 | 2 | 3 | 1756-IB32 | XV-60263_DI_1 | Pin 3 | C2S5:3/RL.35:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263 |  | -
C2-S05-P03 | 5 | 3 | 4 | 1756-IB32 | XV-60263_DI_2 | Pin 4 | C2S5:4/RL.36:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263 |  | -
C2-S05-P04 | 5 | 4 | 5 | 1756-IB32 | XV-60263FJ_DI_1 | Pin 5 | C2S5:5/RL.37:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FJ |  | 3-25-01-602-PD-02
C2-S05-P05 | 5 | 5 | 6 | 1756-IB32 | XV-60263FJ_DI_2 | Pin 6 | C2S5:6/RL.38:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FJ |  | 3-25-01-602-PD-02
C2-S05-P06 | 5 | 6 | 7 | 1756-IB32 | XV-60263FK_DI_1 | Pin 7 | C2S5:7/RL.39:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FK |  | 3-25-01-602-PD-02
C2-S05-P07 | 5 | 7 | 8 | 1756-IB32 | XV-60263FK_DI_2 | Pin 8 | C2S5:8/RL.40:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FK |  | 3-25-01-602-PD-02
C2-S05-P08 | 5 | 8 | 9 | 1756-IB32 | XV-60263FL_DI_1 | Pin 9 | C2S5:9/RL.41:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FL |  | 3-25-01-602-PD-02
C2-S05-P09 | 5 | 9 | 10 | 1756-IB32 | XV-60263FL_DI_2 | Pin 10 | C2S5:10/RL.42:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FL |  | 3-25-01-602-PD-02
C2-S05-P10 | 5 | 10 | 11 | 1756-IB32 | XV-60263FM_DI_1 | Pin 11 | C2S5:11/RL.43:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FM |  | 3-25-01-602-PD-02
C2-S05-P11 | 5 | 11 | 12 | 1756-IB32 | XV-60263FM_DI_2 | Pin 12 | C2S5:12/RL.44:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263FM |  | 3-25-01-602-PD-02
C2-S05-P12 | 5 | 12 | 13 | 1756-IB32 | XV-60263SJ_DI_1 | Pin 13 | C2S5:13/RL.45:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263SJ |  | 3-25-01-602-PD-02
C2-S05-P13 | 5 | 13 | 14 | 1756-IB32 | XV-60263SJ_DI_2 | Pin 14 | C2S5:14/RL.46:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263SJ |  | 3-25-01-602-PD-02
C2-S05-P14 | 5 | 14 | 15 | 1756-IB32 | XV-60263SK_DI_1 | Pin 15 | C2S5:15/RL.47:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263SK |  | 3-25-01-602-PD-02
C2-S05-P15 | 5 | 15 | 16 | 1756-IB32 | XV-60263SK_DI_2 | Pin 16 | C2S5:16/RL.48:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X1 | - | XV-60263SK |  | 3-25-01-602-PD-02
C2-S05-P16 | 5 | 16 | 17 | 1756-IB32 | XV-60263SL_DI_1 | Pin 17 | C2S5:17/C2S05-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X2 | - | XV-60263SL |  | 3-25-01-602-PD-02
C2-S05-P17 | 5 | 17 | 18 | 1756-IB32 | XV-60263SL_DI_2 | Pin 18 | C2S5:18/C2S05-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X2 | - | XV-60263SL |  | 3-25-01-602-PD-02
C2-S05-P18 | 5 | 18 | 19 | 1756-IB32 | XV-60263SM_DI_1 | Pin 19 | C2S5:19/RL.49:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X2 | - | XV-60263SM |  | 3-25-01-602-PD-02
C2-S05-P19 | 5 | 19 | 20 | 1756-IB32 | XV-60263SM_DI_2 | Pin 20 | C2S5:20/RL.50:A1 | DI | 24VDC Dry Contact | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S05-X2 | - | XV-60263SM |  | 3-25-01-602-PD-02
C2-S05-P20 | 5 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C2S5:21/RL.51:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P21 | 5 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C2S5:22/RL.52:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P22 | 5 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C2S5:23/RL.53:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P23 | 5 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C2S5:24/RL.54:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P24 | 5 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C2S5:25/RL.55:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P25 | 5 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C2S5:26/RL.56:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P26 | 5 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C2S5:27/RL.57:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P27 | 5 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C2S5:28/RL.58:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P28 | 5 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C2S5:29/RL.59:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P29 | 5 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C2S5:30/RL.60:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P30 | 5 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C2S5:31/RL.61:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -
C2-S05-P31 | 5 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C2S5:32/RL.62:A1 | DI | 24VDC Dry Contact | SPARE | JB-607 | Spray Dryer 7th Floor | - / Spray Dryer | C2S05-X2 | - | Spare | Spare Channel | -

## Slot_06
KALASIN ENGINEERING — C2 SLOT 06 (1756-OB32 • DO)
Chassis: C2 (I/O Expansion Rack 1 (Chassis 2)) ¦ Panel: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 32 (Active: 12, Spare: 20 / 62.5%) | [16 empty] | Destination: JB-402, JB-602
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C2-S06-P00 | 6 | 0 | 1 | 1756-OB32 | XV-40203F_DO_1 | Pin 1 | C2S6:1/RL.33:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40203F |  | 325-01-402-PD-02
C2-S06-P01 | 6 | 1 | 2 | 1756-OB32 | XV-40204B_DO_1 | Pin 2 | C2S6:2/RL.34:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40204B |  | 325-01-402-PD-01
C2-S06-P02 | 6 | 2 | 3 | 1756-OB32 | XV-40204C_DO_1 | Pin 3 | C2S6:3/RL.35:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40204C |  | 325-01-402-PD-01
C2-S06-P03 | 6 | 3 | 4 | 1756-OB32 | XV-40205A_DO_1 | Pin 4 | C2S6:4/RL.36:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205A |  | 325-01-402-PD-02
C2-S06-P04 | 6 | 4 | 5 | 1756-OB32 | XV-40205B_DO_1 | Pin 5 | C2S6:5/RL.37:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205B |  | 325-01-402-PD-02
C2-S06-P05 | 6 | 5 | 6 | 1756-OB32 | XV-40205C_DO_1 | Pin 6 | C2S6:6/RL.38:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205C |  | 325-01-402-PD-02
C2-S06-P06 | 6 | 6 | 7 | 1756-OB32 | XV-40205D_DO_1 | Pin 7 | C2S6:7/RL.39:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205D |  | 325-01-402-PD-02
C2-S06-P07 | 6 | 7 | 8 | 1756-OB32 | XV-40205F_DO_1 | Pin 8 | C2S6:8/RL.40:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40205F |  | 325-01-402-PD-02
C2-S06-P08 | 6 | 8 | 9 | 1756-OB32 | XV-40222_DO_1 | Pin 9 | C2S6:9/RL.41:A1 | DO | 24VDC Sourcing | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S06-X1 | - | XV-40222 |  | 325-01-402-PD-02
C2-S06-P09 | 6 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C2S6:10/RL.42:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P10 | 6 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C2S6:11/RL.43:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P11 | 6 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C2S6:12/RL.44:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P12 | 6 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C2S6:13/RL.45:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P13 | 6 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C2S6:14/RL.46:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P14 | 6 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C2S6:15/RL.47:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P15 | 6 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C2S6:16/RL.48:A1 | DO | 24VDC Sourcing | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S06-X1 | - | Spare | Spare Channel | -
C2-S06-P16 | 6 | 16 | 17 | 1756-OB32 | XS-60240B_DO_1 | Pin 17 | C2S6:17/C2S06-X2:17 | DO | 24VDC Sourcing | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C2S06-X2 | - | XS-60240B |  | -
C2-S06-P17 | 6 | 17 | 18 | 1756-OB32 | XV-60214_DO_1 | Pin 18 | C2S6:18/C2S06-X2:18 | DO | 24VDC Sourcing | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S06-X2 | - | XV-60214 |  | 3-25-01-602-PD-03
C2-S06-P18 | 6 | 18 | 19 | 1756-OB32 | XV-60241_DO_1 | Pin 19 | C2S6:19/RL.49:A1 | DO | 24VDC Sourcing | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S06-X2 | - | XV-60241 |  | 3-25-01-602-PD-05
C2-S06-P19 | 6 | 19 | 20 | 1756-OB32 | Spare_DO_0 | Pin 20 | C2S6:20/RL.50:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P20 | 6 | 20 | 21 | 1756-OB32 | Spare_DO_0 | Pin 21 | C2S6:21/RL.51:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P21 | 6 | 21 | 22 | 1756-OB32 | Spare_DO_0 | Pin 22 | C2S6:22/RL.52:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P22 | 6 | 22 | 23 | 1756-OB32 | Spare_DO_0 | Pin 23 | C2S6:23/RL.53:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P23 | 6 | 23 | 24 | 1756-OB32 | Spare_DO_0 | Pin 24 | C2S6:24/RL.54:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P24 | 6 | 24 | 25 | 1756-OB32 | Spare_DO_0 | Pin 25 | C2S6:25/RL.55:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P25 | 6 | 25 | 26 | 1756-OB32 | Spare_DO_0 | Pin 26 | C2S6:26/RL.56:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P26 | 6 | 26 | 27 | 1756-OB32 | Spare_DO_0 | Pin 27 | C2S6:27/RL.57:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P27 | 6 | 27 | 28 | 1756-OB32 | Spare_DO_0 | Pin 28 | C2S6:28/RL.58:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P28 | 6 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C2S6:29/RL.59:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P29 | 6 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C2S6:30/RL.60:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P30 | 6 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C2S6:31/RL.61:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -
C2-S06-P31 | 6 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C2S6:32/RL.62:A1 | DO | 24VDC Sourcing | SPARE | JB-602 | Spray Dryer 3rd Floor | Spray Dryer | C2S06-X2 | - | Spare | Spare Channel | -

## Slot_07
KALASIN ENGINEERING — C2 SLOT 07 (1756-OB32 • DO)
Chassis: C2 (I/O Expansion Rack 1 (Chassis 2)) ¦ Panel: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 32 (Active: 31, Spare: 1 / 3.1%) | [16 empty] | Destination: JB-607
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C2-S07-P00 | 7 | 0 | 1 | 1756-OB32 | SV-60207_DO_1 | Pin 1 | C2S7:1/C2S07-X1:1 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | SV-60207 |  | 3-25-01-602-PD-07
C2-S07-P01 | 7 | 1 | 2 | 1756-OB32 | XS-FH-60210C_DO_1 | Pin 2 | C2S7:2/C2S07-X1:2 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XS-FH-60210C |  | -
C2-S07-P02 | 7 | 2 | 3 | 1756-OB32 | XS-FH-60210D_DO_1 | Pin 3 | C2S7:3/C2S07-X1:3 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XS-FH-60210D |  | -
C2-S07-P03 | 7 | 3 | 4 | 1756-OB32 | XV-60201_DO_1 | Pin 4 | C2S7:4/C2S07-X1:4 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60201 |  | 3-25-01-602-PD-02
C2-S07-P04 | 7 | 4 | 5 | 1756-OB32 | XV-60261_DO_1 | Pin 5 | C2S7:5/C2S07-X1:5 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261 |  | -
C2-S07-P05 | 7 | 5 | 6 | 1756-OB32 | XV-60261FA_DO_1 | Pin 6 | C2S7:6/C2S07-X1:6 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261FA |  | 3-25-01-602-PD-02
C2-S07-P06 | 7 | 6 | 7 | 1756-OB32 | XV-60261FB_DO_1 | Pin 7 | C2S7:7/C2S07-X1:7 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261FB |  | 3-25-01-602-PD-02
C2-S07-P07 | 7 | 7 | 8 | 1756-OB32 | XV-60261FC_DO_1 | Pin 8 | C2S7:8/C2S07-X1:8 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261FC |  | 3-25-01-602-PD-02
C2-S07-P08 | 7 | 8 | 9 | 1756-OB32 | XV-60261FD_DO_1 | Pin 9 | C2S7:9/C2S07-X1:9 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261FD |  | 3-25-01-602-PD-02
C2-S07-P09 | 7 | 9 | 10 | 1756-OB32 | XV-60261SA_DO_1 | Pin 10 | C2S7:10/C2S07-X1:10 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261SA |  | 3-25-01-602-PD-02
C2-S07-P10 | 7 | 10 | 11 | 1756-OB32 | XV-60261SB_DO_1 | Pin 11 | C2S7:11/C2S07-X1:11 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261SB |  | 3-25-01-602-PD-02
C2-S07-P11 | 7 | 11 | 12 | 1756-OB32 | XV-60261SC_DO_1 | Pin 12 | C2S7:12/C2S07-X1:12 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261SC |  | 3-25-01-602-PD-02
C2-S07-P12 | 7 | 12 | 13 | 1756-OB32 | XV-60261SD_DO_1 | Pin 13 | C2S7:13/C2S07-X1:13 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60261SD |  | 3-25-01-602-PD-02
C2-S07-P13 | 7 | 13 | 14 | 1756-OB32 | XV-60262_DO_1 | Pin 14 | C2S7:14/C2S07-X1:14 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60262 |  | -
C2-S07-P14 | 7 | 14 | 15 | 1756-OB32 | XV-60262FE_DO_1 | Pin 15 | C2S7:15/C2S07-X1:15 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60262FE |  | 3-25-01-602-PD-02
C2-S07-P15 | 7 | 15 | 16 | 1756-OB32 | XV-60262FF_DO_1 | Pin 16 | C2S7:16/C2S07-X1:16 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X1 | - | XV-60262FF |  | 3-25-01-602-PD-02
C2-S07-P16 | 7 | 16 | 17 | 1756-OB32 | XV-60262FG_DO_1 | Pin 17 | C2S7:17/C2S07-X2:17 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262FG |  | 3-25-01-602-PD-02
C2-S07-P17 | 7 | 17 | 18 | 1756-OB32 | XV-60262FH_DO_1 | Pin 18 | C2S7:18/C2S07-X2:18 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262FH |  | 3-25-01-602-PD-02
C2-S07-P18 | 7 | 18 | 19 | 1756-OB32 | XV-60262SE_DO_1 | Pin 19 | C2S7:19/C2S07-X2:19 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262SE |  | 3-25-01-602-PD-02
C2-S07-P19 | 7 | 19 | 20 | 1756-OB32 | XV-60262SF_DO_1 | Pin 20 | C2S7:20/C2S07-X2:20 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262SF |  | 3-25-01-602-PD-02
C2-S07-P20 | 7 | 20 | 21 | 1756-OB32 | XV-60262SG_DO_1 | Pin 21 | C2S7:21/C2S07-X2:21 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262SG |  | 3-25-01-602-PD-02
C2-S07-P21 | 7 | 21 | 22 | 1756-OB32 | XV-60262SH_DO_1 | Pin 22 | C2S7:22/C2S07-X2:22 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60262SH |  | 3-25-01-602-PD-02
C2-S07-P22 | 7 | 22 | 23 | 1756-OB32 | XV-60263_DO_1 | Pin 23 | C2S7:23/C2S07-X2:23 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263 |  | -
C2-S07-P23 | 7 | 23 | 24 | 1756-OB32 | XV-60263FJ_DO_1 | Pin 24 | C2S7:24/C2S07-X2:24 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263FJ |  | 3-25-01-602-PD-02
C2-S07-P24 | 7 | 24 | 25 | 1756-OB32 | XV-60263FK_DO_1 | Pin 25 | C2S7:25/C2S07-X2:25 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263FK |  | 3-25-01-602-PD-02
C2-S07-P25 | 7 | 25 | 26 | 1756-OB32 | XV-60263FL_DO_1 | Pin 26 | C2S7:26/C2S07-X2:26 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263FL |  | 3-25-01-602-PD-02
C2-S07-P26 | 7 | 26 | 27 | 1756-OB32 | XV-60263FM_DO_1 | Pin 27 | C2S7:27/C2S07-X2:27 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263FM |  | 3-25-01-602-PD-02
C2-S07-P27 | 7 | 27 | 28 | 1756-OB32 | XV-60263SJ_DO_1 | Pin 28 | C2S7:28/C2S07-X2:28 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263SJ |  | 3-25-01-602-PD-02
C2-S07-P28 | 7 | 28 | 29 | 1756-OB32 | XV-60263SK_DO_1 | Pin 29 | C2S7:29/C2S07-X2:29 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263SK |  | 3-25-01-602-PD-02
C2-S07-P29 | 7 | 29 | 30 | 1756-OB32 | XV-60263SL_DO_1 | Pin 30 | C2S7:30/C2S07-X2:30 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263SL |  | 3-25-01-602-PD-02
C2-S07-P30 | 7 | 30 | 31 | 1756-OB32 | XV-60263SM_DO_1 | Pin 31 | C2S7:31/C2S07-X2:31 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S07-X2 | - | XV-60263SM |  | 3-25-01-602-PD-02
C2-S07-P31 | 7 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C2S7:32/C2S07-X2:32 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S07-X2 | - | Spare | Spare Channel | -

## Slot_08
KALASIN ENGINEERING — C2 SLOT 08 (1756-OB32 • DO)
Chassis: C2 (I/O Expansion Rack 1 (Chassis 2)) ¦ Panel: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 32 (Active: 9, Spare: 23 / 71.9%) | [16 empty] | Destination: JB-607
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C2-S08-P00 | 8 | 0 | 1 | 1756-OB32 | XV-60264_DO_1 | Pin 1 | C2S8:1/C2S08-X1:1 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264 |  | -
C2-S08-P01 | 8 | 1 | 2 | 1756-OB32 | XV-60264FN_DO_1 | Pin 2 | C2S8:2/C2S08-X1:2 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264FN |  | 3-25-01-602-PD-02
C2-S08-P02 | 8 | 2 | 3 | 1756-OB32 | XV-60264FP_DO_1 | Pin 3 | C2S8:3/C2S08-X1:3 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264FP |  | 3-25-01-602-PD-02
C2-S08-P03 | 8 | 3 | 4 | 1756-OB32 | XV-60264FQ_DO_1 | Pin 4 | C2S8:4/C2S08-X1:4 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264FQ |  | 3-25-01-602-PD-02
C2-S08-P04 | 8 | 4 | 5 | 1756-OB32 | XV-60264FR_DO_1 | Pin 5 | C2S8:5/C2S08-X1:5 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264FR |  | 3-25-01-602-PD-02
C2-S08-P05 | 8 | 5 | 6 | 1756-OB32 | XV-60264SN_DO_1 | Pin 6 | C2S8:6/C2S08-X1:6 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264SN |  | 3-25-01-602-PD-02
C2-S08-P06 | 8 | 6 | 7 | 1756-OB32 | XV-60264SP_DO_1 | Pin 7 | C2S8:7/C2S08-X1:7 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264SP |  | 3-25-01-602-PD-02
C2-S08-P07 | 8 | 7 | 8 | 1756-OB32 | XV-60264SQ_DO_1 | Pin 8 | C2S8:8/C2S08-X1:8 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264SQ |  | 3-25-01-602-PD-02
C2-S08-P08 | 8 | 8 | 9 | 1756-OB32 | XV-60264SR_DO_1 | Pin 9 | C2S8:9/C2S08-X1:9 | DO | 24VDC Sourcing | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S08-X1 | - | XV-60264SR |  | 3-25-01-602-PD-02
C2-S08-P09 | 8 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C2S8:10/C2S08-X1:10 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P10 | 8 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C2S8:11/C2S08-X1:11 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P11 | 8 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C2S8:12/C2S08-X1:12 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P12 | 8 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C2S8:13/C2S08-X1:13 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P13 | 8 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C2S8:14/C2S08-X1:14 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P14 | 8 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C2S8:15/C2S08-X1:15 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P15 | 8 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C2S8:16/C2S08-X1:16 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X1 | - | Spare | Spare Channel | -
C2-S08-P16 | 8 | 16 | 17 | 1756-OB32 | Spare_DO_0 | Pin 17 | C2S8:17/C2S08-X2:17 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P17 | 8 | 17 | 18 | 1756-OB32 | Spare_DO_0 | Pin 18 | C2S8:18/C2S08-X2:18 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P18 | 8 | 18 | 19 | 1756-OB32 | Spare_DO_0 | Pin 19 | C2S8:19/C2S08-X2:19 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P19 | 8 | 19 | 20 | 1756-OB32 | Spare_DO_0 | Pin 20 | C2S8:20/C2S08-X2:20 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P20 | 8 | 20 | 21 | 1756-OB32 | Spare_DO_0 | Pin 21 | C2S8:21/C2S08-X2:21 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P21 | 8 | 21 | 22 | 1756-OB32 | Spare_DO_0 | Pin 22 | C2S8:22/C2S08-X2:22 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P22 | 8 | 22 | 23 | 1756-OB32 | Spare_DO_0 | Pin 23 | C2S8:23/C2S08-X2:23 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P23 | 8 | 23 | 24 | 1756-OB32 | Spare_DO_0 | Pin 24 | C2S8:24/C2S08-X2:24 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P24 | 8 | 24 | 25 | 1756-OB32 | Spare_DO_0 | Pin 25 | C2S8:25/C2S08-X2:25 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P25 | 8 | 25 | 26 | 1756-OB32 | Spare_DO_0 | Pin 26 | C2S8:26/C2S08-X2:26 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P26 | 8 | 26 | 27 | 1756-OB32 | Spare_DO_0 | Pin 27 | C2S8:27/C2S08-X2:27 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P27 | 8 | 27 | 28 | 1756-OB32 | Spare_DO_0 | Pin 28 | C2S8:28/C2S08-X2:28 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P28 | 8 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C2S8:29/C2S08-X2:29 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P29 | 8 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C2S8:30/C2S08-X2:30 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P30 | 8 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C2S8:31/C2S08-X2:31 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -
C2-S08-P31 | 8 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C2S8:32/C2S08-X2:32 | DO | 24VDC Sourcing | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S08-X2 | - | Spare | Spare Channel | -

## Slot_09
KALASIN ENGINEERING — C2 SLOT 09 (1756-IF16 • AI)
Chassis: C2 (I/O Expansion Rack 1 (Chassis 2)) ¦ Panel: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 16 (Active: 7, Spare: 9 / 56.2%) | [16 empty] | Destination: JB-402
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C2-S09-P00 | 9 | 0 | 1 | 1756-IF16 | FT-40221_AI_1 | Pin 1 | C2S9:1/C2S09-X1:1 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | FT-40221 | Coriolis Flow Transmitter | 325-01-402-PD-02
C2-S09-P01 | 9 | 1 | 2 | 1756-IF16 | FT-40221_AI_2 | Pin 2 | C2S9:2/C2S09-X1:2 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | FT-40221 | Coriolis Flow Transmitter | 325-01-402-PD-02
C2-S09-P02 | 9 | 2 | 3 | 1756-IF16 | FT-40222_AI_1 | Pin 3 | C2S9:3/C2S09-X1:3 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | FT-40222 | Coriolis Flow Transmitter | 325-01-402-PD-02
C2-S09-P03 | 9 | 3 | 4 | 1756-IF16 | FT-40222_AI_2 | Pin 4 | C2S9:4/C2S09-X1:4 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | FT-40222 | Coriolis Flow Transmitter | 325-01-402-PD-02
C2-S09-P04 | 9 | 4 | 5 | 1756-IF16 | PT-40222_AI_1 | Pin 5 | C2S9:5/C2S09-X1:5 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | PT-40222 | Pressure Transmitter | 325-01-402-PD-02
C2-S09-P05 | 9 | 5 | 6 | 1756-IF16 | TT-40221_AI_1 | Pin 6 | C2S9:6/C2S09-X1:6 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | TT-40221 |  | 325-01-402-PD-02
C2-S09-P06 | 9 | 6 | 7 | 1756-IF16 | TT-40222_AI_1 | Pin 7 | C2S9:7/C2S09-X1:7 | AI | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C2S09-X1 | - | TT-40222 |  | 325-01-402-PD-02
C2-S09-P07 | 9 | 7 | 8 | 1756-IF16 | Spare_AI_0 | Pin 8 | C2S9:8/C2S09-X1:8 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P08 | 9 | 8 | 9 | 1756-IF16 | Spare_AI_0 | Pin 9 | C2S9:9/C2S09-X1:9 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P09 | 9 | 9 | 10 | 1756-IF16 | Spare_AI_0 | Pin 10 | C2S9:10/C2S09-X1:10 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P10 | 9 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C2S9:11/C2S09-X1:11 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P11 | 9 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C2S9:12/C2S09-X1:12 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P12 | 9 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C2S9:13/C2S09-X1:13 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P13 | 9 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C2S9:14/C2S09-X1:14 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P14 | 9 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C2S9:15/C2S09-X1:15 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -
C2-S09-P15 | 9 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C2S9:16/C2S09-X1:16 | AI | 4-20mA HART | SPARE | JB-402 | Jet Cooker 2nd Floor | - | C2S09-X1 | - | Spare | Spare Channel | -

## Slot_10
KALASIN ENGINEERING — C2 SLOT 10 (1756-IF16 • AI)
Chassis: C2 (I/O Expansion Rack 1 (Chassis 2)) ¦ Panel: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 16 (Active: 16, Spare: 0 / 0.0%) | [16 empty] | Destination: JB-602
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C2-S10-P00 | 10 | 0 | 1 | 1756-IF16 | AT-60241_AI_1 | Pin 1 | C2S10:1/C2S10-X1:1 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | AT-60241 | Dust Analyzer Transmitter | 3-25-01-602-PD-05
C2-S10-P01 | 10 | 1 | 2 | 1756-IF16 | DPT-60203_AI_1 | Pin 2 | C2S10:2/C2S10-X1:2 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | DPT-60203 | Differential Pressure Transmitte | 3-25-01-602-PD-03
C2-S10-P02 | 10 | 2 | 3 | 1756-IF16 | FT-60202_AI_1 | Pin 3 | C2S10:3/C2S10-X1:3 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | FT-60202 |  | 3-25-01-602-PD-09
C2-S10-P03 | 10 | 3 | 4 | 1756-IF16 | PT-60210_AI_1 | Pin 4 | C2S10:4/C2S10-X1:4 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60210 | Pressure Transmitter | 3-25-01-602-PD-03
C2-S10-P04 | 10 | 4 | 5 | 1756-IF16 | PT-60215_AI_1 | Pin 5 | C2S10:5/C2S10-X1:5 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60215 | Pressure Transmitter | 3-25-01-602-PD-03
C2-S10-P05 | 10 | 5 | 6 | 1756-IF16 | PT-60216_AI_1 | Pin 6 | C2S10:6/C2S10-X1:6 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60216 | Pressure Transmitter | 3-25-01-602-PD-03
C2-S10-P06 | 10 | 6 | 7 | 1756-IF16 | PT-60240_AI_1 | Pin 7 | C2S10:7/C2S10-X1:7 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60240 | Pressure Transmitter | 3-25-01-602-PD-05
C2-S10-P07 | 10 | 7 | 8 | 1756-IF16 | PT-60241_AI_1 | Pin 8 | C2S10:8/C2S10-X1:8 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | PT-60241 | Pressure Transmitter | 3-25-01-602-PD-05
C2-S10-P08 | 10 | 8 | 9 | 1756-IF16 | TT-60210_AI_1 | Pin 9 | C2S10:9/C2S10-X1:9 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60210 |  | 3-25-01-602-PD-03
C2-S10-P09 | 10 | 9 | 10 | 1756-IF16 | TT-60210A_AI_1 | Pin 10 | C2S10:10/C2S10-X1:10 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60210A |  | -
C2-S10-P10 | 10 | 10 | 11 | 1756-IF16 | TT-60210B_AI_1 | Pin 11 | C2S10:11/C2S10-X1:11 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60210B |  | -
C2-S10-P11 | 10 | 11 | 12 | 1756-IF16 | TT-60211_AI_1 | Pin 12 | C2S10:12/C2S10-X1:12 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60211 |  | 3-25-01-602-PD-03
C2-S10-P12 | 10 | 12 | 13 | 1756-IF16 | TT-60212A_AI_1 | Pin 13 | C2S10:13/C2S10-X1:13 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60212A |  | 3-25-01-602-PD-03
C2-S10-P13 | 10 | 13 | 14 | 1756-IF16 | TT-60212B_AI_1 | Pin 14 | C2S10:14/C2S10-X1:14 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60212B |  | 3-25-01-602-PD-03
C2-S10-P14 | 10 | 14 | 15 | 1756-IF16 | TT-60214_AI_1 | Pin 15 | C2S10:15/C2S10-X1:15 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60214 |  | 3-25-01-602-PD-03
C2-S10-P15 | 10 | 15 | 16 | 1756-IF16 | TT-60215A_AI_1 | Pin 16 | C2S10:16/C2S10-X1:16 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S10-X1 | - | TT-60215A |  | 3-25-01-602-PD-03

## Slot_11
KALASIN ENGINEERING — C2 SLOT 11 (1756-IF16 • AI)
Chassis: C2 (I/O Expansion Rack 1 (Chassis 2)) ¦ Panel: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 16 (Active: 13, Spare: 3 / 18.8%) | [16 empty] | Destination: JB-602
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C2-S11-P00 | 11 | 0 | 1 | 1756-IF16 | TT-60215B_AI_1 | Pin 1 | C2S11:1/C2S11-X1:1 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60215B |  | 3-25-01-602-PD-03
C2-S11-P01 | 11 | 1 | 2 | 1756-IF16 | TT-60216_AI_1 | Pin 2 | C2S11:2/C2S11-X1:2 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60216 |  | 3-25-01-602-PD-03
C2-S11-P02 | 11 | 2 | 3 | 1756-IF16 | TT-60240_AI_1 | Pin 3 | C2S11:3/C2S11-X1:3 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60240 |  | 3-25-01-602-PD-05
C2-S11-P03 | 11 | 3 | 4 | 1756-IF16 | TT-60241A_AI_1 | Pin 4 | C2S11:4/C2S11-X1:4 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60241A |  | 3-25-01-602-PD-05
C2-S11-P04 | 11 | 4 | 5 | 1756-IF16 | TT-60241B_AI_1 | Pin 5 | C2S11:5/C2S11-X1:5 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | TT-60241B |  | 3-25-01-602-PD-05
C2-S11-P05 | 11 | 5 | 6 | 1756-IF16 | VT-60210A_AI_1 | Pin 6 | C2S11:6/C2S11-X1:6 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60210A |  | 3-25-01-602-PD-03
C2-S11-P06 | 11 | 6 | 7 | 1756-IF16 | VT-60210B_AI_1 | Pin 7 | C2S11:7/C2S11-X1:7 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60210B |  | 3-25-01-602-PD-03
C2-S11-P07 | 11 | 7 | 8 | 1756-IF16 | VT-60241A_AI_1 | Pin 8 | C2S11:8/C2S11-X1:8 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60241A |  | 3-25-01-602-PD-05
C2-S11-P08 | 11 | 8 | 9 | 1756-IF16 | VT-60241B_AI_1 | Pin 9 | C2S11:9/C2S11-X1:9 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | VT-60241B |  | 3-25-01-602-PD-05
C2-S11-P09 | 11 | 9 | 10 | 1756-IF16 | FT-60210_AI_1 | Pin 10 | C2S11:10/C2S11-X1:10 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60210 |  | 3-25-01-602-PD-03
C2-S11-P10 | 11 | 10 | 11 | 1756-IF16 | FT-60211_AI_1 | Pin 11 | C2S11:11/C2S11-X1:11 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60211 |  | 3-25-01-602-PD-03
C2-S11-P11 | 11 | 11 | 12 | 1756-IF16 | FT-60210_AI_2 | Pin 12 | C2S11:12/C2S11-X1:12 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60210 |  | 3-25-01-602-PD-03
C2-S11-P12 | 11 | 12 | 13 | 1756-IF16 | FT-60211_AI_2 | Pin 13 | C2S11:13/C2S11-X1:13 | AI | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C2S11-X1 | - | FT-60211 |  | 3-25-01-602-PD-03
C2-S11-P13 | 11 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C2S11:14/C2S11-X1:14 | AI | 4-20mA HART | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S11-X1 | - | Spare | Spare Channel | -
C2-S11-P14 | 11 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C2S11:15/C2S11-X1:15 | AI | 4-20mA HART | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S11-X1 | - | Spare | Spare Channel | -
C2-S11-P15 | 11 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C2S11:16/C2S11-X1:16 | AI | 4-20mA HART | SPARE | JB-602 | Spray Dryer 3rd Floor | - | C2S11-X1 | - | Spare | Spare Channel | -

## Slot_12
KALASIN ENGINEERING — C2 SLOT 12 (1756-IF16 • AI)
Chassis: C2 (I/O Expansion Rack 1 (Chassis 2)) ¦ Panel: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 16 (Active: 16, Spare: 0 / 0.0%) | [16 empty] | Destination: JB-607
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C2-S12-P00 | 12 | 0 | 1 | 1756-IF16 | FT-60207_AI_1 | Pin 1 | C2S12:1/C2S12-X1:1 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60207 |  | 3-25-01-602-PD-07
C2-S12-P01 | 12 | 1 | 2 | 1756-IF16 | FT-60221_AI_1 | Pin 2 | C2S12:2/C2S12-X1:2 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60221 |  | 3-25-01-602-PD-04
C2-S12-P02 | 12 | 2 | 3 | 1756-IF16 | FT-60261FA_AI_1 | Pin 3 | C2S12:3/C2S12-X1:3 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60261FA |  | 3-25-01-602-PD-02
C2-S12-P03 | 12 | 3 | 4 | 1756-IF16 | FT-60261FB_AI_1 | Pin 4 | C2S12:4/C2S12-X1:4 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60261FB |  | 3-25-01-602-PD-02
C2-S12-P04 | 12 | 4 | 5 | 1756-IF16 | FT-60261FC_AI_1 | Pin 5 | C2S12:5/C2S12-X1:5 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60261FC |  | 3-25-01-602-PD-02
C2-S12-P05 | 12 | 5 | 6 | 1756-IF16 | FT-60261FD_AI_1 | Pin 6 | C2S12:6/C2S12-X1:6 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60261FD |  | 3-25-01-602-PD-02
C2-S12-P06 | 12 | 6 | 7 | 1756-IF16 | FT-60262FE_AI_1 | Pin 7 | C2S12:7/C2S12-X1:7 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60262FE |  | 3-25-01-602-PD-02
C2-S12-P07 | 12 | 7 | 8 | 1756-IF16 | FT-60262FF_AI_1 | Pin 8 | C2S12:8/C2S12-X1:8 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60262FF |  | 3-25-01-602-PD-02
C2-S12-P08 | 12 | 8 | 9 | 1756-IF16 | FT-60262FG_AI_1 | Pin 9 | C2S12:9/C2S12-X1:9 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60262FG |  | 3-25-01-602-PD-02
C2-S12-P09 | 12 | 9 | 10 | 1756-IF16 | FT-60262FH_AI_1 | Pin 10 | C2S12:10/C2S12-X1:10 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60262FH |  | 3-25-01-602-PD-02
C2-S12-P10 | 12 | 10 | 11 | 1756-IF16 | FT-60263FJ_AI_1 | Pin 11 | C2S12:11/C2S12-X1:11 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60263FJ |  | 3-25-01-602-PD-02
C2-S12-P11 | 12 | 11 | 12 | 1756-IF16 | FT-60263FK_AI_1 | Pin 12 | C2S12:12/C2S12-X1:12 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60263FK |  | 3-25-01-602-PD-02
C2-S12-P12 | 12 | 12 | 13 | 1756-IF16 | FT-60263FL_AI_1 | Pin 13 | C2S12:13/C2S12-X1:13 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60263FL |  | 3-25-01-602-PD-02
C2-S12-P13 | 12 | 13 | 14 | 1756-IF16 | FT-60263FM_AI_1 | Pin 14 | C2S12:14/C2S12-X1:14 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60263FM |  | 3-25-01-602-PD-02
C2-S12-P14 | 12 | 14 | 15 | 1756-IF16 | FT-60264FN_AI_1 | Pin 15 | C2S12:15/C2S12-X1:15 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60264FN |  | 3-25-01-602-PD-02
C2-S12-P15 | 12 | 15 | 16 | 1756-IF16 | FT-60264FP_AI_1 | Pin 16 | C2S12:16/C2S12-X1:16 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S12-X1 | - | FT-60264FP |  | 3-25-01-602-PD-02

## Slot_13
KALASIN ENGINEERING — C2 SLOT 13 (1756-IF16 • AI)
Chassis: C2 (I/O Expansion Rack 1 (Chassis 2)) ¦ Panel: Control Cabinet CA1 (Bay 2) ¦ Net: EN4TR DLR Ring Node 2 (192.168.1.11) ¦ Total Points: 16 (Active: 11, Spare: 5 / 31.2%) | [16 empty] | Destination: JB-607
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C2-S13-P00 | 13 | 0 | 1 | 1756-IF16 | FT-60264FQ_AI_1 | Pin 1 | C2S13:1/C2S13-X1:1 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | FT-60264FQ |  | 3-25-01-602-PD-02
C2-S13-P01 | 13 | 1 | 2 | 1756-IF16 | FT-60264FR_AI_1 | Pin 2 | C2S13:2/C2S13-X1:2 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | FT-60264FR |  | 3-25-01-602-PD-02
C2-S13-P02 | 13 | 2 | 3 | 1756-IF16 | PT-60201_AI_1 | Pin 3 | C2S13:3/C2S13-X1:3 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | PT-60201 | Pressure Transmitter | 3-25-01-602-PD-02
C2-S13-P03 | 13 | 3 | 4 | 1756-IF16 | PT-60207_AI_1 | Pin 4 | C2S13:4/C2S13-X1:4 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | PT-60207 | Pressure Transmitter | 3-25-01-602-PD-07
C2-S13-P04 | 13 | 4 | 5 | 1756-IF16 | PT-60221_AI_1 | Pin 5 | C2S13:5/C2S13-X1:5 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | PT-60221 | Pressure Transmitter | 3-25-01-602-PD-04
C2-S13-P05 | 13 | 5 | 6 | 1756-IF16 | PT-60221_AI_1 | Pin 6 | C2S13:6/C2S13-X1:6 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | PT-60221 | Pressure Transmitter | 3-25-01-602-PD-04
C2-S13-P06 | 13 | 6 | 7 | 1756-IF16 | TI-FH-60210_AI_1 | Pin 7 | C2S13:7/C2S13-X1:7 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | TI-FH-60210 |  | -
C2-S13-P07 | 13 | 7 | 8 | 1756-IF16 | TT-60201_AI_1 | Pin 8 | C2S13:8/C2S13-X1:8 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | TT-60201 |  | 3-25-01-602-PD-02
C2-S13-P08 | 13 | 8 | 9 | 1756-IF16 | TT-60202_AI_1 | Pin 9 | C2S13:9/C2S13-X1:9 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | TT-60202 |  | 3-25-01-602-PD-07
C2-S13-P09 | 13 | 9 | 10 | 1756-IF16 | TT-60207_AI_1 | Pin 10 | C2S13:10/C2S13-X1:10 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | TT-60207 |  | 3-25-01-602-PD-07
C2-S13-P10 | 13 | 10 | 11 | 1756-IF16 | UY-FH-60210A_AI_1 | Pin 11 | C2S13:11/C2S13-X1:11 | AI | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C2S13-X1 | - | UY-FH-60210A |  | -
C2-S13-P11 | 13 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C2S13:12/C2S13-X1:12 | AI | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | -
C2-S13-P12 | 13 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C2S13:13/C2S13-X1:13 | AI | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | -
C2-S13-P13 | 13 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C2S13:14/C2S13-X1:14 | AI | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | -
C2-S13-P14 | 13 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C2S13:15/C2S13-X1:15 | AI | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | -
C2-S13-P15 | 13 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C2S13:16/C2S13-X1:16 | AI | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C2S13-X1 | - | Spare | Spare Channel | -