## C3_Slot_Summary
KALASIN ENGINEERING — C3 (I/O EXPANSION RACK 2 (CHASSIS 3))
Location: Control Cabinet CA1 (Bay 3) ¦ Net: EN4TR DLR Ring Node 3 (192.168.1.12) ¦ Total Active Slots: 6
Slot No. | Module Model | I/O Type | Capacity | Active Points | Spare Points | Spare % | Primary Destinations | Sheet Link
Slot 01 | 1756-IB32 | DI | 27 | 22 | 5 | 18.5% | IS-JB-603, JB-618 | Go to Slot 01 ➔
Slot 02 | 1756-IB32 | DI | 37 | 18 | 19 | 51.4% | IS-JB-618, JB-618 | Go to Slot 02 ➔
Slot 03 | 1756-OB32 | DO | 32 | 9 | 23 | 71.9% | JB-618 | Go to Slot 03 ➔
Slot 04 | 1756-IF16 | AI | 16 | 7 | 9 | 56.2% | IS-JB-603 | Go to Slot 04 ➔
Slot 05 | 1756-IF16 | AI | 16 | 13 | 3 | 18.8% | IS-JB-618, JB-618 | Go to Slot 05 ➔
Slot 13 | 1756-OF8 | AO | 8 | 5 | 3 | 37.5% | JB-402, JB-602, JB-607 | Go to Slot 13 ➔

## Slot_01
KALASIN ENGINEERING — C3 SLOT 01 (1756-IB32 • DI)
Chassis: C3 (I/O Expansion Rack 2 (Chassis 3)) ¦ Panel: Control Cabinet CA1 (Bay 3) ¦ Net: EN4TR DLR Ring Node 3 (192.168.1.12) ¦ Total Points: 27 (Active: 22, Spare: 5 / 18.5%) | [16 empty] | Destination: IS-JB-603, JB-618
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C3-S01-P00 | 1 | 0 | 1 | 1756-IB32 | AT-40201_DI_1 | Pin 1 | C3S1:1/C3S01-X1:1 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | AT-40201 |  | -
C3-S01-P01 | 1 | 1 | 2 | 1756-IB32 | AT-40202_DI_1 | Pin 2 | C3S1:2/C3S01-X1:2 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | AT-40202 |  | -
C3-S01-P02 | 1 | 2 | 3 | 1756-IB32 | AT-40203_DI_1 | Pin 3 | C3S1:3/C3S01-X1:3 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | AT-40203 |  | -
C3-S01-P03 | 1 | 3 | 4 | 1756-IB32 | LSH-60230_DI_1 | Pin 4 | C3S1:4/C3S01-X1:4 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S01-X1 | - | LSH-60230 |  | 3-25-01-602-PD-04
C3-S01-P04 | 1 | 4 | 5 | 1756-IB32 | LSH-60231_DI_1 | Pin 5 | C3S1:5/C3S01-X1:5 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S01-X1 | - | LSH-60231 |  | 3-25-01-602-PD-04
C3-S01-P05 | 1 | 5 | 6 | 1756-IB32 | LSH-60240_DI_1 | Pin 6 | C3S1:6/C3S01-X1:6 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S01-X1 | - | LSH-60240 |  | 3-25-01-602-PD-05
C3-S01-P06 | 1 | 6 | 7 | 1756-IB32 | PD-60202_DI_1 | Pin 7 | C3S1:7/C3S01-X1:7 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | PD-60202 |  | -
C3-S01-P07 | 1 | 7 | 8 | 1756-IB32 | RV-60204_DI_1 | Pin 8 | C3S1:8/C3S01-X1:8 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S01-X1 | - | RV-60204 |  | -
C3-S01-P08 | 1 | 8 | 9 | 1756-IB32 | ZS-60201C_DI_1 | Pin 9 | C3S1:9/C3S01-X1:9 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60201C |  | 3-25-01-602-PD-04
C3-S01-P09 | 1 | 9 | 10 | 1756-IB32 | ZS-60201D_DI_1 | Pin 10 | C3S1:10/C3S01-X1:10 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60201D |  | 3-25-01-602-PD-04
C3-S01-P10 | 1 | 10 | 11 | 1756-IB32 | ZS-60201E_DI_1 | Pin 11 | C3S1:11/C3S01-X1:11 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S01-X1 | - | ZS-60201E |  | 3-25-01-602-PD-04
C3-S01-P11 | 1 | 11 | 12 | 1756-IB32 | ZS-60229_DI_1 | Pin 12 | C3S1:12/C3S01-X1:12 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60229 |  | 3-25-01-602-PD-04
C3-S01-P12 | 1 | 12 | 13 | 1756-IB32 | ZS-60230_DI_1 | Pin 13 | C3S1:13/C3S01-X1:13 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60230 |  | 3-25-01-602-PD-04
C3-S01-P13 | 1 | 13 | 14 | 1756-IB32 | ZS-60231A_DI_1 | Pin 14 | C3S1:14/C3S01-X1:14 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60231A |  | 3-25-01-602-PD-05
C3-S01-P14 | 1 | 14 | 15 | 1756-IB32 | ZS-60231B_DI_1 | Pin 15 | C3S1:15/C3S01-X1:15 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S01-X1 | - | ZS-60231B |  | 3-25-01-602-PD-05
C3-S01-P15 | 1 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C3S1:16/C3S01-X1:16 | DI | 24VDC Dry Contact | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S01-X1 | - | Spare | Spare Channel | -
C3-S01-P16 | 1 | 16 | 17 | 1756-IB32 | DV-61301_DI_1 | Pin 17 | C3S1:17/C3S01-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S01-X2 | - | DV-61301 |  | 3-25-01-613-PD-01
C3-S01-P17 | 1 | 17 | 18 | 1756-IB32 | DV-61301_DI_2 | Pin 18 | C3S1:18/C3S01-X2:18 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S01-X2 | - | DV-61301 |  | 3-25-01-613-PD-01
C3-S01-P18 | 1 | 18 | 19 | 1756-IB32 | DV-61302_DI_1 | Pin 19 | C3S1:19/C3S01-X2:19 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S01-X2 | - | DV-61302 |  | 3-25-01-613-PD-01
C3-S01-P19 | 1 | 19 | 20 | 1756-IB32 | DV-61302_DI_2 | Pin 20 | C3S1:20/C3S01-X2:20 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S01-X2 | - | DV-61302 |  | 3-25-01-613-PD-01
C3-S01-P20 | 1 | 20 | 21 | 1756-IB32 | LS-61303_DI_1 | Pin 21 | C3S1:21/C3S01-X2:21 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 7th / Packing Tower | C3S01-X2 | - | LS-61303 |  | 3-25-01-613-PD-01
C3-S01-P21 | 1 | 21 | 22 | 1756-IB32 | PSL-61301_DI_1 | Pin 22 | C3S1:22/C3S01-X2:22 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S01-X2 | - | PSL-61301 |  | -
C3-S01-P22 | 1 | 22 | 23 | 1756-IB32 | PSL-61302_DI_1 | Pin 23 | C3S1:23/C3S01-X2:23 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S01-X2 | - | PSL-61302 |  | 3-25-01-613-PD-01
C3-S01-P28 | 1 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C3S1:29/C3S01-X2:29 | DI | 24VDC Dry Contact | SPARE | JB-618 | Packing Tower 8th Floor | Packing Tower | C3S01-X2 | - | Spare | Spare Channel | -
C3-S01-P29 | 1 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C3S1:30/C3S01-X2:30 | DI | 24VDC Dry Contact | SPARE | JB-618 | Packing Tower 8th Floor | Packing Tower | C3S01-X2 | - | Spare | Spare Channel | -
C3-S01-P30 | 1 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C3S1:31/C3S01-X2:31 | DI | 24VDC Dry Contact | SPARE | JB-618 | Packing Tower 8th Floor | Packing Tower | C3S01-X2 | - | Spare | Spare Channel | -
C3-S01-P31 | 1 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C3S1:32/C3S01-X2:32 | DI | 24VDC Dry Contact | SPARE | JB-618 | Packing Tower 8th Floor | Packing Tower | C3S01-X2 | - | Spare | Spare Channel | -

## Slot_02
KALASIN ENGINEERING — C3 SLOT 02 (1756-IB32 • DI)
Chassis: C3 (I/O Expansion Rack 2 (Chassis 3)) ¦ Panel: Control Cabinet CA1 (Bay 3) ¦ Net: EN4TR DLR Ring Node 3 (192.168.1.12) ¦ Total Points: 37 (Active: 18, Spare: 19 / 51.4%) | [16 empty] | Destination: IS-JB-618, JB-618
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C3-S02-P00 | 2 | 0 | 1 | 1756-IB32 | ISV-61301_DI_1 | Pin 1 | C3S2:1/C3S02-X1:1 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X1 | - | ISV-61301 |  | 3-25-01-613-PD-01
C3-S02-P01 | 2 | 1 | 2 | 1756-IB32 | LSH-61301_DI_1 | Pin 2 | C3S2:2/C3S02-X1:2 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 7th / Packing Tower | C3S02-X1 | - | LSH-61301 |  | 3-25-01-613-PD-01
C3-S02-P02 | 2 | 2 | 3 | 1756-IB32 | LSH-61303_DI_1 | Pin 3 | C3S2:3/C3S02-X1:3 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 7th / Packing Tower | C3S02-X1 | - | LSH-61303 |  | -
C3-S02-P03 | 2 | 3 | 4 | 1756-IB32 | LSH-61306_DI_1 | Pin 4 | C3S2:4/C3S02-X1:4 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X1 | - | LSH-61306 |  | 3-25-01-613-PD-01
C3-S02-P04 | 2 | 4 | 5 | 1756-IB32 | LSH-61308_DI_1 | Pin 5 | C3S2:5/C3S02-X1:5 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X1 | - | LSH-61308 |  | 3-25-01-613-PD-01
C3-S02-P05 | 2 | 5 | 6 | 1756-IB32 | LSL-61302_DI_1 | Pin 6 | C3S2:6/C3S02-X1:6 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 6th / Packing Tower | C3S02-X1 | - | LSL-61302 |  | 3-25-01-613-PD-01
C3-S02-P06 | 2 | 6 | 7 | 1756-IB32 | PSE-61300_DI_1 | Pin 7 | C3S2:7/C3S02-X1:7 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X1 | - | PSE-61300 |  | 3-25-01-613-PD-01
C3-S02-P07 | 2 | 7 | 8 | 1756-IB32 | PSE-61301_DI_1 | Pin 8 | C3S2:8/C3S02-X1:8 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X1 | - | PSE-61301 |  | 3-25-01-613-PD-01
C3-S02-P08 | 2 | 8 | 9 | 1756-IB32 | PSE-61304_DI_1 | Pin 9 | C3S2:9/C3S02-X1:9 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X1 | - | PSE-61304 |  | 3-25-01-613-PD-01
C3-S02-P09 | 2 | 9 | 10 | 1756-IB32 | PSV-61301A_DI_1 | Pin 10 | C3S2:10/C3S02-X1:10 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X1 | - | PSV-61301A |  | 325-01-613-PD-01
C3-S02-P10 | 2 | 10 | 11 | 1756-IB32 | PSV-61301B_DI_1 | Pin 11 | C3S2:11/C3S02-X1:11 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X1 | - | PSV-61301B |  | 325-01-613-PD-01
C3-S02-P11 | 2 | 11 | 12 | 1756-IB32 | ZS-61310_DI_1 | Pin 12 | C3S2:12/C3S02-X1:12 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | ZS-61310 |  | 3-25-01-613-PD-01
C3-S02-P12 | 2 | 12 | 13 | 1756-IB32 | ZS-61311_DI_1 | Pin 13 | C3S2:13/C3S02-X1:13 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | ZS-61311 |  | 3-25-01-613-PD-01
C3-S02-P13 | 2 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C3S2:14/C3S02-X1:14 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P14 | 2 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C3S2:15/C3S02-X1:15 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P15 | 2 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C3S2:16/C3S02-X1:16 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X1 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P16 | 2 | 16 | 17 | 1756-IB32 | Spare_DI_0 | Pin 17 | C3S2:17/C3S02-X2:17 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P17 | 2 | 17 | 18 | 1756-IB32 | Spare_DI_0 | Pin 18 | C3S2:18/C3S02-X2:18 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P18 | 2 | 18 | 19 | 1756-IB32 | Spare_DI_0 | Pin 19 | C3S2:19/C3S02-X2:19 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P19 | 2 | 19 | 20 | 1756-IB32 | Spare_DI_0 | Pin 20 | C3S2:20/C3S02-X2:20 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P20 | 2 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C3S2:21/C3S02-X2:21 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P21 | 2 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C3S2:22/C3S02-X2:22 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P22 | 2 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C3S2:23/C3S02-X2:23 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P23 | 2 | 23 | 24 | 1756-IB32 | PSL-61311_DI_1 | Pin 24 | C3S2:24/C3S02-X2:24 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S02-X2 | - | PSL-61311 |  | 3-25-01-613-PD-04
C3-S02-P23 | 2 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C3S2:24/C3S02-X2:24 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P24 | 2 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C3S2:25/C3S02-X2:25 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P24 | 2 | 24 | 25 | 1756-IB32 | SV-61304_DI_1 | Pin 25 | C3S2:25/C3S02-X2:25 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X2 | - | SV-61304 |  | 3-25-01-613-PD-01
C3-S02-P25 | 2 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C3S2:26/C3S02-X2:26 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P25 | 2 | 25 | 26 | 1756-IB32 | SV-61304_DI_2 | Pin 26 | C3S2:26/C3S02-X2:26 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S02-X2 | - | SV-61304 |  | 3-25-01-613-PD-01
C3-S02-P26 | 2 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C3S2:27/C3S02-X2:27 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P26 | 2 | 26 | 27 | 1756-IB32 | XV-61301_DI_1 | Pin 27 | C3S2:27/C3S02-X2:27 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | XV-61301 |  | 3-25-01-613-PD-01
C3-S02-P27 | 2 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C3S2:28/C3S02-X2:28 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P27 | 2 | 27 | 28 | 1756-IB32 | XV-61301_DI_2 | Pin 28 | C3S2:28/C3S02-X2:28 | DI | 24VDC Dry Contact | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | XV-61301 |  | 3-25-01-613-PD-01
C3-S02-P28 | 2 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C3S2:29/C3S02-X2:29 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P29 | 2 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C3S2:30/C3S02-X2:30 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P30 | 2 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C3S2:31/C3S02-X2:31 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01
C3-S02-P31 | 2 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C3S2:32/C3S02-X2:32 | DI | 24VDC Dry Contact | SPARE | IS-JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S02-X2 | - | Spare | Spare Channel | 3-25-01-613-PD-01

## Slot_03
KALASIN ENGINEERING — C3 SLOT 03 (1756-OB32 • DO)
Chassis: C3 (I/O Expansion Rack 2 (Chassis 3)) ¦ Panel: Control Cabinet CA1 (Bay 3) ¦ Net: EN4TR DLR Ring Node 3 (192.168.1.12) ¦ Total Points: 32 (Active: 9, Spare: 23 / 71.9%) | [16 empty] | Destination: JB-618
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C3-S03-P00 | 3 | 0 | 1 | 1756-OB32 | DV-61301_DO_1 | Pin 1 | C3S3:1/C3S03-X1:1 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S03-X1 | - | DV-61301 |  | 3-25-01-613-PD-01
C3-S03-P01 | 3 | 1 | 2 | 1756-OB32 | DV-61302_DO_1 | Pin 2 | C3S3:2/C3S03-X1:2 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S03-X1 | - | DV-61302 |  | 3-25-01-613-PD-01
C3-S03-P02 | 3 | 2 | 3 | 1756-OB32 | SV-61301_DO_1 | Pin 3 | C3S3:3/C3S03-X1:3 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S03-X1 | - | SV-61301 |  | -
C3-S03-P03 | 3 | 3 | 4 | 1756-OB32 | SV-61302_DO_1 | Pin 4 | C3S3:4/C3S03-X1:4 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 7th / Packing Tower | C3S03-X1 | - | SV-61302 |  | 3-25-01-613-PD-01
C3-S03-P04 | 3 | 4 | 5 | 1756-OB32 | SV-61303_DO_1 | Pin 5 | C3S3:5/C3S03-X1:5 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S03-X1 | - | SV-61303 |  | 3-25-01-613-PD-01
C3-S03-P05 | 3 | 5 | 6 | 1756-OB32 | SV-61304_DO_1 | Pin 6 | C3S3:6/C3S03-X1:6 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S03-X1 | - | SV-61304 |  | 3-25-01-613-PD-01
C3-S03-P06 | 3 | 6 | 7 | 1756-OB32 | SV-61305_DO_1 | Pin 7 | C3S3:7/C3S03-X1:7 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S03-X1 | - | SV-61305 |  | 3-25-01-613-PD-01
C3-S03-P07 | 3 | 7 | 8 | 1756-OB32 | SV-61306_DO_1 | Pin 8 | C3S3:8/C3S03-X1:8 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S03-X1 | - | SV-61306 |  | 3-25-01-613-PD-01
C3-S03-P08 | 3 | 8 | 9 | 1756-OB32 | XV-61301_DO_1 | Pin 9 | C3S3:9/C3S03-X1:9 | DO | 24VDC Sourcing | ACTIVE | JB-618 | Packing Tower 8th Floor | 5th / Packing Tower | C3S03-X1 | - | XV-61301 |  | 3-25-01-613-PD-01
C3-S03-P09 | 3 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C3S3:10/C3S03-X1:10 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P10 | 3 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C3S3:11/C3S03-X1:11 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P11 | 3 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C3S3:12/C3S03-X1:12 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P12 | 3 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C3S3:13/C3S03-X1:13 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P13 | 3 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C3S3:14/C3S03-X1:14 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P14 | 3 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C3S3:15/C3S03-X1:15 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P15 | 3 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C3S3:16/C3S03-X1:16 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X1 | - | Spare | Spare Channel | -
C3-S03-P16 | 3 | 16 | 17 | 1756-OB32 | Spare_DO_0 | Pin 17 | C3S3:17/C3S03-X2:17 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P17 | 3 | 17 | 18 | 1756-OB32 | Spare_DO_0 | Pin 18 | C3S3:18/C3S03-X2:18 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P18 | 3 | 18 | 19 | 1756-OB32 | Spare_DO_0 | Pin 19 | C3S3:19/C3S03-X2:19 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P19 | 3 | 19 | 20 | 1756-OB32 | Spare_DO_0 | Pin 20 | C3S3:20/C3S03-X2:20 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P20 | 3 | 20 | 21 | 1756-OB32 | Spare_DO_0 | Pin 21 | C3S3:21/C3S03-X2:21 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P21 | 3 | 21 | 22 | 1756-OB32 | Spare_DO_0 | Pin 22 | C3S3:22/C3S03-X2:22 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P22 | 3 | 22 | 23 | 1756-OB32 | Spare_DO_0 | Pin 23 | C3S3:23/C3S03-X2:23 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P23 | 3 | 23 | 24 | 1756-OB32 | Spare_DO_0 | Pin 24 | C3S3:24/C3S03-X2:24 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P24 | 3 | 24 | 25 | 1756-OB32 | Spare_DO_0 | Pin 25 | C3S3:25/C3S03-X2:25 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P25 | 3 | 25 | 26 | 1756-OB32 | Spare_DO_0 | Pin 26 | C3S3:26/C3S03-X2:26 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P26 | 3 | 26 | 27 | 1756-OB32 | Spare_DO_0 | Pin 27 | C3S3:27/C3S03-X2:27 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P27 | 3 | 27 | 28 | 1756-OB32 | Spare_DO_0 | Pin 28 | C3S3:28/C3S03-X2:28 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P28 | 3 | 28 | 29 | 1756-OB32 | Spare_DO_0 | Pin 29 | C3S3:29/C3S03-X2:29 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P29 | 3 | 29 | 30 | 1756-OB32 | Spare_DO_0 | Pin 30 | C3S3:30/C3S03-X2:30 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P30 | 3 | 30 | 31 | 1756-OB32 | Spare_DO_0 | Pin 31 | C3S3:31/C3S03-X2:31 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -
C3-S03-P31 | 3 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C3S3:32/C3S03-X2:32 | DO | 24VDC Sourcing | SPARE | JB-618 | Packing Tower 8th Floor | - | C3S03-X2 | - | Spare | Spare Channel | -

## Slot_04
KALASIN ENGINEERING — C3 SLOT 04 (1756-IF16 • AI)
Chassis: C3 (I/O Expansion Rack 2 (Chassis 3)) ¦ Panel: Control Cabinet CA1 (Bay 3) ¦ Net: EN4TR DLR Ring Node 3 (192.168.1.12) ¦ Total Points: 16 (Active: 7, Spare: 9 / 56.2%) | [16 empty] | Destination: IS-JB-603
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C3-S04-P00 | 4 | 0 | 1 | 1756-IF16 | PT-60230_AI_1 | Pin 1 | C3S4:1/C3S04-X1:1 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S04-X1 | - | PT-60230 | Pressure Transmitter | 3-25-01-602-PD-04
C3-S04-P01 | 4 | 1 | 2 | 1756-IF16 | PT-60231_AI_1 | Pin 2 | C3S4:2/C3S04-X1:2 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S04-X1 | - | PT-60231 | Pressure Transmitter | 3-25-01-602-PD-04
C3-S04-P02 | 4 | 2 | 3 | 1756-IF16 | TT-60224_AI_1 | Pin 3 | C3S4:3/C3S04-X1:3 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 4th / Spray Dryer | C3S04-X1 | - | TT-60224 |  | 3-25-01-602-PD-04
C3-S04-P03 | 4 | 3 | 4 | 1756-IF16 | TT-60225_AI_1 | Pin 4 | C3S4:4/C3S04-X1:4 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S04-X1 | - | TT-60225 |  | 3-25-01-602-PD-04
C3-S04-P04 | 4 | 4 | 5 | 1756-IF16 | TT-60226_AI_1 | Pin 5 | C3S4:5/C3S04-X1:5 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 2nd / Spray Dryer | C3S04-X1 | - | TT-60226 |  | 3-25-01-602-PD-04
C3-S04-P05 | 4 | 5 | 6 | 1756-IF16 | TT-60227_AI_1 | Pin 6 | C3S4:6/C3S04-X1:6 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 1st / Spray Dryer | C3S04-X1 | - | TT-60227 |  | 3-25-01-602-PD-04
C3-S04-P06 | 4 | 6 | 7 | 1756-IF16 | TT-60230_AI_1 | Pin 7 | C3S4:7/C3S04-X1:7 | AI | 4-20mA HART | ACTIVE | IS-JB-603 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S04-X1 | - | TT-60230 |  | 3-25-01-602-PD-04
C3-S04-P07 | 4 | 7 | 8 | 1756-IF16 | Spare_AI_0 | Pin 8 | C3S4:8/C3S04-X1:8 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P08 | 4 | 8 | 9 | 1756-IF16 | Spare_AI_0 | Pin 9 | C3S4:9/C3S04-X1:9 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P09 | 4 | 9 | 10 | 1756-IF16 | Spare_AI_0 | Pin 10 | C3S4:10/C3S04-X1:10 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P10 | 4 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C3S4:11/C3S04-X1:11 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P11 | 4 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C3S4:12/C3S04-X1:12 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P12 | 4 | 12 | 13 | 1756-IF16 | Spare_AI_0 | Pin 13 | C3S4:13/C3S04-X1:13 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P13 | 4 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C3S4:14/C3S04-X1:14 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P14 | 4 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C3S4:15/C3S04-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -
C3-S04-P15 | 4 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C3S4:16/C3S04-X1:16 | AI | 4-20mA HART | SPARE | IS-JB-603 | Spray Dryer 3rd Floor | - | C3S04-X1 | - | Spare | Spare Channel | -

## Slot_05
KALASIN ENGINEERING — C3 SLOT 05 (1756-IF16 • AI)
Chassis: C3 (I/O Expansion Rack 2 (Chassis 3)) ¦ Panel: Control Cabinet CA1 (Bay 3) ¦ Net: EN4TR DLR Ring Node 3 (192.168.1.12) ¦ Total Points: 16 (Active: 13, Spare: 3 / 18.8%) | [16 empty] | Destination: IS-JB-618, JB-618
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C3-S05-P00 | 5 | 0 | 1 | 1756-IF16 | PT-61303_AI_1 | Pin 1 | C3S5:1/C3S05-X1:1 | AI | 4-20mA HART | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | PT-61303 | Pressure Transmitter | 3-25-01-613-PD-01
C3-S05-P01 | 5 | 1 | 2 | 1756-IF16 | PT-61306_AI_1 | Pin 2 | C3S5:2/C3S05-X1:2 | AI | 4-20mA HART | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | PT-61306 |  | 3-25-01-613-PD-01
C3-S05-P02 | 5 | 2 | 3 | 1756-IF16 | TT-61303_AI_1 | Pin 3 | C3S5:3/C3S05-X1:3 | AI | 4-20mA HART | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | TT-61303 |  | 3-25-01-613-PD-01
C3-S05-P03 | 5 | 3 | 4 | 1756-IF16 | TT-61304_AI_1 | Pin 4 | C3S5:4/C3S05-X1:4 | AI | 4-20mA HART | ACTIVE | JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | TT-61304 |  | 3-25-01-613-PD-01
C3-S05-P04 | 5 | 4 | 5 | 1756-IF16 | DPT-61301_AI_1 | Pin 5 | C3S5:5/C3S05-X1:5 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | DPT-61301 | Differential Pressure Transmitte | 3-25-01-613-PD-01
C3-S05-P05 | 5 | 5 | 6 | 1756-IF16 | DPT-61302_AI_1 | Pin 6 | C3S5:6/C3S05-X1:6 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | DPT-61302 | Differential Pressure Transmitte | 3-25-01-613-PD-01
C3-S05-P06 | 5 | 6 | 7 | 1756-IF16 | LT-61301_AI_1 | Pin 7 | C3S5:7/C3S05-X1:7 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | LT-61301 | Level Transmitter | 3-25-01-613-PD-01
C3-S05-P07 | 5 | 7 | 8 | 1756-IF16 | PT-61301_AI_1 | Pin 8 | C3S5:8/C3S05-X1:8 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | PT-61301 | Pressure Transmitter | 3-25-01-613-PD-01
C3-S05-P08 | 5 | 8 | 9 | 1756-IF16 | PT-61303_AI_1 | Pin 9 | C3S5:9/C3S05-X1:9 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 8th / Packing Tower | C3S05-X1 | - | PT-61303 | Pressure Transmitter | 3-25-01-613-PD-01
C3-S05-P09 | 5 | 9 | 10 | 1756-IF16 | PT-61304_AI_1 | Pin 10 | C3S5:10/C3S05-X1:10 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | PT-61304 | Pressure Transmitter | 3-25-01-613-PD-01
C3-S05-P10 | 5 | 10 | 11 | 1756-IF16 | PT-61305_AI_1 | Pin 11 | C3S5:11/C3S05-X1:11 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | PT-61305 | Pressure Transmitter | 3-25-01-613-PD-01
C3-S05-P11 | 5 | 11 | 12 | 1756-IF16 | TT-61301_AI_1 | Pin 12 | C3S5:12/C3S05-X1:12 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | TT-61301 |  | 3-25-01-613-PD-01
C3-S05-P12 | 5 | 12 | 13 | 1756-IF16 | TT-61302_AI_1 | Pin 13 | C3S5:13/C3S05-X1:13 | AI | 4-20mA HART | ACTIVE | IS-JB-618 | Packing Tower 8th Floor | 9th / Packing Tower | C3S05-X1 | - | TT-61302 |  | 3-25-01-613-PD-01
C3-S05-P13 | 5 | 13 | 14 | 1756-IF16 | Spare_AI_0 | Pin 14 | C3S5:14/C3S05-X1:14 | AI | 4-20mA HART | SPARE | IS-JB-618 | Packing Tower 8th Floor | - | C3S05-X1 | - | Spare | Spare Channel | -
C3-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C3S5:15/C3S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-618 | Packing Tower 8th Floor | - | C3S05-X1 | - | Spare | Spare Channel | -
C3-S05-P15 | 5 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C3S5:16/C3S05-X1:16 | AI | 4-20mA HART | SPARE | IS-JB-618 | Packing Tower 8th Floor | - | C3S05-X1 | - | Spare | Spare Channel | -

## Slot_13
KALASIN ENGINEERING — C3 SLOT 13 (1756-OF8 • AO)
Chassis: C3 (I/O Expansion Rack 2 (Chassis 3)) ¦ Panel: Control Cabinet CA1 (Bay 3) ¦ Net: EN4TR DLR Ring Node 3 (192.168.1.12) ¦ Total Points: 8 (Active: 5, Spare: 3 / 37.5%) | [16 empty] | Destination: JB-402, JB-602, JB-6
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C3-S13-P00 | 13 | 0 | 1 | 1756-OF8 | TCV-40222_AO_1 | Pin 1 | C3S13:1/C3S13-X1:1 | AO | 4-20mA HART | ACTIVE | JB-402 | Jet Cooker 2nd Floor | 2nd / Jet Cooker | C3S13-X1 | - | TCV-40222 |  | 325-01-402-PD-02
C3-S13-P01 | 13 | 1 | 2 | 1756-OF8 | TV-60202_AO_1 | Pin 2 | C3S13:2/C3S13-X1:2 | AO | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 3rd / Spray Dryer | C3S13-X1 | - | TV-60202 |  | 3-25-01-602-PD-07
C3-S13-P02 | 13 | 2 | 3 | 1756-OF8 | TV-60214_AO_1 | Pin 3 | C3S13:3/C3S13-X1:3 | AO | 4-20mA HART | ACTIVE | JB-602 | Spray Dryer 3rd Floor | 5th / Spray Dryer | C3S13-X1 | - | TV-60214 |  | 3-25-01-602-PD-03
C3-S13-P03 | 13 | 3 | 4 | 1756-OF8 | PV-60201_AO_1 | Pin 4 | C3S13:4/C3S13-X1:4 | AO | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C3S13-X1 | - | PV-60201 |  | 3-25-01-602-PD-02
C3-S13-P04 | 13 | 4 | 5 | 1756-OF8 | UY-FH-60210B_AO_1 | Pin 5 | C3S13:5/C3S13-X1:5 | AO | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C3S13-X1 | - | UY-FH-60210B |  | -
C3-S13-P05 | 13 | 5 | 6 | 1756-OF8 | Spare_AO_0 | Pin 6 | C3S13:6/C3S13-X1:6 | AO | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C3S13-X1 | - | Spare | Spare Channel | -
C3-S13-P06 | 13 | 6 | 7 | 1756-OF8 | Spare_AO_0 | Pin 7 | C3S13:7/C3S13-X1:7 | AO | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C3S13-X1 | - | Spare | Spare Channel | -
C3-S13-P07 | 13 | 7 | 8 | 1756-OF8 | Spare_AO_0 | Pin 8 | C3S13:8/C3S13-X1:8 | AO | 4-20mA HART | SPARE | JB-607 | Spray Dryer 7th Floor | - | C3S13-X1 | - | Spare | Spare Channel | -