## C4_Slot_Summary
KALASIN ENGINEERING — C4 (I/O EXPANSION RACK 3 (CHASSIS 4))
Location: Control Cabinet CA1 (Bay 4) ¦ Net: EN4TR DLR Ring Node 4 (192.168.1.13) ¦ Total Active Slots: 6
Slot No. | Module Model | I/O Type | Capacity | Active Points | Spare Points | Spare % | Primary Destinations | Sheet Link
Slot 01 | 1756-IB32 | DI | 32 | 11 | 21 | 65.6% | IS-JB-608, JB-606 | Go to Slot 01 ➔
Slot 02 | 1756-IB32 | DI | 32 | 17 | 15 | 46.9% | JB-612 | Go to Slot 02 ➔
Slot 03 | 1756-IB32 | DI | 31 | 15 | 16 | 51.6% | IS-JB-612 | Go to Slot 03 ➔
Slot 04 | 1756-OB32 | DO | 32 | 17 | 15 | 46.9% | IS-JB-608, JB-606, JB-612 | Go to Slot 04 ➔
Slot 05 | 1756-IF16 | AI | 26 | 7 | 19 | 73.1% | IS-JB-608, IS-JB-612, JB-606, JB-608, JB-612 | Go to Slot 05 ➔
Slot 06 | 1756-IF16 | AI | 8 | 8 | 0 | 0.0% | IS-JB-608, IS-JB-612 | Go to Slot 06 ➔

## Slot_01
KALASIN ENGINEERING — C4 SLOT 01 (1756-IB32 • DI)
Chassis: C4 (I/O Expansion Rack 3 (Chassis 4)) ¦ Panel: Control Cabinet CA1 (Bay 4) ¦ Net: EN4TR DLR Ring Node 4 (192.168.1.13) ¦ Total Points: 32 (Active: 11, Spare: 21 / 65.6%) | [16 empty] | Destination: IS-JB-608, JB-606
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C4-S01-P00 | 1 | 0 | 1 | 1756-IB32 | FT-60203_DI_1 | Pin 1 | C4S1:1/C4S01-X1:1 | DI | 24VDC Dry Contact | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S01-X1 | - | FT-60203 |  | 3-25-01-602-PD-09
C4-S01-P01 | 1 | 1 | 2 | 1756-IB32 | LSH-60250_DI_1 | Pin 2 | C4S1:2/C4S01-X1:2 | DI | 24VDC Dry Contact | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S01-X1 | - | LSH-60250 |  | 3-25-01-602-PD-05
C4-S01-P02 | 1 | 2 | 3 | 1756-IB32 | XA-60261_DI_1 | Pin 3 | C4S1:3/C4S01-X1:3 | DI | 24VDC Dry Contact | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S01-X1 | - | XA-60261 |  | -
C4-S01-P03 | 1 | 3 | 4 | 1756-IB32 | XA-60262_DI_1 | Pin 4 | C4S1:4/C4S01-X1:4 | DI | 24VDC Dry Contact | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S01-X1 | - | XA-60262 |  | -
C4-S01-P04 | 1 | 4 | 5 | 1756-IB32 | Spare_DI_0 | Pin 5 | C4S1:5/C4S01-X1:5 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P05 | 1 | 5 | 6 | 1756-IB32 | Spare_DI_0 | Pin 6 | C4S1:6/C4S01-X1:6 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P06 | 1 | 6 | 7 | 1756-IB32 | Spare_DI_0 | Pin 7 | C4S1:7/C4S01-X1:7 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P07 | 1 | 7 | 8 | 1756-IB32 | Spare_DI_0 | Pin 8 | C4S1:8/C4S01-X1:8 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P08 | 1 | 8 | 9 | 1756-IB32 | Spare_DI_0 | Pin 9 | C4S1:9/C4S01-X1:9 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P09 | 1 | 9 | 10 | 1756-IB32 | Spare_DI_0 | Pin 10 | C4S1:10/C4S01-X1:10 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P10 | 1 | 10 | 11 | 1756-IB32 | Spare_DI_0 | Pin 11 | C4S1:11/C4S01-X1:11 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P11 | 1 | 11 | 12 | 1756-IB32 | Spare_DI_0 | Pin 12 | C4S1:12/C4S01-X1:12 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P12 | 1 | 12 | 13 | 1756-IB32 | Spare_DI_0 | Pin 13 | C4S1:13/C4S01-X1:13 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P13 | 1 | 13 | 14 | 1756-IB32 | Spare_DI_0 | Pin 14 | C4S1:14/C4S01-X1:14 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P14 | 1 | 14 | 15 | 1756-IB32 | Spare_DI_0 | Pin 15 | C4S1:15/C4S01-X1:15 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P15 | 1 | 15 | 16 | 1756-IB32 | Spare_DI_0 | Pin 16 | C4S1:16/C4S01-X1:16 | DI | 24VDC Dry Contact | SPARE | JB-606 | Spray Dryer 6th Floor | - | C4S01-X1 | - | Spare | Spare Channel | -
C4-S01-P16 | 1 | 16 | 17 | 1756-IB32 | ZS-60201A_DI_1 | Pin 17 | C4S1:17/C4S01-X2:17 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S01-X2 | - | ZS-60201A |  | 3-25-01-602-PD-04
C4-S01-P17 | 1 | 17 | 18 | 1756-IB32 | ZS-60201B_DI_1 | Pin 18 | C4S1:18/C4S01-X2:18 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S01-X2 | - | ZS-60201B |  | 3-25-01-602-PD-04
C4-S01-P18 | 1 | 18 | 19 | 1756-IB32 | ZS-60231C_DI_1 | Pin 19 | C4S1:19/C4S01-X2:19 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231C |  | 3-25-01-602-PD-04
C4-S01-P19 | 1 | 19 | 20 | 1756-IB32 | ZS-60231D_DI_1 | Pin 20 | C4S1:20/C4S01-X2:20 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231D |  | 3-25-01-602-PD-04
C4-S01-P20 | 1 | 20 | 21 | 1756-IB32 | ZS-60231E_DI_1 | Pin 21 | C4S1:21/C4S01-X2:21 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231E |  | 3-25-01-602-PD-05
C4-S01-P21 | 1 | 21 | 22 | 1756-IB32 | ZS-60231F_DI_1 | Pin 22 | C4S1:22/C4S01-X2:22 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S01-X2 | - | ZS-60231F |  | 3-25-01-602-PD-05
C4-S01-P22 | 1 | 22 | 23 | 1756-IB32 | ZS-60240_DI_1 | Pin 23 | C4S1:23/C4S01-X2:23 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S01-X2 | - | ZS-60240 |  | 3-25-01-602-PD-05
C4-S01-P23 | 1 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C4S1:24/C4S01-X2:24 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P24 | 1 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C4S1:25/C4S01-X2:25 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P25 | 1 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C4S1:26/C4S01-X2:26 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P26 | 1 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C4S1:27/C4S01-X2:27 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P27 | 1 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C4S1:28/C4S01-X2:28 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P28 | 1 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C4S1:29/C4S01-X2:29 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P29 | 1 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C4S1:30/C4S01-X2:30 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P30 | 1 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C4S1:31/C4S01-X2:31 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -
C4-S01-P31 | 1 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C4S1:32/C4S01-X2:32 | DI | 24VDC Dry Contact | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S01-X2 | - | Spare | Spare Channel | -

## Slot_02
KALASIN ENGINEERING — C4 SLOT 02 (1756-IB32 • DI)
Chassis: C4 (I/O Expansion Rack 3 (Chassis 4)) ¦ Panel: Control Cabinet CA1 (Bay 4) ¦ Net: EN4TR DLR Ring Node 4 (192.168.1.13) ¦ Total Points: 32 (Active: 17, Spare: 15 / 46.9%) | [16 empty] | Destination: JB-612
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C4-S02-P00 | 2 | 0 | 1 | 1756-IB32 | PSL-61305_DI_1 | Pin 1 | C4S2:1/C4S02-X1:1 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | PSL-61305 |  | 3-25-01-613-PD-03
C4-S02-P01 | 2 | 1 | 2 | 1756-IB32 | PSL-61306_DI_1 | Pin 2 | C4S2:2/C4S02-X1:2 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | PSL-61306 |  | 3-25-01-613-PD-05
C4-S02-P02 | 2 | 2 | 3 | 1756-IB32 | PVM-61301_DI_1 | Pin 3 | C4S2:3/C4S02-X1:3 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | PVM-61301 |  | -
C4-S02-P03 | 2 | 3 | 4 | 1756-IB32 | PVM-61301_DI_2 | Pin 4 | C4S2:4/C4S02-X1:4 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | PVM-61301 |  | -
C4-S02-P04 | 2 | 4 | 5 | 1756-IB32 | XA-61301A_DI_1 | Pin 5 | C4S2:5/C4S02-X1:5 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301A |  | -
C4-S02-P05 | 2 | 5 | 6 | 1756-IB32 | XA-61301B_DI_1 | Pin 6 | C4S2:6/C4S02-X1:6 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301B |  | -
C4-S02-P06 | 2 | 6 | 7 | 1756-IB32 | XA-61301C_DI_1 | Pin 7 | C4S2:7/C4S02-X1:7 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301C |  | -
C4-S02-P07 | 2 | 7 | 8 | 1756-IB32 | XA-61301D_DI_1 | Pin 8 | C4S2:8/C4S02-X1:8 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301D |  | -
C4-S02-P08 | 2 | 8 | 9 | 1756-IB32 | XA-61301E_DI_1 | Pin 9 | C4S2:9/C4S02-X1:9 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301E |  | -
C4-S02-P09 | 2 | 9 | 10 | 1756-IB32 | XA-61301F_DI_1 | Pin 10 | C4S2:10/C4S02-X1:10 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301F |  | -
C4-S02-P10 | 2 | 10 | 11 | 1756-IB32 | XA-61301G_DI_1 | Pin 11 | C4S2:11/C4S02-X1:11 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301G |  | -
C4-S02-P11 | 2 | 11 | 12 | 1756-IB32 | XA-61301H_DI_1 | Pin 12 | C4S2:12/C4S02-X1:12 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301H |  | -
C4-S02-P12 | 2 | 12 | 13 | 1756-IB32 | XA-61301J_DI_1 | Pin 13 | C4S2:13/C4S02-X1:13 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S02-X1 | - | XA-61301J |  | -
C4-S02-P13 | 2 | 13 | 14 | 1756-IB32 | XV-61302_DI_1 | Pin 14 | C4S2:14/C4S02-X1:14 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | XV-61302 |  | 3-25-01-613-PD-02
C4-S02-P14 | 2 | 14 | 15 | 1756-IB32 | XV-61302_DI_2 | Pin 15 | C4S2:15/C4S02-X1:15 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | XV-61302 |  | 3-25-01-613-PD-02
C4-S02-P15 | 2 | 15 | 16 | 1756-IB32 | XV-61303_DI_1 | Pin 16 | C4S2:16/C4S02-X1:16 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X1 | - | XV-61303 |  | 3-25-01-613-PD-02
C4-S02-P16 | 2 | 16 | 17 | 1756-IB32 | XV-61303_DI_2 | Pin 17 | C4S2:17/C4S02-X2:17 | DI | 24VDC Dry Contact | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S02-X2 | - | XV-61303 |  | 3-25-01-613-PD-02
C4-S02-P17 | 2 | 17 | 18 | 1756-IB32 | Spare_DI_0 | Pin 18 | C4S2:18/C4S02-X2:18 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P18 | 2 | 18 | 19 | 1756-IB32 | Spare_DI_0 | Pin 19 | C4S2:19/C4S02-X2:19 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P19 | 2 | 19 | 20 | 1756-IB32 | Spare_DI_0 | Pin 20 | C4S2:20/C4S02-X2:20 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P20 | 2 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C4S2:21/C4S02-X2:21 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P21 | 2 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C4S2:22/C4S02-X2:22 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P22 | 2 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C4S2:23/C4S02-X2:23 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P23 | 2 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C4S2:24/C4S02-X2:24 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P24 | 2 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C4S2:25/C4S02-X2:25 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P25 | 2 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C4S2:26/C4S02-X2:26 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P26 | 2 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C4S2:27/C4S02-X2:27 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P27 | 2 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C4S2:28/C4S02-X2:28 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P28 | 2 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C4S2:29/C4S02-X2:29 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P29 | 2 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C4S2:30/C4S02-X2:30 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P30 | 2 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C4S2:31/C4S02-X2:31 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -
C4-S02-P31 | 2 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C4S2:32/C4S02-X2:32 | DI | 24VDC Dry Contact | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S02-X2 | - | Spare | Spare Channel | -

## Slot_03
KALASIN ENGINEERING — C4 SLOT 03 (1756-IB32 • DI)
Chassis: C4 (I/O Expansion Rack 3 (Chassis 4)) ¦ Panel: Control Cabinet CA1 (Bay 4) ¦ Net: EN4TR DLR Ring Node 4 (192.168.1.13) ¦ Total Points: 31 (Active: 15, Spare: 16 / 51.6%) | [16 empty] | Destination: IS-JB-612
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C4-S03-P00 | 3 | 0 | 1 | 1756-IB32 | ISV-61303_DI_1 | Pin 1 | C4S3:1/C4S03-X1:1 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | ISV-61303 |  | 3-25-01-613-PD-03
C4-S03-P01 | 3 | 1 | 2 | 1756-IB32 | ISV-61304_DI_1 | Pin 2 | C4S3:2/C4S03-X1:2 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | ISV-61304 |  | 3-25-01-613-PD-05
C4-S03-P02 | 3 | 2 | 3 | 1756-IB32 | LSH-61304_DI_1 | Pin 3 | C4S3:3/C4S03-X1:3 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S03-X1 | - | LSH-61304 |  | 3-25-01-613-PD-03
C4-S03-P03 | 3 | 3 | 4 | 1756-IB32 | LSH-61305_DI_1 | Pin 4 | C4S3:4/C4S03-X1:4 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S03-X1 | - | LSH-61305 |  | 3-25-01-613-PD-05
C4-S03-P04 | 3 | 4 | 5 | 1756-IB32 | LSH-61307_DI_1 | Pin 5 | C4S3:5/C4S03-X1:5 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S03-X1 | - | LSH-61307 |  | 3-25-01-613-PD-01
C4-S03-P05 | 3 | 5 | 6 | 1756-IB32 | LSH-61312_DI_1 | Pin 6 | C4S3:6/C4S03-X1:6 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | LSH-61312 |  | 3-25-01-613-PD-05
C4-S03-P06 | 3 | 6 | 7 | 1756-IB32 | PSE-61302_DI_1 | Pin 7 | C4S3:7/C4S03-X1:7 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | PSE-61302 |  | 3-25-01-613-PD-03
C4-S03-P07 | 3 | 7 | 8 | 1756-IB32 | PSE-61303_DI_1 | Pin 8 | C4S3:8/C4S03-X1:8 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | PSE-61303 |  | 3-25-01-613-PD-05
C4-S03-P09 | 3 | 9 | 10 | 1756-IB32 | RV-61301_DI_1 | Pin 10 | C4S3:10/C4S03-X1:10 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | RV-61301 |  | -
C4-S03-P10 | 3 | 10 | 11 | 1756-IB32 | RV-61304_DI_1 | Pin 11 | C4S3:11/C4S03-X1:11 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | RV-61304 |  | -
C4-S03-P11 | 3 | 11 | 12 | 1756-IB32 | RV-61305_DI_1 | Pin 12 | C4S3:12/C4S03-X1:12 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | RV-61305 |  | -
C4-S03-P12 | 3 | 12 | 13 | 1756-IB32 | SC-61301_DI_1 | Pin 13 | C4S3:13/C4S03-X1:13 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | SC-61301 |  | -
C4-S03-P13 | 3 | 13 | 14 | 1756-IB32 | SC-61302_DI_1 | Pin 14 | C4S3:14/C4S03-X1:14 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S03-X1 | - | SC-61302 |  | -
C4-S03-P14 | 3 | 14 | 15 | 1756-IB32 | ZS-61312_DI_1 | Pin 15 | C4S3:15/C4S03-X1:15 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 3rd / Packing Tower | C4S03-X1 | - | ZS-61312 |  | 3-25-01-613-PD-01
C4-S03-P15 | 3 | 15 | 16 | 1756-IB32 | ZS-61313_DI_1 | Pin 16 | C4S3:16/C4S03-X1:16 | DI | 24VDC Dry Contact | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 3rd / Packing Tower | C4S03-X1 | - | ZS-61313 |  | 3-25-01-613-PD-01
C4-S03-P16 | 3 | 16 | 17 | 1756-IB32 | Spare_DI_0 | Pin 17 | C4S3:17/C4S03-X2:17 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P17 | 3 | 17 | 18 | 1756-IB32 | Spare_DI_0 | Pin 18 | C4S3:18/C4S03-X2:18 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P18 | 3 | 18 | 19 | 1756-IB32 | Spare_DI_0 | Pin 19 | C4S3:19/C4S03-X2:19 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P19 | 3 | 19 | 20 | 1756-IB32 | Spare_DI_0 | Pin 20 | C4S3:20/C4S03-X2:20 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P20 | 3 | 20 | 21 | 1756-IB32 | Spare_DI_0 | Pin 21 | C4S3:21/C4S03-X2:21 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P21 | 3 | 21 | 22 | 1756-IB32 | Spare_DI_0 | Pin 22 | C4S3:22/C4S03-X2:22 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P22 | 3 | 22 | 23 | 1756-IB32 | Spare_DI_0 | Pin 23 | C4S3:23/C4S03-X2:23 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P23 | 3 | 23 | 24 | 1756-IB32 | Spare_DI_0 | Pin 24 | C4S3:24/C4S03-X2:24 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P24 | 3 | 24 | 25 | 1756-IB32 | Spare_DI_0 | Pin 25 | C4S3:25/C4S03-X2:25 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P25 | 3 | 25 | 26 | 1756-IB32 | Spare_DI_0 | Pin 26 | C4S3:26/C4S03-X2:26 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P26 | 3 | 26 | 27 | 1756-IB32 | Spare_DI_0 | Pin 27 | C4S3:27/C4S03-X2:27 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P27 | 3 | 27 | 28 | 1756-IB32 | Spare_DI_0 | Pin 28 | C4S3:28/C4S03-X2:28 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P28 | 3 | 28 | 29 | 1756-IB32 | Spare_DI_0 | Pin 29 | C4S3:29/C4S03-X2:29 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P29 | 3 | 29 | 30 | 1756-IB32 | Spare_DI_0 | Pin 30 | C4S3:30/C4S03-X2:30 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P30 | 3 | 30 | 31 | 1756-IB32 | Spare_DI_0 | Pin 31 | C4S3:31/C4S03-X2:31 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -
C4-S03-P31 | 3 | 31 | 32 | 1756-IB32 | Spare_DI_0 | Pin 32 | C4S3:32/C4S03-X2:32 | DI | 24VDC Dry Contact | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S03-X2 | - | Spare | Spare Channel | -

## Slot_04
KALASIN ENGINEERING — C4 SLOT 04 (1756-OB32 • DO)
Chassis: C4 (I/O Expansion Rack 3 (Chassis 4)) ¦ Panel: Control Cabinet CA1 (Bay 4) ¦ Net: EN4TR DLR Ring Node 4 (192.168.1.13) ¦ Total Points: 32 (Active: 17, Spare: 15 / 46.9%) | [16 empty] | Destination: IS-JB-608, JB-606, J
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C4-S04-P00 | 4 | 0 | 1 | 1756-OB32 | SV-60220_DO_1 | Pin 1 | C4S4:1/C4S04-X1:1 | DO | 24VDC Sourcing | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S04-X1 | - | SV-60220 |  | 3-25-01-602-PD-04
C4-S04-P01 | 4 | 1 | 2 | 1756-OB32 | Spare_DO_0 | Pin 2 | C4S4:2/C4S04-X1:2 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P02 | 4 | 2 | 3 | 1756-OB32 | Spare_DO_0 | Pin 3 | C4S4:3/C4S04-X1:3 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P03 | 4 | 3 | 4 | 1756-OB32 | Spare_DO_0 | Pin 4 | C4S4:4/C4S04-X1:4 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P04 | 4 | 4 | 5 | 1756-OB32 | Spare_DO_0 | Pin 5 | C4S4:5/C4S04-X1:5 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P05 | 4 | 5 | 6 | 1756-OB32 | Spare_DO_0 | Pin 6 | C4S4:6/C4S04-X1:6 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P06 | 4 | 6 | 7 | 1756-OB32 | Spare_DO_0 | Pin 7 | C4S4:7/C4S04-X1:7 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P07 | 4 | 7 | 8 | 1756-OB32 | Spare_DO_0 | Pin 8 | C4S4:8/C4S04-X1:8 | DO | 24VDC Sourcing | SPARE | JB-606 | Spray Dryer 6th Floor | Spray Dryer | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P08 | 4 | 8 | 9 | 1756-OB32 | XA-60201_DO_1 | Pin 9 | C4S4:9/C4S04-X1:9 | DO | 24VDC Sourcing | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S04-X1 | - | XA-60201 |  | 3-25-01-602-PD-03
C4-S04-P09 | 4 | 9 | 10 | 1756-OB32 | Spare_DO_0 | Pin 10 | C4S4:10/C4S04-X1:10 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P10 | 4 | 10 | 11 | 1756-OB32 | Spare_DO_0 | Pin 11 | C4S4:11/C4S04-X1:11 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P11 | 4 | 11 | 12 | 1756-OB32 | Spare_DO_0 | Pin 12 | C4S4:12/C4S04-X1:12 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P12 | 4 | 12 | 13 | 1756-OB32 | Spare_DO_0 | Pin 13 | C4S4:13/C4S04-X1:13 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P13 | 4 | 13 | 14 | 1756-OB32 | Spare_DO_0 | Pin 14 | C4S4:14/C4S04-X1:14 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P14 | 4 | 14 | 15 | 1756-OB32 | Spare_DO_0 | Pin 15 | C4S4:15/C4S04-X1:15 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P15 | 4 | 15 | 16 | 1756-OB32 | Spare_DO_0 | Pin 16 | C4S4:16/C4S04-X1:16 | DO | 24VDC Sourcing | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S04-X1 | - | Spare | Spare Channel | -
C4-S04-P16 | 4 | 16 | 17 | 1756-OB32 | PVM-61301_DO_1 | Pin 17 | C4S4:17/C4S04-X2:17 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | PVM-61301 |  | -
C4-S04-P17 | 4 | 17 | 18 | 1756-OB32 | PVM-61301_DO_2 | Pin 18 | C4S4:18/C4S04-X2:18 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | PVM-61301 |  | -
C4-S04-P18 | 4 | 18 | 19 | 1756-OB32 | SV-61307_DO_1 | Pin 19 | C4S4:19/C4S04-X2:19 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 3rd / Packing Tower | C4S04-X2 | - | SV-61307 |  | 3-25-01-613-PD-01
C4-S04-P19 | 4 | 19 | 20 | 1756-OB32 | SV-61308_DO_1 | Pin 20 | C4S4:20/C4S04-X2:20 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | SV-61308 |  | -
C4-S04-P20 | 4 | 20 | 21 | 1756-OB32 | SV-61309_DO_1 | Pin 21 | C4S4:21/C4S04-X2:21 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | SV-61309 |  | 3-25-01-613-PD-03
C4-S04-P21 | 4 | 21 | 22 | 1756-OB32 | SV-61310_DO_1 | Pin 22 | C4S4:22/C4S04-X2:22 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | SV-61310 |  | -
C4-S04-P22 | 4 | 22 | 23 | 1756-OB32 | SV-61311_DO_1 | Pin 23 | C4S4:23/C4S04-X2:23 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | SV-61311 |  | 3-25-01-613-PD-05
C4-S04-P23 | 4 | 23 | 24 | 1756-OB32 | XS-61301A_DO_1 | Pin 24 | C4S4:24/C4S04-X2:24 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301A |  | -
C4-S04-P24 | 4 | 24 | 25 | 1756-OB32 | XS-61301B_DO_1 | Pin 25 | C4S4:25/C4S04-X2:25 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301B |  | -
C4-S04-P25 | 4 | 25 | 26 | 1756-OB32 | XS-61301C_DO_1 | Pin 26 | C4S4:26/C4S04-X2:26 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301C |  | -
C4-S04-P26 | 4 | 26 | 27 | 1756-OB32 | XS-61301D_DO_1 | Pin 27 | C4S4:27/C4S04-X2:27 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301D |  | -
C4-S04-P27 | 4 | 27 | 28 | 1756-OB32 | XS-61301E_DO_1 | Pin 28 | C4S4:28/C4S04-X2:28 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301E |  | -
C4-S04-P28 | 4 | 28 | 29 | 1756-OB32 | XS-61301F_DO_1 | Pin 29 | C4S4:29/C4S04-X2:29 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S04-X2 | - | XS-61301F |  | -
C4-S04-P29 | 4 | 29 | 30 | 1756-OB32 | XV-61302_DO_1 | Pin 30 | C4S4:30/C4S04-X2:30 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | XV-61302 |  | 3-25-01-613-PD-02
C4-S04-P30 | 4 | 30 | 31 | 1756-OB32 | XV-61303_DO_1 | Pin 31 | C4S4:31/C4S04-X2:31 | DO | 24VDC Sourcing | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S04-X2 | - | XV-61303 |  | 3-25-01-613-PD-02
C4-S04-P31 | 4 | 31 | 32 | 1756-OB32 | Spare_DO_0 | Pin 32 | C4S4:32/C4S04-X2:32 | DO | 24VDC Sourcing | SPARE | JB-612 | Packing Tower 2th Floor | Packing Tower | C4S04-X2 | - | Spare | Spare Channel | -

## Slot_05
KALASIN ENGINEERING — C4 SLOT 05 (1756-IF16 • AI)
Chassis: C4 (I/O Expansion Rack 3 (Chassis 4)) ¦ Panel: Control Cabinet CA1 (Bay 4) ¦ Net: EN4TR DLR Ring Node 4 (192.168.1.13) ¦ Total Points: 26 (Active: 7, Spare: 19 / 73.1%) | [16 empty] | Destination: IS-JB-608, IS-JB-612
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C4-S05-P00 | 5 | 0 | 1 | 1756-IF16 | DPT-60201_AI_1 | Pin 1 | C4S5:1/C4S05-X1:1 | AI | 4-20mA HART | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S05-X1 | - | DPT-60201 | Differential Pressure Transmitte | 3-25-01-602-PD-09
C4-S05-P01 | 5 | 1 | 2 | 1756-IF16 | FT-60203_AI_1 | Pin 2 | C4S5:2/C4S05-X1:2 | AI | 4-20mA HART | ACTIVE | JB-606 | Spray Dryer 6th Floor | 6th / Spray Dryer | C4S05-X1 | - | FT-60203 |  | 3-25-01-602-PD-09
C4-S05-P02 | 5 | 2 | 3 | 1756-IF16 | TT-60245_AI_1 | Pin 3 | C4S5:3/C4S05-X1:3 | AI | 4-20mA HART | ACTIVE | JB-608 | Spray Dryer 8th Floor | 8th / Spray Dryer | C4S05-X1 | - | TT-60245 |  | 3-25-01-602-PD-05
C4-S05-P03 | 5 | 3 | 4 | 1756-IF16 | Spare_AI_0 | Pin 4 | C4S5:4/C4S05-X1:4 | AI | 4-20mA HART | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P04 | 5 | 4 | 5 | 1756-IF16 | Spare_AI_0 | Pin 5 | C4S5:5/C4S05-X1:5 | AI | 4-20mA HART | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P05 | 5 | 5 | 6 | 1756-IF16 | Spare_AI_0 | Pin 6 | C4S5:6/C4S05-X1:6 | AI | 4-20mA HART | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P06 | 5 | 6 | 7 | 1756-IF16 | Spare_AI_0 | Pin 7 | C4S5:7/C4S05-X1:7 | AI | 4-20mA HART | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P06 | 5 | 6 | 7 | 1756-IF16 | Spare_AI_0 | Pin 7 | C4S5:7/C4S05-X1:7 | AI | 4-20mA HART | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P07 | 5 | 7 | 8 | 1756-IF16 | Spare_AI_0 | Pin 8 | C4S5:8/C4S05-X1:8 | AI | 4-20mA HART | SPARE | JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P07 | 5 | 7 | 8 | 1756-IF16 | Spare_AI_0 | Pin 8 | C4S5:8/C4S05-X1:8 | AI | 4-20mA HART | SPARE | IS-JB-608 | Spray Dryer 8th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P08 | 5 | 8 | 9 | 1756-IF16 | PT-61302_AI_1 | Pin 9 | C4S5:9/C4S05-X1:9 | AI | 4-20mA HART | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S05-X1 | - | PT-61302 | Pressure Transmitter | 3-25-01-613-PD-03
C4-S05-P09 | 5 | 9 | 10 | 1756-IF16 | PT-61309_AI_1 | Pin 10 | C4S5:10/C4S05-X1:10 | AI | 4-20mA HART | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S05-X1 | - | PT-61309 | Pressure Transmitter | 3-25-01-613-PD-04
C4-S05-P10 | 5 | 10 | 11 | 1756-IF16 | Spare_AI_0 | Pin 11 | C4S5:11/C4S05-X1:11 | AI | 4-20mA HART | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P11 | 5 | 11 | 12 | 1756-IF16 | Spare_AI_0 | Pin 12 | C4S5:12/C4S05-X1:12 | AI | 4-20mA HART | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P12 | 5 | 12 | 13 | 1756-IF16 | PT-61302_AI_1 | Pin 13 | C4S5:13/C4S05-X1:13 | AI | 4-20mA HART | ACTIVE | JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S05-X1 | - | PT-61302 | Pressure Transmitter | 3-25-01-613-PD-03
C4-S05-P13 | 5 | 13 | 14 | 1756-IF16 | PT-61309_AI_1 | Pin 14 | C4S5:14/C4S05-X1:14 | AI | 4-20mA HART | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C4S05-X1 | - | PT-61309 | Pressure Transmitter | 3-25-01-613-PD-04
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P14 | 5 | 14 | 15 | 1756-IF16 | Spare_AI_0 | Pin 15 | C4S5:15/C4S05-X1:15 | AI | 4-20mA HART | SPARE | IS-JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -
C4-S05-P15 | 5 | 15 | 16 | 1756-IF16 | Spare_AI_0 | Pin 16 | C4S5:16/C4S05-X1:16 | AI | 4-20mA HART | SPARE | JB-612 | Packing Tower 2th Floor | - | C4S05-X1 | - | Spare | Spare Channel | -

## Slot_06
KALASIN ENGINEERING — C4 SLOT 06 (1756-IF16 • AI)
Chassis: C4 (I/O Expansion Rack 3 (Chassis 4)) ¦ Panel: Control Cabinet CA1 (Bay 4) ¦ Net: EN4TR DLR Ring Node 4 (192.168.1.13) ¦ Total Points: 8 (Active: 8, Spare: 0 / 0.0%) | [16 empty] | Destination: IS-JB-608, IS-JB-612
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C4-S06-P00 | 6 | 0 | 1 | 1756-IF16 | PT-60220_AI_1 | Pin 1 | C4S6:1/C4S06-X1:1 | AI | 4-20mA HART | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S06-X1 | - | PT-60220 | Pressure Transmitter | 3-25-01-602-PD-04
C4-S06-P01 | 6 | 1 | 2 | 1756-IF16 | TT-60220_AI_1 | Pin 2 | C4S6:2/C4S06-X1:2 | AI | 4-20mA HART | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S06-X1 | - | TT-60220 |  | 3-25-01-602-PD-04
C4-S06-P02 | 6 | 2 | 3 | 1756-IF16 | TT-60221_AI_1 | Pin 3 | C4S6:3/C4S06-X1:3 | AI | 4-20mA HART | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 6th / Spray Dryer | C4S06-X1 | - | TT-60221 |  | 3-25-01-602-PD-04
C4-S06-P03 | 6 | 3 | 4 | 1756-IF16 | TT-60222_AI_1 | Pin 4 | C4S6:4/C4S06-X1:4 | AI | 4-20mA HART | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S06-X1 | - | TT-60222 |  | 3-25-01-602-PD-04
C4-S06-P04 | 6 | 4 | 5 | 1756-IF16 | TT-60223_AI_1 | Pin 5 | C4S6:5/C4S06-X1:5 | AI | 4-20mA HART | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S06-X1 | - | TT-60223 |  | 3-25-01-602-PD-04
C4-S06-P05 | 6 | 5 | 6 | 1756-IF16 | XT-60201_AI_1 | Pin 6 | C4S6:6/C4S06-X1:6 | AI | 4-20mA HART | ACTIVE | IS-JB-608 | Spray Dryer 8th Floor | 5th / Spray Dryer | C4S06-X1 | - | XT-60201 |  | 3-25-01-602-PD-03
C4-S06-P06 | 6 | 6 | 7 | 1756-IF16 | DPT-61310_AI_1 | Pin 7 | C4S6:7/C4S06-X1:7 | AI | 4-20mA HART | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S06-X1 | - | DPT-61310 | Differential Pressure Transmitte | 3-25-01-613-PD-03
C4-S06-P07 | 6 | 7 | 8 | 1756-IF16 | DPT-61312_AI_1 | Pin 8 | C4S6:8/C4S06-X1:8 | AI | 4-20mA HART | ACTIVE | IS-JB-612 | Packing Tower 2th Floor | 2nd / Packing Tower | C4S06-X1 | - | DPT-61312 |  | 3-25-01-613-PD-05