## C7_Slot_Summary
KALASIN ENGINEERING — C7 (MCC FIELDBUS & NETWORK INTERFACE (CHASSIS 7))
Location: Motor Control Center Room (MCC Panel & Field Bus) ¦ Net: Modbus TCP / EtherNet Trunk ¦ Total Active Slots: 8
Slot No. | Module Model | I/O Type | Capacity | Active Points | Spare Points | Spare % | Primary Destinations | Sheet Link
Slot 00 | I/O Module | BUS | 20 | 20 | 0 | 0.0% | JB-601, JB-607, JB-612, MCC | Go to Slot 00 ➔
Slot 01 | I/O Module | DI | 32 | 24 | 8 | 25.0% | MCC | Go to Slot 01 ➔
Slot 02 | I/O Module | DI | 32 | 32 | 0 | 0.0% | JB-601, MCC | Go to Slot 02 ➔
Slot 03 | I/O Module | DI | 26 | 26 | 0 | 0.0% | JB-601, MCC | Go to Slot 03 ➔
Slot 04 | I/O Module | DI | 28 | 0 | 28 | 100.0% | MCC | Go to Slot 04 ➔
Slot 05 | I/O Module | DO | 32 | 24 | 8 | 25.0% | MCC | Go to Slot 05 ➔
Slot 06 | I/O Module | DO | 32 | 32 | 0 | 0.0% | JB-601, MCC | Go to Slot 06 ➔
Slot 07 | I/O Module | DO | 24 | 0 | 24 | 100.0% | MCC | Go to Slot 07 ➔

## Slot_00
KALASIN ENGINEERING — C7 SLOT 00 (I/O Module • BUS)
Chassis: C7 (MCC Fieldbus & Network Interface (Chassis 7)) ¦ Panel: Motor Control Center Room (MCC Panel & Field Bus) ¦ Net: Modbus TCP / EtherNet Trunk ¦ Total Points: 20 (Active: 20, Spare: 0 / 0.0%) | [16 empty] | Destination: JB-601, JB-607, JB-6
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C7-S00-P00 | 0 | 0 | 1 |  | ATY-40201_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S00- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01
C7-S00-P00 | 0 | 0 | 1 |  | ATY-40202_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S00- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01
C7-S00-P00 | 0 | 0 | 1 |  | ATY-40203_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S00- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02
C7-S00-P00 | 0 | 0 | 1 |  | BFY-60206_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S00- | - | BFY-60206 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-60210_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S00- | - | BFY-60210 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-60211_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S00- | - | BFY-60211 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-60220_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S00- | - | BFY-60220 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-60240_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S00- | - | BFY-60240 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-61301_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S00- | - | BFY-61301 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-61302_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 2nd / Packing Tower | C7S00- | - | BFY-61302 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | BFY-61303_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S00- | - | BFY-61303 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | COM-FH-60210B_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | JB-607 | Spray Dryer 7th Floor | 7th / Spray Dryer | C7S00- | - | COM-FH-60210B |  | -
C7-S00-P00 | 0 | 0 | 1 |  | Communication Signal_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | JB-612 | Packing Tower 2th Floor | 1st / Packing Tower | C7S00- | - | Communication Signal |  | -
C7-S00-P00 | 0 | 0 | 1 |  | PCY-40201_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S00- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01
C7-S00-P00 | 0 | 0 | 1 |  | PCY-40202_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S00- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01
C7-S00-P00 | 0 | 0 | 1 |  | PCY-40203_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S00- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02
C7-S00-P00 | 0 | 0 | 1 |  | PCY-60205_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S00- | - | PCY-60205 |  | -
C7-S00-P00 | 0 | 0 | 1 |  | PCY-60215_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S00- | - | PCY-60215 | PUMP | -
C7-S00-P00 | 0 | 0 | 1 |  | PCY-814201_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C7S00- | - | PCY-814201 | PUMP | -
C7-S00-P00 | 0 | 0 | 1 |  | PCY-814202_BUS_1 | Pin 1 | C7S0:1/C7S00-:1 | BUS | 4-20mA HART | ACTIVE | MCC | MCC Room | 2nd / CIP Water System | C7S00- | - | PCY-814202 | PUMP | -

## Slot_01
KALASIN ENGINEERING — C7 SLOT 01 (I/O Module • DI)
Chassis: C7 (MCC Fieldbus & Network Interface (Chassis 7)) ¦ Panel: Motor Control Center Room (MCC Panel & Field Bus) ¦ Net: Modbus TCP / EtherNet Trunk ¦ Total Points: 32 (Active: 24, Spare: 8 / 25.0%) | [16 empty] | Destination: MCC
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C7-S01-P00 | 1 | 0 | 1 |  | Spare_DI_0 | Pin 1 | C7S1:1/C7S01-:1 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P01 | 1 | 1 | 2 |  | Spare_DI_0 | Pin 2 | C7S1:2/C7S01-:2 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P02 | 1 | 2 | 3 |  | Spare_DI_0 | Pin 3 | C7S1:3/C7S01-:3 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P03 | 1 | 3 | 4 |  | Spare_DI_0 | Pin 4 | C7S1:4/C7S01-:4 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P04 | 1 | 4 | 5 |  | Spare_DI_0 | Pin 5 | C7S1:5/C7S01-:5 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P05 | 1 | 5 | 6 |  | Spare_DI_0 | Pin 6 | C7S1:6/C7S01-:6 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P06 | 1 | 6 | 7 |  | Spare_DI_0 | Pin 7 | C7S1:7/C7S01-:7 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P07 | 1 | 7 | 8 |  | Spare_DI_0 | Pin 8 | C7S1:8/C7S01-:8 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S01-P08 | 1 | 8 | 9 |  | ATY-40201_DI_1 | Pin 9 | C7S1:9/C7S01-:9 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01
C7-S01-P09 | 1 | 9 | 10 |  | ATY-40201_DI_2 | Pin 10 | C7S1:10/C7S01-:10 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01
C7-S01-P10 | 1 | 10 | 11 |  | ATY-40201_DI_3 | Pin 11 | C7S1:11/C7S01-:11 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01
C7-S01-P11 | 1 | 11 | 12 |  | ATY-40202_DI_1 | Pin 12 | C7S1:12/C7S01-:12 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01
C7-S01-P12 | 1 | 12 | 13 |  | ATY-40202_DI_2 | Pin 13 | C7S1:13/C7S01-:13 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01
C7-S01-P13 | 1 | 13 | 14 |  | ATY-40202_DI_3 | Pin 14 | C7S1:14/C7S01-:14 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01
C7-S01-P14 | 1 | 14 | 15 |  | ATY-40203_DI_1 | Pin 15 | C7S1:15/C7S01-:15 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02
C7-S01-P15 | 1 | 15 | 16 |  | ATY-40203_DI_2 | Pin 16 | C7S1:16/C7S01-:16 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02
C7-S01-P16 | 1 | 16 | 17 |  | ATY-40203_DI_3 | Pin 17 | C7S1:17/C7S01-:17 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02
C7-S01-P17 | 1 | 17 | 18 |  | PCY-40201_DI_1 | Pin 18 | C7S1:18/C7S01-:18 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01
C7-S01-P18 | 1 | 18 | 19 |  | PCY-40201_DI_2 | Pin 19 | C7S1:19/C7S01-:19 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01
C7-S01-P19 | 1 | 19 | 20 |  | PCY-40201_DI_3 | Pin 20 | C7S1:20/C7S01-:20 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01
C7-S01-P20 | 1 | 20 | 21 |  | PCY-40202_DI_1 | Pin 21 | C7S1:21/C7S01-:21 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01
C7-S01-P21 | 1 | 21 | 22 |  | PCY-40202_DI_2 | Pin 22 | C7S1:22/C7S01-:22 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01
C7-S01-P22 | 1 | 22 | 23 |  | PCY-40202_DI_3 | Pin 23 | C7S1:23/C7S01-:23 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S01- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01
C7-S01-P23 | 1 | 23 | 24 |  | PCY-40203_DI_1 | Pin 24 | C7S1:24/C7S01-:24 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02
C7-S01-P24 | 1 | 24 | 25 |  | PCY-40203_DI_2 | Pin 25 | C7S1:25/C7S01-:25 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02
C7-S01-P25 | 1 | 25 | 26 |  | PCY-40203_DI_3 | Pin 26 | C7S1:26/C7S01-:26 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S01- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02
C7-S01-P26 | 1 | 26 | 27 |  | BFY-60206_DI_1 | Pin 27 | C7S1:27/C7S01-:27 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | BFY-60206 |  | -
C7-S01-P27 | 1 | 27 | 28 |  | PCM-60205-2_DI_1 | Pin 28 | C7S1:28/C7S01-:28 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-2 |  | -
C7-S01-P28 | 1 | 28 | 29 |  | PCM-60205-2_DI_2 | Pin 29 | C7S1:29/C7S01-:29 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-2 |  | -
C7-S01-P29 | 1 | 29 | 30 |  | PCM-60205-3_DI_1 | Pin 30 | C7S1:30/C7S01-:30 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-3 |  | -
C7-S01-P30 | 1 | 30 | 31 |  | PCM-60205-3_DI_2 | Pin 31 | C7S1:31/C7S01-:31 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-3 |  | -
C7-S01-P31 | 1 | 31 | 32 |  | PCM-60205-4_DI_1 | Pin 32 | C7S1:32/C7S01-:32 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S01- | - | PCM-60205-4 |  | -

## Slot_02
KALASIN ENGINEERING — C7 SLOT 02 (I/O Module • DI)
Chassis: C7 (MCC Fieldbus & Network Interface (Chassis 7)) ¦ Panel: Motor Control Center Room (MCC Panel & Field Bus) ¦ Net: Modbus TCP / EtherNet Trunk ¦ Total Points: 32 (Active: 32, Spare: 0 / 0.0%) | [16 empty] | Destination: JB-601, MCC
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C7-S02-P00 | 2 | 0 | 1 |  | PCM-60205-4_DI_2 | Pin 1 | C7S2:1/C7S02-:1 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | PCM-60205-4 |  | -
C7-S02-P01 | 2 | 1 | 2 |  | PCM-60205-5_DI_1 | Pin 2 | C7S2:2/C7S02-:2 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | PCM-60205-5 |  | -
C7-S02-P02 | 2 | 2 | 3 |  | PCM-60205-5_DI_2 | Pin 3 | C7S2:3/C7S02-:3 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | PCM-60205-5 |  | -
C7-S02-P03 | 2 | 3 | 4 |  | PCY-60205_DI_1 | Pin 4 | C7S2:4/C7S02-:4 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S02- | - | PCY-60205 |  | -
C7-S02-P04 | 2 | 4 | 5 |  | PCY-60205_DI_2 | Pin 5 | C7S2:5/C7S02-:5 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S02- | - | PCY-60205 |  | -
C7-S02-P05 | 2 | 5 | 6 |  | RVM-60201_DI_1 | Pin 6 | C7S2:6/C7S02-:6 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60201 |  | -
C7-S02-P06 | 2 | 6 | 7 |  | RVM-60201_DI_2 | Pin 7 | C7S2:7/C7S02-:7 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60201 |  | -
C7-S02-P07 | 2 | 7 | 8 |  | RVM-60202_DI_1 | Pin 8 | C7S2:8/C7S02-:8 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60202 |  | -
C7-S02-P08 | 2 | 8 | 9 |  | RVM-60202_DI_2 | Pin 9 | C7S2:9/C7S02-:9 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60202 |  | -
C7-S02-P09 | 2 | 9 | 10 |  | RVM-60203_DI_1 | Pin 10 | C7S2:10/C7S02-:10 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60203 |  | -
C7-S02-P10 | 2 | 10 | 11 |  | RVM-60203_DI_2 | Pin 11 | C7S2:11/C7S02-:11 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S02- | - | RVM-60203 |  | -
C7-S02-P11 | 2 | 11 | 12 |  | BFY-60210_DI_1 | Pin 12 | C7S2:12/C7S02-:12 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | BFY-60210 |  | -
C7-S02-P12 | 2 | 12 | 13 |  | BFY-60211_DI_1 | Pin 13 | C7S2:13/C7S02-:13 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | BFY-60211 |  | -
C7-S02-P13 | 2 | 13 | 14 |  | BFY-60240_DI_1 | Pin 14 | C7S2:14/C7S02-:14 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | BFY-60240 |  | -
C7-S02-P14 | 2 | 14 | 15 |  | PCY-60215_DI_1 | Pin 15 | C7S2:15/C7S02-:15 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | PCY-60215 | PUMP | -
C7-S02-P15 | 2 | 15 | 16 |  | PCY-60215_DI_2 | Pin 16 | C7S2:16/C7S02-:16 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | PCY-60215 | PUMP | -
C7-S02-P16 | 2 | 16 | 17 |  | PCY-60215_DI_3 | Pin 17 | C7S2:17/C7S02-:17 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S02- | - | PCY-60215 | PUMP | -
C7-S02-P17 | 2 | 17 | 18 |  | BFY-60220_DI_1 | Pin 18 | C7S2:18/C7S02-:18 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S02- | - | BFY-60220 |  | -
C7-S02-P18 | 2 | 18 | 19 |  | BFY-61302_DI_1 | Pin 19 | C7S2:19/C7S02-:19 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 2nd / Packing Tower | C7S02- | - | BFY-61302 |  | -
C7-S02-P19 | 2 | 19 | 20 |  | HS-61307F_DI_1 | Pin 20 | C7S2:20/C7S02-:20 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S02- | - | HS-61307F |  | 3-25-01-613-PD-03
C7-S02-P20 | 2 | 20 | 21 |  | HS-61307G_DI_1 | Pin 21 | C7S2:21/C7S02-:21 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 3rd / Packing Tower | C7S02- | - | HS-61307G |  | 3-25-01-613-PD-03
C7-S02-P21 | 2 | 21 | 22 |  | HS-61307H_DI_1 | Pin 22 | C7S2:22/C7S02-:22 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 3rd / Packing Tower | C7S02- | - | HS-61307H |  | 3-25-01-613-PD-03
C7-S02-P22 | 2 | 22 | 23 |  | HS-61307I_DI_1 | Pin 23 | C7S2:23/C7S02-:23 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307I |  | 3-25-01-613-PD-03
C7-S02-P23 | 2 | 23 | 24 |  | HS-61307J_DI_1 | Pin 24 | C7S2:24/C7S02-:24 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307J |  | 3-25-01-613-PD-03
C7-S02-P24 | 2 | 24 | 25 |  | HS-61307K_DI_1 | Pin 25 | C7S2:25/C7S02-:25 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307K |  | 3-25-01-613-PD-03
C7-S02-P25 | 2 | 25 | 26 |  | HS-61307L_DI_1 | Pin 26 | C7S2:26/C7S02-:26 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307L |  | 3-25-01-613-PD-03
C7-S02-P26 | 2 | 26 | 27 |  | HS-61307M_DI_1 | Pin 27 | C7S2:27/C7S02-:27 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307M |  | 3-25-01-613-PD-03
C7-S02-P27 | 2 | 27 | 28 |  | HS-61307N_DI_1 | Pin 28 | C7S2:28/C7S02-:28 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307N |  | 3-25-01-613-PD-03
C7-S02-P28 | 2 | 28 | 29 |  | HS-61307O_DI_1 | Pin 29 | C7S2:29/C7S02-:29 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307O |  | 3-25-01-613-PD-03
C7-S02-P29 | 2 | 29 | 30 |  | HS-61307P_DI_1 | Pin 30 | C7S2:30/C7S02-:30 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307P |  | 3-25-01-613-PD-03
C7-S02-P30 | 2 | 30 | 31 |  | HS-61307Q_DI_1 | Pin 31 | C7S2:31/C7S02-:31 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307Q |  | 3-25-01-613-PD-03
C7-S02-P31 | 2 | 31 | 32 |  | HS-61307R_DI_1 | Pin 32 | C7S2:32/C7S02-:32 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S02- | - | HS-61307R |  | 3-25-01-613-PD-03

## Slot_03
KALASIN ENGINEERING — C7 SLOT 03 (I/O Module • DI)
Chassis: C7 (MCC Fieldbus & Network Interface (Chassis 7)) ¦ Panel: Motor Control Center Room (MCC Panel & Field Bus) ¦ Net: Modbus TCP / EtherNet Trunk ¦ Total Points: 26 (Active: 26, Spare: 0 / 0.0%) | [16 empty] | Destination: JB-601, MCC
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C7-S03-P00 | 3 | 0 | 1 |  | RVM-61302_DI_1 | Pin 1 | C7S3:1/C7S03-:1 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S03- | - | RVM-61302 |  | -
C7-S03-P01 | 3 | 1 | 2 |  | RVM-61302_DI_2 | Pin 2 | C7S3:2/C7S03-:2 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S03- | - | RVM-61302 |  | -
C7-S03-P02 | 3 | 2 | 3 |  | RVM-61303_DI_1 | Pin 3 | C7S3:3/C7S03-:3 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S03- | - | RVM-61303 |  | -
C7-S03-P03 | 3 | 3 | 4 |  | RVM-61303_DI_2 | Pin 4 | C7S3:4/C7S03-:4 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S03- | - | RVM-61303 |  | -
C7-S03-P04 | 3 | 4 | 5 |  | SCM-61301_DI_1 | Pin 5 | C7S3:5/C7S03-:5 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S03- | - | SCM-61301 |  | -
C7-S03-P05 | 3 | 5 | 6 |  | SCM-61301_DI_2 | Pin 6 | C7S3:6/C7S03-:6 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S03- | - | SCM-61301 |  | -
C7-S03-P06 | 3 | 6 | 7 |  | SCM-61302_DI_2 | Pin 7 | C7S3:7/C7S03-:7 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S03- | - | SCM-61302 |  | -
C7-S03-P07 | 3 | 7 | 8 |  | SCM-61302_DI_1 | Pin 8 | C7S3:8/C7S03-:8 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S03- | - | SCM-61302 |  | -
C7-S03-P08 | 3 | 8 | 9 |  | BFY-61301_DI_1 | Pin 9 | C7S3:9/C7S03-:9 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S03- | - | BFY-61301 |  | -
C7-S03-P09 | 3 | 9 | 10 |  | BFY-61303_DI_1 | Pin 10 | C7S3:10/C7S03-:10 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | BFY-61303 |  | -
C7-S03-P10 | 3 | 10 | 11 |  | BLM-61302_DI_1 | Pin 11 | C7S3:11/C7S03-:11 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S03- | - | BLM-61302 |  | -
C7-S03-P11 | 3 | 11 | 12 |  | BLM-61302_DI_2 | Pin 12 | C7S3:12/C7S03-:12 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S03- | - | BLM-61302 |  | -
C7-S03-P12 | 3 | 12 | 13 |  | HS-61307A_DI_1 | Pin 13 | C7S3:13/C7S03-:13 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S03- | - | HS-61307A |  | 3-25-01-613-PD-03
C7-S03-P13 | 3 | 13 | 14 |  | HS-61307B_DI_1 | Pin 14 | C7S3:14/C7S03-:14 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S03- | - | HS-61307B |  | 3-25-01-613-PD-03
C7-S03-P14 | 3 | 14 | 15 |  | HS-61307C_DI_1 | Pin 15 | C7S3:15/C7S03-:15 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 7th / Packing Tower | C7S03- | - | HS-61307C |  | 3-25-01-613-PD-03
C7-S03-P15 | 3 | 15 | 16 |  | HS-61307D_DI_1 | Pin 16 | C7S3:16/C7S03-:16 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S03- | - | HS-61307D |  | 3-25-01-613-PD-03
C7-S03-P16 | 3 | 16 | 17 |  | HS-61307E_DI_1 | Pin 17 | C7S3:17/C7S03-:17 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S03- | - | HS-61307E |  | 3-25-01-613-PD-03
C7-S03-P17 | 3 | 17 | 18 |  | RVM-60204_DI_1 | Pin 18 | C7S3:18/C7S03-:18 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-60204 |  | -
C7-S03-P18 | 3 | 18 | 19 |  | RVM-60204_DI_2 | Pin 19 | C7S3:19/C7S03-:19 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-60204 |  | -
C7-S03-P19 | 3 | 19 | 20 |  | RVM-61301_DI_1 | Pin 20 | C7S3:20/C7S03-:20 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 6th / Packing Tower | C7S03- | - | RVM-61301 |  | -
C7-S03-P20 | 3 | 20 | 21 |  | RVM-61301_DI_2 | Pin 21 | C7S3:21/C7S03-:21 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 6th / Packing Tower | C7S03- | - | RVM-61301 |  | -
C7-S03-P21 | 3 | 21 | 22 |  | RVM-61304_DI_1 | Pin 22 | C7S3:22/C7S03-:22 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-61304 |  | -
C7-S03-P22 | 3 | 22 | 23 |  | RVM-61304_DI_2 | Pin 23 | C7S3:23/C7S03-:23 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-61304 |  | -
C7-S03-P23 | 3 | 23 | 24 |  | RVM-61305_DI_1 | Pin 24 | C7S3:24/C7S03-:24 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-61305 |  | -
C7-S03-P24 | 3 | 24 | 25 |  | RVM-61305_DI_2 | Pin 25 | C7S3:25/C7S03-:25 | DI | 24VDC Dry Contact | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S03- | - | RVM-61305 |  | -
C7-S03-P25 | 3 | 25 | 26 |  | PCY-60205_DI_3 | Pin 26 | C7S3:26/C7S03-:26 | DI | 24VDC Dry Contact | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S03- | - | PCY-60205 |  | -

## Slot_04
KALASIN ENGINEERING — C7 SLOT 04 (I/O Module • DI)
Chassis: C7 (MCC Fieldbus & Network Interface (Chassis 7)) ¦ Panel: Motor Control Center Room (MCC Panel & Field Bus) ¦ Net: Modbus TCP / EtherNet Trunk ¦ Total Points: 28 (Active: 0, Spare: 28 / 100.0%) | [16 empty] | Destination: MCC
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C7-S04-P04 | 4 | 4 | 5 |  | Spare_DI_0 | Pin 5 | C7S4:5/C7S04-:5 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P05 | 4 | 5 | 6 |  | Spare_DI_0 | Pin 6 | C7S4:6/C7S04-:6 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P06 | 4 | 6 | 7 |  | Spare_DI_0 | Pin 7 | C7S4:7/C7S04-:7 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P07 | 4 | 7 | 8 |  | Spare_DI_0 | Pin 8 | C7S4:8/C7S04-:8 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P08 | 4 | 8 | 9 |  | Spare_DI_0 | Pin 9 | C7S4:9/C7S04-:9 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P09 | 4 | 9 | 10 |  | Spare_DI_0 | Pin 10 | C7S4:10/C7S04-:10 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P10 | 4 | 10 | 11 |  | Spare_DI_0 | Pin 11 | C7S4:11/C7S04-:11 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P11 | 4 | 11 | 12 |  | Spare_DI_0 | Pin 12 | C7S4:12/C7S04-:12 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P12 | 4 | 12 | 13 |  | Spare_DI_0 | Pin 13 | C7S4:13/C7S04-:13 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P13 | 4 | 13 | 14 |  | Spare_DI_0 | Pin 14 | C7S4:14/C7S04-:14 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P14 | 4 | 14 | 15 |  | Spare_DI_0 | Pin 15 | C7S4:15/C7S04-:15 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P15 | 4 | 15 | 16 |  | Spare_DI_0 | Pin 16 | C7S4:16/C7S04-:16 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P16 | 4 | 16 | 17 |  | Spare_DI_0 | Pin 17 | C7S4:17/C7S04-:17 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P17 | 4 | 17 | 18 |  | Spare_DI_0 | Pin 18 | C7S4:18/C7S04-:18 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P18 | 4 | 18 | 19 |  | Spare_DI_0 | Pin 19 | C7S4:19/C7S04-:19 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P19 | 4 | 19 | 20 |  | Spare_DI_0 | Pin 20 | C7S4:20/C7S04-:20 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P20 | 4 | 20 | 21 |  | Spare_DI_0 | Pin 21 | C7S4:21/C7S04-:21 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P21 | 4 | 21 | 22 |  | Spare_DI_0 | Pin 22 | C7S4:22/C7S04-:22 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P22 | 4 | 22 | 23 |  | Spare_DI_0 | Pin 23 | C7S4:23/C7S04-:23 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P23 | 4 | 23 | 24 |  | Spare_DI_0 | Pin 24 | C7S4:24/C7S04-:24 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P24 | 4 | 24 | 25 |  | Spare_DI_0 | Pin 25 | C7S4:25/C7S04-:25 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P25 | 4 | 25 | 26 |  | Spare_DI_0 | Pin 26 | C7S4:26/C7S04-:26 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P26 | 4 | 26 | 27 |  | Spare_DI_0 | Pin 27 | C7S4:27/C7S04-:27 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P27 | 4 | 27 | 28 |  | Spare_DI_0 | Pin 28 | C7S4:28/C7S04-:28 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P28 | 4 | 28 | 29 |  | Spare_DI_0 | Pin 29 | C7S4:29/C7S04-:29 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P29 | 4 | 29 | 30 |  | Spare_DI_0 | Pin 30 | C7S4:30/C7S04-:30 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P30 | 4 | 30 | 31 |  | Spare_DI_0 | Pin 31 | C7S4:31/C7S04-:31 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -
C7-S04-P31 | 4 | 31 | 32 |  | Spare_DI_0 | Pin 32 | C7S4:32/C7S04-:32 | DI | 24VDC Dry Contact | SPARE | MCC | MCC Room | - | C7S04- | - | Spare | Spare Channel | -

## Slot_05
KALASIN ENGINEERING — C7 SLOT 05 (I/O Module • DO)
Chassis: C7 (MCC Fieldbus & Network Interface (Chassis 7)) ¦ Panel: Motor Control Center Room (MCC Panel & Field Bus) ¦ Net: Modbus TCP / EtherNet Trunk ¦ Total Points: 32 (Active: 24, Spare: 8 / 25.0%) | [16 empty] | Destination: MCC
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C7-S05-P00 | 5 | 0 | 1 |  | Spare_DO_0 | Pin 1 | C7S5:1/C7S05-:1 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P01 | 5 | 1 | 2 |  | Spare_DO_0 | Pin 2 | C7S5:2/C7S05-:2 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P02 | 5 | 2 | 3 |  | Spare_DO_0 | Pin 3 | C7S5:3/C7S05-:3 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P03 | 5 | 3 | 4 |  | Spare_DO_0 | Pin 4 | C7S5:4/C7S05-:4 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P04 | 5 | 4 | 5 |  | Spare_DO_0 | Pin 5 | C7S5:5/C7S05-:5 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P05 | 5 | 5 | 6 |  | Spare_DO_0 | Pin 6 | C7S5:6/C7S05-:6 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P06 | 5 | 6 | 7 |  | Spare_DO_0 | Pin 7 | C7S5:7/C7S05-:7 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P07 | 5 | 7 | 8 |  | Spare_DO_0 | Pin 8 | C7S5:8/C7S05-:8 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | Spare | Spare Channel | 3-25-01-402-PD-01
C7-S05-P08 | 5 | 8 | 9 |  | ATY-40201_DO_1 | Pin 9 | C7S5:9/C7S05-:9 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | ATY-40201 | Tank Agitator | 3-25-01-402-PD-01
C7-S05-P09 | 5 | 9 | 10 |  | ATY-40202_DO_1 | Pin 10 | C7S5:10/C7S05-:10 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | ATY-40202 | Tank Agitator | 3-25-01-402-PD-01
C7-S05-P10 | 5 | 10 | 11 |  | ATY-40203_DO_1 | Pin 11 | C7S5:11/C7S05-:11 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S05- | - | ATY-40203 | Tank Agitator | 3-25-01-402-PD-02
C7-S05-P11 | 5 | 11 | 12 |  | PCY-40201_DO_1 | Pin 12 | C7S5:12/C7S05-:12 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | PCY-40201 | PUMP | 3-25-01-402-PD-01
C7-S05-P12 | 5 | 12 | 13 |  | PCY-40202_DO_1 | Pin 13 | C7S5:13/C7S05-:13 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / PH Adjustment | C7S05- | - | PCY-40202 | PUMP | 3-25-01-402-PD-01
C7-S05-P13 | 5 | 13 | 14 |  | PCY-40203_DO_1 | Pin 14 | C7S5:14/C7S05-:14 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Infeed Tank | C7S05- | - | PCY-40203 | PUMP | 3-25-01-402-PD-02
C7-S05-P14 | 5 | 14 | 15 |  | BFY-60206_DO_1 | Pin 15 | C7S5:15/C7S05-:15 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | BFY-60206 |  | -
C7-S05-P15 | 5 | 15 | 16 |  | PCM-60205-2_DO_1 | Pin 16 | C7S5:16/C7S05-:16 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-2 |  | -
C7-S05-P16 | 5 | 16 | 17 |  | PCM-60205-2_DO_2 | Pin 17 | C7S5:17/C7S05-:17 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-2 |  | -
C7-S05-P17 | 5 | 17 | 18 |  | PCM-60205-3_DO_1 | Pin 18 | C7S5:18/C7S05-:18 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-3 |  | -
C7-S05-P18 | 5 | 18 | 19 |  | PCM-60205-3_DO_2 | Pin 19 | C7S5:19/C7S05-:19 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-3 |  | -
C7-S05-P19 | 5 | 19 | 20 |  | PCM-60205-4_DO_1 | Pin 20 | C7S5:20/C7S05-:20 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-4 |  | -
C7-S05-P20 | 5 | 20 | 21 |  | PCM-60205-4_DO_2 | Pin 21 | C7S5:21/C7S05-:21 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-4 |  | -
C7-S05-P21 | 5 | 21 | 22 |  | PCM-60205-5_DO_1 | Pin 22 | C7S5:22/C7S05-:22 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-5 |  | -
C7-S05-P22 | 5 | 22 | 23 |  | PCM-60205-5_DO_2 | Pin 23 | C7S5:23/C7S05-:23 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | PCM-60205-5 |  | -
C7-S05-P23 | 5 | 23 | 24 |  | RVM-60201_DO_1 | Pin 24 | C7S5:24/C7S05-:24 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60201 |  | -
C7-S05-P24 | 5 | 24 | 25 |  | RVM-60201_DO_2 | Pin 25 | C7S5:25/C7S05-:25 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60201 |  | -
C7-S05-P25 | 5 | 25 | 26 |  | RVM-60202_DO_1 | Pin 26 | C7S5:26/C7S05-:26 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60202 |  | -
C7-S05-P26 | 5 | 26 | 27 |  | RVM-60202_DO_2 | Pin 27 | C7S5:27/C7S05-:27 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60202 |  | -
C7-S05-P27 | 5 | 27 | 28 |  | RVM-60203_DO_1 | Pin 28 | C7S5:28/C7S05-:28 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60203 |  | -
C7-S05-P28 | 5 | 28 | 29 |  | RVM-60203_DO_2 | Pin 29 | C7S5:29/C7S05-:29 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | RVM-60203 |  | -
C7-S05-P29 | 5 | 29 | 30 |  | XS-60205_DO_1 | Pin 30 | C7S5:30/C7S05-:30 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Spray Dryer | C7S05- | - | XS-60205 |  | -
C7-S05-P30 | 5 | 30 | 31 |  | BFY-60210_DO_1 | Pin 31 | C7S5:31/C7S05-:31 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S05- | - | BFY-60210 |  | -
C7-S05-P31 | 5 | 31 | 32 |  | BFY-60211_DO_1 | Pin 32 | C7S5:32/C7S05-:32 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S05- | - | BFY-60211 |  | -

## Slot_06
KALASIN ENGINEERING — C7 SLOT 06 (I/O Module • DO)
Chassis: C7 (MCC Fieldbus & Network Interface (Chassis 7)) ¦ Panel: Motor Control Center Room (MCC Panel & Field Bus) ¦ Net: Modbus TCP / EtherNet Trunk ¦ Total Points: 32 (Active: 32, Spare: 0 / 0.0%) | [16 empty] | Destination: JB-601, MCC
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C7-S06-P00 | 6 | 0 | 1 |  | BFY-60240_DO_1 | Pin 1 | C7S6:1/C7S06-:1 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S06- | - | BFY-60240 |  | -
C7-S06-P01 | 6 | 1 | 2 |  | PCY-60215_DO_1 | Pin 2 | C7S6:2/C7S06-:2 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 5th / Spray Dryer | C7S06- | - | PCY-60215 | PUMP | -
C7-S06-P02 | 6 | 2 | 3 |  | XS-60240A_DO_1 | Pin 3 | C7S6:3/C7S06-:3 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Spray Dryer | C7S06- | - | XS-60240A |  | -
C7-S06-P03 | 6 | 3 | 4 |  | XS-60241A_DO_1 | Pin 4 | C7S6:4/C7S06-:4 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Spray Dryer | C7S06- | - | XS-60241A |  | -
C7-S06-P04 | 6 | 4 | 5 |  | XS-60242A_DO_1 | Pin 5 | C7S6:5/C7S06-:5 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 3rd / Spray Dryer | C7S06- | - | XS-60242A |  | -
C7-S06-P04 | 6 | 4 | 5 |  | XS-60243A_DO_1 | Pin 5 | C7S6:5/C7S06-:5 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Spray Dryer | C7S06- | - | XS-60243A |  | -
C7-S06-P06 | 6 | 6 | 7 |  | XS-60260_DO_1 | Pin 7 | C7S6:7/C7S06-:7 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 6th / Spray Dryer | C7S06- | - | XS-60260 |  | -
C7-S06-P07 | 6 | 7 | 8 |  | BFY-60220_DO_1 | Pin 8 | C7S6:8/C7S06-:8 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S06- | - | BFY-60220 |  | -
C7-S06-P08 | 6 | 8 | 9 |  | XS-FH-60210A_DO_1 | Pin 9 | C7S6:9/C7S06-:9 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S06- | - | XS-FH-60210A |  | -
C7-S06-P09 | 6 | 9 | 10 |  | XS-FH-60210B_DO_1 | Pin 10 | C7S6:10/C7S06-:10 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 7th / Spray Dryer | C7S06- | - | XS-FH-60210B |  | -
C7-S06-P10 | 6 | 10 | 11 |  | BFY-61302_DO_1 | Pin 11 | C7S6:11/C7S06-:11 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 2nd / Packing Tower | C7S06- | - | BFY-61302 |  | -
C7-S06-P11 | 6 | 11 | 12 |  | RVM-61302_DO_1 | Pin 12 | C7S6:12/C7S06-:12 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S06- | - | RVM-61302 |  | -
C7-S06-P12 | 6 | 12 | 13 |  | RVM-61302_DO_2 | Pin 13 | C7S6:13/C7S06-:13 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S06- | - | RVM-61302 |  | -
C7-S06-P13 | 6 | 13 | 14 |  | RVM-61303_DO_1 | Pin 14 | C7S6:14/C7S06-:14 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S06- | - | RVM-61303 |  | -
C7-S06-P14 | 6 | 14 | 15 |  | RVM-61303_DO_2 | Pin 15 | C7S6:15/C7S06-:15 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 1st / Packing Tower | C7S06- | - | RVM-61303 |  | -
C7-S06-P15 | 6 | 15 | 16 |  | SCM-61301_DO_1 | Pin 16 | C7S6:16/C7S06-:16 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S06- | - | SCM-61301 |  | -
C7-S06-P16 | 6 | 16 | 17 |  | SCM-61301_DO_2 | Pin 17 | C7S6:17/C7S06-:17 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S06- | - | SCM-61301 |  | -
C7-S06-P17 | 6 | 17 | 18 |  | SCM-61302_DO_1 | Pin 18 | C7S6:18/C7S06-:18 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S06- | - | SCM-61302 |  | -
C7-S06-P18 | 6 | 18 | 19 |  | SCM-61302_DO_2 | Pin 19 | C7S6:19/C7S06-:19 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 4th / Packing Tower | C7S06- | - | SCM-61302 |  | -
C7-S06-P19 | 6 | 19 | 20 |  | BFY-61301_DO_1 | Pin 20 | C7S6:20/C7S06-:20 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 8th / Packing Tower | C7S06- | - | BFY-61301 |  | -
C7-S06-P20 | 6 | 20 | 21 |  | BFY-61303_DO_1 | Pin 21 | C7S6:21/C7S06-:21 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | BFY-61303 |  | -
C7-S06-P21 | 6 | 21 | 22 |  | BLM-61302_DO_1 | Pin 22 | C7S6:22/C7S06-:22 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S06- | - | BLM-61302 |  | -
C7-S06-P22 | 6 | 22 | 23 |  | BLM-61302_DO_2 | Pin 23 | C7S6:23/C7S06-:23 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 5th / Packing Tower | C7S06- | - | BLM-61302 |  | -
C7-S06-P23 | 6 | 23 | 24 |  | RVM-60204_DO_1 | Pin 24 | C7S6:24/C7S06-:24 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-60204 |  | -
C7-S06-P24 | 6 | 24 | 25 |  | RVM-60204_DO_2 | Pin 25 | C7S6:25/C7S06-:25 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-60204 |  | -
C7-S06-P25 | 6 | 25 | 26 |  | RVM-61301_DO_1 | Pin 26 | C7S6:26/C7S06-:26 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 6th / Packing Tower | C7S06- | - | RVM-61301 |  | -
C7-S06-P26 | 6 | 26 | 27 |  | RVM-61301_DO_2 | Pin 27 | C7S6:27/C7S06-:27 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 6th / Packing Tower | C7S06- | - | RVM-61301 |  | -
C7-S06-P27 | 6 | 27 | 28 |  | RVM-61304_DO_1 | Pin 28 | C7S6:28/C7S06-:28 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-61304 |  | -
C7-S06-P28 | 6 | 28 | 29 |  | RVM-61304_DO_2 | Pin 29 | C7S6:29/C7S06-:29 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-61304 |  | -
C7-S06-P29 | 6 | 29 | 30 |  | RVM-61305_DO_1 | Pin 30 | C7S6:30/C7S06-:30 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-61305 |  | -
C7-S06-P30 | 6 | 30 | 31 |  | RVM-61305_DO_2 | Pin 31 | C7S6:31/C7S06-:31 | DO | 24VDC Sourcing | ACTIVE | MCC | MCC Room | 9th / Packing Tower | C7S06- | - | RVM-61305 |  | -
C7-S06-P31 | 6 | 31 | 32 |  | PCY-60205_DO_1 | Pin 32 | C7S6:32/C7S06-:32 | DO | 24VDC Sourcing | ACTIVE | JB-601 | Spray Dryer 1st Floor | 1st / Spray Dryer | C7S06- | - | PCY-60205 |  | -

## Slot_07
KALASIN ENGINEERING — C7 SLOT 07 (I/O Module • DO)
Chassis: C7 (MCC Fieldbus & Network Interface (Chassis 7)) ¦ Panel: Motor Control Center Room (MCC Panel & Field Bus) ¦ Net: Modbus TCP / EtherNet Trunk ¦ Total Points: 24 (Active: 0, Spare: 24 / 100.0%) | [16 empty] | Destination: MCC
SOURCE SPECIFICATION (PLC RACK / SLOT / TERMINAL / ePLAN WIRE TAG) | [7 empty] | SIGNAL SPECIFICATION |  |  | DESTINATION SPECIFICATION (FIELD JB / MCC / TERMINAL PIN / FIELD DEVICE)
Point Ref ID | Slot | Pt | Ch | Module Model | PLC Tag Name | PLC Card Pin | ePlan Wire Tag | I/O Type | Signal Spec | Point Status | Dest Enclosure | Location / Area | Floor / Zone | Terminal Block | Term Pin | Instrument Tag | Instrument Description | P&ID Drawing No.
C7-S07-P08 | 7 | 8 | 9 |  | Spare_DO_0 | Pin 9 | C7S7:9/C7S07-:9 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P09 | 7 | 9 | 10 |  | Spare_DO_0 | Pin 10 | C7S7:10/C7S07-:10 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P10 | 7 | 10 | 11 |  | Spare_DO_0 | Pin 11 | C7S7:11/C7S07-:11 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P11 | 7 | 11 | 12 |  | Spare_DO_0 | Pin 12 | C7S7:12/C7S07-:12 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P12 | 7 | 12 | 13 |  | Spare_DO_0 | Pin 13 | C7S7:13/C7S07-:13 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P13 | 7 | 13 | 14 |  | Spare_DO_0 | Pin 14 | C7S7:14/C7S07-:14 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P14 | 7 | 14 | 15 |  | Spare_DO_0 | Pin 15 | C7S7:15/C7S07-:15 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P15 | 7 | 15 | 16 |  | Spare_DO_0 | Pin 16 | C7S7:16/C7S07-:16 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P16 | 7 | 16 | 17 |  | Spare_DO_0 | Pin 17 | C7S7:17/C7S07-:17 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P17 | 7 | 17 | 18 |  | Spare_DO_0 | Pin 18 | C7S7:18/C7S07-:18 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P18 | 7 | 18 | 19 |  | Spare_DO_0 | Pin 19 | C7S7:19/C7S07-:19 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P19 | 7 | 19 | 20 |  | Spare_DO_0 | Pin 20 | C7S7:20/C7S07-:20 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P20 | 7 | 20 | 21 |  | Spare_DO_0 | Pin 21 | C7S7:21/C7S07-:21 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P21 | 7 | 21 | 22 |  | Spare_DO_0 | Pin 22 | C7S7:22/C7S07-:22 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P22 | 7 | 22 | 23 |  | Spare_DO_0 | Pin 23 | C7S7:23/C7S07-:23 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P23 | 7 | 23 | 24 |  | Spare_DO_0 | Pin 24 | C7S7:24/C7S07-:24 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P24 | 7 | 24 | 25 |  | Spare_DO_0 | Pin 25 | C7S7:25/C7S07-:25 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P25 | 7 | 25 | 26 |  | Spare_DO_0 | Pin 26 | C7S7:26/C7S07-:26 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P26 | 7 | 26 | 27 |  | Spare_DO_0 | Pin 27 | C7S7:27/C7S07-:27 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P27 | 7 | 27 | 28 |  | Spare_DO_0 | Pin 28 | C7S7:28/C7S07-:28 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P28 | 7 | 28 | 29 |  | Spare_DO_0 | Pin 29 | C7S7:29/C7S07-:29 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P29 | 7 | 29 | 30 |  | Spare_DO_0 | Pin 30 | C7S7:30/C7S07-:30 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P30 | 7 | 30 | 31 |  | Spare_DO_0 | Pin 31 | C7S7:31/C7S07-:31 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -
C7-S07-P31 | 7 | 31 | 32 |  | Spare_DO_0 | Pin 32 | C7S7:32/C7S07-:32 | DO | 24VDC Sourcing | SPARE | MCC | MCC Room | - | C7S07- | - | Spare | Spare Channel | -