## 00_Slot_Index
KALASIN ENGINEERING xCIP-1545 AUTOMATION SYSTEM (Ref: x2608003)
CHASSIS C1 - C4 (13-SLOT STANDARD) & C5: MASTER SLOT CONFIGURATION DIRECTORY
1. CHASSIS HARDWARE OVERVIEW DIRECTORY (CxSlotConfig)
Chassis_Code | Chassis_Overview_Sheet | Chassis_Rack_Description | Physical_Location | Hardware_Chassis_Model | Mounted_Slots | Total_I/O_Channels | Active_Channels | Spare_Channels
C1 | C1SlotConfig | Main Controller Rack (1756-L950TPSXT CPU) | Control Cabinet CA1 (Main Control Room MCP) | 1756-A13 (13-Slot ControlLogix Chassis) | 13 Slots (S0..S12) | 241 | 174 | 99
C2 | C2SlotConfig | Main Expansion Rack (High-Density Field I/O) | Control Cabinet CA1 (Main Control Room MCP) | 1756-A13 (13-Slot ControlLogix Chassis) | 13 Slots (S0..S12) | 324 | 230 | 126
C3 | C3SlotConfig | Remote I/O Rack 1 (Spray Dryer / Packing Tower) | Field RIO Cabinet (Spray Dryer / Packing Tower) | 1756-A13 (13-Slot ControlLogix Chassis) | 13 Slots (S0..S12) | 236 | 169 | 131
C4 | C4SlotConfig | Remote I/O Rack 2 (Upper Spray Dryer 6th/8th Floor) | Field RIO Cabinet (Spray Dryer 6th/8th Floor) | 1756-A13 (13-Slot ControlLogix Chassis) | 13 Slots (S0..S12) | 164 | 103 | 93
C5 | C5SlotConfig | Remote I/O Station 5 (Slurry Building RIO-200) | Slurry Building 2nd Floor (RIO-200) | 1756-A7 (7-Slot ControlLogix Chassis) | 5 Slots (S0..S4) | 116 | 70 | 62
2. MASTER SLOT SCHEDULE & TERMINAL WIRING DIRECTORY (Click Slot Tag to open Sheet)
Slot_Tag | Chassis | Slot_No | Hardware_Card | Signal_Family | Terminals | Destination_Area(s) | Active_Points | Spare_Points
C1S0 | C1 | 0 | 1756-L950TPSXT | CPU (Controller) | 5 | CA1 (Main Control Room) | 5 | -
C1S1 | C1 | 1 | 1756-EN4TR | COMM (EtherNet/IP) | 4 | CA1 / Field RIO (DLR Ring) | 4 | -
C1S2 | C1 | 2 | 1756-EN4TR | COMM (EtherNet/IP) | 4 | CA1 / Field RIO (DLR Ring) | 4 | -
C1S3 | C1 | 3 | 1756-EN4TR | COMM (EtherNet/IP) | 4 | CA1 / Field RIO (DLR Ring) | 4 | -
C1S4 | C1 | 4 | 1756-IB32 | DI (24VDC Digital Input) | 32 | CA1, JB-401 | 16 | 16
C1S5 | C1 | 5 | 1756-IB32 | DI (24VDC Digital Input) | 32 | JB-401 | 32 | -
C1S6 | C1 | 6 | 1756-IB32 | DI (24VDC Digital Input) | 32 | JB-401, JB-601 | 12 | 20
C1S7 | C1 | 7 | 1756-IB32 | DI (24VDC Digital Input) | 32 | JB-601 | 23 | 9
C1S8 | C1 | 8 | 1756-OB32 | DO (24VDC Digital Output) | 32 | CA1, JB-401 | 16 | 16
C1S9 | C1 | 9 | 1756-OB32 | DO (24VDC Digital Output) | 32 | JB-401, JB-601 | 20 | 12
C1S10 | C1 | 10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | JB-401 | 22 | 10
C1S11 | C1 | 11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | JB-601 | 16 | 16
C1S12 | C1 | 12 | 1756-N2 | EMPTY (Reserve Position) | - | Unpopulated / Reserve | - | -
C2S0 | C2 | 0 | 1756-EN4TR | COMM (EtherNet/IP) | 4 | CA1 / Field RIO (DLR Ring) | 4 | -
C2S1 | C2 | 1 | 1756-IB32 | DI (24VDC Digital Input) | 32 | JB-402 | 24 | 8
C2S2 | C2 | 2 | 1756-IB32 | DI (24VDC Digital Input) | 32 | JB-602 | 23 | 9
C2S3 | C2 | 3 | 1756-IB32 | DI (24VDC Digital Input) | 32 | JB-602, JB-607 | 29 | 3
C2S4 | C2 | 4 | 1756-IB32 | DI (24VDC Digital Input) | 32 | JB-607 | 32 | -
C2S5 | C2 | 5 | 1756-IB32 | DI (24VDC Digital Input) | 32 | JB-607 | 20 | 12
C2S6 | C2 | 6 | 1756-OB32 | DO (24VDC Digital Output) | 32 | JB-402, JB-602 | 12 | 20
C2S7 | C2 | 7 | 1756-OB32 | DO (24VDC Digital Output) | 32 | JB-607 | 31 | 1
C2S8 | C2 | 8 | 1756-OB32 | DO (24VDC Digital Output) | 32 | JB-607 | 9 | 23
C2S9 | C2 | 9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | JB-402 | 14 | 18
C2S10 | C2 | 10 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | JB-602 | 32 | -
C2S11 | C2 | 11 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | CA1 | - | 16
C2S12 | C2 | 12 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | CA1 | - | 16
C3S0 | C3 | 0 | 1756-EN4TR | COMM (EtherNet/IP) | 4 | CA1 / Field RIO (DLR Ring) | 4 | -
C3S1 | C3 | 1 | 1756-IB32 | DI (24VDC Digital Input) | 32 | JB-606 | 4 | 28
C3S2 | C3 | 2 | 1756-IB32 | DI (24VDC Digital Input) | 32 | JB-612 | 17 | 15
C3S3 | C3 | 3 | 1756-IB32 | DI (24VDC Digital Input) | 32 | JB-618 | 12 | 20
C3S4 | C3 | 4 | 1756-OB32 | DO (24VDC Digital Output) | 32 | JB-606, JB-612 | 16 | 16
C3S5 | C3 | 5 | 1756-OB32 | DO (24VDC Digital Output) | 32 | JB-618 | 9 | 23
C3S6 | C3 | 6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | JB-602, JB-606 | 30 | 2
C3S7 | C3 | 7 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | JB-607 | 32 | -
C3S8 | C3 | 8 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | JB-607, JB-608 | 24 | 8
C3S9 | C3 | 9 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | JB-612, JB-618 | 16 | 16
C3S10 | C3 | 10 | 1756-N2 | EMPTY (Reserve Position) | - | Unpopulated / Reserve | - | -
C3S11 | C3 | 11 | 1756-N2 | EMPTY (Reserve Position) | - | Unpopulated / Reserve | - | -
C3S12 | C3 | 12 | 1756-OF8 | AO (4-20mA Analog Output) | 8 | JB-402, JB-602, JB-607 | 5 | 3
C4S0 | C4 | 0 | 1756-EN4TR | COMM (EtherNet/IP) | 4 | CA1 / Field RIO (DLR Ring) | 4 | -
C4S1 | C4 | 1 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IS-JB-603, IS-JB-608 | 22 | 10
C4S2 | C4 | 2 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IS-JB-612 | 15 | 17
C4S3 | C4 | 3 | 1756-IB32 | DI (24VDC Digital Input) | 32 | IS-JB-618 | 13 | 19
C4S4 | C4 | 4 | 1756-OB32 | DO (24VDC Digital Output) | 32 | IS-JB-608, JB-618 | 1 | 31
C4S5 | C4 | 5 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IS-JB-603, IS-JB-608 | 26 | 6
C4S6 | C4 | 6 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | IS-JB-612, IS-JB-618 | 22 | 10
C4S7 | C4 | 7 | 1756-N2 | EMPTY (Reserve Position) | - | Unpopulated / Reserve | - | -
C4S8 | C4 | 8 | 1756-N2 | EMPTY (Reserve Position) | - | Unpopulated / Reserve | - | -
C4S9 | C4 | 9 | 1756-N2 | EMPTY (Reserve Position) | - | Unpopulated / Reserve | - | -
C4S10 | C4 | 10 | 1756-N2 | EMPTY (Reserve Position) | - | Unpopulated / Reserve | - | -
C4S11 | C4 | 11 | 1756-N2 | EMPTY (Reserve Position) | - | Unpopulated / Reserve | - | -
C4S12 | C4 | 12 | 1756-N2 | EMPTY (Reserve Position) | - | Unpopulated / Reserve | - | -
C5S0 | C5 | 0 | 1756-EN4TR | COMM (EtherNet/IP) | 4 | CA1 / Field RIO (DLR Ring) | 4 | -
C5S1 | C5 | 1 | 1756-IB32 | DI (24VDC Digital Input) | 32 | RIO-200 | 32 | -
C5S2 | C5 | 2 | 1756-IB32 | DI (24VDC Digital Input) | 32 | RIO-200 | 8 | 24
C5S3 | C5 | 3 | 1756-OB32 | DO (24VDC Digital Output) | 32 | RIO-200 | 8 | 24
C5S4 | C5 | 4 | 1756-IF16 | AI (4-20mA / Voltage / RTD) | 16 | RIO-200 | 18 | 14

## C1SlotConfig
CHASSIS C1 HARDWARE & SLOT CONFIGURATION SCHEDULE
MAIN CONTROLLER RACK (1756-L950TPSXT CPU) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS MODEL: 1756-A13 (13-Slot ControlLogix Chassis) ¦ POWER SUPPLY: 1756-PA75 (85-265V AC Power Supply) ¦ NETWORK: ETHERNET/IP 1GBPS DLR RING
← Back to Master Slot Directory (00_Slot_Index)
Slot_No | Slot_Tag | Module_Catalog | Module_Description | Signal_Family | Terminal_Block_Type | Destination_Area(s) | Total_Channels | Active_Channels | Spare_Channels | Slot_Status
0 | C1S0 | 1756-L950TPSXT | ControlLogix 5580 Controller (40MB User Memory, Conformal Coated) | CPU (Controller) | Integrated (RJ45 / USB / SD Slot) | CA1 (Main Control Room) | 5 | 5 | - | ACTIVE
1 | C1S1 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | COMM (EtherNet/IP) | 2x RJ45 (Gigabit) + 1x USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | - | ACTIVE
2 | C1S2 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | COMM (EtherNet/IP) | 2x RJ45 (Gigabit) + 1x USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | - | ACTIVE
3 | C1S3 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | COMM (EtherNet/IP) | 2x RJ45 (Gigabit) + 1x USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | - | ACTIVE
4 | C1S4 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | CA1, JB-401 | 32 | 16 | 16 | ACTIVE
5 | C1S5 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-401 | 32 | 32 | - | ACTIVE
6 | C1S6 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-401, JB-601 | 32 | 12 | 20 | ACTIVE
7 | C1S7 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-601 | 32 | 23 | 9 | ACTIVE
8 | C1S8 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | CA1, JB-401 | 32 | 16 | 16 | ACTIVE
9 | C1S9 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | JB-401, JB-601 | 32 | 20 | 12 | ACTIVE
10 | C1S10 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-401 | 16 | 22 | 10 | ACTIVE
11 | C1S11 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-601 | 16 | 16 | 16 | ACTIVE
12 | C1S12 | 1756-N2 | Slot Filler / Reserve Unpopulated Position | EMPTY (Reserve Position) | N/A (Blanking Plate) | Unpopulated / Reserve | - | - | - | EMPTY
TOTAL | 13 Slots | - | Chassis C1 Total Configured Capacity | - | - | - | 241 | 174 | 99 | 72% Active

## C1S0
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C1S0
CENTRAL PROCESSING UNIT (1756-L950TPSXT CONTROLLOGIX 5580 CPU) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C1 ¦ SLOT: 0 ¦ MODULE: 1756-L950TPSXT ¦ DESTINATION AREA: CA1 (Main Control Room)
← Back to Chassis Summary (C1SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
RJ45-1 | Embedded 1Gbps EtherNet/IP Port (SCADA / Enterprise Network) | ETH-CORE-01 | C1S0-ETH1/SW-CORE-01 | SW-CORE-01/C1S0-ETH1 | CA1 (Main Control Room) | CPU_Embedded_ETH | PLC-01 | Main Process Controller EtherNet/IP Uplink Port | ACTIVE
USB-1 | USB 2.0 Type-B Programming Port (Maintenance / Diagnostics) | USB-CONSOLE | C1S0-USB/CONSOLE | CONSOLE/C1S0-USB | CA1 (Main Control Room) | CPU_USB_Console | USB-PGM | Engineering Workstation Maintenance Access Port | ACTIVE
SD-1 | 1784-SD2 Industrial SD Memory Card Slot (Firmware & Program Backup) | SD-SLOT | C1S0-SD/INTERNAL | INTERNAL/C1S0-SD | CA1 (Main Control Room) | CPU_SD_Card | 1784-SD2 | Non-volatile System Image & User Program Storage | ACTIVE
ESM-1 | Capacitor Energy Storage Module (Maintenance-free, Battery-free) | ESM-CAP | C1S0-ESM/INTERNAL | INTERNAL/C1S0-ESM | CA1 (Main Control Room) | CPU_ESM_Module | 1756-ESMCAP | Energy Storage Module for Power Loss Data Retention | ACTIVE
DISP-1 | 4-Character Alphanumeric Diagnostic Display & Status LEDs (RUN, FORCE, SD, OK) | DIAG-DISP | C1S0-DISP/DIAG | DIAG/C1S0-DISP | CA1 (Main Control Room) | CPU_Status_Display | DIAG-LED | System Controller Status & Fault Diagnostic Indicators | ACTIVE

## C1S1
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C1S1
ETHERNET COMMUNICATION ADAPTER (1756-EN4TR DLR 2-PORT GIGABIT) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C1 ¦ SLOT: 1 ¦ MODULE: 1756-EN4TR ¦ DESTINATION AREA: CA1
← Back to Chassis Summary (C1SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | ETH-DLR-P1 | C1S1-/- | -/C1S1- | CA1 | C1S1_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | ACTIVE
RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C1S1-P2/ETH | ETH/C1S1-P2 | CA1 | C1S1_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | ACTIVE
USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C1S1-USB/CONSOLE | CONSOLE/C1S1-USB | CA1 | C1S1_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | ACTIVE
DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C1S1-DISP/DIAG | DIAG/C1S1-DISP | CA1 | C1S1_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | ACTIVE

## C1S2
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C1S2
ETHERNET COMMUNICATION ADAPTER (1756-EN4TR DLR 2-PORT GIGABIT) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C1 ¦ SLOT: 2 ¦ MODULE: 1756-EN4TR ¦ DESTINATION AREA: CA1
← Back to Chassis Summary (C1SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | ETH-DLR-P1 | C1S2-/- | -/C1S2- | CA1 | C1S2_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | ACTIVE
RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C1S2-P2/ETH | ETH/C1S2-P2 | CA1 | C1S2_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | ACTIVE
USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C1S2-USB/CONSOLE | CONSOLE/C1S2-USB | CA1 | C1S2_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | ACTIVE
DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C1S2-DISP/DIAG | DIAG/C1S2-DISP | CA1 | C1S2_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | ACTIVE

## C1S3
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C1S3
ETHERNET COMMUNICATION ADAPTER (1756-EN4TR DLR 2-PORT GIGABIT) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C1 ¦ SLOT: 3 ¦ MODULE: 1756-EN4TR ¦ DESTINATION AREA: CA1
← Back to Chassis Summary (C1SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | ETH-DLR-P1 | C1S3-/- | -/C1S3- | CA1 | C1S3_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | ACTIVE
RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C1S3-P2/ETH | ETH/C1S3-P2 | CA1 | C1S3_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | ACTIVE
USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C1S3-USB/CONSOLE | CONSOLE/C1S3-USB | CA1 | C1S3_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | ACTIVE
DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C1S3-DISP/DIAG | DIAG/C1S3-DISP | CA1 | C1S3_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | ACTIVE

## C1S4
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C1S4
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C1 ¦ SLOT: 4 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: CA1, JB-401
← Back to Chassis Summary (C1SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P1-TBDI1-1 | C1S4-1/P1-TBDI1-1 | P1-TBDI1-1/C1S4-1 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
2 | IN-1 | P1-TBDI1-2 | C1S4-2/P1-TBDI1-2 | P1-TBDI1-2/C1S4-2 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
3 | IN-2 | P1-TBDI1-3 | C1S4-3/P1-TBDI1-3 | P1-TBDI1-3/C1S4-3 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
4 | IN-3 | P1-TBDI1-4 | C1S4-4/P1-TBDI1-4 | P1-TBDI1-4/C1S4-4 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
5 | IN-4 | P1-TBDI1-5 | C1S4-5/P1-TBDI1-5 | P1-TBDI1-5/C1S4-5 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
6 | IN-5 | P1-TBDI1-6 | C1S4-6/P1-TBDI1-6 | P1-TBDI1-6/C1S4-6 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
7 | IN-6 | P1-TBDI1-7 | C1S4-7/P1-TBDI1-7 | P1-TBDI1-7/C1S4-7 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
8 | IN-7 | P1-TBDI1-8 | C1S4-8/P1-TBDI1-8 | P1-TBDI1-8/C1S4-8 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
9 | IN-8 | P1-TBDI1-9 | C1S4-9/P1-TBDI1-9 | P1-TBDI1-9/C1S4-9 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
10 | IN-9 | P1-TBDI1-10 | C1S4-10/P1-TBDI1-10 | P1-TBDI1-10/C1S4-10 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
11 | IN-10 | P1-TBDI1-11 | C1S4-11/P1-TBDI1-11 | P1-TBDI1-11/C1S4-11 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
12 | IN-11 | P1-TBDI1-12 | C1S4-12/P1-TBDI1-12 | P1-TBDI1-12/C1S4-12 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
13 | IN-12 | P1-TBDI1-13 | C1S4-13/P1-TBDI1-13 | P1-TBDI1-13/C1S4-13 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
14 | IN-13 | P1-TBDI1-14 | C1S4-14/P1-TBDI1-14 | P1-TBDI1-14/C1S4-14 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
15 | IN-14 | P1-TBDI1-15 | C1S4-15/P1-TBDI1-15 | P1-TBDI1-15/C1S4-15 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
16 | IN-15 | P1-TBDI1-16 | C1S4-16/P1-TBDI1-16 | P1-TBDI1-16/C1S4-16 | CA1 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
17 | GND-0 | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P1-TBDI1-17 | C1S4-19/P1-TBDI1-17 | P1-TBDI1-17/C1S4-19 | JB-401 | FSL-40201_DI_1 | FSL-40201 | Flow Switch | ACTIVE
20 | IN-17 | P1-TBDI1-18 | C1S4-20/P1-TBDI1-18 | P1-TBDI1-18/C1S4-20 | JB-401 | FSL-40202_DI_1 | FSL-40202 | Flow Switch | ACTIVE
21 | IN-18 | P1-TBDI1-19 | C1S4-21/P1-TBDI1-19 | P1-TBDI1-19/C1S4-21 | JB-401 | FT-40201_DI_1 | FT-40201 | Coriolis Flow Transmitter | ACTIVE
22 | IN-19 | P1-TBDI1-20 | C1S4-22/P1-TBDI1-20 | P1-TBDI1-20/C1S4-22 | JB-401 | FT-40202_DI_1 | FT-40202 | Magnetic Flow Transmitter | ACTIVE
23 | IN-20 | P1-TBDI1-21 | C1S4-23/P1-TBDI1-21 | P1-TBDI1-21/C1S4-23 | JB-401 | HV-40201_DI_1 | HV-40201 | Manual Valve With Position Switch | ACTIVE
24 | IN-21 | P1-TBDI1-22 | C1S4-24/P1-TBDI1-22 | P1-TBDI1-22/C1S4-24 | JB-401 | HV-40202_DI_1 | HV-40202 | Manual Valve With Position Switch | ACTIVE
25 | IN-22 | P1-TBDI1-23 | C1S4-25/P1-TBDI1-23 | P1-TBDI1-23/C1S4-25 | JB-401 | HV-40203_DI_1 | HV-40203 | Manual Valve With Position Switch | ACTIVE
26 | IN-23 | P1-TBDI1-24 | C1S4-26/P1-TBDI1-24 | P1-TBDI1-24/C1S4-26 | JB-401 | HV-40204_DI_1 | HV-40204 | Manual Valve With Position Switch | ACTIVE
27 | IN-24 | P1-TBDI1-25 | C1S4-27/P1-TBDI1-25 | P1-TBDI1-25/C1S4-27 | JB-401 | HV-40205_DI_1 | HV-40205 | Manual Valve With Position Switch | ACTIVE
28 | IN-25 | P1-TBDI1-26 | C1S4-28/P1-TBDI1-26 | P1-TBDI1-26/C1S4-28 | JB-401 | HV-40206_DI_1 | HV-40206 | Manual Valve With Position Switch | ACTIVE
29 | IN-26 | P1-TBDI1-27 | C1S4-29/P1-TBDI1-27 | P1-TBDI1-27/C1S4-29 | JB-401 | XV-40201A_DI_1 | XV-40201A | Control Valve Position Feedback | ACTIVE
30 | IN-27 | P1-TBDI1-28 | C1S4-30/P1-TBDI1-28 | P1-TBDI1-28/C1S4-30 | JB-401 | XV-40201A_DI_2 | XV-40201A | Control Valve Position Feedback | ACTIVE
31 | IN-28 | P1-TBDI1-29 | C1S4-31/P1-TBDI1-29 | P1-TBDI1-29/C1S4-31 | JB-401 | XV-40201B_DI_1 | XV-40201B | Control Valve Position Feedback | ACTIVE
32 | IN-29 | P1-TBDI1-30 | C1S4-32/P1-TBDI1-30 | P1-TBDI1-30/C1S4-32 | JB-401 | XV-40201B_DI_2 | XV-40201B | Control Valve Position Feedback | ACTIVE
33 | IN-30 | P1-TBDI1-31 | C1S4-33/P1-TBDI1-31 | P1-TBDI1-31/C1S4-33 | JB-401 | XV-40201C_DI_1 | XV-40201C | Control Valve Position Feedback | ACTIVE
34 | IN-31 | P1-TBDI1-32 | C1S4-34/P1-TBDI1-32 | P1-TBDI1-32/C1S4-34 | JB-401 | XV-40201C_DI_2 | XV-40201C | Control Valve Position Feedback | ACTIVE
35 | GND1 | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C1S5
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C1S5
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C1 ¦ SLOT: 5 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: JB-401
← Back to Chassis Summary (C1SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P1-TBDI2-1 | C1S5-1/P1-TBDI2-1 | P1-TBDI2-1/C1S5-1 | JB-401 | XV-40201D_DI_1 | XV-40201D | Control Valve Position Feedback | ACTIVE
2 | IN-1 | P1-TBDI2-2 | C1S5-2/P1-TBDI2-2 | P1-TBDI2-2/C1S5-2 | JB-401 | XV-40201D_DI_2 | XV-40201D | Control Valve Position Feedback | ACTIVE
3 | IN-2 | P1-TBDI2-3 | C1S5-3/P1-TBDI2-3 | P1-TBDI2-3/C1S5-3 | JB-401 | XV-40201E_DI_1 | XV-40201E | Control Valve Position Feedback | ACTIVE
4 | IN-3 | P1-TBDI2-4 | C1S5-4/P1-TBDI2-4 | P1-TBDI2-4/C1S5-4 | JB-401 | XV-40201E_DI_2 | XV-40201E | Control Valve Position Feedback | ACTIVE
5 | IN-4 | P1-TBDI2-5 | C1S5-5/P1-TBDI2-5 | P1-TBDI2-5/C1S5-5 | JB-401 | XV-40201F_DI_1 | XV-40201F | Control Valve Position Feedback | ACTIVE
6 | IN-5 | P1-TBDI2-6 | C1S5-6/P1-TBDI2-6 | P1-TBDI2-6/C1S5-6 | JB-401 | XV-40201F_DI_2 | XV-40201F | Control Valve Position Feedback | ACTIVE
7 | IN-6 | P1-TBDI2-7 | C1S5-7/P1-TBDI2-7 | P1-TBDI2-7/C1S5-7 | JB-401 | XV-40201G_DI_1 | XV-40201G | Control Valve Position Feedback | ACTIVE
8 | IN-7 | P1-TBDI2-8 | C1S5-8/P1-TBDI2-8 | P1-TBDI2-8/C1S5-8 | JB-401 | XV-40201G_DI_2 | XV-40201G | Control Valve Position Feedback | ACTIVE
9 | IN-8 | P1-TBDI2-9 | C1S5-9/P1-TBDI2-9 | P1-TBDI2-9/C1S5-9 | JB-401 | XV-40201H_DI_1 | XV-40201H | Control Valve Position Feedback | ACTIVE
10 | IN-9 | P1-TBDI2-10 | C1S5-10/P1-TBDI2-10 | P1-TBDI2-10/C1S5-10 | JB-401 | XV-40201H_DI_2 | XV-40201H | Control Valve Position Feedback | ACTIVE
11 | IN-10 | P1-TBDI2-11 | C1S5-11/P1-TBDI2-11 | P1-TBDI2-11/C1S5-11 | JB-401 | XV-40202A_DI_2 | XV-40202A | Control Valve Position Feedback | ACTIVE
12 | IN-11 | P1-TBDI2-12 | C1S5-12/P1-TBDI2-12 | P1-TBDI2-12/C1S5-12 | JB-401 | XV-40202B_DI_1 | XV-40202B | Control Valve Position Feedback | ACTIVE
13 | IN-12 | P1-TBDI2-13 | C1S5-13/P1-TBDI2-13 | P1-TBDI2-13/C1S5-13 | JB-401 | XV-40202B_DI_2 | XV-40202B | Control Valve Position Feedback | ACTIVE
14 | IN-13 | P1-TBDI2-14 | C1S5-14/P1-TBDI2-14 | P1-TBDI2-14/C1S5-14 | JB-401 | XV-40202C_DI_1 | XV-40202C | Control Valve Position Feedback | ACTIVE
15 | IN-14 | P1-TBDI2-15 | C1S5-15/P1-TBDI2-15 | P1-TBDI2-15/C1S5-15 | JB-401 | XV-40202C_DI_2 | XV-40202C | Control Valve Position Feedback | ACTIVE
16 | IN-15 | P1-TBDI2-16 | C1S5-16/P1-TBDI2-16 | P1-TBDI2-16/C1S5-16 | JB-401 | XV-40202D_DI_1 | XV-40202D | Control Valve Position Feedback | ACTIVE
17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P1-TBDI2-17 | C1S5-19/P1-TBDI2-17 | P1-TBDI2-17/C1S5-19 | JB-401 | XV-40202D_DI_2 | XV-40202D | Control Valve Position Feedback | ACTIVE
20 | IN-17 | P1-TBDI2-18 | C1S5-20/P1-TBDI2-18 | P1-TBDI2-18/C1S5-20 | JB-401 | XV-40202E_DI_1 | XV-40202E | Control Valve Position Feedback | ACTIVE
21 | IN-18 | P1-TBDI2-19 | C1S5-21/P1-TBDI2-19 | P1-TBDI2-19/C1S5-21 | JB-401 | XV-40202A_DI_1 | XV-40202A | Control Valve Position Feedback | ACTIVE
22 | IN-19 | P1-TBDI2-20 | C1S5-22/P1-TBDI2-20 | P1-TBDI2-20/C1S5-22 | JB-401 | XV-40202E_DI_2 | XV-40202E | Control Valve Position Feedback | ACTIVE
23 | IN-20 | P1-TBDI2-21 | C1S5-23/P1-TBDI2-21 | P1-TBDI2-21/C1S5-23 | JB-401 | XV-40202F_DI_1 | XV-40202F | Control Valve Position Feedback | ACTIVE
24 | IN-21 | P1-TBDI2-22 | C1S5-24/P1-TBDI2-22 | P1-TBDI2-22/C1S5-24 | JB-401 | XV-40202F_DI_2 | XV-40202F | Control Valve Position Feedback | ACTIVE
25 | IN-22 | P1-TBDI2-23 | C1S5-25/P1-TBDI2-23 | P1-TBDI2-23/C1S5-25 | JB-401 | XV-40202G_DI_1 | XV-40202G | Control Valve Position Feedback | ACTIVE
26 | IN-23 | P1-TBDI2-24 | C1S5-26/P1-TBDI2-24 | P1-TBDI2-24/C1S5-26 | JB-401 | XV-40202G_DI_2 | XV-40202G | Control Valve Position Feedback | ACTIVE
27 | IN-24 | P1-TBDI2-25 | C1S5-27/P1-TBDI2-25 | P1-TBDI2-25/C1S5-27 | JB-401 | XV-40202H_DI_1 | XV-40202H | Control Valve Position Feedback | ACTIVE
28 | IN-25 | P1-TBDI2-26 | C1S5-28/P1-TBDI2-26 | P1-TBDI2-26/C1S5-28 | JB-401 | XV-40202H_DI_2 | XV-40202H | Control Valve Position Feedback | ACTIVE
29 | IN-26 | P1-TBDI2-27 | C1S5-29/P1-TBDI2-27 | P1-TBDI2-27/C1S5-29 | JB-401 | XV-40203B_DI_1 | XV-40203B | Control Valve Position Feedback | ACTIVE
30 | IN-27 | P1-TBDI2-28 | C1S5-30/P1-TBDI2-28 | P1-TBDI2-28/C1S5-30 | JB-401 | XV-40203B_DI_2 | XV-40203B | Control Valve Position Feedback | ACTIVE
31 | IN-28 | P1-TBDI2-29 | C1S5-31/P1-TBDI2-29 | P1-TBDI2-29/C1S5-31 | JB-401 | XV-40203C_DI_1 | XV-40203C | Control Valve Position Feedback | ACTIVE
32 | IN-29 | P1-TBDI2-30 | C1S5-32/P1-TBDI2-30 | P1-TBDI2-30/C1S5-32 | JB-401 | XV-40203C_DI_2 | XV-40203C | Control Valve Position Feedback | ACTIVE
33 | IN-30 | P1-TBDI2-31 | C1S5-33/P1-TBDI2-31 | P1-TBDI2-31/C1S5-33 | JB-401 | XV-40203D_DI_1 | XV-40203D | Control Valve Position Feedback | ACTIVE
34 | IN-31 | P1-TBDI2-32 | C1S5-34/P1-TBDI2-32 | P1-TBDI2-32/C1S5-34 | JB-401 | XV-40203D_DI_2 | XV-40203D | Control Valve Position Feedback | ACTIVE
35 | GND1 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C1S6
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C1S6
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C1 ¦ SLOT: 6 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: JB-401, JB-601
← Back to Chassis Summary (C1SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P1-TBDI3-1 | C1S6-1/P1-TBDI3-1 | P1-TBDI3-1/C1S6-1 | JB-401 | XV-40203E_DI_1 | XV-40203E | Control Valve Position Feedback | ACTIVE
2 | IN-1 | P1-TBDI3-2 | C1S6-2/P1-TBDI3-2 | P1-TBDI3-2/C1S6-2 | JB-401 | XV-40203E_DI_2 | XV-40203E | Control Valve Position Feedback | ACTIVE
3 | IN-2 | P1-TBDI3-3 | C1S6-3/P1-TBDI3-3 | P1-TBDI3-3/C1S6-3 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
4 | IN-3 | P1-TBDI3-4 | C1S6-4/P1-TBDI3-4 | P1-TBDI3-4/C1S6-4 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
5 | IN-4 | P1-TBDI3-5 | C1S6-5/P1-TBDI3-5 | P1-TBDI3-5/C1S6-5 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
6 | IN-5 | P1-TBDI3-6 | C1S6-6/P1-TBDI3-6 | P1-TBDI3-6/C1S6-6 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
7 | IN-6 | P1-TBDI3-7 | C1S6-7/P1-TBDI3-7 | P1-TBDI3-7/C1S6-7 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
8 | IN-7 | P1-TBDI3-8 | C1S6-8/P1-TBDI3-8 | P1-TBDI3-8/C1S6-8 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
9 | IN-8 | P1-TBDI3-9 | C1S6-9/P1-TBDI3-9 | P1-TBDI3-9/C1S6-9 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
10 | IN-9 | P1-TBDI3-10 | C1S6-10/P1-TBDI3-10 | P1-TBDI3-10/C1S6-10 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
11 | IN-10 | P1-TBDI3-11 | C1S6-11/P1-TBDI3-11 | P1-TBDI3-11/C1S6-11 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
12 | IN-11 | P1-TBDI3-12 | C1S6-12/P1-TBDI3-12 | P1-TBDI3-12/C1S6-12 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
13 | IN-12 | P1-TBDI3-13 | C1S6-13/P1-TBDI3-13 | P1-TBDI3-13/C1S6-13 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
14 | IN-13 | P1-TBDI3-14 | C1S6-14/P1-TBDI3-14 | P1-TBDI3-14/C1S6-14 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
15 | IN-14 | P1-TBDI3-15 | C1S6-15/P1-TBDI3-15 | P1-TBDI3-15/C1S6-15 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
16 | IN-15 | P1-TBDI3-16 | C1S6-16/P1-TBDI3-16 | P1-TBDI3-16/C1S6-16 | JB-401 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P1-TBDI3-17 | C1S6-19/P1-TBDI3-17 | P1-TBDI3-17/C1S6-19 | JB-601 | ES-60202_DI_1 | ES-60202 | Process Instrument | ACTIVE
20 | IN-17 | P1-TBDI3-18 | C1S6-20/P1-TBDI3-18 | P1-TBDI3-18/C1S6-20 | JB-601 | FS-60205_DI_1 | FS-60205 | Flow Switch | ACTIVE
21 | IN-18 | P1-TBDI3-19 | C1S6-21/P1-TBDI3-19 | P1-TBDI3-19/C1S6-21 | JB-601 | LSL-60201_DI_1 | LSL-60201 | Process Instrument | ACTIVE
22 | IN-19 | P1-TBDI3-20 | C1S6-22/P1-TBDI3-20 | P1-TBDI3-20/C1S6-22 | JB-601 | SV-60201_DI_1 | SV-60201 | Process Instrument | ACTIVE
23 | IN-20 | P1-TBDI3-21 | C1S6-23/P1-TBDI3-21 | P1-TBDI3-21/C1S6-23 | JB-601 | SV-60201_DI_2 | SV-60201 | Process Instrument | ACTIVE
24 | IN-21 | P1-TBDI3-22 | C1S6-24/P1-TBDI3-22 | P1-TBDI3-22/C1S6-24 | JB-601 | SV-60202_DI_1 | SV-60202 | Process Instrument | ACTIVE
25 | IN-22 | P1-TBDI3-23 | C1S6-25/P1-TBDI3-23 | P1-TBDI3-23/C1S6-25 | JB-601 | SV-60202_DI_2 | SV-60202 | Process Instrument | ACTIVE
26 | IN-23 | P1-TBDI3-24 | C1S6-26/P1-TBDI3-24 | P1-TBDI3-24/C1S6-26 | JB-601 | SV-60203_DI_1 | SV-60203 | Process Instrument | ACTIVE
27 | IN-24 | P1-TBDI3-25 | C1S6-27/P1-TBDI3-25 | P1-TBDI3-25/C1S6-27 | JB-601 | SV-60203_DI_2 | SV-60203 | Process Instrument | ACTIVE
28 | IN-25 | P1-TBDI3-26 | C1S6-28/P1-TBDI3-26 | P1-TBDI3-26/C1S6-28 | JB-601 | VS-60205_DI_1 | VS-60205 | Vibration Switch | ACTIVE
29 | IN-26 | P1-TBDI3-27 | C1S6-29/P1-TBDI3-27 | P1-TBDI3-27/C1S6-29 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-27 | P1-TBDI3-28 | C1S6-30/P1-TBDI3-28 | P1-TBDI3-28/C1S6-30 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
31 | IN-28 | P1-TBDI3-29 | C1S6-31/P1-TBDI3-29 | P1-TBDI3-29/C1S6-31 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-29 | P1-TBDI3-30 | C1S6-32/P1-TBDI3-30 | P1-TBDI3-30/C1S6-32 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
33 | IN-30 | P1-TBDI3-31 | C1S6-33/P1-TBDI3-31 | P1-TBDI3-31/C1S6-33 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-31 | P1-TBDI3-32 | C1S6-34/P1-TBDI3-32 | P1-TBDI3-32/C1S6-34 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
35 | GND1 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C1S7
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C1S7
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C1 ¦ SLOT: 7 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: JB-601
← Back to Chassis Summary (C1SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P1-TBDI4-1 | C1S7-1/P1-TBDI4-1 | P1-TBDI4-1/C1S7-1 | JB-601 | XA-60202A_DI_1 | XA-60202A | Process Instrument | ACTIVE
2 | IN-1 | P1-TBDI4-2 | C1S7-2/P1-TBDI4-2 | P1-TBDI4-2/C1S7-2 | JB-601 | XA-60202B_DI_1 | XA-60202B | Process Instrument | ACTIVE
3 | IN-2 | P1-TBDI4-3 | C1S7-3/P1-TBDI4-3 | P1-TBDI4-3/C1S7-3 | JB-601 | XA-60202C_DI_1 | XA-60202C | Process Instrument | ACTIVE
4 | IN-3 | P1-TBDI4-4 | C1S7-4/P1-TBDI4-4 | P1-TBDI4-4/C1S7-4 | JB-601 | XA-60202D_DI_1 | XA-60202D | Process Instrument | ACTIVE
5 | IN-4 | P1-TBDI4-5 | C1S7-5/P1-TBDI4-5 | P1-TBDI4-5/C1S7-5 | JB-601 | XA-60202E_DI_1 | XA-60202E | Process Instrument | ACTIVE
6 | IN-5 | P1-TBDI4-6 | C1S7-6/P1-TBDI4-6 | P1-TBDI4-6/C1S7-6 | JB-601 | XA-60202F_DI_1 | XA-60202F | Process Instrument | ACTIVE
7 | IN-6 | P1-TBDI4-7 | C1S7-7/P1-TBDI4-7 | P1-TBDI4-7/C1S7-7 | JB-601 | XA-60202G_DI_1 | XA-60202G | Process Instrument | ACTIVE
8 | IN-7 | P1-TBDI4-8 | C1S7-8/P1-TBDI4-8 | P1-TBDI4-8/C1S7-8 | JB-601 | XA-60202H_DI_1 | XA-60202H | Process Instrument | ACTIVE
9 | IN-8 | P1-TBDI4-9 | C1S7-9/P1-TBDI4-9 | P1-TBDI4-9/C1S7-9 | JB-601 | XA-60202I_DI_1 | XA-60202I | Process Instrument | ACTIVE
10 | IN-9 | P1-TBDI4-10 | C1S7-10/P1-TBDI4-10 | P1-TBDI4-10/C1S7-10 | JB-601 | XA-60202J_DI_1 | XA-60202J | Process Instrument | ACTIVE
11 | IN-10 | P1-TBDI4-11 | C1S7-11/P1-TBDI4-11 | P1-TBDI4-11/C1S7-11 | JB-601 | XA-60202K_DI_1 | XA-60202K | Process Instrument | ACTIVE
12 | IN-11 | P1-TBDI4-12 | C1S7-12/P1-TBDI4-12 | P1-TBDI4-12/C1S7-12 | JB-601 | XA-60202L_DI_1 | XA-60202L | Process Instrument | ACTIVE
13 | IN-12 | P1-TBDI4-13 | C1S7-13/P1-TBDI4-13 | P1-TBDI4-13/C1S7-13 | JB-601 | XA-60202M_DI_1 | XA-60202M | Process Instrument | ACTIVE
14 | IN-13 | P1-TBDI4-14 | C1S7-14/P1-TBDI4-14 | P1-TBDI4-14/C1S7-14 | JB-601 | XV-60202_DI_1 | XV-60202 | Control Valve Position Feedback | ACTIVE
15 | IN-14 | P1-TBDI4-15 | C1S7-15/P1-TBDI4-15 | P1-TBDI4-15/C1S7-15 | JB-601 | XV-60202_DI_2 | XV-60202 | Control Valve Position Feedback | ACTIVE
16 | IN-15 | P1-TBDI4-16 | C1S7-16/P1-TBDI4-16 | P1-TBDI4-16/C1S7-16 | JB-601 | XV-60205A_DI_1 | XV-60205A | Control Valve Position Feedback | ACTIVE
17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P1-TBDI4-17 | C1S7-19/P1-TBDI4-17 | P1-TBDI4-17/C1S7-19 | JB-601 | XV-60205A_DI_2 | XV-60205A | Control Valve Position Feedback | ACTIVE
20 | IN-17 | P1-TBDI4-18 | C1S7-20/P1-TBDI4-18 | P1-TBDI4-18/C1S7-20 | JB-601 | XV-60240D_DI_1 | XV-60240D | Control Valve Position Feedback | ACTIVE
21 | IN-18 | P1-TBDI4-19 | C1S7-21/P1-TBDI4-19 | P1-TBDI4-19/C1S7-21 | JB-601 | XV-60240D_DI_2 | XV-60240D | Control Valve Position Feedback | ACTIVE
22 | IN-19 | P1-TBDI4-20 | C1S7-22/P1-TBDI4-20 | P1-TBDI4-20/C1S7-22 | JB-601 | XV-60240D_DI_1 | XV-60240D | Control Valve Position Feedback | ACTIVE
23 | IN-20 | P1-TBDI4-21 | C1S7-23/P1-TBDI4-21 | P1-TBDI4-21/C1S7-23 | JB-601 | XV-60240D_DI_2 | XV-60240D | Control Valve Position Feedback | ACTIVE
24 | IN-21 | P1-TBDI4-22 | C1S7-24/P1-TBDI4-22 | P1-TBDI4-22/C1S7-24 | JB-601 | YA-60205_DI_1 | YA-60205 | Process Instrument | ACTIVE
25 | IN-22 | P1-TBDI4-23 | C1S7-25/P1-TBDI4-23 | P1-TBDI4-23/C1S7-25 | JB-601 | YI-60205_DI_1 | YI-60205 | Process Instrument | ACTIVE
26 | IN-23 | P1-TBDI4-24 | C1S7-26/P1-TBDI4-24 | P1-TBDI4-24/C1S7-26 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
27 | IN-24 | P1-TBDI4-25 | C1S7-27/P1-TBDI4-25 | P1-TBDI4-25/C1S7-27 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
28 | IN-25 | P1-TBDI4-26 | C1S7-28/P1-TBDI4-26 | P1-TBDI4-26/C1S7-28 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
29 | IN-26 | P1-TBDI4-27 | C1S7-29/P1-TBDI4-27 | P1-TBDI4-27/C1S7-29 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-27 | P1-TBDI4-28 | C1S7-30/P1-TBDI4-28 | P1-TBDI4-28/C1S7-30 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
31 | IN-28 | P1-TBDI4-29 | C1S7-31/P1-TBDI4-29 | P1-TBDI4-29/C1S7-31 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-29 | P1-TBDI4-30 | C1S7-32/P1-TBDI4-30 | P1-TBDI4-30/C1S7-32 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
33 | IN-30 | P1-TBDI4-31 | C1S7-33/P1-TBDI4-31 | P1-TBDI4-31/C1S7-33 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-31 | P1-TBDI4-32 | C1S7-34/P1-TBDI4-32 | P1-TBDI4-32/C1S7-34 | JB-601 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
35 | GND1 | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C1S8
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C1S8
DIGITAL OUTPUT CARD (1756-OB32 32-CH 24VDC SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C1 ¦ SLOT: 8 ¦ MODULE: 1756-OB32 ¦ DESTINATION AREA: CA1, JB-401
← Back to Chassis Summary (C1SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBRLx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | OUT-0 | P1-TBRL1-1 | C1S8-1/P1-TBRL1-1 | P1-TBRL1-1/C1S8-1 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
2 | OUT-1 | P1-TBRL1-2 | C1S8-2/P1-TBRL1-2 | P1-TBRL1-2/C1S8-2 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
3 | OUT-2 | P1-TBRL1-3 | C1S8-3/P1-TBRL1-3 | P1-TBRL1-3/C1S8-3 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
4 | OUT-3 | P1-TBRL1-4 | C1S8-4/P1-TBRL1-4 | P1-TBRL1-4/C1S8-4 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
5 | OUT-4 | P1-TBRL1-5 | C1S8-5/P1-TBRL1-5 | P1-TBRL1-5/C1S8-5 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
6 | OUT-5 | P1-TBRL1-6 | C1S8-6/P1-TBRL1-6 | P1-TBRL1-6/C1S8-6 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
7 | OUT-6 | P1-TBRL1-7 | C1S8-7/P1-TBRL1-7 | P1-TBRL1-7/C1S8-7 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
8 | OUT-7 | P1-TBRL1-8 | C1S8-8/P1-TBRL1-8 | P1-TBRL1-8/C1S8-8 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
9 | OUT-8 | P1-TBRL1-9 | C1S8-9/P1-TBRL1-9 | P1-TBRL1-9/C1S8-9 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
10 | OUT-9 | P1-TBRL1-10 | C1S8-10/P1-TBRL1-10 | P1-TBRL1-10/C1S8-10 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
11 | OUT-10 | P1-TBRL1-11 | C1S8-11/P1-TBRL1-11 | P1-TBRL1-11/C1S8-11 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
12 | OUT-11 | P1-TBRL1-12 | C1S8-12/P1-TBRL1-12 | P1-TBRL1-12/C1S8-12 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
13 | OUT-12 | P1-TBRL1-13 | C1S8-13/P1-TBRL1-13 | P1-TBRL1-13/C1S8-13 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
14 | OUT-13 | P1-TBRL1-14 | C1S8-14/P1-TBRL1-14 | P1-TBRL1-14/C1S8-14 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
15 | OUT-14 | P1-TBRL1-15 | C1S8-15/P1-TBRL1-15 | P1-TBRL1-15/C1S8-15 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
16 | OUT-15 | P1-TBRL1-16 | C1S8-16/P1-TBRL1-16 | P1-TBRL1-16/C1S8-16 | CA1 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
17 | RTN OUT-0 | P1-TBRL1-17 | C1S8-17/P1-TBRL1-17 | P1-TBRL1-17/C1S8-17 | CA1 | Spare_DO_17 | Spare | Spare Reserve Channel | SPARE
18 | DC-0(+) | +24VDC | +24VDC | +24VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | OUT-16 | P1-TBRL1-17 | C1S8-19/P1-TBRL1-17 | P1-TBRL1-17/C1S8-19 | JB-401 | XV-40202E_DO_1 | XV-40202E | Control Valve Position Feedback | ACTIVE
20 | OUT-17 | P1-TBRL1-18 | C1S8-20/P1-TBRL1-18 | P1-TBRL1-18/C1S8-20 | JB-401 | XV-40202F_DO_1 | XV-40202F | Control Valve Position Feedback | ACTIVE
21 | OUT-18 | P1-TBRL1-19 | C1S8-21/P1-TBRL1-19 | P1-TBRL1-19/C1S8-21 | JB-401 | XV-40202G_DO_1 | XV-40202G | Control Valve Position Feedback | ACTIVE
22 | OUT-19 | P1-TBRL1-20 | C1S8-22/P1-TBRL1-20 | P1-TBRL1-20/C1S8-22 | JB-401 | XV-40202H_DO_1 | XV-40202H | Control Valve Position Feedback | ACTIVE
23 | OUT-20 | P1-TBRL1-21 | C1S8-23/P1-TBRL1-21 | P1-TBRL1-21/C1S8-23 | JB-401 | XV-40203B_DO_1 | XV-40203B | Control Valve Position Feedback | ACTIVE
24 | OUT-21 | P1-TBRL1-22 | C1S8-24/P1-TBRL1-22 | P1-TBRL1-22/C1S8-24 | JB-401 | XV-40203C_DO_1 | XV-40203C | Control Valve Position Feedback | ACTIVE
25 | OUT-22 | P1-TBRL1-23 | C1S8-25/P1-TBRL1-23 | P1-TBRL1-23/C1S8-25 | JB-401 | XV-40203D_DO_1 | XV-40203D | Control Valve Position Feedback | ACTIVE
26 | OUT-23 | P1-TBRL1-24 | C1S8-26/P1-TBRL1-24 | P1-TBRL1-24/C1S8-26 | JB-401 | XV-40203E_DO_1 | XV-40203E | Control Valve Position Feedback | ACTIVE
27 | OUT-24 | P1-TBRL1-25 | C1S8-27/P1-TBRL1-25 | P1-TBRL1-25/C1S8-27 | JB-401 | SV-40201_DO_1 | SV-40201 | Process Instrument | ACTIVE
28 | OUT-25 | P1-TBRL1-26 | C1S8-28/P1-TBRL1-26 | P1-TBRL1-26/C1S8-28 | JB-401 | SV-40202_DO_1 | SV-40202 | Process Instrument | ACTIVE
29 | OUT-26 | P1-TBRL1-27 | C1S8-29/P1-TBRL1-27 | P1-TBRL1-27/C1S8-29 | JB-401 | SV-40203_DO_1 | SV-40203 | Process Instrument | ACTIVE
30 | OUT-27 | P1-TBRL1-28 | C1S8-30/P1-TBRL1-28 | P1-TBRL1-28/C1S8-30 | JB-401 | SV-40204_DO_1 | SV-40204 | Process Instrument | ACTIVE
31 | OUT-28 | P1-TBRL1-29 | C1S8-31/P1-TBRL1-29 | P1-TBRL1-29/C1S8-31 | JB-401 | XV-40201A_DO_1 | XV-40201A | Control Valve Position Feedback | ACTIVE
32 | OUT-29 | P1-TBRL1-30 | C1S8-32/P1-TBRL1-30 | P1-TBRL1-30/C1S8-32 | JB-401 | XV-40201B_DO_1 | XV-40201B | Control Valve Position Feedback | ACTIVE
33 | OUT-30 | P1-TBRL1-31 | C1S8-33/P1-TBRL1-31 | P1-TBRL1-31/C1S8-33 | JB-401 | XV-40201C_DO_1 | XV-40201C | Control Valve Position Feedback | ACTIVE
34 | OUT-31 | P1-TBRL1-32 | C1S8-34/P1-TBRL1-32 | P1-TBRL1-32/C1S8-34 | JB-401 | XV-40201D_DO_1 | XV-40201D | Control Valve Position Feedback | ACTIVE
35 | RTN OUT-1 | P1-TBRL1-35 | C1S8-35/P1-TBRL1-35 | P1-TBRL1-35/C1S8-35 | CA1 | Spare_DO_35 | Spare | Spare Reserve Channel | SPARE
36 | DC-1(+) | +24VDC | +24VDC | +24VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C1S9
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C1S9
DIGITAL OUTPUT CARD (1756-OB32 32-CH 24VDC SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C1 ¦ SLOT: 9 ¦ MODULE: 1756-OB32 ¦ DESTINATION AREA: JB-401, JB-601
← Back to Chassis Summary (C1SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBRLx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | OUT-0 | P1-TBRL2-1 | C1S9-1/P1-TBRL2-1 | P1-TBRL2-1/C1S9-1 | JB-401 | XV-40201E_DO_1 | XV-40201E | Control Valve Position Feedback | ACTIVE
2 | OUT-1 | P1-TBRL2-2 | C1S9-2/P1-TBRL2-2 | P1-TBRL2-2/C1S9-2 | JB-401 | XV-40201F_DO_1 | XV-40201F | Control Valve Position Feedback | ACTIVE
3 | OUT-2 | P1-TBRL2-3 | C1S9-3/P1-TBRL2-3 | P1-TBRL2-3/C1S9-3 | JB-401 | XV-40201G_DO_1 | XV-40201G | Control Valve Position Feedback | ACTIVE
4 | OUT-3 | P1-TBRL2-4 | C1S9-4/P1-TBRL2-4 | P1-TBRL2-4/C1S9-4 | JB-401 | XV-40201H_DO_1 | XV-40201H | Control Valve Position Feedback | ACTIVE
5 | OUT-4 | P1-TBRL2-5 | C1S9-5/P1-TBRL2-5 | P1-TBRL2-5/C1S9-5 | JB-401 | XV-40202A_DO_1 | XV-40202A | Control Valve Position Feedback | ACTIVE
6 | OUT-5 | P1-TBRL2-6 | C1S9-6/P1-TBRL2-6 | P1-TBRL2-6/C1S9-6 | JB-401 | XV-40202B_DO_1 | XV-40202B | Control Valve Position Feedback | ACTIVE
7 | OUT-6 | P1-TBRL2-7 | C1S9-7/P1-TBRL2-7 | P1-TBRL2-7/C1S9-7 | JB-401 | XV-40202C_DO_1 | XV-40202C | Control Valve Position Feedback | ACTIVE
8 | OUT-7 | P1-TBRL2-8 | C1S9-8/P1-TBRL2-8 | P1-TBRL2-8/C1S9-8 | JB-401 | XV-40202D_DO_1 | XV-40202D | Control Valve Position Feedback | ACTIVE
9 | OUT-8 | P1-TBRL2-9 | C1S9-9/P1-TBRL2-9 | P1-TBRL2-9/C1S9-9 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
10 | OUT-9 | P1-TBRL2-10 | C1S9-10/P1-TBRL2-10 | P1-TBRL2-10/C1S9-10 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
11 | OUT-10 | P1-TBRL2-11 | C1S9-11/P1-TBRL2-11 | P1-TBRL2-11/C1S9-11 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
12 | OUT-11 | P1-TBRL2-12 | C1S9-12/P1-TBRL2-12 | P1-TBRL2-12/C1S9-12 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
13 | OUT-12 | P1-TBRL2-13 | C1S9-13/P1-TBRL2-13 | P1-TBRL2-13/C1S9-13 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
14 | OUT-13 | P1-TBRL2-14 | C1S9-14/P1-TBRL2-14 | P1-TBRL2-14/C1S9-14 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
15 | OUT-14 | P1-TBRL2-15 | C1S9-15/P1-TBRL2-15 | P1-TBRL2-15/C1S9-15 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
16 | OUT-15 | P1-TBRL2-16 | C1S9-16/P1-TBRL2-16 | P1-TBRL2-16/C1S9-16 | JB-401 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
17 | RTN OUT-0 | P1-TBRL2-17 | C1S9-17/P1-TBRL2-17 | P1-TBRL2-17/C1S9-17 | JB-401 | Spare_DO_17 | Spare | Spare Reserve Channel | SPARE
18 | DC-0(+) | +24VDC | +24VDC | +24VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | OUT-16 | P1-TBRL2-17 | C1S9-19/P1-TBRL2-17 | P1-TBRL2-17/C1S9-19 | JB-601 | SV-60201_DO_1 | SV-60201 | Process Instrument | ACTIVE
20 | OUT-17 | P1-TBRL2-18 | C1S9-20/P1-TBRL2-18 | P1-TBRL2-18/C1S9-20 | JB-601 | SV-60202_DO_1 | SV-60202 | Process Instrument | ACTIVE
21 | OUT-18 | P1-TBRL2-19 | C1S9-21/P1-TBRL2-19 | P1-TBRL2-19/C1S9-21 | JB-601 | SV-60230_DO_1 | SV-60230 | Process Instrument | ACTIVE
22 | OUT-19 | P1-TBRL2-20 | C1S9-22/P1-TBRL2-20 | P1-TBRL2-20/C1S9-22 | JB-601 | SV-60203_DO_1 | SV-60203 | Process Instrument | ACTIVE
23 | OUT-20 | P1-TBRL2-21 | C1S9-23/P1-TBRL2-21 | P1-TBRL2-21/C1S9-23 | JB-601 | SV-60240A_DO_1 | SV-60240A | Process Instrument | ACTIVE
24 | OUT-21 | P1-TBRL2-22 | C1S9-24/P1-TBRL2-22 | P1-TBRL2-22/C1S9-24 | JB-601 | SV-60231_DO_1 | SV-60231 | Process Instrument | ACTIVE
25 | OUT-22 | P1-TBRL2-23 | C1S9-25/P1-TBRL2-23 | P1-TBRL2-23/C1S9-25 | JB-601 | SV-60240B_DO_1 | SV-60240B | Process Instrument | ACTIVE
26 | OUT-23 | P1-TBRL2-24 | C1S9-26/P1-TBRL2-24 | P1-TBRL2-24/C1S9-26 | JB-601 | SV-60240C_DO_1 | SV-60240C | Process Instrument | ACTIVE
27 | OUT-24 | P1-TBRL2-25 | C1S9-27/P1-TBRL2-25 | P1-TBRL2-25/C1S9-27 | JB-601 | XV-60240D_DO_1 | XV-60240D | Control Valve Position Feedback | ACTIVE
28 | OUT-25 | P1-TBRL2-26 | C1S9-28/P1-TBRL2-26 | P1-TBRL2-26/C1S9-28 | JB-601 | XV-60251_DO_1 | XV-60251 | Control Valve Position Feedback | ACTIVE
29 | OUT-26 | P1-TBRL2-27 | C1S9-29/P1-TBRL2-27 | P1-TBRL2-27/C1S9-29 | JB-601 | XV-60202_DO_1 | XV-60202 | Control Valve Position Feedback | ACTIVE
30 | OUT-27 | P1-TBRL2-28 | C1S9-30/P1-TBRL2-28 | P1-TBRL2-28/C1S9-30 | JB-601 | XV-60205A_DO_1 | XV-60205A | Control Valve Position Feedback | ACTIVE
31 | OUT-28 | P1-TBRL2-29 | C1S9-31/P1-TBRL2-29 | P1-TBRL2-29/C1S9-31 | JB-601 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
32 | OUT-29 | P1-TBRL2-30 | C1S9-32/P1-TBRL2-30 | P1-TBRL2-30/C1S9-32 | JB-601 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
33 | OUT-30 | P1-TBRL2-31 | C1S9-33/P1-TBRL2-31 | P1-TBRL2-31/C1S9-33 | JB-601 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
34 | OUT-31 | P1-TBRL2-32 | C1S9-34/P1-TBRL2-32 | P1-TBRL2-32/C1S9-34 | JB-601 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
35 | RTN OUT-1 | P1-TBRL2-35 | C1S9-35/P1-TBRL2-35 | P1-TBRL2-35/C1S9-35 | JB-401 | Spare_DO_35 | Spare | Spare Reserve Channel | SPARE
36 | DC-1(+) | +24VDC | +24VDC | +24VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C1S10
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C1S10
ANALOG INPUT CARD (1756-IF16 16-CH CURRENT/VOLTAGE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C1 ¦ SLOT: 10 ¦ MODULE: 1756-IF16 ¦ DESTINATION AREA: JB-401
← Back to Chassis Summary (C1SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | i RTN-0 | P1-TBAI1-1(B) | C1S10-1/P1-TBAI1-1(B) | P1-TBAI1-1(B)/C1S10-1 | JB-401 | FT-40201_AI_1 | FT-40201 | Coriolis Flow Transmitter | ACTIVE
2 | IN-0 | P1-TBAI1-1(A) | C1S10-2/P1-TBAI1-1(A) | P1-TBAI1-1(A)/C1S10-2 | JB-401 | FT-40201_AI_1 | FT-40201 | Coriolis Flow Transmitter | ACTIVE
3 | i RTN-1 | P1-TBAI1-2(B) | C1S10-3/P1-TBAI1-2(B) | P1-TBAI1-2(B)/C1S10-3 | JB-401 | FT-40201_AI_2 | FT-40201 | Coriolis Flow Transmitter | ACTIVE
4 | IN-1 | P1-TBAI1-2(A) | C1S10-4/P1-TBAI1-2(A) | P1-TBAI1-2(A)/C1S10-4 | JB-401 | FT-40201_AI_2 | FT-40201 | Coriolis Flow Transmitter | ACTIVE
5 | i RTN-2 | P1-TBAI1-3(B) | C1S10-5/P1-TBAI1-3(B) | P1-TBAI1-3(B)/C1S10-5 | JB-401 | FT-40202_AI_1 | FT-40202 | Magnetic Flow Transmitter | ACTIVE
6 | IN-2 | P1-TBAI1-3(A) | C1S10-6/P1-TBAI1-3(A) | P1-TBAI1-3(A)/C1S10-6 | JB-401 | FT-40202_AI_1 | FT-40202 | Magnetic Flow Transmitter | ACTIVE
7 | i RTN-3 | P1-TBAI1-4(B) | C1S10-7/P1-TBAI1-4(B) | P1-TBAI1-4(B)/C1S10-7 | JB-401 | LT-40203_AI_1 | LT-40203 | Level Transmitter | ACTIVE
8 | IN-3 | P1-TBAI1-4(A) | C1S10-8/P1-TBAI1-4(A) | P1-TBAI1-4(A)/C1S10-8 | JB-401 | LT-40203_AI_1 | LT-40203 | Level Transmitter | ACTIVE
9 | RTN | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
10 | RTN | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
11 | i RTN-4 | P1-TBAI1-5(B) | C1S10-11/P1-TBAI1-5(B) | P1-TBAI1-5(B)/C1S10-11 | JB-401 | LT-40201_AI_1 | LT-40201 | Level Transmitter | ACTIVE
12 | IN-4 | P1-TBAI1-5(A) | C1S10-12/P1-TBAI1-5(A) | P1-TBAI1-5(A)/C1S10-12 | JB-401 | LT-40201_AI_1 | LT-40201 | Level Transmitter | ACTIVE
13 | i RTN-5 | P1-TBAI1-6(B) | C1S10-13/P1-TBAI1-6(B) | P1-TBAI1-6(B)/C1S10-13 | JB-401 | LT-40202_AI_1 | LT-40202 | Level Transmitter | ACTIVE
14 | IN-5 | P1-TBAI1-6(A) | C1S10-14/P1-TBAI1-6(A) | P1-TBAI1-6(A)/C1S10-14 | JB-401 | LT-40202_AI_1 | LT-40202 | Level Transmitter | ACTIVE
15 | i RTN-6 | P1-TBAI1-7(B) | C1S10-15/P1-TBAI1-7(B) | P1-TBAI1-7(B)/C1S10-15 | JB-401 | pHT-40201_AI_1 | pHT-40201 | PH Transmitter | ACTIVE
16 | IN-6 | P1-TBAI1-7(A) | C1S10-16/P1-TBAI1-7(A) | P1-TBAI1-7(A)/C1S10-16 | JB-401 | pHT-40201_AI_1 | pHT-40201 | PH Transmitter | ACTIVE
17 | i RTN-7 | P1-TBAI1-8(B) | C1S10-17/P1-TBAI1-8(B) | P1-TBAI1-8(B)/C1S10-17 | JB-401 | pHT-40202_AI_1 | pHT-40202 | PH Transmitter | ACTIVE
18 | IN-7 | P1-TBAI1-8(A) | C1S10-18/P1-TBAI1-8(A) | P1-TBAI1-8(A)/C1S10-18 | JB-401 | pHT-40202_AI_1 | pHT-40202 | PH Transmitter | ACTIVE
19 | i RTN-8 | P1-TBAI1-9(B) | C1S10-19/P1-TBAI1-9(B) | P1-TBAI1-9(B)/C1S10-19 | JB-401 | PT-40201_AI_1 | PT-40201 | Pressure Transmitter | ACTIVE
20 | IN-8 | P1-TBAI1-9(A) | C1S10-20/P1-TBAI1-9(A) | P1-TBAI1-9(A)/C1S10-20 | JB-401 | PT-40201_AI_1 | PT-40201 | Pressure Transmitter | ACTIVE
21 | i RTN-9 | P1-TBAI1-10(B) | C1S10-21/P1-TBAI1-10(B) | P1-TBAI1-10(B)/C1S10-21 | JB-401 | PT-40202_AI_1 | PT-40202 | Pressure Transmitter | ACTIVE
22 | IN-9 | P1-TBAI1-10(A) | C1S10-22/P1-TBAI1-10(A) | P1-TBAI1-10(A)/C1S10-22 | JB-401 | PT-40202_AI_1 | PT-40202 | Pressure Transmitter | ACTIVE
23 | i RTN-10 | P1-TBAI1-11(B) | C1S10-23/P1-TBAI1-11(B) | P1-TBAI1-11(B)/C1S10-23 | JB-401 | PT-60202_AI_1 | PT-60202 | Pressure Transmitter | ACTIVE
24 | IN-10 | P1-TBAI1-11(A) | C1S10-24/P1-TBAI1-11(A) | P1-TBAI1-11(A)/C1S10-24 | JB-401 | PT-60202_AI_1 | PT-60202 | Pressure Transmitter | ACTIVE
25 | i RTN-11 | P1-TBAI1-12(B) | C1S10-25/P1-TBAI1-12(B) | P1-TBAI1-12(B)/C1S10-25 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
26 | IN-11 | P1-TBAI1-12(A) | C1S10-26/P1-TBAI1-12(A) | P1-TBAI1-12(A)/C1S10-26 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
27 | RTN | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
28 | RTN | 0VDC | 0VDC | 0VDC | JB-401 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
29 | i RTN-12 | P1-TBAI1-13(B) | C1S10-29/P1-TBAI1-13(B) | P1-TBAI1-13(B)/C1S10-29 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-12 | P1-TBAI1-13(A) | C1S10-30/P1-TBAI1-13(A) | P1-TBAI1-13(A)/C1S10-30 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
31 | i RTN-13 | P1-TBAI1-14(B) | C1S10-31/P1-TBAI1-14(B) | P1-TBAI1-14(B)/C1S10-31 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-13 | P1-TBAI1-14(A) | C1S10-32/P1-TBAI1-14(A) | P1-TBAI1-14(A)/C1S10-32 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
33 | i RTN-14 | P1-TBAI1-15(B) | C1S10-33/P1-TBAI1-15(B) | P1-TBAI1-15(B)/C1S10-33 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-14 | P1-TBAI1-15(A) | C1S10-34/P1-TBAI1-15(A) | P1-TBAI1-15(A)/C1S10-34 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
35 | i RTN-15 | P1-TBAI1-16(B) | C1S10-35/P1-TBAI1-16(B) | P1-TBAI1-16(B)/C1S10-35 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
36 | IN-15 | P1-TBAI1-16(A) | C1S10-36/P1-TBAI1-16(A) | P1-TBAI1-16(A)/C1S10-36 | JB-401 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE

## C1S11
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C1S11
ANALOG INPUT CARD (1756-IF16 16-CH CURRENT/VOLTAGE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C1 ¦ SLOT: 11 ¦ MODULE: 1756-IF16 ¦ DESTINATION AREA: JB-601
← Back to Chassis Summary (C1SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | i RTN-0 | P1-TBAI2-1(B) | C1S11-1/P1-TBAI2-1(B) | P1-TBAI2-1(B)/C1S11-1 | JB-601 | DPI-60240_AI_1 | DPI-60240 | Process Instrument | ACTIVE
2 | IN-0 | P1-TBAI2-1(A) | C1S11-2/P1-TBAI2-1(A) | P1-TBAI2-1(A)/C1S11-2 | JB-601 | DPI-60240_AI_1 | DPI-60240 | Process Instrument | ACTIVE
3 | i RTN-1 | P1-TBAI2-2(B) | C1S11-3/P1-TBAI2-2(B) | P1-TBAI2-2(B)/C1S11-3 | JB-601 | DPT-60202_AI_1 | DPT-60202 | Differential Pressure Transmitte | ACTIVE
4 | IN-1 | P1-TBAI2-2(A) | C1S11-4/P1-TBAI2-2(A) | P1-TBAI2-2(A)/C1S11-4 | JB-601 | DPT-60202_AI_1 | DPT-60202 | Differential Pressure Transmitte | ACTIVE
5 | i RTN-2 | P1-TBAI2-3(B) | C1S11-5/P1-TBAI2-3(B) | P1-TBAI2-3(B)/C1S11-5 | JB-601 | FT-60201_AI_1 | FT-60201 | Flow Transmitter | ACTIVE
6 | IN-2 | P1-TBAI2-3(A) | C1S11-6/P1-TBAI2-3(A) | P1-TBAI2-3(A)/C1S11-6 | JB-601 | FT-60201_AI_1 | FT-60201 | Flow Transmitter | ACTIVE
7 | i RTN-3 | P1-TBAI2-4(B) | C1S11-7/P1-TBAI2-4(B) | P1-TBAI2-4(B)/C1S11-7 | JB-601 | FT-60204_AI_1 | FT-60204 | Flow Transmitter | ACTIVE
8 | IN-3 | P1-TBAI2-4(A) | C1S11-8/P1-TBAI2-4(A) | P1-TBAI2-4(A)/C1S11-8 | JB-601 | FT-60204_AI_1 | FT-60204 | Flow Transmitter | ACTIVE
9 | RTN | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
10 | RTN | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
11 | i RTN-4 | P1-TBAI2-5(B) | C1S11-11/P1-TBAI2-5(B) | P1-TBAI2-5(B)/C1S11-11 | JB-601 | FT-61307_AI_1 | FT-61307 | Flow Transmitter | ACTIVE
12 | IN-4 | P1-TBAI2-5(A) | C1S11-12/P1-TBAI2-5(A) | P1-TBAI2-5(A)/C1S11-12 | JB-601 | FT-61307_AI_1 | FT-61307 | Flow Transmitter | ACTIVE
13 | i RTN-5 | P1-TBAI2-6(B) | C1S11-13/P1-TBAI2-6(B) | P1-TBAI2-6(B)/C1S11-13 | JB-601 | PT-60203_AI_1 | PT-60203 | Pressure Transmitter | ACTIVE
14 | IN-5 | P1-TBAI2-6(A) | C1S11-14/P1-TBAI2-6(A) | P1-TBAI2-6(A)/C1S11-14 | JB-601 | PT-60203_AI_1 | PT-60203 | Pressure Transmitter | ACTIVE
15 | i RTN-6 | P1-TBAI2-7(B) | C1S11-15/P1-TBAI2-7(B) | P1-TBAI2-7(B)/C1S11-15 | JB-601 | PT-60204_AI_1 | PT-60204 | Pressure Transmitter | ACTIVE
16 | IN-6 | P1-TBAI2-7(A) | C1S11-16/P1-TBAI2-7(A) | P1-TBAI2-7(A)/C1S11-16 | JB-601 | PT-60204_AI_1 | PT-60204 | Pressure Transmitter | ACTIVE
17 | i RTN-7 | P1-TBAI2-8(B) | C1S11-17/P1-TBAI2-8(B) | P1-TBAI2-8(B)/C1S11-17 | JB-601 | PT-60205_AI_1 | PT-60205 | Pressure Transmitter | ACTIVE
18 | IN-7 | P1-TBAI2-8(A) | C1S11-18/P1-TBAI2-8(A) | P1-TBAI2-8(A)/C1S11-18 | JB-601 | PT-60205_AI_1 | PT-60205 | Pressure Transmitter | ACTIVE
19 | i RTN-8 | P1-TBAI2-9(B) | C1S11-19/P1-TBAI2-9(B) | P1-TBAI2-9(B)/C1S11-19 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
20 | IN-8 | P1-TBAI2-9(A) | C1S11-20/P1-TBAI2-9(A) | P1-TBAI2-9(A)/C1S11-20 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
21 | i RTN-9 | P1-TBAI2-10(B) | C1S11-21/P1-TBAI2-10(B) | P1-TBAI2-10(B)/C1S11-21 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
22 | IN-9 | P1-TBAI2-10(A) | C1S11-22/P1-TBAI2-10(A) | P1-TBAI2-10(A)/C1S11-22 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
23 | i RTN-10 | P1-TBAI2-11(B) | C1S11-23/P1-TBAI2-11(B) | P1-TBAI2-11(B)/C1S11-23 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
24 | IN-10 | P1-TBAI2-11(A) | C1S11-24/P1-TBAI2-11(A) | P1-TBAI2-11(A)/C1S11-24 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
25 | i RTN-11 | P1-TBAI2-12(B) | C1S11-25/P1-TBAI2-12(B) | P1-TBAI2-12(B)/C1S11-25 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
26 | IN-11 | P1-TBAI2-12(A) | C1S11-26/P1-TBAI2-12(A) | P1-TBAI2-12(A)/C1S11-26 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
27 | RTN | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
28 | RTN | 0VDC | 0VDC | 0VDC | JB-601 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
29 | i RTN-12 | P1-TBAI2-13(B) | C1S11-29/P1-TBAI2-13(B) | P1-TBAI2-13(B)/C1S11-29 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-12 | P1-TBAI2-13(A) | C1S11-30/P1-TBAI2-13(A) | P1-TBAI2-13(A)/C1S11-30 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
31 | i RTN-13 | P1-TBAI2-14(B) | C1S11-31/P1-TBAI2-14(B) | P1-TBAI2-14(B)/C1S11-31 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-13 | P1-TBAI2-14(A) | C1S11-32/P1-TBAI2-14(A) | P1-TBAI2-14(A)/C1S11-32 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
33 | i RTN-14 | P1-TBAI2-15(B) | C1S11-33/P1-TBAI2-15(B) | P1-TBAI2-15(B)/C1S11-33 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-14 | P1-TBAI2-15(A) | C1S11-34/P1-TBAI2-15(A) | P1-TBAI2-15(A)/C1S11-34 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
35 | i RTN-15 | P1-TBAI2-16(B) | C1S11-35/P1-TBAI2-16(B) | P1-TBAI2-16(B)/C1S11-35 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
36 | IN-15 | P1-TBAI2-16(A) | C1S11-36/P1-TBAI2-16(A) | P1-TBAI2-16(A)/C1S11-36 | JB-601 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE

## C1S12
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C1S12
RESERVE / EMPTY SLOT (1756-N2) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C1 ¦ SLOT: 12 ¦ MODULE: 1756-N2 ¦ DESTINATION AREA: CA1
← Back to Chassis Summary (C1SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
- | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | EMPTY

## C2SlotConfig
CHASSIS C2 HARDWARE & SLOT CONFIGURATION SCHEDULE
MAIN EXPANSION RACK (HIGH-DENSITY FIELD I/O) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS MODEL: 1756-A13 (13-Slot ControlLogix Chassis) ¦ POWER SUPPLY: 1756-PA75 (85-265V AC Power Supply) ¦ NETWORK: ETHERNET/IP 1GBPS DLR RING
← Back to Master Slot Directory (00_Slot_Index)
Slot_No | Slot_Tag | Module_Catalog | Module_Description | Signal_Family | Terminal_Block_Type | Destination_Area(s) | Total_Channels | Active_Channels | Spare_Channels | Slot_Status
0 | C2S0 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | COMM (EtherNet/IP) | 2x RJ45 (Gigabit) + 1x USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | - | ACTIVE
1 | C2S1 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-402 | 32 | 24 | 8 | ACTIVE
2 | C2S2 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-602 | 32 | 23 | 9 | ACTIVE
3 | C2S3 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-602, JB-607 | 32 | 29 | 3 | ACTIVE
4 | C2S4 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-607 | 32 | 32 | - | ACTIVE
5 | C2S5 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-607 | 32 | 20 | 12 | ACTIVE
6 | C2S6 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | JB-402, JB-602 | 32 | 12 | 20 | ACTIVE
7 | C2S7 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | JB-607 | 32 | 31 | 1 | ACTIVE
8 | C2S8 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | JB-607 | 32 | 9 | 23 | ACTIVE
9 | C2S9 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-402 | 16 | 14 | 18 | ACTIVE
10 | C2S10 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-602 | 16 | 32 | - | ACTIVE
11 | C2S11 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | CA1 | 16 | - | 16 | SPARE RESERVE
12 | C2S12 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | CA1 | 16 | - | 16 | SPARE RESERVE
TOTAL | 13 Slots | - | Chassis C2 Total Configured Capacity | - | - | - | 324 | 230 | 126 | 71% Active

## C2S0
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C2S0
ETHERNET COMMUNICATION ADAPTER (1756-EN4TR DLR 2-PORT GIGABIT) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C2 ¦ SLOT: 0 ¦ MODULE: 1756-EN4TR ¦ DESTINATION AREA: CA1 / Field RIO (EtherNet/IP DLR Trunk)
← Back to Chassis Summary (C2SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | -16(A) | C2S0-36/-16(A) | -16(A)/C2S0-36 | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C2S0_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | ACTIVE
RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C2S0-P2/ETH | ETH/C2S0-P2 | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C2S0_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | ACTIVE
USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C2S0-USB/CONSOLE | CONSOLE/C2S0-USB | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C2S0_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | ACTIVE
DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C2S0-DISP/DIAG | DIAG/C2S0-DISP | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C2S0_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | ACTIVE

## C2S1
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C2S1
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C2 ¦ SLOT: 1 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: JB-402
← Back to Chassis Summary (C2SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P2-TBDI1-1 | C2S1-1/P2-TBDI1-1 | P2-TBDI1-1/C2S1-1 | JB-402 | FS-40204_DI_1 | FS-40204 | Flow Switch | ACTIVE
2 | IN-1 | P2-TBDI1-2 | C2S1-2/P2-TBDI1-2 | P2-TBDI1-2/C2S1-2 | JB-402 | FS-40205_DI_1 | FS-40205 | Flow Switch | ACTIVE
3 | IN-2 | P2-TBDI1-3 | C2S1-3/P2-TBDI1-3 | P2-TBDI1-3/C2S1-3 | JB-402 | FT-40221_DI_1 | FT-40221 | Coriolis Flow Transmitter | ACTIVE
4 | IN-3 | P2-TBDI1-4 | C2S1-4/P2-TBDI1-4 | P2-TBDI1-4/C2S1-4 | JB-402 | FT-40222_DI_1 | FT-40222 | Coriolis Flow Transmitter | ACTIVE
5 | IN-4 | P2-TBDI1-5 | C2S1-5/P2-TBDI1-5 | P2-TBDI1-5/C2S1-5 | JB-402 | HV-40207_DI_1 | HV-40207 | Manual Valve With Position Switch | ACTIVE
6 | IN-5 | P2-TBDI1-6 | C2S1-6/P2-TBDI1-6 | P2-TBDI1-6/C2S1-6 | JB-402 | HV-40208_DI_1 | HV-40208 | Manual Valve With Position Switch | ACTIVE
7 | IN-6 | P2-TBDI1-7 | C2S1-7/P2-TBDI1-7 | P2-TBDI1-7/C2S1-7 | JB-402 | XV-40203F_DI_1 | XV-40203F | Control Valve Position Feedback | ACTIVE
8 | IN-7 | P2-TBDI1-8 | C2S1-8/P2-TBDI1-8 | P2-TBDI1-8/C2S1-8 | JB-402 | XV-40203F_DI_2 | XV-40203F | Control Valve Position Feedback | ACTIVE
9 | IN-8 | P2-TBDI1-9 | C2S1-9/P2-TBDI1-9 | P2-TBDI1-9/C2S1-9 | JB-402 | XV-40204B_DI_1 | XV-40204B | Control Valve Position Feedback | ACTIVE
10 | IN-9 | P2-TBDI1-10 | C2S1-10/P2-TBDI1-10 | P2-TBDI1-10/C2S1-10 | JB-402 | XV-40204B_DI_2 | XV-40204B | Control Valve Position Feedback | ACTIVE
11 | IN-10 | P2-TBDI1-11 | C2S1-11/P2-TBDI1-11 | P2-TBDI1-11/C2S1-11 | JB-402 | XV-40204C_DI_1 | XV-40204C | Control Valve Position Feedback | ACTIVE
12 | IN-11 | P2-TBDI1-12 | C2S1-12/P2-TBDI1-12 | P2-TBDI1-12/C2S1-12 | JB-402 | XV-40204C_DI_2 | XV-40204C | Control Valve Position Feedback | ACTIVE
13 | IN-12 | P2-TBDI1-13 | C2S1-13/P2-TBDI1-13 | P2-TBDI1-13/C2S1-13 | JB-402 | XV-40205A_DI_1 | XV-40205A | Control Valve Position Feedback | ACTIVE
14 | IN-13 | P2-TBDI1-14 | C2S1-14/P2-TBDI1-14 | P2-TBDI1-14/C2S1-14 | JB-402 | XV-40205A_DI_2 | XV-40205A | Control Valve Position Feedback | ACTIVE
15 | IN-14 | P2-TBDI1-15 | C2S1-15/P2-TBDI1-15 | P2-TBDI1-15/C2S1-15 | JB-402 | XV-40205B_DI_1 | XV-40205B | Control Valve Position Feedback | ACTIVE
16 | IN-15 | P2-TBDI1-16 | C2S1-16/P2-TBDI1-16 | P2-TBDI1-16/C2S1-16 | JB-402 | XV-40205B_DI_2 | XV-40205B | Control Valve Position Feedback | ACTIVE
17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P2-TBDI1-17 | C2S1-19/P2-TBDI1-17 | P2-TBDI1-17/C2S1-19 | JB-402 | XV-40205C_DI_1 | XV-40205C | Control Valve Position Feedback | ACTIVE
20 | IN-17 | P2-TBDI1-18 | C2S1-20/P2-TBDI1-18 | P2-TBDI1-18/C2S1-20 | JB-402 | XV-40205C_DI_2 | XV-40205C | Control Valve Position Feedback | ACTIVE
21 | IN-18 | P2-TBDI1-19 | C2S1-21/P2-TBDI1-19 | P2-TBDI1-19/C2S1-21 | JB-402 | XV-40205D_DI_1 | XV-40205D | Control Valve Position Feedback | ACTIVE
22 | IN-19 | P2-TBDI1-20 | C2S1-22/P2-TBDI1-20 | P2-TBDI1-20/C2S1-22 | JB-402 | XV-40205D_DI_2 | XV-40205D | Control Valve Position Feedback | ACTIVE
23 | IN-20 | P2-TBDI1-21 | C2S1-23/P2-TBDI1-21 | P2-TBDI1-21/C2S1-23 | JB-402 | XV-40205F_DI_1 | XV-40205F | Control Valve Position Feedback | ACTIVE
24 | IN-21 | P2-TBDI1-22 | C2S1-24/P2-TBDI1-22 | P2-TBDI1-22/C2S1-24 | JB-402 | XV-40205F_DI_2 | XV-40205F | Control Valve Position Feedback | ACTIVE
25 | IN-22 | P2-TBDI1-23 | C2S1-25/P2-TBDI1-23 | P2-TBDI1-23/C2S1-25 | JB-402 | XV-40222_DI_1 | XV-40222 | Control Valve Position Feedback | ACTIVE
26 | IN-23 | P2-TBDI1-24 | C2S1-26/P2-TBDI1-24 | P2-TBDI1-24/C2S1-26 | JB-402 | XV-40222_DI_2 | XV-40222 | Control Valve Position Feedback | ACTIVE
27 | IN-24 | P2-TBDI1-25 | C2S1-27/P2-TBDI1-25 | P2-TBDI1-25/C2S1-27 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | SPARE
28 | IN-25 | P2-TBDI1-26 | C2S1-28/P2-TBDI1-26 | P2-TBDI1-26/C2S1-28 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | SPARE
29 | IN-26 | P2-TBDI1-27 | C2S1-29/P2-TBDI1-27 | P2-TBDI1-27/C2S1-29 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | SPARE
30 | IN-27 | P2-TBDI1-28 | C2S1-30/P2-TBDI1-28 | P2-TBDI1-28/C2S1-30 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | SPARE
31 | IN-28 | P2-TBDI1-29 | C2S1-31/P2-TBDI1-29 | P2-TBDI1-29/C2S1-31 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | SPARE
32 | IN-29 | P2-TBDI1-30 | C2S1-32/P2-TBDI1-30 | P2-TBDI1-30/C2S1-32 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | SPARE
33 | IN-30 | P2-TBDI1-31 | C2S1-33/P2-TBDI1-31 | P2-TBDI1-31/C2S1-33 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | SPARE
34 | IN-31 | P2-TBDI1-32 | C2S1-34/P2-TBDI1-32 | P2-TBDI1-32/C2S1-34 | JB-402 | Spare_DI_2 | Spare | Spare Reserve Channel | SPARE
35 | GND1 | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C2S2
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C2S2
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C2 ¦ SLOT: 2 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: JB-602
← Back to Chassis Summary (C2SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P2-TBDI2-1 | C2S2-1/P2-TBDI2-1 | P2-TBDI2-1/C2S2-1 | JB-602 | FT-60202_DI_1 | FT-60202 | Flow Transmitter | ACTIVE
2 | IN-1 | P2-TBDI2-2 | C2S2-2/P2-TBDI2-2 | P2-TBDI2-2/C2S2-2 | JB-602 | LSH-60251_DI_1 | LSH-60251 | Process Instrument | ACTIVE
3 | IN-2 | P2-TBDI2-3 | C2S2-3/P2-TBDI2-3 | P2-TBDI2-3/C2S2-3 | JB-602 | PSL-60220_DI_1 | PSL-60220 | Process Instrument | ACTIVE
4 | IN-3 | P2-TBDI2-4 | C2S2-4/P2-TBDI2-4 | P2-TBDI2-4/C2S2-4 | JB-602 | TSH-60230_DI_1 | TSH-60230 | Process Instrument | ACTIVE
5 | IN-4 | P2-TBDI2-5 | C2S2-5/P2-TBDI2-5 | P2-TBDI2-5/C2S2-5 | JB-602 | TSH-60240_DI_1 | TSH-60240 | Process Instrument | ACTIVE
6 | IN-5 | P2-TBDI2-6 | C2S2-6/P2-TBDI2-6 | P2-TBDI2-6/C2S2-6 | JB-602 | TSH-60241A_DI_1 | TSH-60241A | Process Instrument | ACTIVE
7 | IN-6 | P2-TBDI2-7 | C2S2-7/P2-TBDI2-7 | P2-TBDI2-7/C2S2-7 | JB-602 | TSH-60242A_DI_1 | TSH-60242A | Process Instrument | ACTIVE
8 | IN-7 | P2-TBDI2-8 | C2S2-8/P2-TBDI2-8 | P2-TBDI2-8/C2S2-8 | JB-602 | TSH-60243A_DI_1 | TSH-60243A | Process Instrument | ACTIVE
9 | IN-8 | P2-TBDI2-9 | C2S2-9/P2-TBDI2-9 | P2-TBDI2-9/C2S2-9 | JB-602 | TSL-60241B_DI_1 | TSL-60241B | Process Instrument | ACTIVE
10 | IN-9 | P2-TBDI2-10 | C2S2-10/P2-TBDI2-10 | P2-TBDI2-10/C2S2-10 | JB-602 | TSL-60242B_DI_1 | TSL-60242B | Process Instrument | ACTIVE
11 | IN-10 | P2-TBDI2-11 | C2S2-11/P2-TBDI2-11 | P2-TBDI2-11/C2S2-11 | JB-602 | TSL-60243B_DI_1 | TSL-60243B | Process Instrument | ACTIVE
12 | IN-11 | P2-TBDI2-12 | C2S2-12/P2-TBDI2-12 | P2-TBDI2-12/C2S2-12 | JB-602 | XA-60240A_DI_1 | XA-60240A | Process Instrument | ACTIVE
13 | IN-12 | P2-TBDI2-13 | C2S2-13/P2-TBDI2-13 | P2-TBDI2-13/C2S2-13 | JB-602 | XA-60240B_DI_1 | XA-60240B | Process Instrument | ACTIVE
14 | IN-13 | P2-TBDI2-14 | C2S2-14/P2-TBDI2-14 | P2-TBDI2-14/C2S2-14 | JB-602 | XA-60241A_DI_1 | XA-60241A | Process Instrument | ACTIVE
15 | IN-14 | P2-TBDI2-15 | C2S2-15/P2-TBDI2-15 | P2-TBDI2-15/C2S2-15 | JB-602 | XA-60241B_DI_1 | XA-60241B | Process Instrument | ACTIVE
16 | IN-15 | P2-TBDI2-16 | C2S2-16/P2-TBDI2-16 | P2-TBDI2-16/C2S2-16 | JB-602 | XA-60242A_DI_1 | XA-60242A | Process Instrument | ACTIVE
17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P2-TBDI2-17 | C2S2-19/P2-TBDI2-17 | P2-TBDI2-17/C2S2-19 | JB-602 | XA-60242B_DI_1 | XA-60242B | Process Instrument | ACTIVE
20 | IN-17 | P2-TBDI2-18 | C2S2-20/P2-TBDI2-18 | P2-TBDI2-18/C2S2-20 | JB-602 | XA-60243A_DI_1 | XA-60243A | Process Instrument | ACTIVE
21 | IN-18 | P2-TBDI2-19 | C2S2-21/P2-TBDI2-19 | P2-TBDI2-19/C2S2-21 | JB-602 | XA-60243B_DI_1 | XA-60243B | Process Instrument | ACTIVE
22 | IN-19 | P2-TBDI2-20 | C2S2-22/P2-TBDI2-20 | P2-TBDI2-20/C2S2-22 | JB-602 | XV-60214_DI_1 | XV-60214 | Control Valve Position Feedback | ACTIVE
23 | IN-20 | P2-TBDI2-21 | C2S2-23/P2-TBDI2-21 | P2-TBDI2-21/C2S2-23 | JB-602 | XV-60214_DI_2 | XV-60214 | Control Valve Position Feedback | ACTIVE
24 | IN-21 | P2-TBDI2-22 | C2S2-24/P2-TBDI2-22 | P2-TBDI2-22/C2S2-24 | JB-602 | XV-60241_DI_1 | XV-60241 | Control Valve Position Feedback | ACTIVE
25 | IN-22 | P2-TBDI2-23 | C2S2-25/P2-TBDI2-23 | P2-TBDI2-23/C2S2-25 | JB-602 | XV-60241_DI_2 | XV-60241 | Control Valve Position Feedback | ACTIVE
26 | IN-23 | P2-TBDI2-24 | C2S2-26/P2-TBDI2-24 | P2-TBDI2-24/C2S2-26 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
27 | IN-24 | P2-TBDI2-25 | C2S2-27/P2-TBDI2-25 | P2-TBDI2-25/C2S2-27 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
28 | IN-25 | P2-TBDI2-26 | C2S2-28/P2-TBDI2-26 | P2-TBDI2-26/C2S2-28 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
29 | IN-26 | P2-TBDI2-27 | C2S2-29/P2-TBDI2-27 | P2-TBDI2-27/C2S2-29 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-27 | P2-TBDI2-28 | C2S2-30/P2-TBDI2-28 | P2-TBDI2-28/C2S2-30 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
31 | IN-28 | P2-TBDI2-29 | C2S2-31/P2-TBDI2-29 | P2-TBDI2-29/C2S2-31 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-29 | P2-TBDI2-30 | C2S2-32/P2-TBDI2-30 | P2-TBDI2-30/C2S2-32 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
33 | IN-30 | P2-TBDI2-31 | C2S2-33/P2-TBDI2-31 | P2-TBDI2-31/C2S2-33 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-31 | P2-TBDI2-32 | C2S2-34/P2-TBDI2-32 | P2-TBDI2-32/C2S2-34 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
35 | GND1 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C2S3
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C2S3
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C2 ¦ SLOT: 3 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: JB-602, JB-607
← Back to Chassis Summary (C2SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P2-TBDI3-1 | C2S3-1/P2-TBDI3-1 | P2-TBDI3-1/C2S3-1 | JB-607 | XA-FH-60210A_DI_1 | XA-FH-60210A | Process Instrument | ACTIVE
2 | IN-1 | P2-TBDI3-2 | C2S3-2/P2-TBDI3-2 | P2-TBDI3-2/C2S3-2 | JB-607 | XA-FH-60210B_DI_1 | XA-FH-60210B | Process Instrument | ACTIVE
3 | IN-2 | P2-TBDI3-3 | C2S3-3/P2-TBDI3-3 | P2-TBDI3-3/C2S3-3 | JB-607 | XA-FH-60210C_DI_1 | XA-FH-60210C | Process Instrument | ACTIVE
4 | IN-3 | P2-TBDI3-4 | C2S3-4/P2-TBDI3-4 | P2-TBDI3-4/C2S3-4 | JB-607 | XA-FH-60210D_DI_1 | XA-FH-60210D | Process Instrument | ACTIVE
5 | IN-4 | P2-TBDI3-5 | C2S3-5/P2-TBDI3-5 | P2-TBDI3-5/C2S3-5 | JB-607 | XA-FH-60210E_DI_1 | XA-FH-60210E | Process Instrument | ACTIVE
6 | IN-5 | P2-TBDI3-6 | C2S3-6/P2-TBDI3-6 | P2-TBDI3-6/C2S3-6 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
7 | IN-6 | P2-TBDI3-7 | C2S3-7/P2-TBDI3-7 | P2-TBDI3-7/C2S3-7 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
8 | IN-7 | P2-TBDI3-8 | C2S3-8/P2-TBDI3-8 | P2-TBDI3-8/C2S3-8 | JB-602 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
9 | IN-8 | P2-TBDI3-9 | C2S3-9/P2-TBDI3-9 | P2-TBDI3-9/C2S3-9 | JB-607 | SV-60207_DI_1 | SV-60207 | Process Instrument | ACTIVE
10 | IN-9 | P2-TBDI3-10 | C2S3-10/P2-TBDI3-10 | P2-TBDI3-10/C2S3-10 | JB-607 | SV-60207_DI_2 | SV-60207 | Process Instrument | ACTIVE
11 | IN-10 | P2-TBDI3-11 | C2S3-11/P2-TBDI3-11 | P2-TBDI3-11/C2S3-11 | JB-607 | XV-60264_DI_1 | XV-60264 | Control Valve Position Feedback | ACTIVE
12 | IN-11 | P2-TBDI3-12 | C2S3-12/P2-TBDI3-12 | P2-TBDI3-12/C2S3-12 | JB-607 | XV-60264_DI_2 | XV-60264 | Control Valve Position Feedback | ACTIVE
13 | IN-12 | P2-TBDI3-13 | C2S3-13/P2-TBDI3-13 | P2-TBDI3-13/C2S3-13 | JB-607 | XV-60264FN_DI_1 | XV-60264FN | Control Valve Position Feedback | ACTIVE
14 | IN-13 | P2-TBDI3-14 | C2S3-14/P2-TBDI3-14 | P2-TBDI3-14/C2S3-14 | JB-607 | XV-60264FN_DI_2 | XV-60264FN | Control Valve Position Feedback | ACTIVE
15 | IN-14 | P2-TBDI3-15 | C2S3-15/P2-TBDI3-15 | P2-TBDI3-15/C2S3-15 | JB-607 | XV-60264FP_DI_1 | XV-60264FP | Control Valve Position Feedback | ACTIVE
16 | IN-15 | P2-TBDI3-16 | C2S3-16/P2-TBDI3-16 | P2-TBDI3-16/C2S3-16 | JB-607 | XV-60264FP_DI_2 | XV-60264FP | Control Valve Position Feedback | ACTIVE
17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P2-TBDI3-17 | C2S3-19/P2-TBDI3-17 | P2-TBDI3-17/C2S3-19 | JB-607 | XV-60201_DI_1 | XV-60201 | Control Valve Position Feedback | ACTIVE
20 | IN-17 | P2-TBDI3-18 | C2S3-20/P2-TBDI3-18 | P2-TBDI3-18/C2S3-20 | JB-607 | XV-60201_DI_2 | XV-60201 | Control Valve Position Feedback | ACTIVE
21 | IN-18 | P2-TBDI3-19 | C2S3-21/P2-TBDI3-19 | P2-TBDI3-19/C2S3-21 | JB-607 | XV-60264FQ_DI_1 | XV-60264FQ | Control Valve Position Feedback | ACTIVE
22 | IN-19 | P2-TBDI3-20 | C2S3-22/P2-TBDI3-20 | P2-TBDI3-20/C2S3-22 | JB-607 | XV-60264FQ_DI_2 | XV-60264FQ | Control Valve Position Feedback | ACTIVE
23 | IN-20 | P2-TBDI3-21 | C2S3-23/P2-TBDI3-21 | P2-TBDI3-21/C2S3-23 | JB-607 | XV-60261_DI_1 | XV-60261 | Control Valve Position Feedback | ACTIVE
24 | IN-21 | P2-TBDI3-22 | C2S3-24/P2-TBDI3-22 | P2-TBDI3-22/C2S3-24 | JB-607 | XV-60261_DI_2 | XV-60261 | Control Valve Position Feedback | ACTIVE
25 | IN-22 | P2-TBDI3-23 | C2S3-25/P2-TBDI3-23 | P2-TBDI3-23/C2S3-25 | JB-607 | XV-60264FR_DI_1 | XV-60264FR | Control Valve Position Feedback | ACTIVE
26 | IN-23 | P2-TBDI3-24 | C2S3-26/P2-TBDI3-24 | P2-TBDI3-24/C2S3-26 | JB-607 | XV-60264FR_DI_2 | XV-60264FR | Control Valve Position Feedback | ACTIVE
27 | IN-24 | P2-TBDI3-25 | C2S3-27/P2-TBDI3-25 | P2-TBDI3-25/C2S3-27 | JB-607 | XV-60261FA_DI_1 | XV-60261FA | Control Valve Position Feedback | ACTIVE
28 | IN-25 | P2-TBDI3-26 | C2S3-28/P2-TBDI3-26 | P2-TBDI3-26/C2S3-28 | JB-607 | XV-60261FA_DI_2 | XV-60261FA | Control Valve Position Feedback | ACTIVE
29 | IN-26 | P2-TBDI3-27 | C2S3-29/P2-TBDI3-27 | P2-TBDI3-27/C2S3-29 | JB-607 | XV-60264SN_DI_1 | XV-60264SN | Control Valve Position Feedback | ACTIVE
30 | IN-27 | P2-TBDI3-28 | C2S3-30/P2-TBDI3-28 | P2-TBDI3-28/C2S3-30 | JB-607 | XV-60264SN_DI_2 | XV-60264SN | Control Valve Position Feedback | ACTIVE
31 | IN-28 | P2-TBDI3-29 | C2S3-31/P2-TBDI3-29 | P2-TBDI3-29/C2S3-31 | JB-607 | XV-60261FB_DI_1 | XV-60261FB | Control Valve Position Feedback | ACTIVE
32 | IN-29 | P2-TBDI3-30 | C2S3-32/P2-TBDI3-30 | P2-TBDI3-30/C2S3-32 | JB-607 | XV-60261FB_DI_2 | XV-60261FB | Control Valve Position Feedback | ACTIVE
33 | IN-30 | P2-TBDI3-31 | C2S3-33/P2-TBDI3-31 | P2-TBDI3-31/C2S3-33 | JB-607 | XV-60264SP_DI_1 | XV-60264SP | Control Valve Position Feedback | ACTIVE
34 | IN-31 | P2-TBDI3-32 | C2S3-34/P2-TBDI3-32 | P2-TBDI3-32/C2S3-34 | JB-607 | XV-60264SP_DI_2 | XV-60264SP | Control Valve Position Feedback | ACTIVE
35 | GND1 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C2S4
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C2S4
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C2 ¦ SLOT: 4 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: JB-607
← Back to Chassis Summary (C2SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P2-TBDI4-1 | C2S4-1/P2-TBDI4-1 | P2-TBDI4-1/C2S4-1 | JB-607 | XV-60261FC_DI_1 | XV-60261FC | Control Valve Position Feedback | ACTIVE
2 | IN-1 | P2-TBDI4-2 | C2S4-2/P2-TBDI4-2 | P2-TBDI4-2/C2S4-2 | JB-607 | XV-60261FC_DI_2 | XV-60261FC | Control Valve Position Feedback | ACTIVE
3 | IN-2 | P2-TBDI4-3 | C2S4-3/P2-TBDI4-3 | P2-TBDI4-3/C2S4-3 | JB-607 | XV-60264SQ_DI_1 | XV-60264SQ | Control Valve Position Feedback | ACTIVE
4 | IN-3 | P2-TBDI4-4 | C2S4-4/P2-TBDI4-4 | P2-TBDI4-4/C2S4-4 | JB-607 | XV-60264SQ_DI_2 | XV-60264SQ | Control Valve Position Feedback | ACTIVE
5 | IN-4 | P2-TBDI4-5 | C2S4-5/P2-TBDI4-5 | P2-TBDI4-5/C2S4-5 | JB-607 | XV-60261FD_DI_1 | XV-60261FD | Control Valve Position Feedback | ACTIVE
6 | IN-5 | P2-TBDI4-6 | C2S4-6/P2-TBDI4-6 | P2-TBDI4-6/C2S4-6 | JB-607 | XV-60261FD_DI_2 | XV-60261FD | Control Valve Position Feedback | ACTIVE
7 | IN-6 | P2-TBDI4-7 | C2S4-7/P2-TBDI4-7 | P2-TBDI4-7/C2S4-7 | JB-607 | XV-60264SR_DI_1 | XV-60264SR | Control Valve Position Feedback | ACTIVE
8 | IN-7 | P2-TBDI4-8 | C2S4-8/P2-TBDI4-8 | P2-TBDI4-8/C2S4-8 | JB-607 | XV-60264SR_DI_2 | XV-60264SR | Control Valve Position Feedback | ACTIVE
9 | IN-8 | P2-TBDI4-9 | C2S4-9/P2-TBDI4-9 | P2-TBDI4-9/C2S4-9 | JB-607 | XV-60261SA_DI_1 | XV-60261SA | Control Valve Position Feedback | ACTIVE
10 | IN-9 | P2-TBDI4-10 | C2S4-10/P2-TBDI4-10 | P2-TBDI4-10/C2S4-10 | JB-607 | XV-60261SA_DI_2 | XV-60261SA | Control Valve Position Feedback | ACTIVE
11 | IN-10 | P2-TBDI4-11 | C2S4-11/P2-TBDI4-11 | P2-TBDI4-11/C2S4-11 | JB-607 | XV-60261SB_DI_1 | XV-60261SB | Control Valve Position Feedback | ACTIVE
12 | IN-11 | P2-TBDI4-12 | C2S4-12/P2-TBDI4-12 | P2-TBDI4-12/C2S4-12 | JB-607 | XV-60261SB_DI_2 | XV-60261SB | Control Valve Position Feedback | ACTIVE
13 | IN-12 | P2-TBDI4-13 | C2S4-13/P2-TBDI4-13 | P2-TBDI4-13/C2S4-13 | JB-607 | XV-60261SC_DI_1 | XV-60261SC | Control Valve Position Feedback | ACTIVE
14 | IN-13 | P2-TBDI4-14 | C2S4-14/P2-TBDI4-14 | P2-TBDI4-14/C2S4-14 | JB-607 | XV-60261SC_DI_2 | XV-60261SC | Control Valve Position Feedback | ACTIVE
15 | IN-14 | P2-TBDI4-15 | C2S4-15/P2-TBDI4-15 | P2-TBDI4-15/C2S4-15 | JB-607 | XV-60261SD_DI_1 | XV-60261SD | Control Valve Position Feedback | ACTIVE
16 | IN-15 | P2-TBDI4-16 | C2S4-16/P2-TBDI4-16 | P2-TBDI4-16/C2S4-16 | JB-607 | XV-60261SD_DI_2 | XV-60261SD | Control Valve Position Feedback | ACTIVE
17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P2-TBDI4-17 | C2S4-19/P2-TBDI4-17 | P2-TBDI4-17/C2S4-19 | JB-607 | XV-60262_DI_1 | XV-60262 | Control Valve Position Feedback | ACTIVE
20 | IN-17 | P2-TBDI4-18 | C2S4-20/P2-TBDI4-18 | P2-TBDI4-18/C2S4-20 | JB-607 | XV-60262_DI_2 | XV-60262 | Control Valve Position Feedback | ACTIVE
21 | IN-18 | P2-TBDI4-19 | C2S4-21/P2-TBDI4-19 | P2-TBDI4-19/C2S4-21 | JB-607 | XV-60262FE_DI_1 | XV-60262FE | Control Valve Position Feedback | ACTIVE
22 | IN-19 | P2-TBDI4-20 | C2S4-22/P2-TBDI4-20 | P2-TBDI4-20/C2S4-22 | JB-607 | XV-60262FE_DI_2 | XV-60262FE | Control Valve Position Feedback | ACTIVE
23 | IN-20 | P2-TBDI4-21 | C2S4-23/P2-TBDI4-21 | P2-TBDI4-21/C2S4-23 | JB-607 | XV-60262FF_DI_1 | XV-60262FF | Control Valve Position Feedback | ACTIVE
24 | IN-21 | P2-TBDI4-22 | C2S4-24/P2-TBDI4-22 | P2-TBDI4-22/C2S4-24 | JB-607 | XV-60262FF_DI_2 | XV-60262FF | Control Valve Position Feedback | ACTIVE
25 | IN-22 | P2-TBDI4-23 | C2S4-25/P2-TBDI4-23 | P2-TBDI4-23/C2S4-25 | JB-607 | XV-60262FG_DI_1 | XV-60262FG | Control Valve Position Feedback | ACTIVE
26 | IN-23 | P2-TBDI4-24 | C2S4-26/P2-TBDI4-24 | P2-TBDI4-24/C2S4-26 | JB-607 | XV-60262FG_DI_2 | XV-60262FG | Control Valve Position Feedback | ACTIVE
27 | IN-24 | P2-TBDI4-25 | C2S4-27/P2-TBDI4-25 | P2-TBDI4-25/C2S4-27 | JB-607 | XV-60262FH_DI_1 | XV-60262FH | Control Valve Position Feedback | ACTIVE
28 | IN-25 | P2-TBDI4-26 | C2S4-28/P2-TBDI4-26 | P2-TBDI4-26/C2S4-28 | JB-607 | XV-60262FH_DI_2 | XV-60262FH | Control Valve Position Feedback | ACTIVE
29 | IN-26 | P2-TBDI4-27 | C2S4-29/P2-TBDI4-27 | P2-TBDI4-27/C2S4-29 | JB-607 | XV-60262SE_DI_1 | XV-60262SE | Control Valve Position Feedback | ACTIVE
30 | IN-27 | P2-TBDI4-28 | C2S4-30/P2-TBDI4-28 | P2-TBDI4-28/C2S4-30 | JB-607 | XV-60262SE_DI_2 | XV-60262SE | Control Valve Position Feedback | ACTIVE
31 | IN-28 | P2-TBDI4-29 | C2S4-31/P2-TBDI4-29 | P2-TBDI4-29/C2S4-31 | JB-607 | XV-60262SF_DI_1 | XV-60262SF | Control Valve Position Feedback | ACTIVE
32 | IN-29 | P2-TBDI4-30 | C2S4-32/P2-TBDI4-30 | P2-TBDI4-30/C2S4-32 | JB-607 | XV-60262SF_DI_2 | XV-60262SF | Control Valve Position Feedback | ACTIVE
33 | IN-30 | P2-TBDI4-31 | C2S4-33/P2-TBDI4-31 | P2-TBDI4-31/C2S4-33 | JB-607 | XV-60262SG_DI_1 | XV-60262SG | Control Valve Position Feedback | ACTIVE
34 | IN-31 | P2-TBDI4-32 | C2S4-34/P2-TBDI4-32 | P2-TBDI4-32/C2S4-34 | JB-607 | XV-60262SG_DI_2 | XV-60262SG | Control Valve Position Feedback | ACTIVE
35 | GND1 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C2S5
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C2S5
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C2 ¦ SLOT: 5 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: JB-607
← Back to Chassis Summary (C2SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P2-TBDI5-1 | C2S5-1/P2-TBDI5-1 | P2-TBDI5-1/C2S5-1 | JB-607 | XV-60262SH_DI_1 | XV-60262SH | Control Valve Position Feedback | ACTIVE
2 | IN-1 | P2-TBDI5-2 | C2S5-2/P2-TBDI5-2 | P2-TBDI5-2/C2S5-2 | JB-607 | XV-60262SH_DI_2 | XV-60262SH | Control Valve Position Feedback | ACTIVE
3 | IN-2 | P2-TBDI5-3 | C2S5-3/P2-TBDI5-3 | P2-TBDI5-3/C2S5-3 | JB-607 | XV-60263_DI_1 | XV-60263 | Control Valve Position Feedback | ACTIVE
4 | IN-3 | P2-TBDI5-4 | C2S5-4/P2-TBDI5-4 | P2-TBDI5-4/C2S5-4 | JB-607 | XV-60263_DI_2 | XV-60263 | Control Valve Position Feedback | ACTIVE
5 | IN-4 | P2-TBDI5-5 | C2S5-5/P2-TBDI5-5 | P2-TBDI5-5/C2S5-5 | JB-607 | XV-60263FJ_DI_1 | XV-60263FJ | Control Valve Position Feedback | ACTIVE
6 | IN-5 | P2-TBDI5-6 | C2S5-6/P2-TBDI5-6 | P2-TBDI5-6/C2S5-6 | JB-607 | XV-60263FJ_DI_2 | XV-60263FJ | Control Valve Position Feedback | ACTIVE
7 | IN-6 | P2-TBDI5-7 | C2S5-7/P2-TBDI5-7 | P2-TBDI5-7/C2S5-7 | JB-607 | XV-60263FK_DI_1 | XV-60263FK | Control Valve Position Feedback | ACTIVE
8 | IN-7 | P2-TBDI5-8 | C2S5-8/P2-TBDI5-8 | P2-TBDI5-8/C2S5-8 | JB-607 | XV-60263FK_DI_2 | XV-60263FK | Control Valve Position Feedback | ACTIVE
9 | IN-8 | P2-TBDI5-9 | C2S5-9/P2-TBDI5-9 | P2-TBDI5-9/C2S5-9 | JB-607 | XV-60263FL_DI_1 | XV-60263FL | Control Valve Position Feedback | ACTIVE
10 | IN-9 | P2-TBDI5-10 | C2S5-10/P2-TBDI5-10 | P2-TBDI5-10/C2S5-10 | JB-607 | XV-60263FL_DI_2 | XV-60263FL | Control Valve Position Feedback | ACTIVE
11 | IN-10 | P2-TBDI5-11 | C2S5-11/P2-TBDI5-11 | P2-TBDI5-11/C2S5-11 | JB-607 | XV-60263FM_DI_1 | XV-60263FM | Control Valve Position Feedback | ACTIVE
12 | IN-11 | P2-TBDI5-12 | C2S5-12/P2-TBDI5-12 | P2-TBDI5-12/C2S5-12 | JB-607 | XV-60263FM_DI_2 | XV-60263FM | Control Valve Position Feedback | ACTIVE
13 | IN-12 | P2-TBDI5-13 | C2S5-13/P2-TBDI5-13 | P2-TBDI5-13/C2S5-13 | JB-607 | XV-60263SJ_DI_1 | XV-60263SJ | Control Valve Position Feedback | ACTIVE
14 | IN-13 | P2-TBDI5-14 | C2S5-14/P2-TBDI5-14 | P2-TBDI5-14/C2S5-14 | JB-607 | XV-60263SJ_DI_2 | XV-60263SJ | Control Valve Position Feedback | ACTIVE
15 | IN-14 | P2-TBDI5-15 | C2S5-15/P2-TBDI5-15 | P2-TBDI5-15/C2S5-15 | JB-607 | XV-60263SK_DI_1 | XV-60263SK | Control Valve Position Feedback | ACTIVE
16 | IN-15 | P2-TBDI5-16 | C2S5-16/P2-TBDI5-16 | P2-TBDI5-16/C2S5-16 | JB-607 | XV-60263SK_DI_2 | XV-60263SK | Control Valve Position Feedback | ACTIVE
17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P2-TBDI5-17 | C2S5-19/P2-TBDI5-17 | P2-TBDI5-17/C2S5-19 | JB-607 | XV-60263SL_DI_1 | XV-60263SL | Control Valve Position Feedback | ACTIVE
20 | IN-17 | P2-TBDI5-18 | C2S5-20/P2-TBDI5-18 | P2-TBDI5-18/C2S5-20 | JB-607 | XV-60263SL_DI_2 | XV-60263SL | Control Valve Position Feedback | ACTIVE
21 | IN-18 | P2-TBDI5-19 | C2S5-21/P2-TBDI5-19 | P2-TBDI5-19/C2S5-21 | JB-607 | XV-60263SM_DI_1 | XV-60263SM | Control Valve Position Feedback | ACTIVE
22 | IN-19 | P2-TBDI5-20 | C2S5-22/P2-TBDI5-20 | P2-TBDI5-20/C2S5-22 | JB-607 | XV-60263SM_DI_2 | XV-60263SM | Control Valve Position Feedback | ACTIVE
23 | IN-20 | P2-TBDI5-21 | C2S5-23/P2-TBDI5-21 | P2-TBDI5-21/C2S5-23 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
24 | IN-21 | P2-TBDI5-22 | C2S5-24/P2-TBDI5-22 | P2-TBDI5-22/C2S5-24 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
25 | IN-22 | P2-TBDI5-23 | C2S5-25/P2-TBDI5-23 | P2-TBDI5-23/C2S5-25 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
26 | IN-23 | P2-TBDI5-24 | C2S5-26/P2-TBDI5-24 | P2-TBDI5-24/C2S5-26 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
27 | IN-24 | P2-TBDI5-25 | C2S5-27/P2-TBDI5-25 | P2-TBDI5-25/C2S5-27 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
28 | IN-25 | P2-TBDI5-26 | C2S5-28/P2-TBDI5-26 | P2-TBDI5-26/C2S5-28 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
29 | IN-26 | P2-TBDI5-27 | C2S5-29/P2-TBDI5-27 | P2-TBDI5-27/C2S5-29 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-27 | P2-TBDI5-28 | C2S5-30/P2-TBDI5-28 | P2-TBDI5-28/C2S5-30 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
31 | IN-28 | P2-TBDI5-29 | C2S5-31/P2-TBDI5-29 | P2-TBDI5-29/C2S5-31 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-29 | P2-TBDI5-30 | C2S5-32/P2-TBDI5-30 | P2-TBDI5-30/C2S5-32 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
33 | IN-30 | P2-TBDI5-31 | C2S5-33/P2-TBDI5-31 | P2-TBDI5-31/C2S5-33 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-31 | P2-TBDI5-32 | C2S5-34/P2-TBDI5-32 | P2-TBDI5-32/C2S5-34 | JB-607 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
35 | GND1 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C2S6
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C2S6
DIGITAL OUTPUT CARD (1756-OB32 32-CH 24VDC SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C2 ¦ SLOT: 6 ¦ MODULE: 1756-OB32 ¦ DESTINATION AREA: JB-402, JB-602
← Back to Chassis Summary (C2SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBRLx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | OUT-0 | P2-TBRL1-1 | C2S6-1/P2-TBRL1-1 | P2-TBRL1-1/C2S6-1 | JB-402 | XV-40203F_DO_1 | XV-40203F | Control Valve Position Feedback | ACTIVE
2 | OUT-1 | P2-TBRL1-2 | C2S6-2/P2-TBRL1-2 | P2-TBRL1-2/C2S6-2 | JB-402 | XV-40204B_DO_1 | XV-40204B | Control Valve Position Feedback | ACTIVE
3 | OUT-2 | P2-TBRL1-3 | C2S6-3/P2-TBRL1-3 | P2-TBRL1-3/C2S6-3 | JB-402 | XV-40204C_DO_1 | XV-40204C | Control Valve Position Feedback | ACTIVE
4 | OUT-3 | P2-TBRL1-4 | C2S6-4/P2-TBRL1-4 | P2-TBRL1-4/C2S6-4 | JB-402 | XV-40205A_DO_1 | XV-40205A | Control Valve Position Feedback | ACTIVE
5 | OUT-4 | P2-TBRL1-5 | C2S6-5/P2-TBRL1-5 | P2-TBRL1-5/C2S6-5 | JB-402 | XV-40205B_DO_1 | XV-40205B | Control Valve Position Feedback | ACTIVE
6 | OUT-5 | P2-TBRL1-6 | C2S6-6/P2-TBRL1-6 | P2-TBRL1-6/C2S6-6 | JB-402 | XV-40205C_DO_1 | XV-40205C | Control Valve Position Feedback | ACTIVE
7 | OUT-6 | P2-TBRL1-7 | C2S6-7/P2-TBRL1-7 | P2-TBRL1-7/C2S6-7 | JB-402 | XV-40205D_DO_1 | XV-40205D | Control Valve Position Feedback | ACTIVE
8 | OUT-7 | P2-TBRL1-8 | C2S6-8/P2-TBRL1-8 | P2-TBRL1-8/C2S6-8 | JB-402 | XV-40205F_DO_1 | XV-40205F | Control Valve Position Feedback | ACTIVE
9 | OUT-8 | P2-TBRL1-9 | C2S6-9/P2-TBRL1-9 | P2-TBRL1-9/C2S6-9 | JB-402 | XV-40222_DO_1 | XV-40222 | Control Valve Position Feedback | ACTIVE
10 | OUT-9 | P2-TBRL1-10 | C2S6-10/P2-TBRL1-10 | P2-TBRL1-10/C2S6-10 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
11 | OUT-10 | P2-TBRL1-11 | C2S6-11/P2-TBRL1-11 | P2-TBRL1-11/C2S6-11 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
12 | OUT-11 | P2-TBRL1-12 | C2S6-12/P2-TBRL1-12 | P2-TBRL1-12/C2S6-12 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
13 | OUT-12 | P2-TBRL1-13 | C2S6-13/P2-TBRL1-13 | P2-TBRL1-13/C2S6-13 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
14 | OUT-13 | P2-TBRL1-14 | C2S6-14/P2-TBRL1-14 | P2-TBRL1-14/C2S6-14 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
15 | OUT-14 | P2-TBRL1-15 | C2S6-15/P2-TBRL1-15 | P2-TBRL1-15/C2S6-15 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
16 | OUT-15 | P2-TBRL1-16 | C2S6-16/P2-TBRL1-16 | P2-TBRL1-16/C2S6-16 | JB-402 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
17 | RTN OUT-0 | P2-TBRL1-17 | C2S6-17/P2-TBRL1-17 | P2-TBRL1-17/C2S6-17 | JB-402 | Spare_DO_17 | Spare | Spare Reserve Channel | SPARE
18 | DC-0(+) | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | OUT-16 | P2-TBRL1-17 | C2S6-19/P2-TBRL1-17 | P2-TBRL1-17/C2S6-19 | JB-602 | XS-60240B_DO_1 | XS-60240B | Process Instrument | ACTIVE
20 | OUT-17 | P2-TBRL1-18 | C2S6-20/P2-TBRL1-18 | P2-TBRL1-18/C2S6-20 | JB-602 | XV-60214_DO_1 | XV-60214 | Control Valve Position Feedback | ACTIVE
21 | OUT-18 | P2-TBRL1-19 | C2S6-21/P2-TBRL1-19 | P2-TBRL1-19/C2S6-21 | JB-602 | XV-60241_DO_1 | XV-60241 | Control Valve Position Feedback | ACTIVE
22 | OUT-19 | P2-TBRL1-20 | C2S6-22/P2-TBRL1-20 | P2-TBRL1-20/C2S6-22 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
23 | OUT-20 | P2-TBRL1-21 | C2S6-23/P2-TBRL1-21 | P2-TBRL1-21/C2S6-23 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
24 | OUT-21 | P2-TBRL1-22 | C2S6-24/P2-TBRL1-22 | P2-TBRL1-22/C2S6-24 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
25 | OUT-22 | P2-TBRL1-23 | C2S6-25/P2-TBRL1-23 | P2-TBRL1-23/C2S6-25 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
26 | OUT-23 | P2-TBRL1-24 | C2S6-26/P2-TBRL1-24 | P2-TBRL1-24/C2S6-26 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
27 | OUT-24 | P2-TBRL1-25 | C2S6-27/P2-TBRL1-25 | P2-TBRL1-25/C2S6-27 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
28 | OUT-25 | P2-TBRL1-26 | C2S6-28/P2-TBRL1-26 | P2-TBRL1-26/C2S6-28 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
29 | OUT-26 | P2-TBRL1-27 | C2S6-29/P2-TBRL1-27 | P2-TBRL1-27/C2S6-29 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
30 | OUT-27 | P2-TBRL1-28 | C2S6-30/P2-TBRL1-28 | P2-TBRL1-28/C2S6-30 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
31 | OUT-28 | P2-TBRL1-29 | C2S6-31/P2-TBRL1-29 | P2-TBRL1-29/C2S6-31 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
32 | OUT-29 | P2-TBRL1-30 | C2S6-32/P2-TBRL1-30 | P2-TBRL1-30/C2S6-32 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
33 | OUT-30 | P2-TBRL1-31 | C2S6-33/P2-TBRL1-31 | P2-TBRL1-31/C2S6-33 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
34 | OUT-31 | P2-TBRL1-32 | C2S6-34/P2-TBRL1-32 | P2-TBRL1-32/C2S6-34 | JB-602 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
35 | RTN OUT-1 | P2-TBRL1-35 | C2S6-35/P2-TBRL1-35 | P2-TBRL1-35/C2S6-35 | JB-402 | Spare_DO_35 | Spare | Spare Reserve Channel | SPARE
36 | DC-1(+) | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C2S7
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C2S7
DIGITAL OUTPUT CARD (1756-OB32 32-CH 24VDC SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C2 ¦ SLOT: 7 ¦ MODULE: 1756-OB32 ¦ DESTINATION AREA: JB-607
← Back to Chassis Summary (C2SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBRLx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | OUT-0 | P2-TBRL2-1 | C2S7-1/P2-TBRL2-1 | P2-TBRL2-1/C2S7-1 | JB-607 | SV-60207_DO_1 | SV-60207 | Process Instrument | ACTIVE
2 | OUT-1 | P2-TBRL2-2 | C2S7-2/P2-TBRL2-2 | P2-TBRL2-2/C2S7-2 | JB-607 | XS-FH-60210C_DO_1 | XS-FH-60210C | Process Instrument | ACTIVE
3 | OUT-2 | P2-TBRL2-3 | C2S7-3/P2-TBRL2-3 | P2-TBRL2-3/C2S7-3 | JB-607 | XS-FH-60210D_DO_1 | XS-FH-60210D | Process Instrument | ACTIVE
4 | OUT-3 | P2-TBRL2-4 | C2S7-4/P2-TBRL2-4 | P2-TBRL2-4/C2S7-4 | JB-607 | XV-60201_DO_1 | XV-60201 | Control Valve Position Feedback | ACTIVE
5 | OUT-4 | P2-TBRL2-5 | C2S7-5/P2-TBRL2-5 | P2-TBRL2-5/C2S7-5 | JB-607 | XV-60261_DO_1 | XV-60261 | Control Valve Position Feedback | ACTIVE
6 | OUT-5 | P2-TBRL2-6 | C2S7-6/P2-TBRL2-6 | P2-TBRL2-6/C2S7-6 | JB-607 | XV-60261FA_DO_1 | XV-60261FA | Control Valve Position Feedback | ACTIVE
7 | OUT-6 | P2-TBRL2-7 | C2S7-7/P2-TBRL2-7 | P2-TBRL2-7/C2S7-7 | JB-607 | XV-60261FB_DO_1 | XV-60261FB | Control Valve Position Feedback | ACTIVE
8 | OUT-7 | P2-TBRL2-8 | C2S7-8/P2-TBRL2-8 | P2-TBRL2-8/C2S7-8 | JB-607 | XV-60261FC_DO_1 | XV-60261FC | Control Valve Position Feedback | ACTIVE
9 | OUT-8 | P2-TBRL2-9 | C2S7-9/P2-TBRL2-9 | P2-TBRL2-9/C2S7-9 | JB-607 | XV-60261FD_DO_1 | XV-60261FD | Control Valve Position Feedback | ACTIVE
10 | OUT-9 | P2-TBRL2-10 | C2S7-10/P2-TBRL2-10 | P2-TBRL2-10/C2S7-10 | JB-607 | XV-60261SA_DO_1 | XV-60261SA | Control Valve Position Feedback | ACTIVE
11 | OUT-10 | P2-TBRL2-11 | C2S7-11/P2-TBRL2-11 | P2-TBRL2-11/C2S7-11 | JB-607 | XV-60261SB_DO_1 | XV-60261SB | Control Valve Position Feedback | ACTIVE
12 | OUT-11 | P2-TBRL2-12 | C2S7-12/P2-TBRL2-12 | P2-TBRL2-12/C2S7-12 | JB-607 | XV-60261SC_DO_1 | XV-60261SC | Control Valve Position Feedback | ACTIVE
13 | OUT-12 | P2-TBRL2-13 | C2S7-13/P2-TBRL2-13 | P2-TBRL2-13/C2S7-13 | JB-607 | XV-60261SD_DO_1 | XV-60261SD | Control Valve Position Feedback | ACTIVE
14 | OUT-13 | P2-TBRL2-14 | C2S7-14/P2-TBRL2-14 | P2-TBRL2-14/C2S7-14 | JB-607 | XV-60262_DO_1 | XV-60262 | Control Valve Position Feedback | ACTIVE
15 | OUT-14 | P2-TBRL2-15 | C2S7-15/P2-TBRL2-15 | P2-TBRL2-15/C2S7-15 | JB-607 | XV-60262FE_DO_1 | XV-60262FE | Control Valve Position Feedback | ACTIVE
16 | OUT-15 | P2-TBRL2-16 | C2S7-16/P2-TBRL2-16 | P2-TBRL2-16/C2S7-16 | JB-607 | XV-60262FF_DO_1 | XV-60262FF | Control Valve Position Feedback | ACTIVE
17 | RTN OUT-0 | P2-TBRL2-17 | C2S7-17/P2-TBRL2-17 | P2-TBRL2-17/C2S7-17 | JB-607 | Spare_DO_17 | Spare | Spare Reserve Channel | SPARE
18 | DC-0(+) | +24VDC | +24VDC | +24VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | OUT-16 | P2-TBRL2-17 | C2S7-19/P2-TBRL2-17 | P2-TBRL2-17/C2S7-19 | JB-607 | XV-60262FG_DO_1 | XV-60262FG | Control Valve Position Feedback | ACTIVE
20 | OUT-17 | P2-TBRL2-18 | C2S7-20/P2-TBRL2-18 | P2-TBRL2-18/C2S7-20 | JB-607 | XV-60262FH_DO_1 | XV-60262FH | Control Valve Position Feedback | ACTIVE
21 | OUT-18 | P2-TBRL2-19 | C2S7-21/P2-TBRL2-19 | P2-TBRL2-19/C2S7-21 | JB-607 | XV-60262SE_DO_1 | XV-60262SE | Control Valve Position Feedback | ACTIVE
22 | OUT-19 | P2-TBRL2-20 | C2S7-22/P2-TBRL2-20 | P2-TBRL2-20/C2S7-22 | JB-607 | XV-60262SF_DO_1 | XV-60262SF | Control Valve Position Feedback | ACTIVE
23 | OUT-20 | P2-TBRL2-21 | C2S7-23/P2-TBRL2-21 | P2-TBRL2-21/C2S7-23 | JB-607 | XV-60262SG_DO_1 | XV-60262SG | Control Valve Position Feedback | ACTIVE
24 | OUT-21 | P2-TBRL2-22 | C2S7-24/P2-TBRL2-22 | P2-TBRL2-22/C2S7-24 | JB-607 | XV-60262SH_DO_1 | XV-60262SH | Control Valve Position Feedback | ACTIVE
25 | OUT-22 | P2-TBRL2-23 | C2S7-25/P2-TBRL2-23 | P2-TBRL2-23/C2S7-25 | JB-607 | XV-60263_DO_1 | XV-60263 | Control Valve Position Feedback | ACTIVE
26 | OUT-23 | P2-TBRL2-24 | C2S7-26/P2-TBRL2-24 | P2-TBRL2-24/C2S7-26 | JB-607 | XV-60263FJ_DO_1 | XV-60263FJ | Control Valve Position Feedback | ACTIVE
27 | OUT-24 | P2-TBRL2-25 | C2S7-27/P2-TBRL2-25 | P2-TBRL2-25/C2S7-27 | JB-607 | XV-60263FK_DO_1 | XV-60263FK | Control Valve Position Feedback | ACTIVE
28 | OUT-25 | P2-TBRL2-26 | C2S7-28/P2-TBRL2-26 | P2-TBRL2-26/C2S7-28 | JB-607 | XV-60263FL_DO_1 | XV-60263FL | Control Valve Position Feedback | ACTIVE
29 | OUT-26 | P2-TBRL2-27 | C2S7-29/P2-TBRL2-27 | P2-TBRL2-27/C2S7-29 | JB-607 | XV-60263FM_DO_1 | XV-60263FM | Control Valve Position Feedback | ACTIVE
30 | OUT-27 | P2-TBRL2-28 | C2S7-30/P2-TBRL2-28 | P2-TBRL2-28/C2S7-30 | JB-607 | XV-60263SJ_DO_1 | XV-60263SJ | Control Valve Position Feedback | ACTIVE
31 | OUT-28 | P2-TBRL2-29 | C2S7-31/P2-TBRL2-29 | P2-TBRL2-29/C2S7-31 | JB-607 | XV-60263SK_DO_1 | XV-60263SK | Control Valve Position Feedback | ACTIVE
32 | OUT-29 | P2-TBRL2-30 | C2S7-32/P2-TBRL2-30 | P2-TBRL2-30/C2S7-32 | JB-607 | XV-60263SL_DO_1 | XV-60263SL | Control Valve Position Feedback | ACTIVE
33 | OUT-30 | P2-TBRL2-31 | C2S7-33/P2-TBRL2-31 | P2-TBRL2-31/C2S7-33 | JB-607 | XV-60263SM_DO_1 | XV-60263SM | Control Valve Position Feedback | ACTIVE
34 | OUT-31 | P2-TBRL2-32 | C2S7-34/P2-TBRL2-32 | P2-TBRL2-32/C2S7-34 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
35 | RTN OUT-1 | P2-TBRL2-35 | C2S7-35/P2-TBRL2-35 | P2-TBRL2-35/C2S7-35 | JB-607 | Spare_DO_35 | Spare | Spare Reserve Channel | SPARE
36 | DC-1(+) | +24VDC | +24VDC | +24VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C2S8
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C2S8
DIGITAL OUTPUT CARD (1756-OB32 32-CH 24VDC SOURCE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C2 ¦ SLOT: 8 ¦ MODULE: 1756-OB32 ¦ DESTINATION AREA: JB-607
← Back to Chassis Summary (C2SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBRLx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | OUT-0 | P2-TBRL3-1 | C2S8-1/P2-TBRL3-1 | P2-TBRL3-1/C2S8-1 | JB-607 | XV-60264_DO_1 | XV-60264 | Control Valve Position Feedback | ACTIVE
2 | OUT-1 | P2-TBRL3-2 | C2S8-2/P2-TBRL3-2 | P2-TBRL3-2/C2S8-2 | JB-607 | XV-60264FN_DO_1 | XV-60264FN | Control Valve Position Feedback | ACTIVE
3 | OUT-2 | P2-TBRL3-3 | C2S8-3/P2-TBRL3-3 | P2-TBRL3-3/C2S8-3 | JB-607 | XV-60264FP_DO_1 | XV-60264FP | Control Valve Position Feedback | ACTIVE
4 | OUT-3 | P2-TBRL3-4 | C2S8-4/P2-TBRL3-4 | P2-TBRL3-4/C2S8-4 | JB-607 | XV-60264FQ_DO_1 | XV-60264FQ | Control Valve Position Feedback | ACTIVE
5 | OUT-4 | P2-TBRL3-5 | C2S8-5/P2-TBRL3-5 | P2-TBRL3-5/C2S8-5 | JB-607 | XV-60264FR_DO_1 | XV-60264FR | Control Valve Position Feedback | ACTIVE
6 | OUT-5 | P2-TBRL3-6 | C2S8-6/P2-TBRL3-6 | P2-TBRL3-6/C2S8-6 | JB-607 | XV-60264SN_DO_1 | XV-60264SN | Control Valve Position Feedback | ACTIVE
7 | OUT-6 | P2-TBRL3-7 | C2S8-7/P2-TBRL3-7 | P2-TBRL3-7/C2S8-7 | JB-607 | XV-60264SP_DO_1 | XV-60264SP | Control Valve Position Feedback | ACTIVE
8 | OUT-7 | P2-TBRL3-8 | C2S8-8/P2-TBRL3-8 | P2-TBRL3-8/C2S8-8 | JB-607 | XV-60264SQ_DO_1 | XV-60264SQ | Control Valve Position Feedback | ACTIVE
9 | OUT-8 | P2-TBRL3-9 | C2S8-9/P2-TBRL3-9 | P2-TBRL3-9/C2S8-9 | JB-607 | XV-60264SR_DO_1 | XV-60264SR | Control Valve Position Feedback | ACTIVE
10 | OUT-9 | P2-TBRL3-10 | C2S8-10/P2-TBRL3-10 | P2-TBRL3-10/C2S8-10 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
11 | OUT-10 | P2-TBRL3-11 | C2S8-11/P2-TBRL3-11 | P2-TBRL3-11/C2S8-11 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
12 | OUT-11 | P2-TBRL3-12 | C2S8-12/P2-TBRL3-12 | P2-TBRL3-12/C2S8-12 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
13 | OUT-12 | P2-TBRL3-13 | C2S8-13/P2-TBRL3-13 | P2-TBRL3-13/C2S8-13 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
14 | OUT-13 | P2-TBRL3-14 | C2S8-14/P2-TBRL3-14 | P2-TBRL3-14/C2S8-14 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
15 | OUT-14 | P2-TBRL3-15 | C2S8-15/P2-TBRL3-15 | P2-TBRL3-15/C2S8-15 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
16 | OUT-15 | P2-TBRL3-16 | C2S8-16/P2-TBRL3-16 | P2-TBRL3-16/C2S8-16 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
17 | RTN OUT-0 | P2-TBRL3-17 | C2S8-17/P2-TBRL3-17 | P2-TBRL3-17/C2S8-17 | JB-607 | Spare_DO_17 | Spare | Spare Reserve Channel | SPARE
18 | DC-0(+) | +24VDC | +24VDC | +24VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | OUT-16 | P2-TBRL3-17 | C2S8-19/P2-TBRL3-17 | P2-TBRL3-17/C2S8-19 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
20 | OUT-17 | P2-TBRL3-18 | C2S8-20/P2-TBRL3-18 | P2-TBRL3-18/C2S8-20 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
21 | OUT-18 | P2-TBRL3-19 | C2S8-21/P2-TBRL3-19 | P2-TBRL3-19/C2S8-21 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
22 | OUT-19 | P2-TBRL3-20 | C2S8-22/P2-TBRL3-20 | P2-TBRL3-20/C2S8-22 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
23 | OUT-20 | P2-TBRL3-21 | C2S8-23/P2-TBRL3-21 | P2-TBRL3-21/C2S8-23 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
24 | OUT-21 | P2-TBRL3-22 | C2S8-24/P2-TBRL3-22 | P2-TBRL3-22/C2S8-24 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
25 | OUT-22 | P2-TBRL3-23 | C2S8-25/P2-TBRL3-23 | P2-TBRL3-23/C2S8-25 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
26 | OUT-23 | P2-TBRL3-24 | C2S8-26/P2-TBRL3-24 | P2-TBRL3-24/C2S8-26 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
27 | OUT-24 | P2-TBRL3-25 | C2S8-27/P2-TBRL3-25 | P2-TBRL3-25/C2S8-27 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
28 | OUT-25 | P2-TBRL3-26 | C2S8-28/P2-TBRL3-26 | P2-TBRL3-26/C2S8-28 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
29 | OUT-26 | P2-TBRL3-27 | C2S8-29/P2-TBRL3-27 | P2-TBRL3-27/C2S8-29 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
30 | OUT-27 | P2-TBRL3-28 | C2S8-30/P2-TBRL3-28 | P2-TBRL3-28/C2S8-30 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
31 | OUT-28 | P2-TBRL3-29 | C2S8-31/P2-TBRL3-29 | P2-TBRL3-29/C2S8-31 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
32 | OUT-29 | P2-TBRL3-30 | C2S8-32/P2-TBRL3-30 | P2-TBRL3-30/C2S8-32 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
33 | OUT-30 | P2-TBRL3-31 | C2S8-33/P2-TBRL3-31 | P2-TBRL3-31/C2S8-33 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
34 | OUT-31 | P2-TBRL3-32 | C2S8-34/P2-TBRL3-32 | P2-TBRL3-32/C2S8-34 | JB-607 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
35 | RTN OUT-1 | P2-TBRL3-35 | C2S8-35/P2-TBRL3-35 | P2-TBRL3-35/C2S8-35 | JB-607 | Spare_DO_35 | Spare | Spare Reserve Channel | SPARE
36 | DC-1(+) | +24VDC | +24VDC | +24VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C2S9
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C2S9
ANALOG INPUT CARD (1756-IF16 16-CH CURRENT/VOLTAGE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C2 ¦ SLOT: 9 ¦ MODULE: 1756-IF16 ¦ DESTINATION AREA: JB-402
← Back to Chassis Summary (C2SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | i RTN-0 | P2-TBAI1-1(B) | C2S9-1/P2-TBAI1-1(B) | P2-TBAI1-1(B)/C2S9-1 | JB-402 | FT-40221_AI_1 | FT-40221 | Coriolis Flow Transmitter | ACTIVE
2 | IN-0 | P2-TBAI1-1(A) | C2S9-2/P2-TBAI1-1(A) | P2-TBAI1-1(A)/C2S9-2 | JB-402 | FT-40221_AI_1 | FT-40221 | Coriolis Flow Transmitter | ACTIVE
3 | i RTN-1 | P2-TBAI1-2(B) | C2S9-3/P2-TBAI1-2(B) | P2-TBAI1-2(B)/C2S9-3 | JB-402 | FT-40221_AI_2 | FT-40221 | Coriolis Flow Transmitter | ACTIVE
4 | IN-1 | P2-TBAI1-2(A) | C2S9-4/P2-TBAI1-2(A) | P2-TBAI1-2(A)/C2S9-4 | JB-402 | FT-40221_AI_2 | FT-40221 | Coriolis Flow Transmitter | ACTIVE
5 | i RTN-2 | P2-TBAI1-3(B) | C2S9-5/P2-TBAI1-3(B) | P2-TBAI1-3(B)/C2S9-5 | JB-402 | FT-40222_AI_1 | FT-40222 | Coriolis Flow Transmitter | ACTIVE
6 | IN-2 | P2-TBAI1-3(A) | C2S9-6/P2-TBAI1-3(A) | P2-TBAI1-3(A)/C2S9-6 | JB-402 | FT-40222_AI_1 | FT-40222 | Coriolis Flow Transmitter | ACTIVE
7 | i RTN-3 | P2-TBAI1-4(B) | C2S9-7/P2-TBAI1-4(B) | P2-TBAI1-4(B)/C2S9-7 | JB-402 | FT-40222_AI_2 | FT-40222 | Coriolis Flow Transmitter | ACTIVE
8 | IN-3 | P2-TBAI1-4(A) | C2S9-8/P2-TBAI1-4(A) | P2-TBAI1-4(A)/C2S9-8 | JB-402 | FT-40222_AI_2 | FT-40222 | Coriolis Flow Transmitter | ACTIVE
9 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
10 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
11 | i RTN-4 | P2-TBAI1-5(B) | C2S9-11/P2-TBAI1-5(B) | P2-TBAI1-5(B)/C2S9-11 | JB-402 | PT-40222_AI_1 | PT-40222 | Pressure Transmitter | ACTIVE
12 | IN-4 | P2-TBAI1-5(A) | C2S9-12/P2-TBAI1-5(A) | P2-TBAI1-5(A)/C2S9-12 | JB-402 | PT-40222_AI_1 | PT-40222 | Pressure Transmitter | ACTIVE
13 | i RTN-5 | P2-TBAI1-6(B) | C2S9-13/P2-TBAI1-6(B) | P2-TBAI1-6(B)/C2S9-13 | JB-402 | TT-40221_AI_1 | TT-40221 | Temperature Transmitter | ACTIVE
14 | IN-5 | P2-TBAI1-6(A) | C2S9-14/P2-TBAI1-6(A) | P2-TBAI1-6(A)/C2S9-14 | JB-402 | TT-40221_AI_1 | TT-40221 | Temperature Transmitter | ACTIVE
15 | i RTN-6 | P2-TBAI1-7(B) | C2S9-15/P2-TBAI1-7(B) | P2-TBAI1-7(B)/C2S9-15 | JB-402 | TT-40222_AI_1 | TT-40222 | Temperature Transmitter | ACTIVE
16 | IN-6 | P2-TBAI1-7(A) | C2S9-16/P2-TBAI1-7(A) | P2-TBAI1-7(A)/C2S9-16 | JB-402 | TT-40222_AI_1 | TT-40222 | Temperature Transmitter | ACTIVE
17 | i RTN-7 | P2-TBAI1-8(B) | C2S9-17/P2-TBAI1-8(B) | P2-TBAI1-8(B)/C2S9-17 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
18 | IN-7 | P2-TBAI1-8(A) | C2S9-18/P2-TBAI1-8(A) | P2-TBAI1-8(A)/C2S9-18 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
19 | i RTN-8 | P2-TBAI1-9(B) | C2S9-19/P2-TBAI1-9(B) | P2-TBAI1-9(B)/C2S9-19 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
20 | IN-8 | P2-TBAI1-9(A) | C2S9-20/P2-TBAI1-9(A) | P2-TBAI1-9(A)/C2S9-20 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
21 | i RTN-9 | P2-TBAI1-10(B) | C2S9-21/P2-TBAI1-10(B) | P2-TBAI1-10(B)/C2S9-21 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
22 | IN-9 | P2-TBAI1-10(A) | C2S9-22/P2-TBAI1-10(A) | P2-TBAI1-10(A)/C2S9-22 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
23 | i RTN-10 | P2-TBAI1-11(B) | C2S9-23/P2-TBAI1-11(B) | P2-TBAI1-11(B)/C2S9-23 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
24 | IN-10 | P2-TBAI1-11(A) | C2S9-24/P2-TBAI1-11(A) | P2-TBAI1-11(A)/C2S9-24 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
25 | i RTN-11 | P2-TBAI1-12(B) | C2S9-25/P2-TBAI1-12(B) | P2-TBAI1-12(B)/C2S9-25 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
26 | IN-11 | P2-TBAI1-12(A) | C2S9-26/P2-TBAI1-12(A) | P2-TBAI1-12(A)/C2S9-26 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
27 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
28 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
29 | i RTN-12 | P2-TBAI1-13(B) | C2S9-29/P2-TBAI1-13(B) | P2-TBAI1-13(B)/C2S9-29 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-12 | P2-TBAI1-13(A) | C2S9-30/P2-TBAI1-13(A) | P2-TBAI1-13(A)/C2S9-30 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
31 | i RTN-13 | P2-TBAI1-14(B) | C2S9-31/P2-TBAI1-14(B) | P2-TBAI1-14(B)/C2S9-31 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-13 | P2-TBAI1-14(A) | C2S9-32/P2-TBAI1-14(A) | P2-TBAI1-14(A)/C2S9-32 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
33 | i RTN-14 | P2-TBAI1-15(B) | C2S9-33/P2-TBAI1-15(B) | P2-TBAI1-15(B)/C2S9-33 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-14 | P2-TBAI1-15(A) | C2S9-34/P2-TBAI1-15(A) | P2-TBAI1-15(A)/C2S9-34 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
35 | i RTN-15 | P2-TBAI1-16(B) | C2S9-35/P2-TBAI1-16(B) | P2-TBAI1-16(B)/C2S9-35 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
36 | IN-15 | P2-TBAI1-16(A) | C2S9-36/P2-TBAI1-16(A) | P2-TBAI1-16(A)/C2S9-36 | JB-402 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE

## C2S10
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C2S10
ANALOG INPUT CARD (1756-IF16 16-CH CURRENT/VOLTAGE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C2 ¦ SLOT: 10 ¦ MODULE: 1756-IF16 ¦ DESTINATION AREA: JB-602
← Back to Chassis Summary (C2SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | i RTN-0 | P2-TBAI2-1(B) | C2S10-1/P2-TBAI2-1(B) | P2-TBAI2-1(B)/C2S10-1 | JB-602 | AT-60241_AI_1 | AT-60241 | Dust Analyzer Transmitter | ACTIVE
2 | IN-0 | P2-TBAI2-1(A) | C2S10-2/P2-TBAI2-1(A) | P2-TBAI2-1(A)/C2S10-2 | JB-602 | AT-60241_AI_1 | AT-60241 | Dust Analyzer Transmitter | ACTIVE
3 | i RTN-1 | P2-TBAI2-2(B) | C2S10-3/P2-TBAI2-2(B) | P2-TBAI2-2(B)/C2S10-3 | JB-602 | DPT-60203_AI_1 | DPT-60203 | Differential Pressure Transmitte | ACTIVE
4 | IN-1 | P2-TBAI2-2(A) | C2S10-4/P2-TBAI2-2(A) | P2-TBAI2-2(A)/C2S10-4 | JB-602 | DPT-60203_AI_1 | DPT-60203 | Differential Pressure Transmitte | ACTIVE
5 | i RTN-2 | P2-TBAI2-3(B) | C2S10-5/P2-TBAI2-3(B) | P2-TBAI2-3(B)/C2S10-5 | JB-602 | FT-60202_AI_1 | FT-60202 | Flow Transmitter | ACTIVE
6 | IN-2 | P2-TBAI2-3(A) | C2S10-6/P2-TBAI2-3(A) | P2-TBAI2-3(A)/C2S10-6 | JB-602 | FT-60202_AI_1 | FT-60202 | Flow Transmitter | ACTIVE
7 | i RTN-3 | P2-TBAI2-4(B) | C2S10-7/P2-TBAI2-4(B) | P2-TBAI2-4(B)/C2S10-7 | JB-602 | PT-60210_AI_1 | PT-60210 | Pressure Transmitter | ACTIVE
8 | IN-3 | P2-TBAI2-4(A) | C2S10-8/P2-TBAI2-4(A) | P2-TBAI2-4(A)/C2S10-8 | JB-602 | PT-60210_AI_1 | PT-60210 | Pressure Transmitter | ACTIVE
9 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
10 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
11 | i RTN-4 | P2-TBAI2-5(B) | C2S10-11/P2-TBAI2-5(B) | P2-TBAI2-5(B)/C2S10-11 | JB-602 | PT-60215_AI_1 | PT-60215 | Pressure Transmitter | ACTIVE
12 | IN-4 | P2-TBAI2-5(A) | C2S10-12/P2-TBAI2-5(A) | P2-TBAI2-5(A)/C2S10-12 | JB-602 | PT-60215_AI_1 | PT-60215 | Pressure Transmitter | ACTIVE
13 | i RTN-5 | P2-TBAI2-6(B) | C2S10-13/P2-TBAI2-6(B) | P2-TBAI2-6(B)/C2S10-13 | JB-602 | PT-60216_AI_1 | PT-60216 | Pressure Transmitter | ACTIVE
14 | IN-5 | P2-TBAI2-6(A) | C2S10-14/P2-TBAI2-6(A) | P2-TBAI2-6(A)/C2S10-14 | JB-602 | PT-60216_AI_1 | PT-60216 | Pressure Transmitter | ACTIVE
15 | i RTN-6 | P2-TBAI2-7(B) | C2S10-15/P2-TBAI2-7(B) | P2-TBAI2-7(B)/C2S10-15 | JB-602 | PT-60240_AI_1 | PT-60240 | Pressure Transmitter | ACTIVE
16 | IN-6 | P2-TBAI2-7(A) | C2S10-16/P2-TBAI2-7(A) | P2-TBAI2-7(A)/C2S10-16 | JB-602 | PT-60240_AI_1 | PT-60240 | Pressure Transmitter | ACTIVE
17 | i RTN-7 | P2-TBAI2-8(B) | C2S10-17/P2-TBAI2-8(B) | P2-TBAI2-8(B)/C2S10-17 | JB-602 | PT-60241_AI_1 | PT-60241 | Pressure Transmitter | ACTIVE
18 | IN-7 | P2-TBAI2-8(A) | C2S10-18/P2-TBAI2-8(A) | P2-TBAI2-8(A)/C2S10-18 | JB-602 | PT-60241_AI_1 | PT-60241 | Pressure Transmitter | ACTIVE
19 | i RTN-8 | P2-TBAI2-9(B) | C2S10-19/P2-TBAI2-9(B) | P2-TBAI2-9(B)/C2S10-19 | JB-602 | TT-60210_AI_1 | TT-60210 | Temperature Transmitter | ACTIVE
20 | IN-8 | P2-TBAI2-9(A) | C2S10-20/P2-TBAI2-9(A) | P2-TBAI2-9(A)/C2S10-20 | JB-602 | TT-60210_AI_1 | TT-60210 | Temperature Transmitter | ACTIVE
21 | i RTN-9 | P2-TBAI2-10(B) | C2S10-21/P2-TBAI2-10(B) | P2-TBAI2-10(B)/C2S10-21 | JB-602 | TT-60210A_AI_1 | TT-60210A | Temperature Transmitter | ACTIVE
22 | IN-9 | P2-TBAI2-10(A) | C2S10-22/P2-TBAI2-10(A) | P2-TBAI2-10(A)/C2S10-22 | JB-602 | TT-60210A_AI_1 | TT-60210A | Temperature Transmitter | ACTIVE
23 | i RTN-10 | P2-TBAI2-11(B) | C2S10-23/P2-TBAI2-11(B) | P2-TBAI2-11(B)/C2S10-23 | JB-602 | TT-60210B_AI_1 | TT-60210B | Temperature Transmitter | ACTIVE
24 | IN-10 | P2-TBAI2-11(A) | C2S10-24/P2-TBAI2-11(A) | P2-TBAI2-11(A)/C2S10-24 | JB-602 | TT-60210B_AI_1 | TT-60210B | Temperature Transmitter | ACTIVE
25 | i RTN-11 | P2-TBAI2-12(B) | C2S10-25/P2-TBAI2-12(B) | P2-TBAI2-12(B)/C2S10-25 | JB-602 | TT-60211_AI_1 | TT-60211 | Temperature Transmitter | ACTIVE
26 | IN-11 | P2-TBAI2-12(A) | C2S10-26/P2-TBAI2-12(A) | P2-TBAI2-12(A)/C2S10-26 | JB-602 | TT-60211_AI_1 | TT-60211 | Temperature Transmitter | ACTIVE
27 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
28 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
29 | i RTN-12 | P2-TBAI2-13(B) | C2S10-29/P2-TBAI2-13(B) | P2-TBAI2-13(B)/C2S10-29 | JB-602 | TT-60212A_AI_1 | TT-60212A | Temperature Transmitter | ACTIVE
30 | IN-12 | P2-TBAI2-13(A) | C2S10-30/P2-TBAI2-13(A) | P2-TBAI2-13(A)/C2S10-30 | JB-602 | TT-60212A_AI_1 | TT-60212A | Temperature Transmitter | ACTIVE
31 | i RTN-13 | P2-TBAI2-14(B) | C2S10-31/P2-TBAI2-14(B) | P2-TBAI2-14(B)/C2S10-31 | JB-602 | TT-60212B_AI_1 | TT-60212B | Temperature Transmitter | ACTIVE
32 | IN-13 | P2-TBAI2-14(A) | C2S10-32/P2-TBAI2-14(A) | P2-TBAI2-14(A)/C2S10-32 | JB-602 | TT-60212B_AI_1 | TT-60212B | Temperature Transmitter | ACTIVE
33 | i RTN-14 | P2-TBAI2-15(B) | C2S10-33/P2-TBAI2-15(B) | P2-TBAI2-15(B)/C2S10-33 | JB-602 | TT-60214_AI_1 | TT-60214 | Temperature Transmitter | ACTIVE
34 | IN-14 | P2-TBAI2-15(A) | C2S10-34/P2-TBAI2-15(A) | P2-TBAI2-15(A)/C2S10-34 | JB-602 | TT-60214_AI_1 | TT-60214 | Temperature Transmitter | ACTIVE
35 | i RTN-15 | P2-TBAI2-16(B) | C2S10-35/P2-TBAI2-16(B) | P2-TBAI2-16(B)/C2S10-35 | JB-602 | TT-60215A_AI_1 | TT-60215A | Temperature Transmitter | ACTIVE
36 | IN-15 | P2-TBAI2-16(A) | C2S10-36/P2-TBAI2-16(A) | P2-TBAI2-16(A)/C2S10-36 | JB-602 | TT-60215A_AI_1 | TT-60215A | Temperature Transmitter | ACTIVE

## C2S11
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C2S11
ANALOG INPUT CARD (1756-IF16 16-CH CURRENT/VOLTAGE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C2 ¦ SLOT: 11 ¦ MODULE: 1756-IF16 ¦ DESTINATION AREA: CA1
← Back to Chassis Summary (C2SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | i RTN-0 | P2-TBAI3-1(B) | C2S11-1/P2-TBAI3-1(B) | P2-TBAI3-1(B)/C2S11-1 | CA1 | Spare_AI_1 | Spare | Spare Reserve Channel | SPARE
2 | IN-0 | P2-TBAI3-1(A) | C2S11-2/P2-TBAI3-1(A) | P2-TBAI3-1(A)/C2S11-2 | CA1 | Spare_AI_1 | Spare | Spare Reserve Channel | SPARE
3 | i RTN-1 | P2-TBAI3-2(B) | C2S11-3/P2-TBAI3-2(B) | P2-TBAI3-2(B)/C2S11-3 | CA1 | Spare_AI_2 | Spare | Spare Reserve Channel | SPARE
4 | IN-1 | P2-TBAI3-2(A) | C2S11-4/P2-TBAI3-2(A) | P2-TBAI3-2(A)/C2S11-4 | CA1 | Spare_AI_2 | Spare | Spare Reserve Channel | SPARE
5 | i RTN-2 | P2-TBAI3-3(B) | C2S11-5/P2-TBAI3-3(B) | P2-TBAI3-3(B)/C2S11-5 | CA1 | Spare_AI_3 | Spare | Spare Reserve Channel | SPARE
6 | IN-2 | P2-TBAI3-3(A) | C2S11-6/P2-TBAI3-3(A) | P2-TBAI3-3(A)/C2S11-6 | CA1 | Spare_AI_3 | Spare | Spare Reserve Channel | SPARE
7 | i RTN-3 | P2-TBAI3-4(B) | C2S11-7/P2-TBAI3-4(B) | P2-TBAI3-4(B)/C2S11-7 | CA1 | Spare_AI_4 | Spare | Spare Reserve Channel | SPARE
8 | IN-3 | P2-TBAI3-4(A) | C2S11-8/P2-TBAI3-4(A) | P2-TBAI3-4(A)/C2S11-8 | CA1 | Spare_AI_4 | Spare | Spare Reserve Channel | SPARE
9 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
10 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
11 | i RTN-4 | P2-TBAI3-5(B) | C2S11-11/P2-TBAI3-5(B) | P2-TBAI3-5(B)/C2S11-11 | CA1 | Spare_AI_5 | Spare | Spare Reserve Channel | SPARE
12 | IN-4 | P2-TBAI3-5(A) | C2S11-12/P2-TBAI3-5(A) | P2-TBAI3-5(A)/C2S11-12 | CA1 | Spare_AI_5 | Spare | Spare Reserve Channel | SPARE
13 | i RTN-5 | P2-TBAI3-6(B) | C2S11-13/P2-TBAI3-6(B) | P2-TBAI3-6(B)/C2S11-13 | CA1 | Spare_AI_6 | Spare | Spare Reserve Channel | SPARE
14 | IN-5 | P2-TBAI3-6(A) | C2S11-14/P2-TBAI3-6(A) | P2-TBAI3-6(A)/C2S11-14 | CA1 | Spare_AI_6 | Spare | Spare Reserve Channel | SPARE
15 | i RTN-6 | P2-TBAI3-7(B) | C2S11-15/P2-TBAI3-7(B) | P2-TBAI3-7(B)/C2S11-15 | CA1 | Spare_AI_7 | Spare | Spare Reserve Channel | SPARE
16 | IN-6 | P2-TBAI3-7(A) | C2S11-16/P2-TBAI3-7(A) | P2-TBAI3-7(A)/C2S11-16 | CA1 | Spare_AI_7 | Spare | Spare Reserve Channel | SPARE
17 | i RTN-7 | P2-TBAI3-8(B) | C2S11-17/P2-TBAI3-8(B) | P2-TBAI3-8(B)/C2S11-17 | CA1 | Spare_AI_8 | Spare | Spare Reserve Channel | SPARE
18 | IN-7 | P2-TBAI3-8(A) | C2S11-18/P2-TBAI3-8(A) | P2-TBAI3-8(A)/C2S11-18 | CA1 | Spare_AI_8 | Spare | Spare Reserve Channel | SPARE
19 | i RTN-8 | P2-TBAI3-9(B) | C2S11-19/P2-TBAI3-9(B) | P2-TBAI3-9(B)/C2S11-19 | CA1 | Spare_AI_9 | Spare | Spare Reserve Channel | SPARE
20 | IN-8 | P2-TBAI3-9(A) | C2S11-20/P2-TBAI3-9(A) | P2-TBAI3-9(A)/C2S11-20 | CA1 | Spare_AI_9 | Spare | Spare Reserve Channel | SPARE
21 | i RTN-9 | P2-TBAI3-10(B) | C2S11-21/P2-TBAI3-10(B) | P2-TBAI3-10(B)/C2S11-21 | CA1 | Spare_AI_10 | Spare | Spare Reserve Channel | SPARE
22 | IN-9 | P2-TBAI3-10(A) | C2S11-22/P2-TBAI3-10(A) | P2-TBAI3-10(A)/C2S11-22 | CA1 | Spare_AI_10 | Spare | Spare Reserve Channel | SPARE
23 | i RTN-10 | P2-TBAI3-11(B) | C2S11-23/P2-TBAI3-11(B) | P2-TBAI3-11(B)/C2S11-23 | CA1 | Spare_AI_11 | Spare | Spare Reserve Channel | SPARE
24 | IN-10 | P2-TBAI3-11(A) | C2S11-24/P2-TBAI3-11(A) | P2-TBAI3-11(A)/C2S11-24 | CA1 | Spare_AI_11 | Spare | Spare Reserve Channel | SPARE
25 | i RTN-11 | P2-TBAI3-12(B) | C2S11-25/P2-TBAI3-12(B) | P2-TBAI3-12(B)/C2S11-25 | CA1 | Spare_AI_12 | Spare | Spare Reserve Channel | SPARE
26 | IN-11 | P2-TBAI3-12(A) | C2S11-26/P2-TBAI3-12(A) | P2-TBAI3-12(A)/C2S11-26 | CA1 | Spare_AI_12 | Spare | Spare Reserve Channel | SPARE
27 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
28 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
29 | i RTN-12 | P2-TBAI3-13(B) | C2S11-29/P2-TBAI3-13(B) | P2-TBAI3-13(B)/C2S11-29 | CA1 | Spare_AI_13 | Spare | Spare Reserve Channel | SPARE
30 | IN-12 | P2-TBAI3-13(A) | C2S11-30/P2-TBAI3-13(A) | P2-TBAI3-13(A)/C2S11-30 | CA1 | Spare_AI_13 | Spare | Spare Reserve Channel | SPARE
31 | i RTN-13 | P2-TBAI3-14(B) | C2S11-31/P2-TBAI3-14(B) | P2-TBAI3-14(B)/C2S11-31 | CA1 | Spare_AI_14 | Spare | Spare Reserve Channel | SPARE
32 | IN-13 | P2-TBAI3-14(A) | C2S11-32/P2-TBAI3-14(A) | P2-TBAI3-14(A)/C2S11-32 | CA1 | Spare_AI_14 | Spare | Spare Reserve Channel | SPARE
33 | i RTN-14 | P2-TBAI3-15(B) | C2S11-33/P2-TBAI3-15(B) | P2-TBAI3-15(B)/C2S11-33 | CA1 | Spare_AI_15 | Spare | Spare Reserve Channel | SPARE
34 | IN-14 | P2-TBAI3-15(A) | C2S11-34/P2-TBAI3-15(A) | P2-TBAI3-15(A)/C2S11-34 | CA1 | Spare_AI_15 | Spare | Spare Reserve Channel | SPARE
35 | i RTN-15 | P2-TBAI3-16(B) | C2S11-35/P2-TBAI3-16(B) | P2-TBAI3-16(B)/C2S11-35 | CA1 | Spare_AI_16 | Spare | Spare Reserve Channel | SPARE
36 | IN-15 | P2-TBAI3-16(A) | C2S11-36/P2-TBAI3-16(A) | P2-TBAI3-16(A)/C2S11-36 | CA1 | Spare_AI_16 | Spare | Spare Reserve Channel | SPARE

## C2S12
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C2S12
ANALOG INPUT CARD (1756-IF16 16-CH CURRENT/VOLTAGE) ¦ LOCATION: CONTROL CABINET CA1 (MAIN CONTROL ROOM MCP)
CHASSIS: C2 ¦ SLOT: 12 ¦ MODULE: 1756-IF16 ¦ DESTINATION AREA: CA1
← Back to Chassis Summary (C2SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | i RTN-0 | P2-TBAI4-1(B) | C2S12-1/P2-TBAI4-1(B) | P2-TBAI4-1(B)/C2S12-1 | CA1 | Spare_AI_1 | Spare | Spare Reserve Channel | SPARE
2 | IN-0 | P2-TBAI4-1(A) | C2S12-2/P2-TBAI4-1(A) | P2-TBAI4-1(A)/C2S12-2 | CA1 | Spare_AI_1 | Spare | Spare Reserve Channel | SPARE
3 | i RTN-1 | P2-TBAI4-2(B) | C2S12-3/P2-TBAI4-2(B) | P2-TBAI4-2(B)/C2S12-3 | CA1 | Spare_AI_2 | Spare | Spare Reserve Channel | SPARE
4 | IN-1 | P2-TBAI4-2(A) | C2S12-4/P2-TBAI4-2(A) | P2-TBAI4-2(A)/C2S12-4 | CA1 | Spare_AI_2 | Spare | Spare Reserve Channel | SPARE
5 | i RTN-2 | P2-TBAI4-3(B) | C2S12-5/P2-TBAI4-3(B) | P2-TBAI4-3(B)/C2S12-5 | CA1 | Spare_AI_3 | Spare | Spare Reserve Channel | SPARE
6 | IN-2 | P2-TBAI4-3(A) | C2S12-6/P2-TBAI4-3(A) | P2-TBAI4-3(A)/C2S12-6 | CA1 | Spare_AI_3 | Spare | Spare Reserve Channel | SPARE
7 | i RTN-3 | P2-TBAI4-4(B) | C2S12-7/P2-TBAI4-4(B) | P2-TBAI4-4(B)/C2S12-7 | CA1 | Spare_AI_4 | Spare | Spare Reserve Channel | SPARE
8 | IN-3 | P2-TBAI4-4(A) | C2S12-8/P2-TBAI4-4(A) | P2-TBAI4-4(A)/C2S12-8 | CA1 | Spare_AI_4 | Spare | Spare Reserve Channel | SPARE
9 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
10 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
11 | i RTN-4 | P2-TBAI4-5(B) | C2S12-11/P2-TBAI4-5(B) | P2-TBAI4-5(B)/C2S12-11 | CA1 | Spare_AI_5 | Spare | Spare Reserve Channel | SPARE
12 | IN-4 | P2-TBAI4-5(A) | C2S12-12/P2-TBAI4-5(A) | P2-TBAI4-5(A)/C2S12-12 | CA1 | Spare_AI_5 | Spare | Spare Reserve Channel | SPARE
13 | i RTN-5 | P2-TBAI4-6(B) | C2S12-13/P2-TBAI4-6(B) | P2-TBAI4-6(B)/C2S12-13 | CA1 | Spare_AI_6 | Spare | Spare Reserve Channel | SPARE
14 | IN-5 | P2-TBAI4-6(A) | C2S12-14/P2-TBAI4-6(A) | P2-TBAI4-6(A)/C2S12-14 | CA1 | Spare_AI_6 | Spare | Spare Reserve Channel | SPARE
15 | i RTN-6 | P2-TBAI4-7(B) | C2S12-15/P2-TBAI4-7(B) | P2-TBAI4-7(B)/C2S12-15 | CA1 | Spare_AI_7 | Spare | Spare Reserve Channel | SPARE
16 | IN-6 | P2-TBAI4-7(A) | C2S12-16/P2-TBAI4-7(A) | P2-TBAI4-7(A)/C2S12-16 | CA1 | Spare_AI_7 | Spare | Spare Reserve Channel | SPARE
17 | i RTN-7 | P2-TBAI4-8(B) | C2S12-17/P2-TBAI4-8(B) | P2-TBAI4-8(B)/C2S12-17 | CA1 | Spare_AI_8 | Spare | Spare Reserve Channel | SPARE
18 | IN-7 | P2-TBAI4-8(A) | C2S12-18/P2-TBAI4-8(A) | P2-TBAI4-8(A)/C2S12-18 | CA1 | Spare_AI_8 | Spare | Spare Reserve Channel | SPARE
19 | i RTN-8 | P2-TBAI4-9(B) | C2S12-19/P2-TBAI4-9(B) | P2-TBAI4-9(B)/C2S12-19 | CA1 | Spare_AI_9 | Spare | Spare Reserve Channel | SPARE
20 | IN-8 | P2-TBAI4-9(A) | C2S12-20/P2-TBAI4-9(A) | P2-TBAI4-9(A)/C2S12-20 | CA1 | Spare_AI_9 | Spare | Spare Reserve Channel | SPARE
21 | i RTN-9 | P2-TBAI4-10(B) | C2S12-21/P2-TBAI4-10(B) | P2-TBAI4-10(B)/C2S12-21 | CA1 | Spare_AI_10 | Spare | Spare Reserve Channel | SPARE
22 | IN-9 | P2-TBAI4-10(A) | C2S12-22/P2-TBAI4-10(A) | P2-TBAI4-10(A)/C2S12-22 | CA1 | Spare_AI_10 | Spare | Spare Reserve Channel | SPARE
23 | i RTN-10 | P2-TBAI4-11(B) | C2S12-23/P2-TBAI4-11(B) | P2-TBAI4-11(B)/C2S12-23 | CA1 | Spare_AI_11 | Spare | Spare Reserve Channel | SPARE
24 | IN-10 | P2-TBAI4-11(A) | C2S12-24/P2-TBAI4-11(A) | P2-TBAI4-11(A)/C2S12-24 | CA1 | Spare_AI_11 | Spare | Spare Reserve Channel | SPARE
25 | i RTN-11 | P2-TBAI4-12(B) | C2S12-25/P2-TBAI4-12(B) | P2-TBAI4-12(B)/C2S12-25 | CA1 | Spare_AI_12 | Spare | Spare Reserve Channel | SPARE
26 | IN-11 | P2-TBAI4-12(A) | C2S12-26/P2-TBAI4-12(A) | P2-TBAI4-12(A)/C2S12-26 | CA1 | Spare_AI_12 | Spare | Spare Reserve Channel | SPARE
27 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
28 | RTN | 0VDC | 0VDC | 0VDC | CA1 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
29 | i RTN-12 | P2-TBAI4-13(B) | C2S12-29/P2-TBAI4-13(B) | P2-TBAI4-13(B)/C2S12-29 | CA1 | Spare_AI_13 | Spare | Spare Reserve Channel | SPARE
30 | IN-12 | P2-TBAI4-13(A) | C2S12-30/P2-TBAI4-13(A) | P2-TBAI4-13(A)/C2S12-30 | CA1 | Spare_AI_13 | Spare | Spare Reserve Channel | SPARE
31 | i RTN-13 | P2-TBAI4-14(B) | C2S12-31/P2-TBAI4-14(B) | P2-TBAI4-14(B)/C2S12-31 | CA1 | Spare_AI_14 | Spare | Spare Reserve Channel | SPARE
32 | IN-13 | P2-TBAI4-14(A) | C2S12-32/P2-TBAI4-14(A) | P2-TBAI4-14(A)/C2S12-32 | CA1 | Spare_AI_14 | Spare | Spare Reserve Channel | SPARE
33 | i RTN-14 | P2-TBAI4-15(B) | C2S12-33/P2-TBAI4-15(B) | P2-TBAI4-15(B)/C2S12-33 | CA1 | Spare_AI_15 | Spare | Spare Reserve Channel | SPARE
34 | IN-14 | P2-TBAI4-15(A) | C2S12-34/P2-TBAI4-15(A) | P2-TBAI4-15(A)/C2S12-34 | CA1 | Spare_AI_15 | Spare | Spare Reserve Channel | SPARE
35 | i RTN-15 | P2-TBAI4-16(B) | C2S12-35/P2-TBAI4-16(B) | P2-TBAI4-16(B)/C2S12-35 | CA1 | Spare_AI_16 | Spare | Spare Reserve Channel | SPARE
36 | IN-15 | P2-TBAI4-16(A) | C2S12-36/P2-TBAI4-16(A) | P2-TBAI4-16(A)/C2S12-36 | CA1 | Spare_AI_16 | Spare | Spare Reserve Channel | SPARE

## C3SlotConfig
CHASSIS C3 HARDWARE & SLOT CONFIGURATION SCHEDULE
REMOTE I/O RACK 1 (SPRAY DRYER / PACKING TOWER) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS MODEL: 1756-A13 (13-Slot ControlLogix Chassis) ¦ POWER SUPPLY: 1756-PA75 (85-265V AC Power Supply) ¦ NETWORK: ETHERNET/IP 1GBPS DLR RING
← Back to Master Slot Directory (00_Slot_Index)
Slot_No | Slot_Tag | Module_Catalog | Module_Description | Signal_Family | Terminal_Block_Type | Destination_Area(s) | Total_Channels | Active_Channels | Spare_Channels | Slot_Status
0 | C3S0 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | COMM (EtherNet/IP) | 2x RJ45 (Gigabit) + 1x USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | - | ACTIVE
1 | C3S1 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-606 | 32 | 4 | 28 | ACTIVE
2 | C3S2 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-612 | 32 | 17 | 15 | ACTIVE
3 | C3S3 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | JB-618 | 32 | 12 | 20 | ACTIVE
4 | C3S4 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | JB-606, JB-612 | 32 | 16 | 16 | ACTIVE
5 | C3S5 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | JB-618 | 32 | 9 | 23 | ACTIVE
6 | C3S6 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-602, JB-606 | 16 | 30 | 2 | ACTIVE
7 | C3S7 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-607 | 16 | 32 | - | ACTIVE
8 | C3S8 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-607, JB-608 | 16 | 24 | 8 | ACTIVE
9 | C3S9 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | JB-612, JB-618 | 16 | 16 | 16 | ACTIVE
10 | C3S10 | 1756-N2 | Slot Filler / Reserve Unpopulated Position | EMPTY (Reserve Position) | N/A (Blanking Plate) | Unpopulated / Reserve | - | - | - | EMPTY
11 | C3S11 | 1756-N2 | Slot Filler / Reserve Unpopulated Position | EMPTY (Reserve Position) | N/A (Blanking Plate) | Unpopulated / Reserve | - | - | - | EMPTY
12 | C3S12 | 1756-OF8 | 8-Point High-Resolution Analog Current/Voltage Output Module | AO (4-20mA Analog Output) | 1756-TBNH (20-Pin RTB) | JB-402, JB-602, JB-607 | 8 | 5 | 3 | ACTIVE
TOTAL | 13 Slots | - | Chassis C3 Total Configured Capacity | - | - | - | 236 | 169 | 131 | 72% Active

## C3S0
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C3S0
ETHERNET COMMUNICATION ADAPTER (1756-EN4TR DLR 2-PORT GIGABIT) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS: C3 ¦ SLOT: 0 ¦ MODULE: 1756-EN4TR ¦ DESTINATION AREA: CA1 / Field RIO (EtherNet/IP DLR Trunk)
← Back to Chassis Summary (C3SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | ETH-DLR-P1 | C3S0-/- | -/C3S0- | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C3S0_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | ACTIVE
RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C3S0-P2/ETH | ETH/C3S0-P2 | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C3S0_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | ACTIVE
USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C3S0-USB/CONSOLE | CONSOLE/C3S0-USB | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C3S0_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | ACTIVE
DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C3S0-DISP/DIAG | DIAG/C3S0-DISP | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C3S0_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | ACTIVE

## C3S1
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C3S1
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS: C3 ¦ SLOT: 1 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: JB-606
← Back to Chassis Summary (C3SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P3-TBDI1-1 | C3S1-1/P3-TBDI1-1 | P3-TBDI1-1/C3S1-1 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
2 | IN-1 | P3-TBDI1-2 | C3S1-2/P3-TBDI1-2 | P3-TBDI1-2/C3S1-2 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
3 | IN-2 | P3-TBDI1-3 | C3S1-3/P3-TBDI1-3 | P3-TBDI1-3/C3S1-3 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
4 | IN-3 | P3-TBDI1-4 | C3S1-4/P3-TBDI1-4 | P3-TBDI1-4/C3S1-4 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
5 | IN-4 | P3-TBDI1-5 | C3S1-5/P3-TBDI1-5 | P3-TBDI1-5/C3S1-5 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
6 | IN-5 | P3-TBDI1-6 | C3S1-6/P3-TBDI1-6 | P3-TBDI1-6/C3S1-6 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
7 | IN-6 | P3-TBDI1-7 | C3S1-7/P3-TBDI1-7 | P3-TBDI1-7/C3S1-7 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
8 | IN-7 | P3-TBDI1-8 | C3S1-8/P3-TBDI1-8 | P3-TBDI1-8/C3S1-8 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
9 | IN-8 | P3-TBDI1-9 | C3S1-9/P3-TBDI1-9 | P3-TBDI1-9/C3S1-9 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
10 | IN-9 | P3-TBDI1-10 | C3S1-10/P3-TBDI1-10 | P3-TBDI1-10/C3S1-10 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
11 | IN-10 | P3-TBDI1-11 | C3S1-11/P3-TBDI1-11 | P3-TBDI1-11/C3S1-11 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
12 | IN-11 | P3-TBDI1-12 | C3S1-12/P3-TBDI1-12 | P3-TBDI1-12/C3S1-12 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
13 | IN-12 | P3-TBDI1-13 | C3S1-13/P3-TBDI1-13 | P3-TBDI1-13/C3S1-13 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
14 | IN-13 | P3-TBDI1-14 | C3S1-14/P3-TBDI1-14 | P3-TBDI1-14/C3S1-14 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
15 | IN-14 | P3-TBDI1-15 | C3S1-15/P3-TBDI1-15 | P3-TBDI1-15/C3S1-15 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
16 | IN-15 | P3-TBDI1-16 | C3S1-16/P3-TBDI1-16 | P3-TBDI1-16/C3S1-16 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-606 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-606 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P3-TBDI1-17 | C3S1-19/P3-TBDI1-17 | P3-TBDI1-17/C3S1-19 | JB-606 | FT-60203_DI_1 | FT-60203 | Flow Transmitter | ACTIVE
20 | IN-17 | P3-TBDI1-18 | C3S1-20/P3-TBDI1-18 | P3-TBDI1-18/C3S1-20 | JB-606 | LSH-60250_DI_1 | LSH-60250 | Process Instrument | ACTIVE
21 | IN-18 | P3-TBDI1-19 | C3S1-21/P3-TBDI1-19 | P3-TBDI1-19/C3S1-21 | JB-606 | XA-60261_DI_1 | XA-60261 | Process Instrument | ACTIVE
22 | IN-19 | P3-TBDI1-20 | C3S1-22/P3-TBDI1-20 | P3-TBDI1-20/C3S1-22 | JB-606 | XA-60262_DI_1 | XA-60262 | Process Instrument | ACTIVE
23 | IN-20 | P3-TBDI1-21 | C3S1-23/P3-TBDI1-21 | P3-TBDI1-21/C3S1-23 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
24 | IN-21 | P3-TBDI1-22 | C3S1-24/P3-TBDI1-22 | P3-TBDI1-22/C3S1-24 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
25 | IN-22 | P3-TBDI1-23 | C3S1-25/P3-TBDI1-23 | P3-TBDI1-23/C3S1-25 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
26 | IN-23 | P3-TBDI1-24 | C3S1-26/P3-TBDI1-24 | P3-TBDI1-24/C3S1-26 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
27 | IN-24 | P3-TBDI1-25 | C3S1-27/P3-TBDI1-25 | P3-TBDI1-25/C3S1-27 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
28 | IN-25 | P3-TBDI1-26 | C3S1-28/P3-TBDI1-26 | P3-TBDI1-26/C3S1-28 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
29 | IN-26 | P3-TBDI1-27 | C3S1-29/P3-TBDI1-27 | P3-TBDI1-27/C3S1-29 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-27 | P3-TBDI1-28 | C3S1-30/P3-TBDI1-28 | P3-TBDI1-28/C3S1-30 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
31 | IN-28 | P3-TBDI1-29 | C3S1-31/P3-TBDI1-29 | P3-TBDI1-29/C3S1-31 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-29 | P3-TBDI1-30 | C3S1-32/P3-TBDI1-30 | P3-TBDI1-30/C3S1-32 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
33 | IN-30 | P3-TBDI1-31 | C3S1-33/P3-TBDI1-31 | P3-TBDI1-31/C3S1-33 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-31 | P3-TBDI1-32 | C3S1-34/P3-TBDI1-32 | P3-TBDI1-32/C3S1-34 | JB-606 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
35 | GND1 | 0VDC | 0VDC | 0VDC | JB-606 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | JB-606 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C3S2
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C3S2
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS: C3 ¦ SLOT: 2 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: JB-612
← Back to Chassis Summary (C3SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P3-TBDI2-1 | C3S2-1/P3-TBDI2-1 | P3-TBDI2-1/C3S2-1 | JB-612 | PSL-61305_DI_1 | PSL-61305 | Process Instrument | ACTIVE
2 | IN-1 | P3-TBDI2-2 | C3S2-2/P3-TBDI2-2 | P3-TBDI2-2/C3S2-2 | JB-612 | PSL-61306_DI_1 | PSL-61306 | Process Instrument | ACTIVE
3 | IN-2 | P3-TBDI2-3 | C3S2-3/P3-TBDI2-3 | P3-TBDI2-3/C3S2-3 | JB-612 | PVM-61301_DI_1 | PVM-61301 | Process Instrument | ACTIVE
4 | IN-3 | P3-TBDI2-4 | C3S2-4/P3-TBDI2-4 | P3-TBDI2-4/C3S2-4 | JB-612 | PVM-61301_DI_2 | PVM-61301 | Process Instrument | ACTIVE
5 | IN-4 | P3-TBDI2-5 | C3S2-5/P3-TBDI2-5 | P3-TBDI2-5/C3S2-5 | JB-612 | XA-61301A_DI_1 | XA-61301A | Process Instrument | ACTIVE
6 | IN-5 | P3-TBDI2-6 | C3S2-6/P3-TBDI2-6 | P3-TBDI2-6/C3S2-6 | JB-612 | XA-61301B_DI_1 | XA-61301B | Process Instrument | ACTIVE
7 | IN-6 | P3-TBDI2-7 | C3S2-7/P3-TBDI2-7 | P3-TBDI2-7/C3S2-7 | JB-612 | XA-61301C_DI_1 | XA-61301C | Process Instrument | ACTIVE
8 | IN-7 | P3-TBDI2-8 | C3S2-8/P3-TBDI2-8 | P3-TBDI2-8/C3S2-8 | JB-612 | XA-61301D_DI_1 | XA-61301D | Process Instrument | ACTIVE
9 | IN-8 | P3-TBDI2-9 | C3S2-9/P3-TBDI2-9 | P3-TBDI2-9/C3S2-9 | JB-612 | XA-61301E_DI_1 | XA-61301E | Process Instrument | ACTIVE
10 | IN-9 | P3-TBDI2-10 | C3S2-10/P3-TBDI2-10 | P3-TBDI2-10/C3S2-10 | JB-612 | XA-61301F_DI_1 | XA-61301F | Process Instrument | ACTIVE
11 | IN-10 | P3-TBDI2-11 | C3S2-11/P3-TBDI2-11 | P3-TBDI2-11/C3S2-11 | JB-612 | XA-61301G_DI_1 | XA-61301G | Process Instrument | ACTIVE
12 | IN-11 | P3-TBDI2-12 | C3S2-12/P3-TBDI2-12 | P3-TBDI2-12/C3S2-12 | JB-612 | XA-61301H_DI_1 | XA-61301H | Process Instrument | ACTIVE
13 | IN-12 | P3-TBDI2-13 | C3S2-13/P3-TBDI2-13 | P3-TBDI2-13/C3S2-13 | JB-612 | XA-61301J_DI_1 | XA-61301J | Process Instrument | ACTIVE
14 | IN-13 | P3-TBDI2-14 | C3S2-14/P3-TBDI2-14 | P3-TBDI2-14/C3S2-14 | JB-612 | XV-61302_DI_1 | XV-61302 | Control Valve Position Feedback | ACTIVE
15 | IN-14 | P3-TBDI2-15 | C3S2-15/P3-TBDI2-15 | P3-TBDI2-15/C3S2-15 | JB-612 | XV-61302_DI_2 | XV-61302 | Control Valve Position Feedback | ACTIVE
16 | IN-15 | P3-TBDI2-16 | C3S2-16/P3-TBDI2-16 | P3-TBDI2-16/C3S2-16 | JB-612 | XV-61303_DI_1 | XV-61303 | Control Valve Position Feedback | ACTIVE
17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P3-TBDI2-17 | C3S2-19/P3-TBDI2-17 | P3-TBDI2-17/C3S2-19 | JB-612 | XV-61303_DI_2 | XV-61303 | Control Valve Position Feedback | ACTIVE
20 | IN-17 | P3-TBDI2-18 | C3S2-20/P3-TBDI2-18 | P3-TBDI2-18/C3S2-20 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
21 | IN-18 | P3-TBDI2-19 | C3S2-21/P3-TBDI2-19 | P3-TBDI2-19/C3S2-21 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
22 | IN-19 | P3-TBDI2-20 | C3S2-22/P3-TBDI2-20 | P3-TBDI2-20/C3S2-22 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
23 | IN-20 | P3-TBDI2-21 | C3S2-23/P3-TBDI2-21 | P3-TBDI2-21/C3S2-23 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
24 | IN-21 | P3-TBDI2-22 | C3S2-24/P3-TBDI2-22 | P3-TBDI2-22/C3S2-24 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
25 | IN-22 | P3-TBDI2-23 | C3S2-25/P3-TBDI2-23 | P3-TBDI2-23/C3S2-25 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
26 | IN-23 | P3-TBDI2-24 | C3S2-26/P3-TBDI2-24 | P3-TBDI2-24/C3S2-26 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
27 | IN-24 | P3-TBDI2-25 | C3S2-27/P3-TBDI2-25 | P3-TBDI2-25/C3S2-27 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
28 | IN-25 | P3-TBDI2-26 | C3S2-28/P3-TBDI2-26 | P3-TBDI2-26/C3S2-28 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
29 | IN-26 | P3-TBDI2-27 | C3S2-29/P3-TBDI2-27 | P3-TBDI2-27/C3S2-29 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-27 | P3-TBDI2-28 | C3S2-30/P3-TBDI2-28 | P3-TBDI2-28/C3S2-30 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
31 | IN-28 | P3-TBDI2-29 | C3S2-31/P3-TBDI2-29 | P3-TBDI2-29/C3S2-31 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-29 | P3-TBDI2-30 | C3S2-32/P3-TBDI2-30 | P3-TBDI2-30/C3S2-32 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
33 | IN-30 | P3-TBDI2-31 | C3S2-33/P3-TBDI2-31 | P3-TBDI2-31/C3S2-33 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-31 | P3-TBDI2-32 | C3S2-34/P3-TBDI2-32 | P3-TBDI2-32/C3S2-34 | JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
35 | GND1 | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C3S3
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C3S3
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS: C3 ¦ SLOT: 3 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: JB-618
← Back to Chassis Summary (C3SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P3-TBDI3-1 | C3S3-1/P3-TBDI3-1 | P3-TBDI3-1/C3S3-1 | JB-618 | DV-61301_DI_1 | DV-61301 | Process Instrument | ACTIVE
2 | IN-1 | P3-TBDI3-2 | C3S3-2/P3-TBDI3-2 | P3-TBDI3-2/C3S3-2 | JB-618 | DV-61301_DI_2 | DV-61301 | Process Instrument | ACTIVE
3 | IN-2 | P3-TBDI3-3 | C3S3-3/P3-TBDI3-3 | P3-TBDI3-3/C3S3-3 | JB-618 | DV-61302_DI_1 | DV-61302 | Process Instrument | ACTIVE
4 | IN-3 | P3-TBDI3-4 | C3S3-4/P3-TBDI3-4 | P3-TBDI3-4/C3S3-4 | JB-618 | DV-61302_DI_2 | DV-61302 | Process Instrument | ACTIVE
5 | IN-4 | P3-TBDI3-5 | C3S3-5/P3-TBDI3-5 | P3-TBDI3-5/C3S3-5 | JB-618 | LS-61303_DI_1 | LS-61303 | Process Instrument | ACTIVE
6 | IN-5 | P3-TBDI3-6 | C3S3-6/P3-TBDI3-6 | P3-TBDI3-6/C3S3-6 | JB-618 | PSL-61301_DI_1 | PSL-61301 | Process Instrument | ACTIVE
7 | IN-6 | P3-TBDI3-7 | C3S3-7/P3-TBDI3-7 | P3-TBDI3-7/C3S3-7 | JB-618 | PSL-61302_DI_1 | PSL-61302 | Process Instrument | ACTIVE
8 | IN-7 | P3-TBDI3-8 | C3S3-8/P3-TBDI3-8 | P3-TBDI3-8/C3S3-8 | JB-618 | PSL-61311_DI_1 | PSL-61311 | Process Instrument | ACTIVE
9 | IN-8 | P3-TBDI3-9 | C3S3-9/P3-TBDI3-9 | P3-TBDI3-9/C3S3-9 | JB-618 | SV-61304_DI_1 | SV-61304 | Process Instrument | ACTIVE
10 | IN-9 | P3-TBDI3-10 | C3S3-10/P3-TBDI3-10 | P3-TBDI3-10/C3S3-10 | JB-618 | SV-61304_DI_2 | SV-61304 | Process Instrument | ACTIVE
11 | IN-10 | P3-TBDI3-11 | C3S3-11/P3-TBDI3-11 | P3-TBDI3-11/C3S3-11 | JB-618 | XV-61301_DI_1 | XV-61301 | Control Valve Position Feedback | ACTIVE
12 | IN-11 | P3-TBDI3-12 | C3S3-12/P3-TBDI3-12 | P3-TBDI3-12/C3S3-12 | JB-618 | XV-61301_DI_2 | XV-61301 | Control Valve Position Feedback | ACTIVE
13 | IN-12 | P3-TBDI3-13 | C3S3-13/P3-TBDI3-13 | P3-TBDI3-13/C3S3-13 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
14 | IN-13 | P3-TBDI3-14 | C3S3-14/P3-TBDI3-14 | P3-TBDI3-14/C3S3-14 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
15 | IN-14 | P3-TBDI3-15 | C3S3-15/P3-TBDI3-15 | P3-TBDI3-15/C3S3-15 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
16 | IN-15 | P3-TBDI3-16 | C3S3-16/P3-TBDI3-16 | P3-TBDI3-16/C3S3-16 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
17 | GND-0 | 0VDC | 0VDC | 0VDC | JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P3-TBDI3-17 | C3S3-19/P3-TBDI3-17 | P3-TBDI3-17/C3S3-19 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
20 | IN-17 | P3-TBDI3-18 | C3S3-20/P3-TBDI3-18 | P3-TBDI3-18/C3S3-20 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
21 | IN-18 | P3-TBDI3-19 | C3S3-21/P3-TBDI3-19 | P3-TBDI3-19/C3S3-21 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
22 | IN-19 | P3-TBDI3-20 | C3S3-22/P3-TBDI3-20 | P3-TBDI3-20/C3S3-22 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
23 | IN-20 | P3-TBDI3-21 | C3S3-23/P3-TBDI3-21 | P3-TBDI3-21/C3S3-23 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
24 | IN-21 | P3-TBDI3-22 | C3S3-24/P3-TBDI3-22 | P3-TBDI3-22/C3S3-24 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
25 | IN-22 | P3-TBDI3-23 | C3S3-25/P3-TBDI3-23 | P3-TBDI3-23/C3S3-25 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
26 | IN-23 | P3-TBDI3-24 | C3S3-26/P3-TBDI3-24 | P3-TBDI3-24/C3S3-26 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
27 | IN-24 | P3-TBDI3-25 | C3S3-27/P3-TBDI3-25 | P3-TBDI3-25/C3S3-27 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
28 | IN-25 | P3-TBDI3-26 | C3S3-28/P3-TBDI3-26 | P3-TBDI3-26/C3S3-28 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
29 | IN-26 | P3-TBDI3-27 | C3S3-29/P3-TBDI3-27 | P3-TBDI3-27/C3S3-29 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-27 | P3-TBDI3-28 | C3S3-30/P3-TBDI3-28 | P3-TBDI3-28/C3S3-30 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
31 | IN-28 | P3-TBDI3-29 | C3S3-31/P3-TBDI3-29 | P3-TBDI3-29/C3S3-31 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-29 | P3-TBDI3-30 | C3S3-32/P3-TBDI3-30 | P3-TBDI3-30/C3S3-32 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
33 | IN-30 | P3-TBDI3-31 | C3S3-33/P3-TBDI3-31 | P3-TBDI3-31/C3S3-33 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-31 | P3-TBDI3-32 | C3S3-34/P3-TBDI3-32 | P3-TBDI3-32/C3S3-34 | JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
35 | GND1 | 0VDC | 0VDC | 0VDC | JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C3S4
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C3S4
DIGITAL OUTPUT CARD (1756-OB32 32-CH 24VDC SOURCE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS: C3 ¦ SLOT: 4 ¦ MODULE: 1756-OB32 ¦ DESTINATION AREA: JB-606, JB-612
← Back to Chassis Summary (C3SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBRLx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | OUT-0 | P3-TBRL1-1 | C3S4-1/P3-TBRL1-1 | P3-TBRL1-1/C3S4-1 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
2 | OUT-1 | P3-TBRL1-2 | C3S4-2/P3-TBRL1-2 | P3-TBRL1-2/C3S4-2 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
3 | OUT-2 | P3-TBRL1-3 | C3S4-3/P3-TBRL1-3 | P3-TBRL1-3/C3S4-3 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
4 | OUT-3 | P3-TBRL1-4 | C3S4-4/P3-TBRL1-4 | P3-TBRL1-4/C3S4-4 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
5 | OUT-4 | P3-TBRL1-5 | C3S4-5/P3-TBRL1-5 | P3-TBRL1-5/C3S4-5 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
6 | OUT-5 | P3-TBRL1-6 | C3S4-6/P3-TBRL1-6 | P3-TBRL1-6/C3S4-6 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
7 | OUT-6 | P3-TBRL1-7 | C3S4-7/P3-TBRL1-7 | P3-TBRL1-7/C3S4-7 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
8 | OUT-7 | P3-TBRL1-8 | C3S4-8/P3-TBRL1-8 | P3-TBRL1-8/C3S4-8 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
9 | OUT-8 | P3-TBRL1-9 | C3S4-9/P3-TBRL1-9 | P3-TBRL1-9/C3S4-9 | JB-606 | SV-60220_DO_1 | SV-60220 | Process Instrument | ACTIVE
10 | OUT-9 | P3-TBRL1-10 | C3S4-10/P3-TBRL1-10 | P3-TBRL1-10/C3S4-10 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
11 | OUT-10 | P3-TBRL1-11 | C3S4-11/P3-TBRL1-11 | P3-TBRL1-11/C3S4-11 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
12 | OUT-11 | P3-TBRL1-12 | C3S4-12/P3-TBRL1-12 | P3-TBRL1-12/C3S4-12 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
13 | OUT-12 | P3-TBRL1-13 | C3S4-13/P3-TBRL1-13 | P3-TBRL1-13/C3S4-13 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
14 | OUT-13 | P3-TBRL1-14 | C3S4-14/P3-TBRL1-14 | P3-TBRL1-14/C3S4-14 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
15 | OUT-14 | P3-TBRL1-15 | C3S4-15/P3-TBRL1-15 | P3-TBRL1-15/C3S4-15 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
16 | OUT-15 | P3-TBRL1-16 | C3S4-16/P3-TBRL1-16 | P3-TBRL1-16/C3S4-16 | JB-606 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
17 | RTN OUT-0 | P3-TBRL1-17 | C3S4-17/P3-TBRL1-17 | P3-TBRL1-17/C3S4-17 | JB-606 | Spare_DO_17 | Spare | Spare Reserve Channel | SPARE
18 | DC-0(+) | +24VDC | +24VDC | +24VDC | JB-606 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | OUT-16 | P3-TBRL1-17 | C3S4-19/P3-TBRL1-17 | P3-TBRL1-17/C3S4-19 | JB-612 | PVM-61301_DO_1 | PVM-61301 | Process Instrument | ACTIVE
20 | OUT-17 | P3-TBRL1-18 | C3S4-20/P3-TBRL1-18 | P3-TBRL1-18/C3S4-20 | JB-612 | PVM-61301_DO_2 | PVM-61301 | Process Instrument | ACTIVE
21 | OUT-18 | P3-TBRL1-19 | C3S4-21/P3-TBRL1-19 | P3-TBRL1-19/C3S4-21 | JB-612 | SV-61307_DO_1 | SV-61307 | Process Instrument | ACTIVE
22 | OUT-19 | P3-TBRL1-20 | C3S4-22/P3-TBRL1-20 | P3-TBRL1-20/C3S4-22 | JB-612 | SV-61308_DO_1 | SV-61308 | Process Instrument | ACTIVE
23 | OUT-20 | P3-TBRL1-21 | C3S4-23/P3-TBRL1-21 | P3-TBRL1-21/C3S4-23 | JB-612 | SV-61309_DO_1 | SV-61309 | Process Instrument | ACTIVE
24 | OUT-21 | P3-TBRL1-22 | C3S4-24/P3-TBRL1-22 | P3-TBRL1-22/C3S4-24 | JB-612 | SV-61310_DO_1 | SV-61310 | Process Instrument | ACTIVE
25 | OUT-22 | P3-TBRL1-23 | C3S4-25/P3-TBRL1-23 | P3-TBRL1-23/C3S4-25 | JB-612 | SV-61311_DO_1 | SV-61311 | Process Instrument | ACTIVE
26 | OUT-23 | P3-TBRL1-24 | C3S4-26/P3-TBRL1-24 | P3-TBRL1-24/C3S4-26 | JB-612 | XS-61301A_DO_1 | XS-61301A | Process Instrument | ACTIVE
27 | OUT-24 | P3-TBRL1-25 | C3S4-27/P3-TBRL1-25 | P3-TBRL1-25/C3S4-27 | JB-612 | XS-61301B_DO_1 | XS-61301B | Process Instrument | ACTIVE
28 | OUT-25 | P3-TBRL1-26 | C3S4-28/P3-TBRL1-26 | P3-TBRL1-26/C3S4-28 | JB-612 | XS-61301C_DO_1 | XS-61301C | Process Instrument | ACTIVE
29 | OUT-26 | P3-TBRL1-27 | C3S4-29/P3-TBRL1-27 | P3-TBRL1-27/C3S4-29 | JB-612 | XS-61301D_DO_1 | XS-61301D | Process Instrument | ACTIVE
30 | OUT-27 | P3-TBRL1-28 | C3S4-30/P3-TBRL1-28 | P3-TBRL1-28/C3S4-30 | JB-612 | XS-61301E_DO_1 | XS-61301E | Process Instrument | ACTIVE
31 | OUT-28 | P3-TBRL1-29 | C3S4-31/P3-TBRL1-29 | P3-TBRL1-29/C3S4-31 | JB-612 | XS-61301F_DO_1 | XS-61301F | Process Instrument | ACTIVE
32 | OUT-29 | P3-TBRL1-30 | C3S4-32/P3-TBRL1-30 | P3-TBRL1-30/C3S4-32 | JB-612 | XV-61302_DO_1 | XV-61302 | Control Valve Position Feedback | ACTIVE
33 | OUT-30 | P3-TBRL1-31 | C3S4-33/P3-TBRL1-31 | P3-TBRL1-31/C3S4-33 | JB-612 | XV-61303_DO_1 | XV-61303 | Control Valve Position Feedback | ACTIVE
34 | OUT-31 | P3-TBRL1-32 | C3S4-34/P3-TBRL1-32 | P3-TBRL1-32/C3S4-34 | JB-612 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
35 | RTN OUT-1 | P3-TBRL1-35 | C3S4-35/P3-TBRL1-35 | P3-TBRL1-35/C3S4-35 | JB-606 | Spare_DO_35 | Spare | Spare Reserve Channel | SPARE
36 | DC-1(+) | +24VDC | +24VDC | +24VDC | JB-606 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C3S5
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C3S5
DIGITAL OUTPUT CARD (1756-OB32 32-CH 24VDC SOURCE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS: C3 ¦ SLOT: 5 ¦ MODULE: 1756-OB32 ¦ DESTINATION AREA: JB-618
← Back to Chassis Summary (C3SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBRLx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | OUT-0 | P3-TBRL2-1 | C3S5-1/P3-TBRL2-1 | P3-TBRL2-1/C3S5-1 | JB-618 | DV-61301_DO_1 | DV-61301 | Process Instrument | ACTIVE
2 | OUT-1 | P3-TBRL2-2 | C3S5-2/P3-TBRL2-2 | P3-TBRL2-2/C3S5-2 | JB-618 | DV-61302_DO_1 | DV-61302 | Process Instrument | ACTIVE
3 | OUT-2 | P3-TBRL2-3 | C3S5-3/P3-TBRL2-3 | P3-TBRL2-3/C3S5-3 | JB-618 | SV-61301_DO_1 | SV-61301 | Process Instrument | ACTIVE
4 | OUT-3 | P3-TBRL2-4 | C3S5-4/P3-TBRL2-4 | P3-TBRL2-4/C3S5-4 | JB-618 | SV-61302_DO_1 | SV-61302 | Process Instrument | ACTIVE
5 | OUT-4 | P3-TBRL2-5 | C3S5-5/P3-TBRL2-5 | P3-TBRL2-5/C3S5-5 | JB-618 | SV-61303_DO_1 | SV-61303 | Process Instrument | ACTIVE
6 | OUT-5 | P3-TBRL2-6 | C3S5-6/P3-TBRL2-6 | P3-TBRL2-6/C3S5-6 | JB-618 | SV-61304_DO_1 | SV-61304 | Process Instrument | ACTIVE
7 | OUT-6 | P3-TBRL2-7 | C3S5-7/P3-TBRL2-7 | P3-TBRL2-7/C3S5-7 | JB-618 | SV-61305_DO_1 | SV-61305 | Process Instrument | ACTIVE
8 | OUT-7 | P3-TBRL2-8 | C3S5-8/P3-TBRL2-8 | P3-TBRL2-8/C3S5-8 | JB-618 | SV-61306_DO_1 | SV-61306 | Process Instrument | ACTIVE
9 | OUT-8 | P3-TBRL2-9 | C3S5-9/P3-TBRL2-9 | P3-TBRL2-9/C3S5-9 | JB-618 | XV-61301_DO_1 | XV-61301 | Control Valve Position Feedback | ACTIVE
10 | OUT-9 | P3-TBRL2-10 | C3S5-10/P3-TBRL2-10 | P3-TBRL2-10/C3S5-10 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
11 | OUT-10 | P3-TBRL2-11 | C3S5-11/P3-TBRL2-11 | P3-TBRL2-11/C3S5-11 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
12 | OUT-11 | P3-TBRL2-12 | C3S5-12/P3-TBRL2-12 | P3-TBRL2-12/C3S5-12 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
13 | OUT-12 | P3-TBRL2-13 | C3S5-13/P3-TBRL2-13 | P3-TBRL2-13/C3S5-13 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
14 | OUT-13 | P3-TBRL2-14 | C3S5-14/P3-TBRL2-14 | P3-TBRL2-14/C3S5-14 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
15 | OUT-14 | P3-TBRL2-15 | C3S5-15/P3-TBRL2-15 | P3-TBRL2-15/C3S5-15 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
16 | OUT-15 | P3-TBRL2-16 | C3S5-16/P3-TBRL2-16 | P3-TBRL2-16/C3S5-16 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
17 | RTN OUT-0 | P3-TBRL2-17 | C3S5-17/P3-TBRL2-17 | P3-TBRL2-17/C3S5-17 | JB-618 | Spare_DO_17 | Spare | Spare Reserve Channel | SPARE
18 | DC-0(+) | +24VDC | +24VDC | +24VDC | JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | OUT-16 | P3-TBRL2-17 | C3S5-19/P3-TBRL2-17 | P3-TBRL2-17/C3S5-19 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
20 | OUT-17 | P3-TBRL2-18 | C3S5-20/P3-TBRL2-18 | P3-TBRL2-18/C3S5-20 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
21 | OUT-18 | P3-TBRL2-19 | C3S5-21/P3-TBRL2-19 | P3-TBRL2-19/C3S5-21 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
22 | OUT-19 | P3-TBRL2-20 | C3S5-22/P3-TBRL2-20 | P3-TBRL2-20/C3S5-22 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
23 | OUT-20 | P3-TBRL2-21 | C3S5-23/P3-TBRL2-21 | P3-TBRL2-21/C3S5-23 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
24 | OUT-21 | P3-TBRL2-22 | C3S5-24/P3-TBRL2-22 | P3-TBRL2-22/C3S5-24 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
25 | OUT-22 | P3-TBRL2-23 | C3S5-25/P3-TBRL2-23 | P3-TBRL2-23/C3S5-25 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
26 | OUT-23 | P3-TBRL2-24 | C3S5-26/P3-TBRL2-24 | P3-TBRL2-24/C3S5-26 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
27 | OUT-24 | P3-TBRL2-25 | C3S5-27/P3-TBRL2-25 | P3-TBRL2-25/C3S5-27 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
28 | OUT-25 | P3-TBRL2-26 | C3S5-28/P3-TBRL2-26 | P3-TBRL2-26/C3S5-28 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
29 | OUT-26 | P3-TBRL2-27 | C3S5-29/P3-TBRL2-27 | P3-TBRL2-27/C3S5-29 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
30 | OUT-27 | P3-TBRL2-28 | C3S5-30/P3-TBRL2-28 | P3-TBRL2-28/C3S5-30 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
31 | OUT-28 | P3-TBRL2-29 | C3S5-31/P3-TBRL2-29 | P3-TBRL2-29/C3S5-31 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
32 | OUT-29 | P3-TBRL2-30 | C3S5-32/P3-TBRL2-30 | P3-TBRL2-30/C3S5-32 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
33 | OUT-30 | P3-TBRL2-31 | C3S5-33/P3-TBRL2-31 | P3-TBRL2-31/C3S5-33 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
34 | OUT-31 | P3-TBRL2-32 | C3S5-34/P3-TBRL2-32 | P3-TBRL2-32/C3S5-34 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
35 | RTN OUT-1 | P3-TBRL2-35 | C3S5-35/P3-TBRL2-35 | P3-TBRL2-35/C3S5-35 | JB-618 | Spare_DO_35 | Spare | Spare Reserve Channel | SPARE
36 | DC-1(+) | +24VDC | +24VDC | +24VDC | JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C3S6
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C3S6
ANALOG INPUT CARD (1756-IF16 16-CH CURRENT/VOLTAGE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS: C3 ¦ SLOT: 6 ¦ MODULE: 1756-IF16 ¦ DESTINATION AREA: JB-602, JB-606
← Back to Chassis Summary (C3SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | i RTN-0 | P3-TBAI1-1(B) | C3S6-1/P3-TBAI1-1(B) | P3-TBAI1-1(B)/C3S6-1 | JB-602 | TT-60215B_AI_1 | TT-60215B | Temperature Transmitter | ACTIVE
2 | IN-0 | P3-TBAI1-1(A) | C3S6-2/P3-TBAI1-1(A) | P3-TBAI1-1(A)/C3S6-2 | JB-602 | TT-60215B_AI_1 | TT-60215B | Temperature Transmitter | ACTIVE
3 | i RTN-1 | P3-TBAI1-2(B) | C3S6-3/P3-TBAI1-2(B) | P3-TBAI1-2(B)/C3S6-3 | JB-602 | TT-60216_AI_1 | TT-60216 | Temperature Transmitter | ACTIVE
4 | IN-1 | P3-TBAI1-2(A) | C3S6-4/P3-TBAI1-2(A) | P3-TBAI1-2(A)/C3S6-4 | JB-602 | TT-60216_AI_1 | TT-60216 | Temperature Transmitter | ACTIVE
5 | i RTN-2 | P3-TBAI1-3(B) | C3S6-5/P3-TBAI1-3(B) | P3-TBAI1-3(B)/C3S6-5 | JB-602 | TT-60240_AI_1 | TT-60240 | Temperature Transmitter | ACTIVE
6 | IN-2 | P3-TBAI1-3(A) | C3S6-6/P3-TBAI1-3(A) | P3-TBAI1-3(A)/C3S6-6 | JB-602 | TT-60240_AI_1 | TT-60240 | Temperature Transmitter | ACTIVE
7 | i RTN-3 | P3-TBAI1-4(B) | C3S6-7/P3-TBAI1-4(B) | P3-TBAI1-4(B)/C3S6-7 | JB-602 | TT-60241A_AI_1 | TT-60241A | Temperature Transmitter | ACTIVE
8 | IN-3 | P3-TBAI1-4(A) | C3S6-8/P3-TBAI1-4(A) | P3-TBAI1-4(A)/C3S6-8 | JB-602 | TT-60241A_AI_1 | TT-60241A | Temperature Transmitter | ACTIVE
9 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
10 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
11 | i RTN-4 | P3-TBAI1-5(B) | C3S6-11/P3-TBAI1-5(B) | P3-TBAI1-5(B)/C3S6-11 | JB-602 | TT-60241B_AI_1 | TT-60241B | Temperature Transmitter | ACTIVE
12 | IN-4 | P3-TBAI1-5(A) | C3S6-12/P3-TBAI1-5(A) | P3-TBAI1-5(A)/C3S6-12 | JB-602 | TT-60241B_AI_1 | TT-60241B | Temperature Transmitter | ACTIVE
13 | i RTN-5 | P3-TBAI1-6(B) | C3S6-13/P3-TBAI1-6(B) | P3-TBAI1-6(B)/C3S6-13 | JB-602 | VT-60210A_AI_1 | VT-60210A | Vibration Transmitter | ACTIVE
14 | IN-5 | P3-TBAI1-6(A) | C3S6-14/P3-TBAI1-6(A) | P3-TBAI1-6(A)/C3S6-14 | JB-602 | VT-60210A_AI_1 | VT-60210A | Vibration Transmitter | ACTIVE
15 | i RTN-6 | P3-TBAI1-7(B) | C3S6-15/P3-TBAI1-7(B) | P3-TBAI1-7(B)/C3S6-15 | JB-602 | VT-60210B_AI_1 | VT-60210B | Vibration Transmitter | ACTIVE
16 | IN-6 | P3-TBAI1-7(A) | C3S6-16/P3-TBAI1-7(A) | P3-TBAI1-7(A)/C3S6-16 | JB-602 | VT-60210B_AI_1 | VT-60210B | Vibration Transmitter | ACTIVE
17 | i RTN-7 | P3-TBAI1-8(B) | C3S6-17/P3-TBAI1-8(B) | P3-TBAI1-8(B)/C3S6-17 | JB-602 | VT-60241A_AI_1 | VT-60241A | Vibration Transmitter | ACTIVE
18 | IN-7 | P3-TBAI1-8(A) | C3S6-18/P3-TBAI1-8(A) | P3-TBAI1-8(A)/C3S6-18 | JB-602 | VT-60241A_AI_1 | VT-60241A | Vibration Transmitter | ACTIVE
19 | i RTN-8 | P3-TBAI1-9(B) | C3S6-19/P3-TBAI1-9(B) | P3-TBAI1-9(B)/C3S6-19 | JB-602 | VT-60241B_AI_1 | VT-60241B | Vibration Transmitter | ACTIVE
20 | IN-8 | P3-TBAI1-9(A) | C3S6-20/P3-TBAI1-9(A) | P3-TBAI1-9(A)/C3S6-20 | JB-602 | VT-60241B_AI_1 | VT-60241B | Vibration Transmitter | ACTIVE
21 | i RTN-9 | P3-TBAI1-10(B) | C3S6-21/P3-TBAI1-10(B) | P3-TBAI1-10(B)/C3S6-21 | JB-602 | FT-60210_AI_1 | FT-60210 | Flow Transmitter | ACTIVE
22 | IN-9 | P3-TBAI1-10(A) | C3S6-22/P3-TBAI1-10(A) | P3-TBAI1-10(A)/C3S6-22 | JB-602 | FT-60210_AI_1 | FT-60210 | Flow Transmitter | ACTIVE
23 | i RTN-10 | P3-TBAI1-11(B) | C3S6-23/P3-TBAI1-11(B) | P3-TBAI1-11(B)/C3S6-23 | JB-602 | FT-60211_AI_1 | FT-60211 | Flow Transmitter | ACTIVE
24 | IN-10 | P3-TBAI1-11(A) | C3S6-24/P3-TBAI1-11(A) | P3-TBAI1-11(A)/C3S6-24 | JB-602 | FT-60211_AI_1 | FT-60211 | Flow Transmitter | ACTIVE
25 | i RTN-11 | P3-TBAI1-12(B) | C3S6-25/P3-TBAI1-12(B) | P3-TBAI1-12(B)/C3S6-25 | JB-602 | FT-60210_AI_2 | FT-60210 | Flow Transmitter | ACTIVE
26 | IN-11 | P3-TBAI1-12(A) | C3S6-26/P3-TBAI1-12(A) | P3-TBAI1-12(A)/C3S6-26 | JB-602 | FT-60210_AI_2 | FT-60210 | Flow Transmitter | ACTIVE
27 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
28 | RTN | 0VDC | 0VDC | 0VDC | JB-602 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
29 | i RTN-12 | P3-TBAI1-13(B) | C3S6-29/P3-TBAI1-13(B) | P3-TBAI1-13(B)/C3S6-29 | JB-602 | FT-60211_AI_2 | FT-60211 | Flow Transmitter | ACTIVE
30 | IN-12 | P3-TBAI1-13(A) | C3S6-30/P3-TBAI1-13(A) | P3-TBAI1-13(A)/C3S6-30 | JB-602 | FT-60211_AI_2 | FT-60211 | Flow Transmitter | ACTIVE
31 | i RTN-13 | P3-TBAI1-14(B) | C3S6-31/P3-TBAI1-14(B) | P3-TBAI1-14(B)/C3S6-31 | JB-602 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-13 | P3-TBAI1-14(A) | C3S6-32/P3-TBAI1-14(A) | P3-TBAI1-14(A)/C3S6-32 | JB-602 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
33 | i RTN-14 | P3-TBAI1-15(B) | C3S6-33/P3-TBAI1-15(B) | P3-TBAI1-15(B)/C3S6-33 | JB-606 | DPT-60201_AI_1 | DPT-60201 | Differential Pressure Transmitte | ACTIVE
34 | IN-14 | P3-TBAI1-15(A) | C3S6-34/P3-TBAI1-15(A) | P3-TBAI1-15(A)/C3S6-34 | JB-606 | DPT-60201_AI_1 | DPT-60201 | Differential Pressure Transmitte | ACTIVE
35 | i RTN-15 | P3-TBAI1-16(B) | C3S6-35/P3-TBAI1-16(B) | P3-TBAI1-16(B)/C3S6-35 | JB-606 | FT-60203_AI_1 | FT-60203 | Flow Transmitter | ACTIVE
36 | IN-15 | P3-TBAI1-16(A) | C3S6-36/P3-TBAI1-16(A) | P3-TBAI1-16(A)/C3S6-36 | JB-606 | FT-60203_AI_1 | FT-60203 | Flow Transmitter | ACTIVE

## C3S7
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C3S7
ANALOG INPUT CARD (1756-IF16 16-CH CURRENT/VOLTAGE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS: C3 ¦ SLOT: 7 ¦ MODULE: 1756-IF16 ¦ DESTINATION AREA: JB-607
← Back to Chassis Summary (C3SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | i RTN-0 | P3-TBAI2-1(B) | C3S7-1/P3-TBAI2-1(B) | P3-TBAI2-1(B)/C3S7-1 | JB-607 | FT-60207_AI_1 | FT-60207 | Flow Transmitter | ACTIVE
2 | IN-0 | P3-TBAI2-1(A) | C3S7-2/P3-TBAI2-1(A) | P3-TBAI2-1(A)/C3S7-2 | JB-607 | FT-60207_AI_1 | FT-60207 | Flow Transmitter | ACTIVE
3 | i RTN-1 | P3-TBAI2-2(B) | C3S7-3/P3-TBAI2-2(B) | P3-TBAI2-2(B)/C3S7-3 | JB-607 | FT-60221_AI_1 | FT-60221 | Flow Transmitter | ACTIVE
4 | IN-1 | P3-TBAI2-2(A) | C3S7-4/P3-TBAI2-2(A) | P3-TBAI2-2(A)/C3S7-4 | JB-607 | FT-60221_AI_1 | FT-60221 | Flow Transmitter | ACTIVE
5 | i RTN-2 | P3-TBAI2-3(B) | C3S7-5/P3-TBAI2-3(B) | P3-TBAI2-3(B)/C3S7-5 | JB-607 | FT-60261FA_AI_1 | FT-60261FA | Flow Transmitter | ACTIVE
6 | IN-2 | P3-TBAI2-3(A) | C3S7-6/P3-TBAI2-3(A) | P3-TBAI2-3(A)/C3S7-6 | JB-607 | FT-60261FA_AI_1 | FT-60261FA | Flow Transmitter | ACTIVE
7 | i RTN-3 | P3-TBAI2-4(B) | C3S7-7/P3-TBAI2-4(B) | P3-TBAI2-4(B)/C3S7-7 | JB-607 | FT-60261FB_AI_1 | FT-60261FB | Flow Transmitter | ACTIVE
8 | IN-3 | P3-TBAI2-4(A) | C3S7-8/P3-TBAI2-4(A) | P3-TBAI2-4(A)/C3S7-8 | JB-607 | FT-60261FB_AI_1 | FT-60261FB | Flow Transmitter | ACTIVE
9 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
10 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
11 | i RTN-4 | P3-TBAI2-5(B) | C3S7-11/P3-TBAI2-5(B) | P3-TBAI2-5(B)/C3S7-11 | JB-607 | FT-60261FC_AI_1 | FT-60261FC | Flow Transmitter | ACTIVE
12 | IN-4 | P3-TBAI2-5(A) | C3S7-12/P3-TBAI2-5(A) | P3-TBAI2-5(A)/C3S7-12 | JB-607 | FT-60261FC_AI_1 | FT-60261FC | Flow Transmitter | ACTIVE
13 | i RTN-5 | P3-TBAI2-6(B) | C3S7-13/P3-TBAI2-6(B) | P3-TBAI2-6(B)/C3S7-13 | JB-607 | FT-60261FD_AI_1 | FT-60261FD | Flow Transmitter | ACTIVE
14 | IN-5 | P3-TBAI2-6(A) | C3S7-14/P3-TBAI2-6(A) | P3-TBAI2-6(A)/C3S7-14 | JB-607 | FT-60261FD_AI_1 | FT-60261FD | Flow Transmitter | ACTIVE
15 | i RTN-6 | P3-TBAI2-7(B) | C3S7-15/P3-TBAI2-7(B) | P3-TBAI2-7(B)/C3S7-15 | JB-607 | FT-60262FE_AI_1 | FT-60262FE | Flow Transmitter | ACTIVE
16 | IN-6 | P3-TBAI2-7(A) | C3S7-16/P3-TBAI2-7(A) | P3-TBAI2-7(A)/C3S7-16 | JB-607 | FT-60262FE_AI_1 | FT-60262FE | Flow Transmitter | ACTIVE
17 | i RTN-7 | P3-TBAI2-8(B) | C3S7-17/P3-TBAI2-8(B) | P3-TBAI2-8(B)/C3S7-17 | JB-607 | FT-60262FF_AI_1 | FT-60262FF | Flow Transmitter | ACTIVE
18 | IN-7 | P3-TBAI2-8(A) | C3S7-18/P3-TBAI2-8(A) | P3-TBAI2-8(A)/C3S7-18 | JB-607 | FT-60262FF_AI_1 | FT-60262FF | Flow Transmitter | ACTIVE
19 | i RTN-8 | P3-TBAI2-9(B) | C3S7-19/P3-TBAI2-9(B) | P3-TBAI2-9(B)/C3S7-19 | JB-607 | FT-60262FG_AI_1 | FT-60262FG | Flow Transmitter | ACTIVE
20 | IN-8 | P3-TBAI2-9(A) | C3S7-20/P3-TBAI2-9(A) | P3-TBAI2-9(A)/C3S7-20 | JB-607 | FT-60262FG_AI_1 | FT-60262FG | Flow Transmitter | ACTIVE
21 | i RTN-9 | P3-TBAI2-10(B) | C3S7-21/P3-TBAI2-10(B) | P3-TBAI2-10(B)/C3S7-21 | JB-607 | FT-60262FH_AI_1 | FT-60262FH | Flow Transmitter | ACTIVE
22 | IN-9 | P3-TBAI2-10(A) | C3S7-22/P3-TBAI2-10(A) | P3-TBAI2-10(A)/C3S7-22 | JB-607 | FT-60262FH_AI_1 | FT-60262FH | Flow Transmitter | ACTIVE
23 | i RTN-10 | P3-TBAI2-11(B) | C3S7-23/P3-TBAI2-11(B) | P3-TBAI2-11(B)/C3S7-23 | JB-607 | FT-60263FJ_AI_1 | FT-60263FJ | Flow Transmitter | ACTIVE
24 | IN-10 | P3-TBAI2-11(A) | C3S7-24/P3-TBAI2-11(A) | P3-TBAI2-11(A)/C3S7-24 | JB-607 | FT-60263FJ_AI_1 | FT-60263FJ | Flow Transmitter | ACTIVE
25 | i RTN-11 | P3-TBAI2-12(B) | C3S7-25/P3-TBAI2-12(B) | P3-TBAI2-12(B)/C3S7-25 | JB-607 | FT-60263FK_AI_1 | FT-60263FK | Flow Transmitter | ACTIVE
26 | IN-11 | P3-TBAI2-12(A) | C3S7-26/P3-TBAI2-12(A) | P3-TBAI2-12(A)/C3S7-26 | JB-607 | FT-60263FK_AI_1 | FT-60263FK | Flow Transmitter | ACTIVE
27 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
28 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
29 | i RTN-12 | P3-TBAI2-13(B) | C3S7-29/P3-TBAI2-13(B) | P3-TBAI2-13(B)/C3S7-29 | JB-607 | FT-60263FL_AI_1 | FT-60263FL | Flow Transmitter | ACTIVE
30 | IN-12 | P3-TBAI2-13(A) | C3S7-30/P3-TBAI2-13(A) | P3-TBAI2-13(A)/C3S7-30 | JB-607 | FT-60263FL_AI_1 | FT-60263FL | Flow Transmitter | ACTIVE
31 | i RTN-13 | P3-TBAI2-14(B) | C3S7-31/P3-TBAI2-14(B) | P3-TBAI2-14(B)/C3S7-31 | JB-607 | FT-60263FM_AI_1 | FT-60263FM | Flow Transmitter | ACTIVE
32 | IN-13 | P3-TBAI2-14(A) | C3S7-32/P3-TBAI2-14(A) | P3-TBAI2-14(A)/C3S7-32 | JB-607 | FT-60263FM_AI_1 | FT-60263FM | Flow Transmitter | ACTIVE
33 | i RTN-14 | P3-TBAI2-15(B) | C3S7-33/P3-TBAI2-15(B) | P3-TBAI2-15(B)/C3S7-33 | JB-607 | FT-60264FN_AI_1 | FT-60264FN | Flow Transmitter | ACTIVE
34 | IN-14 | P3-TBAI2-15(A) | C3S7-34/P3-TBAI2-15(A) | P3-TBAI2-15(A)/C3S7-34 | JB-607 | FT-60264FN_AI_1 | FT-60264FN | Flow Transmitter | ACTIVE
35 | i RTN-15 | P3-TBAI2-16(B) | C3S7-35/P3-TBAI2-16(B) | P3-TBAI2-16(B)/C3S7-35 | JB-607 | FT-60264FP_AI_1 | FT-60264FP | Flow Transmitter | ACTIVE
36 | IN-15 | P3-TBAI2-16(A) | C3S7-36/P3-TBAI2-16(A) | P3-TBAI2-16(A)/C3S7-36 | JB-607 | FT-60264FP_AI_1 | FT-60264FP | Flow Transmitter | ACTIVE

## C3S8
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C3S8
ANALOG INPUT CARD (1756-IF16 16-CH CURRENT/VOLTAGE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS: C3 ¦ SLOT: 8 ¦ MODULE: 1756-IF16 ¦ DESTINATION AREA: JB-607, JB-608
← Back to Chassis Summary (C3SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | i RTN-0 | P3-TBAI3-1(B) | C3S8-1/P3-TBAI3-1(B) | P3-TBAI3-1(B)/C3S8-1 | JB-607 | FT-60264FQ_AI_1 | FT-60264FQ | Flow Transmitter | ACTIVE
2 | IN-0 | P3-TBAI3-1(A) | C3S8-2/P3-TBAI3-1(A) | P3-TBAI3-1(A)/C3S8-2 | JB-607 | FT-60264FQ_AI_1 | FT-60264FQ | Flow Transmitter | ACTIVE
3 | i RTN-1 | P3-TBAI3-2(B) | C3S8-3/P3-TBAI3-2(B) | P3-TBAI3-2(B)/C3S8-3 | JB-607 | FT-60264FR_AI_1 | FT-60264FR | Flow Transmitter | ACTIVE
4 | IN-1 | P3-TBAI3-2(A) | C3S8-4/P3-TBAI3-2(A) | P3-TBAI3-2(A)/C3S8-4 | JB-607 | FT-60264FR_AI_1 | FT-60264FR | Flow Transmitter | ACTIVE
5 | i RTN-2 | P3-TBAI3-3(B) | C3S8-5/P3-TBAI3-3(B) | P3-TBAI3-3(B)/C3S8-5 | JB-607 | PT-60201_AI_1 | PT-60201 | Pressure Transmitter | ACTIVE
6 | IN-2 | P3-TBAI3-3(A) | C3S8-6/P3-TBAI3-3(A) | P3-TBAI3-3(A)/C3S8-6 | JB-607 | PT-60201_AI_1 | PT-60201 | Pressure Transmitter | ACTIVE
7 | i RTN-3 | P3-TBAI3-4(B) | C3S8-7/P3-TBAI3-4(B) | P3-TBAI3-4(B)/C3S8-7 | JB-607 | PT-60207_AI_1 | PT-60207 | Pressure Transmitter | ACTIVE
8 | IN-3 | P3-TBAI3-4(A) | C3S8-8/P3-TBAI3-4(A) | P3-TBAI3-4(A)/C3S8-8 | JB-607 | PT-60207_AI_1 | PT-60207 | Pressure Transmitter | ACTIVE
9 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
10 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
11 | i RTN-4 | P3-TBAI3-5(B) | C3S8-11/P3-TBAI3-5(B) | P3-TBAI3-5(B)/C3S8-11 | JB-607 | PT-60221_AI_1 | PT-60221 | Pressure Transmitter | ACTIVE
12 | IN-4 | P3-TBAI3-5(A) | C3S8-12/P3-TBAI3-5(A) | P3-TBAI3-5(A)/C3S8-12 | JB-607 | PT-60221_AI_1 | PT-60221 | Pressure Transmitter | ACTIVE
13 | i RTN-5 | P3-TBAI3-6(B) | C3S8-13/P3-TBAI3-6(B) | P3-TBAI3-6(B)/C3S8-13 | JB-607 | PT-60221_AI_1 | PT-60221 | Pressure Transmitter | ACTIVE
14 | IN-5 | P3-TBAI3-6(A) | C3S8-14/P3-TBAI3-6(A) | P3-TBAI3-6(A)/C3S8-14 | JB-607 | PT-60221_AI_1 | PT-60221 | Pressure Transmitter | ACTIVE
15 | i RTN-6 | P3-TBAI3-7(B) | C3S8-15/P3-TBAI3-7(B) | P3-TBAI3-7(B)/C3S8-15 | JB-607 | TI-FH-60210_AI_1 | TI-FH-60210 | Temperature Indicator / Sensor | ACTIVE
16 | IN-6 | P3-TBAI3-7(A) | C3S8-16/P3-TBAI3-7(A) | P3-TBAI3-7(A)/C3S8-16 | JB-607 | TI-FH-60210_AI_1 | TI-FH-60210 | Temperature Indicator / Sensor | ACTIVE
17 | i RTN-7 | P3-TBAI3-8(B) | C3S8-17/P3-TBAI3-8(B) | P3-TBAI3-8(B)/C3S8-17 | JB-607 | TT-60201_AI_1 | TT-60201 | Temperature Transmitter | ACTIVE
18 | IN-7 | P3-TBAI3-8(A) | C3S8-18/P3-TBAI3-8(A) | P3-TBAI3-8(A)/C3S8-18 | JB-607 | TT-60201_AI_1 | TT-60201 | Temperature Transmitter | ACTIVE
19 | i RTN-8 | P3-TBAI3-9(B) | C3S8-19/P3-TBAI3-9(B) | P3-TBAI3-9(B)/C3S8-19 | JB-607 | TT-60202_AI_1 | TT-60202 | Temperature Transmitter | ACTIVE
20 | IN-8 | P3-TBAI3-9(A) | C3S8-20/P3-TBAI3-9(A) | P3-TBAI3-9(A)/C3S8-20 | JB-607 | TT-60202_AI_1 | TT-60202 | Temperature Transmitter | ACTIVE
21 | i RTN-9 | P3-TBAI3-10(B) | C3S8-21/P3-TBAI3-10(B) | P3-TBAI3-10(B)/C3S8-21 | JB-607 | TT-60207_AI_1 | TT-60207 | Temperature Transmitter | ACTIVE
22 | IN-9 | P3-TBAI3-10(A) | C3S8-22/P3-TBAI3-10(A) | P3-TBAI3-10(A)/C3S8-22 | JB-607 | TT-60207_AI_1 | TT-60207 | Temperature Transmitter | ACTIVE
23 | i RTN-10 | P3-TBAI3-11(B) | C3S8-23/P3-TBAI3-11(B) | P3-TBAI3-11(B)/C3S8-23 | JB-607 | UY-FH-60210A_AI_1 | UY-FH-60210A | I/P Converter Control Valve | ACTIVE
24 | IN-10 | P3-TBAI3-11(A) | C3S8-24/P3-TBAI3-11(A) | P3-TBAI3-11(A)/C3S8-24 | JB-607 | UY-FH-60210A_AI_1 | UY-FH-60210A | I/P Converter Control Valve | ACTIVE
25 | i RTN-11 | P3-TBAI3-12(B) | C3S8-25/P3-TBAI3-12(B) | P3-TBAI3-12(B)/C3S8-25 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
26 | IN-11 | P3-TBAI3-12(A) | C3S8-26/P3-TBAI3-12(A) | P3-TBAI3-12(A)/C3S8-26 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
27 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
28 | RTN | 0VDC | 0VDC | 0VDC | JB-607 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
29 | i RTN-12 | P3-TBAI3-13(B) | C3S8-29/P3-TBAI3-13(B) | P3-TBAI3-13(B)/C3S8-29 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-12 | P3-TBAI3-13(A) | C3S8-30/P3-TBAI3-13(A) | P3-TBAI3-13(A)/C3S8-30 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
31 | i RTN-13 | P3-TBAI3-14(B) | C3S8-31/P3-TBAI3-14(B) | P3-TBAI3-14(B)/C3S8-31 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-13 | P3-TBAI3-14(A) | C3S8-32/P3-TBAI3-14(A) | P3-TBAI3-14(A)/C3S8-32 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
33 | i RTN-14 | P3-TBAI3-15(B) | C3S8-33/P3-TBAI3-15(B) | P3-TBAI3-15(B)/C3S8-33 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-14 | P3-TBAI3-15(A) | C3S8-34/P3-TBAI3-15(A) | P3-TBAI3-15(A)/C3S8-34 | JB-607 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
35 | i RTN-15 | P3-TBAI3-16(B) | C3S8-35/P3-TBAI3-16(B) | P3-TBAI3-16(B)/C3S8-35 | JB-608 | TT-60245_AI_1 | TT-60245 | Temperature Transmitter | ACTIVE
36 | IN-15 | P3-TBAI3-16(A) | C3S8-36/P3-TBAI3-16(A) | P3-TBAI3-16(A)/C3S8-36 | JB-608 | TT-60245_AI_1 | TT-60245 | Temperature Transmitter | ACTIVE

## C3S9
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C3S9
ANALOG INPUT CARD (1756-IF16 16-CH CURRENT/VOLTAGE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS: C3 ¦ SLOT: 9 ¦ MODULE: 1756-IF16 ¦ DESTINATION AREA: JB-612, JB-618
← Back to Chassis Summary (C3SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | i RTN-0 | P3-TBAI4-1(B) | C3S9-1/P3-TBAI4-1(B) | P3-TBAI4-1(B)/C3S9-1 | JB-618 | PT-61303_AI_1 | PT-61303 | Pressure Transmitter | ACTIVE
2 | IN-0 | P3-TBAI4-1(A) | C3S9-2/P3-TBAI4-1(A) | P3-TBAI4-1(A)/C3S9-2 | JB-618 | PT-61303_AI_1 | PT-61303 | Pressure Transmitter | ACTIVE
3 | i RTN-1 | P3-TBAI4-2(B) | C3S9-3/P3-TBAI4-2(B) | P3-TBAI4-2(B)/C3S9-3 | JB-618 | PT-61306_AI_1 | PT-61306 | Pressure Transmitter | ACTIVE
4 | IN-1 | P3-TBAI4-2(A) | C3S9-4/P3-TBAI4-2(A) | P3-TBAI4-2(A)/C3S9-4 | JB-618 | PT-61306_AI_1 | PT-61306 | Pressure Transmitter | ACTIVE
5 | i RTN-2 | P3-TBAI4-3(B) | C3S9-5/P3-TBAI4-3(B) | P3-TBAI4-3(B)/C3S9-5 | JB-618 | TT-61303_AI_1 | TT-61303 | Temperature Transmitter | ACTIVE
6 | IN-2 | P3-TBAI4-3(A) | C3S9-6/P3-TBAI4-3(A) | P3-TBAI4-3(A)/C3S9-6 | JB-618 | TT-61303_AI_1 | TT-61303 | Temperature Transmitter | ACTIVE
7 | i RTN-3 | P3-TBAI4-4(B) | C3S9-7/P3-TBAI4-4(B) | P3-TBAI4-4(B)/C3S9-7 | JB-618 | TT-61304_AI_1 | TT-61304 | Temperature Transmitter | ACTIVE
8 | IN-3 | P3-TBAI4-4(A) | C3S9-8/P3-TBAI4-4(A) | P3-TBAI4-4(A)/C3S9-8 | JB-618 | TT-61304_AI_1 | TT-61304 | Temperature Transmitter | ACTIVE
9 | RTN | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
10 | RTN | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
11 | i RTN-4 | P3-TBAI4-5(B) | C3S9-11/P3-TBAI4-5(B) | P3-TBAI4-5(B)/C3S9-11 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
12 | IN-4 | P3-TBAI4-5(A) | C3S9-12/P3-TBAI4-5(A) | P3-TBAI4-5(A)/C3S9-12 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
13 | i RTN-5 | P3-TBAI4-6(B) | C3S9-13/P3-TBAI4-6(B) | P3-TBAI4-6(B)/C3S9-13 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
14 | IN-5 | P3-TBAI4-6(A) | C3S9-14/P3-TBAI4-6(A) | P3-TBAI4-6(A)/C3S9-14 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
15 | i RTN-6 | P3-TBAI4-7(B) | C3S9-15/P3-TBAI4-7(B) | P3-TBAI4-7(B)/C3S9-15 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
16 | IN-6 | P3-TBAI4-7(A) | C3S9-16/P3-TBAI4-7(A) | P3-TBAI4-7(A)/C3S9-16 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
17 | i RTN-7 | P3-TBAI4-8(B) | C3S9-17/P3-TBAI4-8(B) | P3-TBAI4-8(B)/C3S9-17 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
18 | IN-7 | P3-TBAI4-8(A) | C3S9-18/P3-TBAI4-8(A) | P3-TBAI4-8(A)/C3S9-18 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
19 | i RTN-8 | P3-TBAI4-9(B) | C3S9-19/P3-TBAI4-9(B) | P3-TBAI4-9(B)/C3S9-19 | JB-612 | PT-61302_AI_1 | PT-61302 | Pressure Transmitter | ACTIVE
20 | IN-8 | P3-TBAI4-9(A) | C3S9-20/P3-TBAI4-9(A) | P3-TBAI4-9(A)/C3S9-20 | JB-612 | PT-61302_AI_1 | PT-61302 | Pressure Transmitter | ACTIVE
21 | i RTN-9 | P3-TBAI4-10(B) | C3S9-21/P3-TBAI4-10(B) | P3-TBAI4-10(B)/C3S9-21 | JB-612 | PT-61309_AI_1 | PT-61309 | Pressure Transmitter | ACTIVE
22 | IN-9 | P3-TBAI4-10(A) | C3S9-22/P3-TBAI4-10(A) | P3-TBAI4-10(A)/C3S9-22 | JB-612 | PT-61309_AI_1 | PT-61309 | Pressure Transmitter | ACTIVE
23 | i RTN-10 | P3-TBAI4-11(B) | C3S9-23/P3-TBAI4-11(B) | P3-TBAI4-11(B)/C3S9-23 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
24 | IN-10 | P3-TBAI4-11(A) | C3S9-24/P3-TBAI4-11(A) | P3-TBAI4-11(A)/C3S9-24 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
25 | i RTN-11 | P3-TBAI4-12(B) | C3S9-25/P3-TBAI4-12(B) | P3-TBAI4-12(B)/C3S9-25 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
26 | IN-11 | P3-TBAI4-12(A) | C3S9-26/P3-TBAI4-12(A) | P3-TBAI4-12(A)/C3S9-26 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
27 | RTN | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
28 | RTN | 0VDC | 0VDC | 0VDC | JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
29 | i RTN-12 | P3-TBAI4-13(B) | C3S9-29/P3-TBAI4-13(B) | P3-TBAI4-13(B)/C3S9-29 | JB-612 | PT-61302_AI_1 | PT-61302 | Pressure Transmitter | ACTIVE
30 | IN-12 | P3-TBAI4-13(A) | C3S9-30/P3-TBAI4-13(A) | P3-TBAI4-13(A)/C3S9-30 | JB-612 | PT-61302_AI_1 | PT-61302 | Pressure Transmitter | ACTIVE
31 | i RTN-13 | P3-TBAI4-14(B) | C3S9-31/P3-TBAI4-14(B) | P3-TBAI4-14(B)/C3S9-31 | JB-612 | PT-61309_AI_1 | PT-61309 | Pressure Transmitter | ACTIVE
32 | IN-13 | P3-TBAI4-14(A) | C3S9-32/P3-TBAI4-14(A) | P3-TBAI4-14(A)/C3S9-32 | JB-612 | PT-61309_AI_1 | PT-61309 | Pressure Transmitter | ACTIVE
33 | i RTN-14 | P3-TBAI4-15(B) | C3S9-33/P3-TBAI4-15(B) | P3-TBAI4-15(B)/C3S9-33 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-14 | P3-TBAI4-15(A) | C3S9-34/P3-TBAI4-15(A) | P3-TBAI4-15(A)/C3S9-34 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
35 | i RTN-15 | P3-TBAI4-16(B) | C3S9-35/P3-TBAI4-16(B) | P3-TBAI4-16(B)/C3S9-35 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
36 | IN-15 | P3-TBAI4-16(A) | C3S9-36/P3-TBAI4-16(A) | P3-TBAI4-16(A)/C3S9-36 | JB-612 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE

## C3S10
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C3S10
RESERVE / EMPTY SLOT (1756-N2) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS: C3 ¦ SLOT: 10 ¦ MODULE: 1756-N2 ¦ DESTINATION AREA: Field RIO
← Back to Chassis Summary (C3SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
- | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | EMPTY

## C3S11
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C3S11
RESERVE / EMPTY SLOT (1756-N2) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS: C3 ¦ SLOT: 11 ¦ MODULE: 1756-N2 ¦ DESTINATION AREA: Field RIO
← Back to Chassis Summary (C3SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
- | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | EMPTY

## C3S12
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C3S12
ANALOG OUTPUT CARD (1756-OF8 8-CH CURRENT/VOLTAGE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER / PACKING TOWER)
CHASSIS: C3 ¦ SLOT: 12 ¦ MODULE: 1756-OF8 ¦ DESTINATION AREA: JB-402, JB-602, JB-607
← Back to Chassis Summary (C3SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAOx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | VOUT-0 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | COMMON
2 | VOUT-4 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | COMMON
3 | IOUT-0 | P3-TBAO1-1 | C3S12-3/P3-TBAO1-1 | P3-TBAO1-1/C3S12-3 | JB-402 | TCV-40222_AO_1 | TCV-40222 | Temperature Control Valve | ACTIVE
4 | IOUT-4 | P3-TBAO1-5 | C3S12-4/P3-TBAO1-5 | P3-TBAO1-5/C3S12-4 | JB-607 | UY-FH-60210B_AO_1 | UY-FH-60210B | I/P Converter Control Valve | ACTIVE
5 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
6 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
7 | VOUT-1 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | COMMON
8 | VOUT-5 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | COMMON
9 | IOUT-1 | P3-TBAO1-2 | C3S12-9/P3-TBAO1-2 | P3-TBAO1-2/C3S12-9 | JB-602 | TV-60202_AO_1 | TV-60202 | Temperature Control Valve | ACTIVE
10 | IOUT-5 | P3-TBAO1-6 | C3S12-10/P3-TBAO1-6 | P3-TBAO1-6/C3S12-10 | JB-607 | Spare_AO_0 | Spare | Spare Reserve Channel | SPARE
11 | VOUT-2 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | COMMON
12 | VOUT-6 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | COMMON
13 | IOUT-2 | P3-TBAO1-3 | C3S12-13/P3-TBAO1-3 | P3-TBAO1-3/C3S12-13 | JB-602 | TV-60214_AO_1 | TV-60214 | Temperature Control Valve | ACTIVE
14 | IOUT-6 | P3-TBAO1-7 | C3S12-14/P3-TBAO1-7 | P3-TBAO1-7/C3S12-14 | JB-607 | Spare_AO_0 | Spare | Spare Reserve Channel | SPARE
15 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
16 | RTN | 0VDC | 0VDC | 0VDC | JB-402 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
17 | VOUT-3 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | COMMON
18 | VOUT-7 | +24VDC | +24VDC | +24VDC | JB-402 | Internal Power Common | - | Loop Power Terminal (+24VDC) | COMMON
19 | IOUT-3 | P3-TBAO1-4 | C3S12-19/P3-TBAO1-4 | P3-TBAO1-4/C3S12-19 | JB-607 | PV-60201_AO_1 | PV-60201 | Pressure Control Valve | ACTIVE
20 | IOUT-7 | P3-TBAO1-8 | C3S12-20/P3-TBAO1-8 | P3-TBAO1-8/C3S12-20 | JB-607 | Spare_AO_0 | Spare | Spare Reserve Channel | SPARE

## C4SlotConfig
CHASSIS C4 HARDWARE & SLOT CONFIGURATION SCHEDULE
REMOTE I/O RACK 2 (UPPER SPRAY DRYER 6TH/8TH FLOOR) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS MODEL: 1756-A13 (13-Slot ControlLogix Chassis) ¦ POWER SUPPLY: 1756-PA75 (85-265V AC Power Supply) ¦ NETWORK: ETHERNET/IP 1GBPS DLR RING
← Back to Master Slot Directory (00_Slot_Index)
Slot_No | Slot_Tag | Module_Catalog | Module_Description | Signal_Family | Terminal_Block_Type | Destination_Area(s) | Total_Channels | Active_Channels | Spare_Channels | Slot_Status
0 | C4S0 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | COMM (EtherNet/IP) | 2x RJ45 (Gigabit) + 1x USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | - | ACTIVE
1 | C4S1 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | IS-JB-603, IS-JB-608 | 32 | 22 | 10 | ACTIVE
2 | C4S2 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | IS-JB-612 | 32 | 15 | 17 | ACTIVE
3 | C4S3 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | IS-JB-618 | 32 | 13 | 19 | ACTIVE
4 | C4S4 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | IS-JB-608, JB-618 | 32 | 1 | 31 | ACTIVE
5 | C4S5 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | IS-JB-603, IS-JB-608 | 16 | 26 | 6 | ACTIVE
6 | C4S6 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | IS-JB-612, IS-JB-618 | 16 | 22 | 10 | ACTIVE
7 | C4S7 | 1756-N2 | Slot Filler / Reserve Unpopulated Position | EMPTY (Reserve Position) | N/A (Blanking Plate) | Unpopulated / Reserve | - | - | - | EMPTY
8 | C4S8 | 1756-N2 | Slot Filler / Reserve Unpopulated Position | EMPTY (Reserve Position) | N/A (Blanking Plate) | Unpopulated / Reserve | - | - | - | EMPTY
9 | C4S9 | 1756-N2 | Slot Filler / Reserve Unpopulated Position | EMPTY (Reserve Position) | N/A (Blanking Plate) | Unpopulated / Reserve | - | - | - | EMPTY
10 | C4S10 | 1756-N2 | Slot Filler / Reserve Unpopulated Position | EMPTY (Reserve Position) | N/A (Blanking Plate) | Unpopulated / Reserve | - | - | - | EMPTY
11 | C4S11 | 1756-N2 | Slot Filler / Reserve Unpopulated Position | EMPTY (Reserve Position) | N/A (Blanking Plate) | Unpopulated / Reserve | - | - | - | EMPTY
12 | C4S12 | 1756-N2 | Slot Filler / Reserve Unpopulated Position | EMPTY (Reserve Position) | N/A (Blanking Plate) | Unpopulated / Reserve | - | - | - | EMPTY
TOTAL | 13 Slots | - | Chassis C4 Total Configured Capacity | - | - | - | 164 | 103 | 93 | 63% Active

## C4S0
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C4S0
ETHERNET COMMUNICATION ADAPTER (1756-EN4TR DLR 2-PORT GIGABIT) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS: C4 ¦ SLOT: 0 ¦ MODULE: 1756-EN4TR ¦ DESTINATION AREA: CA1 / Field RIO (EtherNet/IP DLR Trunk)
← Back to Chassis Summary (C4SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | ETH-DLR-P1 | C4S0-/- | -/C4S0- | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C4S0_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | ACTIVE
RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C4S0-P2/ETH | ETH/C4S0-P2 | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C4S0_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | ACTIVE
USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C4S0-USB/CONSOLE | CONSOLE/C4S0-USB | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C4S0_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | ACTIVE
DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C4S0-DISP/DIAG | DIAG/C4S0-DISP | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C4S0_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | ACTIVE

## C4S1
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C4S1
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS: C4 ¦ SLOT: 1 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: IS-JB-603, IS-JB-608
C4S1
← Back to Chassis Summary (C4SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P4-TBSI1-1 | C4S1-1/P4-TBSI1-1 | P4-TBSI1-1/C4S1-1 | IS-JB-603 | AT-40201_DI_1 | AT-40201 | Process Instrument | ACTIVE
2 | IN-1 | P4-TBSI1-2 | C4S1-2/P4-TBSI1-2 | P4-TBSI1-2/C4S1-2 | IS-JB-603 | AT-40202_DI_1 | AT-40202 | Process Instrument | ACTIVE
3 | IN-2 | P4-TBSI1-3 | C4S1-3/P4-TBSI1-3 | P4-TBSI1-3/C4S1-3 | IS-JB-603 | AT-40203_DI_1 | AT-40203 | Process Instrument | ACTIVE
4 | IN-3 | P4-TBSI1-4 | C4S1-4/P4-TBSI1-4 | P4-TBSI1-4/C4S1-4 | IS-JB-603 | LSH-60230_DI_1 | LSH-60230 | Process Instrument | ACTIVE
5 | IN-4 | P4-TBSI1-5 | C4S1-5/P4-TBSI1-5 | P4-TBSI1-5/C4S1-5 | IS-JB-603 | LSH-60231_DI_1 | LSH-60231 | Process Instrument | ACTIVE
6 | IN-5 | P4-TBSI1-6 | C4S1-6/P4-TBSI1-6 | P4-TBSI1-6/C4S1-6 | IS-JB-603 | LSH-60240_DI_1 | LSH-60240 | Process Instrument | ACTIVE
7 | IN-6 | P4-TBSI1-7 | C4S1-7/P4-TBSI1-7 | P4-TBSI1-7/C4S1-7 | IS-JB-603 | PD-60202_DI_1 | PD-60202 | Process Instrument | ACTIVE
8 | IN-7 | P4-TBSI1-8 | C4S1-8/P4-TBSI1-8 | P4-TBSI1-8/C4S1-8 | IS-JB-603 | RV-60204_DI_1 | RV-60204 | Process Instrument | ACTIVE
9 | IN-8 | P4-TBSI1-9 | C4S1-9/P4-TBSI1-9 | P4-TBSI1-9/C4S1-9 | IS-JB-603 | ZS-60201C_DI_1 | ZS-60201C | Process Instrument | ACTIVE
10 | IN-9 | P4-TBSI1-10 | C4S1-10/P4-TBSI1-10 | P4-TBSI1-10/C4S1-10 | IS-JB-603 | ZS-60201D_DI_1 | ZS-60201D | Process Instrument | ACTIVE
11 | IN-10 | P4-TBSI1-11 | C4S1-11/P4-TBSI1-11 | P4-TBSI1-11/C4S1-11 | IS-JB-603 | ZS-60201E_DI_1 | ZS-60201E | Process Instrument | ACTIVE
12 | IN-11 | P4-TBSI1-12 | C4S1-12/P4-TBSI1-12 | P4-TBSI1-12/C4S1-12 | IS-JB-603 | ZS-60229_DI_1 | ZS-60229 | Process Instrument | ACTIVE
13 | IN-12 | P4-TBSI1-13 | C4S1-13/P4-TBSI1-13 | P4-TBSI1-13/C4S1-13 | IS-JB-603 | ZS-60230_DI_1 | ZS-60230 | Process Instrument | ACTIVE
14 | IN-13 | P4-TBSI1-14 | C4S1-14/P4-TBSI1-14 | P4-TBSI1-14/C4S1-14 | IS-JB-603 | ZS-60231A_DI_1 | ZS-60231A | Process Instrument | ACTIVE
15 | IN-14 | P4-TBSI1-15 | C4S1-15/P4-TBSI1-15 | P4-TBSI1-15/C4S1-15 | IS-JB-603 | ZS-60231B_DI_1 | ZS-60231B | Process Instrument | ACTIVE
16 | IN-15 | P4-TBSI1-16 | C4S1-16/P4-TBSI1-16 | P4-TBSI1-16/C4S1-16 | IS-JB-603 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
17 | GND-0 | 0VDC | C4S1-17/0VDC | 0VDC/C4S1-17 | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | C4S1-18/0VDC | 0VDC/C4S1-18 | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P4-TBSI2-1 | C4S1-19/P4-TBSI2-1 | P4-TBSI2-1/C4S1-19 | IS-JB-608 | ZS-60201A_DI_1 | ZS-60201A | Process Instrument | ACTIVE
20 | IN-17 | P4-TBSI2-2 | C4S1-20/P4-TBSI2-2 | P4-TBSI2-2/C4S1-20 | IS-JB-608 | ZS-60201B_DI_1 | ZS-60201B | Process Instrument | ACTIVE
21 | IN-18 | P4-TBSI2-3 | C4S1-21/P4-TBSI2-3 | P4-TBSI2-3/C4S1-21 | IS-JB-608 | ZS-60231C_DI_1 | ZS-60231C | Process Instrument | ACTIVE
22 | IN-19 | P4-TBSI2-4 | C4S1-22/P4-TBSI2-4 | P4-TBSI2-4/C4S1-22 | IS-JB-608 | ZS-60231D_DI_1 | ZS-60231D | Process Instrument | ACTIVE
23 | IN-20 | P4-TBSI2-5 | C4S1-23/P4-TBSI2-5 | P4-TBSI2-5/C4S1-23 | IS-JB-608 | ZS-60231E_DI_1 | ZS-60231E | Process Instrument | ACTIVE
24 | IN-21 | P4-TBSI2-6 | C4S1-24/P4-TBSI2-6 | P4-TBSI2-6/C4S1-24 | IS-JB-608 | ZS-60231F_DI_1 | ZS-60231F | Process Instrument | ACTIVE
25 | IN-22 | P4-TBSI2-7 | C4S1-25/P4-TBSI2-7 | P4-TBSI2-7/C4S1-25 | IS-JB-608 | ZS-60240_DI_1 | ZS-60240 | Process Instrument | ACTIVE
26 | IN-23 | P4-TBSI2-8 | C4S1-26/P4-TBSI2-8 | P4-TBSI2-8/C4S1-26 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
27 | IN-24 | P4-TBSI2-9 | C4S1-27/P4-TBSI2-9 | P4-TBSI2-9/C4S1-27 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
28 | IN-25 | P4-TBSI2-10 | C4S1-28/P4-TBSI2-10 | P4-TBSI2-10/C4S1-28 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
29 | IN-26 | P4-TBSI2-11 | C4S1-29/P4-TBSI2-11 | P4-TBSI2-11/C4S1-29 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-27 | P4-TBSI2-12 | C4S1-30/P4-TBSI2-12 | P4-TBSI2-12/C4S1-30 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
31 | IN-28 | P4-TBSI2-13 | C4S1-31/P4-TBSI2-13 | P4-TBSI2-13/C4S1-31 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-29 | P4-TBSI2-14 | C4S1-32/P4-TBSI2-14 | P4-TBSI2-14/C4S1-32 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
33 | IN-30 | P4-TBSI2-15 | C4S1-33/P4-TBSI2-15 | P4-TBSI2-15/C4S1-33 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-31 | P4-TBSI2-16 | C4S1-34/P4-TBSI2-16 | P4-TBSI2-16/C4S1-34 | IS-JB-608 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
35 | GND1 | 0VDC | C4S1-35/0VDC | 0VDC/C4S1-35 | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | C4S1-36/0VDC | 0VDC/C4S1-36 | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C4S2
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C4S2
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS: C4 ¦ SLOT: 2 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: IS-JB-612
← Back to Chassis Summary (C4SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P4-TBDI2-1 | C4S2-1/P4-TBDI2-1 | P4-TBDI2-1/C4S2-1 | IS-JB-612 | ISV-61303_DI_1 | ISV-61303 | Process Instrument | ACTIVE
2 | IN-1 | P4-TBDI2-2 | C4S2-2/P4-TBDI2-2 | P4-TBDI2-2/C4S2-2 | IS-JB-612 | ISV-61304_DI_1 | ISV-61304 | Process Instrument | ACTIVE
3 | IN-2 | P4-TBDI2-3 | C4S2-3/P4-TBDI2-3 | P4-TBDI2-3/C4S2-3 | IS-JB-612 | LSH-61304_DI_1 | LSH-61304 | Process Instrument | ACTIVE
4 | IN-3 | P4-TBDI2-4 | C4S2-4/P4-TBDI2-4 | P4-TBDI2-4/C4S2-4 | IS-JB-612 | LSH-61305_DI_1 | LSH-61305 | Process Instrument | ACTIVE
5 | IN-4 | P4-TBDI2-5 | C4S2-5/P4-TBDI2-5 | P4-TBDI2-5/C4S2-5 | IS-JB-612 | LSH-61307_DI_1 | LSH-61307 | Process Instrument | ACTIVE
6 | IN-5 | P4-TBDI2-6 | C4S2-6/P4-TBDI2-6 | P4-TBDI2-6/C4S2-6 | IS-JB-612 | LSH-61312_DI_1 | LSH-61312 | Process Instrument | ACTIVE
7 | IN-6 | P4-TBDI2-7 | C4S2-7/P4-TBDI2-7 | P4-TBDI2-7/C4S2-7 | IS-JB-612 | PSE-61302_DI_1 | PSE-61302 | Process Instrument | ACTIVE
8 | IN-7 | P4-TBDI2-8 | C4S2-8/P4-TBDI2-8 | P4-TBDI2-8/C4S2-8 | IS-JB-612 | PSE-61303_DI_1 | PSE-61303 | Process Instrument | ACTIVE
9 | IN-8 | P4-TBDI2-9 | C4S2-9/P4-TBDI2-9 | P4-TBDI2-9/C4S2-9 | IS-JB-612 | RV-61301_DI_1 | RV-61301 | Process Instrument | ACTIVE
10 | IN-9 | P4-TBDI2-10 | C4S2-10/P4-TBDI2-10 | P4-TBDI2-10/C4S2-10 | IS-JB-612 | RV-61304_DI_1 | RV-61304 | Process Instrument | ACTIVE
11 | IN-10 | P4-TBDI2-11 | C4S2-11/P4-TBDI2-11 | P4-TBDI2-11/C4S2-11 | IS-JB-612 | RV-61305_DI_1 | RV-61305 | Process Instrument | ACTIVE
12 | IN-11 | P4-TBDI2-12 | C4S2-12/P4-TBDI2-12 | P4-TBDI2-12/C4S2-12 | IS-JB-612 | SC-61301_DI_1 | SC-61301 | Process Instrument | ACTIVE
13 | IN-12 | P4-TBDI2-13 | C4S2-13/P4-TBDI2-13 | P4-TBDI2-13/C4S2-13 | IS-JB-612 | SC-61302_DI_1 | SC-61302 | Process Instrument | ACTIVE
14 | IN-13 | P4-TBDI2-14 | C4S2-14/P4-TBDI2-14 | P4-TBDI2-14/C4S2-14 | IS-JB-612 | ZS-61312_DI_1 | ZS-61312 | Process Instrument | ACTIVE
15 | IN-14 | P4-TBDI2-15 | C4S2-15/P4-TBDI2-15 | P4-TBDI2-15/C4S2-15 | IS-JB-612 | ZS-61313_DI_1 | ZS-61313 | Process Instrument | ACTIVE
16 | IN-15 | P4-TBDI2-16 | C4S2-16/P4-TBDI2-16 | P4-TBDI2-16/C4S2-16 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
17 | GND-0 | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P4-TBDI2-17 | C4S2-19/P4-TBDI2-17 | P4-TBDI2-17/C4S2-19 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
20 | IN-17 | P4-TBDI2-18 | C4S2-20/P4-TBDI2-18 | P4-TBDI2-18/C4S2-20 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
21 | IN-18 | P4-TBDI2-19 | C4S2-21/P4-TBDI2-19 | P4-TBDI2-19/C4S2-21 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
22 | IN-19 | P4-TBDI2-20 | C4S2-22/P4-TBDI2-20 | P4-TBDI2-20/C4S2-22 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
23 | IN-20 | P4-TBDI2-21 | C4S2-23/P4-TBDI2-21 | P4-TBDI2-21/C4S2-23 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
24 | IN-21 | P4-TBDI2-22 | C4S2-24/P4-TBDI2-22 | P4-TBDI2-22/C4S2-24 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
25 | IN-22 | P4-TBDI2-23 | C4S2-25/P4-TBDI2-23 | P4-TBDI2-23/C4S2-25 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
26 | IN-23 | P4-TBDI2-24 | C4S2-26/P4-TBDI2-24 | P4-TBDI2-24/C4S2-26 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
27 | IN-24 | P4-TBDI2-25 | C4S2-27/P4-TBDI2-25 | P4-TBDI2-25/C4S2-27 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
28 | IN-25 | P4-TBDI2-26 | C4S2-28/P4-TBDI2-26 | P4-TBDI2-26/C4S2-28 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
29 | IN-26 | P4-TBDI2-27 | C4S2-29/P4-TBDI2-27 | P4-TBDI2-27/C4S2-29 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-27 | P4-TBDI2-28 | C4S2-30/P4-TBDI2-28 | P4-TBDI2-28/C4S2-30 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
31 | IN-28 | P4-TBDI2-29 | C4S2-31/P4-TBDI2-29 | P4-TBDI2-29/C4S2-31 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-29 | P4-TBDI2-30 | C4S2-32/P4-TBDI2-30 | P4-TBDI2-30/C4S2-32 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
33 | IN-30 | P4-TBDI2-31 | C4S2-33/P4-TBDI2-31 | P4-TBDI2-31/C4S2-33 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-31 | P4-TBDI2-32 | C4S2-34/P4-TBDI2-32 | P4-TBDI2-32/C4S2-34 | IS-JB-612 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
35 | GND1 | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C4S3
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C4S3
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS: C4 ¦ SLOT: 3 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: IS-JB-618
← Back to Chassis Summary (C4SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P4-TBDI3-1 | C4S3-1/P4-TBDI3-1 | P4-TBDI3-1/C4S3-1 | IS-JB-618 | ISV-61301_DI_1 | ISV-61301 | Process Instrument | ACTIVE
2 | IN-1 | P4-TBDI3-2 | C4S3-2/P4-TBDI3-2 | P4-TBDI3-2/C4S3-2 | IS-JB-618 | LSH-61301_DI_1 | LSH-61301 | Process Instrument | ACTIVE
3 | IN-2 | P4-TBDI3-3 | C4S3-3/P4-TBDI3-3 | P4-TBDI3-3/C4S3-3 | IS-JB-618 | LSH-61303_DI_1 | LSH-61303 | Process Instrument | ACTIVE
4 | IN-3 | P4-TBDI3-4 | C4S3-4/P4-TBDI3-4 | P4-TBDI3-4/C4S3-4 | IS-JB-618 | LSH-61306_DI_1 | LSH-61306 | Process Instrument | ACTIVE
5 | IN-4 | P4-TBDI3-5 | C4S3-5/P4-TBDI3-5 | P4-TBDI3-5/C4S3-5 | IS-JB-618 | LSH-61308_DI_1 | LSH-61308 | Process Instrument | ACTIVE
6 | IN-5 | P4-TBDI3-6 | C4S3-6/P4-TBDI3-6 | P4-TBDI3-6/C4S3-6 | IS-JB-618 | LSL-61302_DI_1 | LSL-61302 | Process Instrument | ACTIVE
7 | IN-6 | P4-TBDI3-7 | C4S3-7/P4-TBDI3-7 | P4-TBDI3-7/C4S3-7 | IS-JB-618 | PSE-61300_DI_1 | PSE-61300 | Process Instrument | ACTIVE
8 | IN-7 | P4-TBDI3-8 | C4S3-8/P4-TBDI3-8 | P4-TBDI3-8/C4S3-8 | IS-JB-618 | PSE-61301_DI_1 | PSE-61301 | Process Instrument | ACTIVE
9 | IN-8 | P4-TBDI3-9 | C4S3-9/P4-TBDI3-9 | P4-TBDI3-9/C4S3-9 | IS-JB-618 | PSE-61304_DI_1 | PSE-61304 | Process Instrument | ACTIVE
10 | IN-9 | P4-TBDI3-10 | C4S3-10/P4-TBDI3-10 | P4-TBDI3-10/C4S3-10 | IS-JB-618 | PSV-61301A_DI_1 | PSV-61301A | Process Instrument | ACTIVE
11 | IN-10 | P4-TBDI3-11 | C4S3-11/P4-TBDI3-11 | P4-TBDI3-11/C4S3-11 | IS-JB-618 | PSV-61301B_DI_1 | PSV-61301B | Process Instrument | ACTIVE
12 | IN-11 | P4-TBDI3-12 | C4S3-12/P4-TBDI3-12 | P4-TBDI3-12/C4S3-12 | IS-JB-618 | ZS-61310_DI_1 | ZS-61310 | Process Instrument | ACTIVE
13 | IN-12 | P4-TBDI3-13 | C4S3-13/P4-TBDI3-13 | P4-TBDI3-13/C4S3-13 | IS-JB-618 | ZS-61311_DI_1 | ZS-61311 | Process Instrument | ACTIVE
14 | IN-13 | P4-TBDI3-14 | C4S3-14/P4-TBDI3-14 | P4-TBDI3-14/C4S3-14 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
15 | IN-14 | P4-TBDI3-15 | C4S3-15/P4-TBDI3-15 | P4-TBDI3-15/C4S3-15 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
16 | IN-15 | P4-TBDI3-16 | C4S3-16/P4-TBDI3-16 | P4-TBDI3-16/C4S3-16 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
17 | GND-0 | 0VDC | 0VDC | 0VDC | IS-JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | IS-JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P4-TBDI3-17 | C4S3-19/P4-TBDI3-17 | P4-TBDI3-17/C4S3-19 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
20 | IN-17 | P4-TBDI3-18 | C4S3-20/P4-TBDI3-18 | P4-TBDI3-18/C4S3-20 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
21 | IN-18 | P4-TBDI3-19 | C4S3-21/P4-TBDI3-19 | P4-TBDI3-19/C4S3-21 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
22 | IN-19 | P4-TBDI3-20 | C4S3-22/P4-TBDI3-20 | P4-TBDI3-20/C4S3-22 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
23 | IN-20 | P4-TBDI3-21 | C4S3-23/P4-TBDI3-21 | P4-TBDI3-21/C4S3-23 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
24 | IN-21 | P4-TBDI3-22 | C4S3-24/P4-TBDI3-22 | P4-TBDI3-22/C4S3-24 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
25 | IN-22 | P4-TBDI3-23 | C4S3-25/P4-TBDI3-23 | P4-TBDI3-23/C4S3-25 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
26 | IN-23 | P4-TBDI3-24 | C4S3-26/P4-TBDI3-24 | P4-TBDI3-24/C4S3-26 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
27 | IN-24 | P4-TBDI3-25 | C4S3-27/P4-TBDI3-25 | P4-TBDI3-25/C4S3-27 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
28 | IN-25 | P4-TBDI3-26 | C4S3-28/P4-TBDI3-26 | P4-TBDI3-26/C4S3-28 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
29 | IN-26 | P4-TBDI3-27 | C4S3-29/P4-TBDI3-27 | P4-TBDI3-27/C4S3-29 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-27 | P4-TBDI3-28 | C4S3-30/P4-TBDI3-28 | P4-TBDI3-28/C4S3-30 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
31 | IN-28 | P4-TBDI3-29 | C4S3-31/P4-TBDI3-29 | P4-TBDI3-29/C4S3-31 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-29 | P4-TBDI3-30 | C4S3-32/P4-TBDI3-30 | P4-TBDI3-30/C4S3-32 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
33 | IN-30 | P4-TBDI3-31 | C4S3-33/P4-TBDI3-31 | P4-TBDI3-31/C4S3-33 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-31 | P4-TBDI3-32 | C4S3-34/P4-TBDI3-32 | P4-TBDI3-32/C4S3-34 | IS-JB-618 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
35 | GND1 | 0VDC | 0VDC | 0VDC | IS-JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | IS-JB-618 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C4S4
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C4S4
DIGITAL OUTPUT CARD (1756-OB32 32-CH 24VDC SOURCE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS: C4 ¦ SLOT: 4 ¦ MODULE: 1756-OB32 ¦ DESTINATION AREA: IS-JB-608, JB-618
← Back to Chassis Summary (C4SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBRLx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | OUT-0 | P4-TBRL1-1 | C4S4-1/P4-TBRL1-1 | P4-TBRL1-1/C4S4-1 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
2 | OUT-1 | P4-TBRL1-2 | C4S4-2/P4-TBRL1-2 | P4-TBRL1-2/C4S4-2 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
3 | OUT-2 | P4-TBRL1-3 | C4S4-3/P4-TBRL1-3 | P4-TBRL1-3/C4S4-3 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
4 | OUT-3 | P4-TBRL1-4 | C4S4-4/P4-TBRL1-4 | P4-TBRL1-4/C4S4-4 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
5 | OUT-4 | P4-TBRL1-5 | C4S4-5/P4-TBRL1-5 | P4-TBRL1-5/C4S4-5 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
6 | OUT-5 | P4-TBRL1-6 | C4S4-6/P4-TBRL1-6 | P4-TBRL1-6/C4S4-6 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
7 | OUT-6 | P4-TBRL1-7 | C4S4-7/P4-TBRL1-7 | P4-TBRL1-7/C4S4-7 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
8 | OUT-7 | P4-TBRL1-8 | C4S4-8/P4-TBRL1-8 | P4-TBRL1-8/C4S4-8 | JB-618 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
9 | OUT-8 | P4-TBRL1-9 | C4S4-9/P4-TBRL1-9 | P4-TBRL1-9/C4S4-9 | IS-JB-608 | XA-60201_DO_1 | XA-60201 | Process Instrument | ACTIVE
10 | OUT-9 | P4-TBRL1-10 | C4S4-10/P4-TBRL1-10 | P4-TBRL1-10/C4S4-10 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
11 | OUT-10 | P4-TBRL1-11 | C4S4-11/P4-TBRL1-11 | P4-TBRL1-11/C4S4-11 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
12 | OUT-11 | P4-TBRL1-12 | C4S4-12/P4-TBRL1-12 | P4-TBRL1-12/C4S4-12 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
13 | OUT-12 | P4-TBRL1-13 | C4S4-13/P4-TBRL1-13 | P4-TBRL1-13/C4S4-13 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
14 | OUT-13 | P4-TBRL1-14 | C4S4-14/P4-TBRL1-14 | P4-TBRL1-14/C4S4-14 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
15 | OUT-14 | P4-TBRL1-15 | C4S4-15/P4-TBRL1-15 | P4-TBRL1-15/C4S4-15 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
16 | OUT-15 | P4-TBRL1-16 | C4S4-16/P4-TBRL1-16 | P4-TBRL1-16/C4S4-16 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
17 | RTN OUT-0 | P4-TBRL1-17 | C4S4-17/P4-TBRL1-17 | P4-TBRL1-17/C4S4-17 | IS-JB-608 | Spare_DO_17 | Spare | Spare Reserve Channel | SPARE
18 | DC-0(+) | +24VDC | +24VDC | +24VDC | IS-JB-608 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | OUT-16 | P4-TBRL1-17 | C4S4-19/P4-TBRL1-17 | P4-TBRL1-17/C4S4-19 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
20 | OUT-17 | P4-TBRL1-18 | C4S4-20/P4-TBRL1-18 | P4-TBRL1-18/C4S4-20 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
21 | OUT-18 | P4-TBRL1-19 | C4S4-21/P4-TBRL1-19 | P4-TBRL1-19/C4S4-21 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
22 | OUT-19 | P4-TBRL1-20 | C4S4-22/P4-TBRL1-20 | P4-TBRL1-20/C4S4-22 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
23 | OUT-20 | P4-TBRL1-21 | C4S4-23/P4-TBRL1-21 | P4-TBRL1-21/C4S4-23 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
24 | OUT-21 | P4-TBRL1-22 | C4S4-24/P4-TBRL1-22 | P4-TBRL1-22/C4S4-24 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
25 | OUT-22 | P4-TBRL1-23 | C4S4-25/P4-TBRL1-23 | P4-TBRL1-23/C4S4-25 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
26 | OUT-23 | P4-TBRL1-24 | C4S4-26/P4-TBRL1-24 | P4-TBRL1-24/C4S4-26 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
27 | OUT-24 | P4-TBRL1-25 | C4S4-27/P4-TBRL1-25 | P4-TBRL1-25/C4S4-27 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
28 | OUT-25 | P4-TBRL1-26 | C4S4-28/P4-TBRL1-26 | P4-TBRL1-26/C4S4-28 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
29 | OUT-26 | P4-TBRL1-27 | C4S4-29/P4-TBRL1-27 | P4-TBRL1-27/C4S4-29 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
30 | OUT-27 | P4-TBRL1-28 | C4S4-30/P4-TBRL1-28 | P4-TBRL1-28/C4S4-30 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
31 | OUT-28 | P4-TBRL1-29 | C4S4-31/P4-TBRL1-29 | P4-TBRL1-29/C4S4-31 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
32 | OUT-29 | P4-TBRL1-30 | C4S4-32/P4-TBRL1-30 | P4-TBRL1-30/C4S4-32 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
33 | OUT-30 | P4-TBRL1-31 | C4S4-33/P4-TBRL1-31 | P4-TBRL1-31/C4S4-33 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
34 | OUT-31 | P4-TBRL1-32 | C4S4-34/P4-TBRL1-32 | P4-TBRL1-32/C4S4-34 | IS-JB-608 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
35 | RTN OUT-1 | P4-TBRL1-35 | C4S4-35/P4-TBRL1-35 | P4-TBRL1-35/C4S4-35 | IS-JB-608 | Spare_DO_35 | Spare | Spare Reserve Channel | SPARE
36 | DC-1(+) | +24VDC | +24VDC | +24VDC | IS-JB-608 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C4S5
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C4S5
ANALOG INPUT CARD (1756-IF16 16-CH CURRENT/VOLTAGE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS: C4 ¦ SLOT: 5 ¦ MODULE: 1756-IF16 ¦ DESTINATION AREA: IS-JB-603, IS-JB-608
← Back to Chassis Summary (C4SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | i RTN-0 | P4-TBAI1-1(B) | C4S5-1/P4-TBAI1-1(B) | P4-TBAI1-1(B)/C4S5-1 | IS-JB-603 | PT-60230_AI_1 | PT-60230 | Pressure Transmitter | ACTIVE
2 | IN-0 | P4-TBAI1-1(A) | C4S5-2/P4-TBAI1-1(A) | P4-TBAI1-1(A)/C4S5-2 | IS-JB-603 | PT-60230_AI_1 | PT-60230 | Pressure Transmitter | ACTIVE
3 | i RTN-1 | P4-TBAI1-2(B) | C4S5-3/P4-TBAI1-2(B) | P4-TBAI1-2(B)/C4S5-3 | IS-JB-603 | PT-60231_AI_1 | PT-60231 | Pressure Transmitter | ACTIVE
4 | IN-1 | P4-TBAI1-2(A) | C4S5-4/P4-TBAI1-2(A) | P4-TBAI1-2(A)/C4S5-4 | IS-JB-603 | PT-60231_AI_1 | PT-60231 | Pressure Transmitter | ACTIVE
5 | i RTN-2 | P4-TBAI1-3(B) | C4S5-5/P4-TBAI1-3(B) | P4-TBAI1-3(B)/C4S5-5 | IS-JB-603 | TT-60224_AI_1 | TT-60224 | Temperature Transmitter | ACTIVE
6 | IN-2 | P4-TBAI1-3(A) | C4S5-6/P4-TBAI1-3(A) | P4-TBAI1-3(A)/C4S5-6 | IS-JB-603 | TT-60224_AI_1 | TT-60224 | Temperature Transmitter | ACTIVE
7 | i RTN-3 | P4-TBAI1-4(B) | C4S5-7/P4-TBAI1-4(B) | P4-TBAI1-4(B)/C4S5-7 | IS-JB-603 | TT-60225_AI_1 | TT-60225 | Temperature Transmitter | ACTIVE
8 | IN-3 | P4-TBAI1-4(A) | C4S5-8/P4-TBAI1-4(A) | P4-TBAI1-4(A)/C4S5-8 | IS-JB-603 | TT-60225_AI_1 | TT-60225 | Temperature Transmitter | ACTIVE
9 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
10 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
11 | i RTN-4 | P4-TBAI1-5(B) | C4S5-11/P4-TBAI1-5(B) | P4-TBAI1-5(B)/C4S5-11 | IS-JB-603 | TT-60226_AI_1 | TT-60226 | Temperature Transmitter | ACTIVE
12 | IN-4 | P4-TBAI1-5(A) | C4S5-12/P4-TBAI1-5(A) | P4-TBAI1-5(A)/C4S5-12 | IS-JB-603 | TT-60226_AI_1 | TT-60226 | Temperature Transmitter | ACTIVE
13 | i RTN-5 | P4-TBAI1-6(B) | C4S5-13/P4-TBAI1-6(B) | P4-TBAI1-6(B)/C4S5-13 | IS-JB-603 | TT-60227_AI_1 | TT-60227 | Temperature Transmitter | ACTIVE
14 | IN-5 | P4-TBAI1-6(A) | C4S5-14/P4-TBAI1-6(A) | P4-TBAI1-6(A)/C4S5-14 | IS-JB-603 | TT-60227_AI_1 | TT-60227 | Temperature Transmitter | ACTIVE
15 | i RTN-6 | P4-TBAI1-7(B) | C4S5-15/P4-TBAI1-7(B) | P4-TBAI1-7(B)/C4S5-15 | IS-JB-603 | TT-60230_AI_1 | TT-60230 | Temperature Transmitter | ACTIVE
16 | IN-6 | P4-TBAI1-7(A) | C4S5-16/P4-TBAI1-7(A) | P4-TBAI1-7(A)/C4S5-16 | IS-JB-603 | TT-60230_AI_1 | TT-60230 | Temperature Transmitter | ACTIVE
17 | i RTN-7 | P4-TBAI1-8(B) | C4S5-17/P4-TBAI1-8(B) | P4-TBAI1-8(B)/C4S5-17 | IS-JB-603 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
18 | IN-7 | P4-TBAI1-8(A) | C4S5-18/P4-TBAI1-8(A) | P4-TBAI1-8(A)/C4S5-18 | IS-JB-603 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
19 | i RTN-8 | P4-TBAI1-9(B) | C4S5-19/P4-TBAI1-9(B) | P4-TBAI1-9(B)/C4S5-19 | IS-JB-608 | PT-60220_AI_1 | PT-60220 | Pressure Transmitter | ACTIVE
20 | IN-8 | P4-TBAI1-9(A) | C4S5-20/P4-TBAI1-9(A) | P4-TBAI1-9(A)/C4S5-20 | IS-JB-608 | PT-60220_AI_1 | PT-60220 | Pressure Transmitter | ACTIVE
21 | i RTN-9 | P4-TBAI1-10(B) | C4S5-21/P4-TBAI1-10(B) | P4-TBAI1-10(B)/C4S5-21 | IS-JB-608 | TT-60220_AI_1 | TT-60220 | Temperature Transmitter | ACTIVE
22 | IN-9 | P4-TBAI1-10(A) | C4S5-22/P4-TBAI1-10(A) | P4-TBAI1-10(A)/C4S5-22 | IS-JB-608 | TT-60220_AI_1 | TT-60220 | Temperature Transmitter | ACTIVE
23 | i RTN-10 | P4-TBAI1-11(B) | C4S5-23/P4-TBAI1-11(B) | P4-TBAI1-11(B)/C4S5-23 | IS-JB-608 | TT-60221_AI_1 | TT-60221 | Temperature Transmitter | ACTIVE
24 | IN-10 | P4-TBAI1-11(A) | C4S5-24/P4-TBAI1-11(A) | P4-TBAI1-11(A)/C4S5-24 | IS-JB-608 | TT-60221_AI_1 | TT-60221 | Temperature Transmitter | ACTIVE
25 | i RTN-11 | P4-TBAI1-12(B) | C4S5-25/P4-TBAI1-12(B) | P4-TBAI1-12(B)/C4S5-25 | IS-JB-608 | TT-60222_AI_1 | TT-60222 | Temperature Transmitter | ACTIVE
26 | IN-11 | P4-TBAI1-12(A) | C4S5-26/P4-TBAI1-12(A) | P4-TBAI1-12(A)/C4S5-26 | IS-JB-608 | TT-60222_AI_1 | TT-60222 | Temperature Transmitter | ACTIVE
27 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
28 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-603 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
29 | i RTN-12 | P4-TBAI1-13(B) | C4S5-29/P4-TBAI1-13(B) | P4-TBAI1-13(B)/C4S5-29 | IS-JB-608 | TT-60223_AI_1 | TT-60223 | Temperature Transmitter | ACTIVE
30 | IN-12 | P4-TBAI1-13(A) | C4S5-30/P4-TBAI1-13(A) | P4-TBAI1-13(A)/C4S5-30 | IS-JB-608 | TT-60223_AI_1 | TT-60223 | Temperature Transmitter | ACTIVE
31 | i RTN-13 | P4-TBAI1-14(B) | C4S5-31/P4-TBAI1-14(B) | P4-TBAI1-14(B)/C4S5-31 | IS-JB-608 | XT-60201_AI_1 | XT-60201 | Speed / Position Transmitter | ACTIVE
32 | IN-13 | P4-TBAI1-14(A) | C4S5-32/P4-TBAI1-14(A) | P4-TBAI1-14(A)/C4S5-32 | IS-JB-608 | XT-60201_AI_1 | XT-60201 | Speed / Position Transmitter | ACTIVE
33 | i RTN-14 | P4-TBAI1-15(B) | C4S5-33/P4-TBAI1-15(B) | P4-TBAI1-15(B)/C4S5-33 | IS-JB-608 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-14 | P4-TBAI1-15(A) | C4S5-34/P4-TBAI1-15(A) | P4-TBAI1-15(A)/C4S5-34 | IS-JB-608 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
35 | i RTN-15 | P4-TBAI1-16(B) | C4S5-35/P4-TBAI1-16(B) | P4-TBAI1-16(B)/C4S5-35 | IS-JB-608 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
36 | IN-15 | P4-TBAI1-16(A) | C4S5-36/P4-TBAI1-16(A) | P4-TBAI1-16(A)/C4S5-36 | IS-JB-608 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE

## C4S6
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C4S6
ANALOG INPUT CARD (1756-IF16 16-CH CURRENT/VOLTAGE) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS: C4 ¦ SLOT: 6 ¦ MODULE: 1756-IF16 ¦ DESTINATION AREA: IS-JB-612, IS-JB-618
← Back to Chassis Summary (C4SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | i RTN-0 | P4-TBAI2-1(B) | C4S6-1/P4-TBAI2-1(B) | P4-TBAI2-1(B)/C4S6-1 | IS-JB-612 | DPT-61310_AI_1 | DPT-61310 | Differential Pressure Transmitte | ACTIVE
2 | IN-0 | P4-TBAI2-1(A) | C4S6-2/P4-TBAI2-1(A) | P4-TBAI2-1(A)/C4S6-2 | IS-JB-612 | DPT-61310_AI_1 | DPT-61310 | Differential Pressure Transmitte | ACTIVE
3 | i RTN-1 | P4-TBAI2-2(B) | C4S6-3/P4-TBAI2-2(B) | P4-TBAI2-2(B)/C4S6-3 | IS-JB-612 | DPT-61312_AI_1 | DPT-61312 | Differential Pressure Transmitter | ACTIVE
4 | IN-1 | P4-TBAI2-2(A) | C4S6-4/P4-TBAI2-2(A) | P4-TBAI2-2(A)/C4S6-4 | IS-JB-612 | DPT-61312_AI_1 | DPT-61312 | Differential Pressure Transmitter | ACTIVE
5 | i RTN-2 | P4-TBAI2-3(B) | C4S6-5/P4-TBAI2-3(B) | P4-TBAI2-3(B)/C4S6-5 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
6 | IN-2 | P4-TBAI2-3(A) | C4S6-6/P4-TBAI2-3(A) | P4-TBAI2-3(A)/C4S6-6 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
7 | i RTN-3 | P4-TBAI2-4(B) | C4S6-7/P4-TBAI2-4(B) | P4-TBAI2-4(B)/C4S6-7 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
8 | IN-3 | P4-TBAI2-4(A) | C4S6-8/P4-TBAI2-4(A) | P4-TBAI2-4(A)/C4S6-8 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
9 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
10 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
11 | i RTN-4 | P4-TBAI2-5(B) | C4S6-11/P4-TBAI2-5(B) | P4-TBAI2-5(B)/C4S6-11 | IS-JB-618 | DPT-61301_AI_1 | DPT-61301 | Differential Pressure Transmitte | ACTIVE
12 | IN-4 | P4-TBAI2-5(A) | C4S6-12/P4-TBAI2-5(A) | P4-TBAI2-5(A)/C4S6-12 | IS-JB-618 | DPT-61301_AI_1 | DPT-61301 | Differential Pressure Transmitte | ACTIVE
13 | i RTN-5 | P4-TBAI2-6(B) | C4S6-13/P4-TBAI2-6(B) | P4-TBAI2-6(B)/C4S6-13 | IS-JB-618 | DPT-61302_AI_1 | DPT-61302 | Differential Pressure Transmitte | ACTIVE
14 | IN-5 | P4-TBAI2-6(A) | C4S6-14/P4-TBAI2-6(A) | P4-TBAI2-6(A)/C4S6-14 | IS-JB-618 | DPT-61302_AI_1 | DPT-61302 | Differential Pressure Transmitte | ACTIVE
15 | i RTN-6 | P4-TBAI2-7(B) | C4S6-15/P4-TBAI2-7(B) | P4-TBAI2-7(B)/C4S6-15 | IS-JB-618 | LT-61301_AI_1 | LT-61301 | Level Transmitter | ACTIVE
16 | IN-6 | P4-TBAI2-7(A) | C4S6-16/P4-TBAI2-7(A) | P4-TBAI2-7(A)/C4S6-16 | IS-JB-618 | LT-61301_AI_1 | LT-61301 | Level Transmitter | ACTIVE
17 | i RTN-7 | P4-TBAI2-8(B) | C4S6-17/P4-TBAI2-8(B) | P4-TBAI2-8(B)/C4S6-17 | IS-JB-618 | PT-61301_AI_1 | PT-61301 | Pressure Transmitter | ACTIVE
18 | IN-7 | P4-TBAI2-8(A) | C4S6-18/P4-TBAI2-8(A) | P4-TBAI2-8(A)/C4S6-18 | IS-JB-618 | PT-61301_AI_1 | PT-61301 | Pressure Transmitter | ACTIVE
19 | i RTN-8 | P4-TBAI2-9(B) | C4S6-19/P4-TBAI2-9(B) | P4-TBAI2-9(B)/C4S6-19 | IS-JB-618 | PT-61303_AI_1 | PT-61303 | Pressure Transmitter | ACTIVE
20 | IN-8 | P4-TBAI2-9(A) | C4S6-20/P4-TBAI2-9(A) | P4-TBAI2-9(A)/C4S6-20 | IS-JB-618 | PT-61303_AI_1 | PT-61303 | Pressure Transmitter | ACTIVE
21 | i RTN-9 | P4-TBAI2-10(B) | C4S6-21/P4-TBAI2-10(B) | P4-TBAI2-10(B)/C4S6-21 | IS-JB-618 | PT-61304_AI_1 | PT-61304 | Pressure Transmitter | ACTIVE
22 | IN-9 | P4-TBAI2-10(A) | C4S6-22/P4-TBAI2-10(A) | P4-TBAI2-10(A)/C4S6-22 | IS-JB-618 | PT-61304_AI_1 | PT-61304 | Pressure Transmitter | ACTIVE
23 | i RTN-10 | P4-TBAI2-11(B) | C4S6-23/P4-TBAI2-11(B) | P4-TBAI2-11(B)/C4S6-23 | IS-JB-618 | PT-61305_AI_1 | PT-61305 | Pressure Transmitter | ACTIVE
24 | IN-10 | P4-TBAI2-11(A) | C4S6-24/P4-TBAI2-11(A) | P4-TBAI2-11(A)/C4S6-24 | IS-JB-618 | PT-61305_AI_1 | PT-61305 | Pressure Transmitter | ACTIVE
25 | i RTN-11 | P4-TBAI2-12(B) | C4S6-25/P4-TBAI2-12(B) | P4-TBAI2-12(B)/C4S6-25 | IS-JB-618 | TT-61301_AI_1 | TT-61301 | Temperature Transmitter | ACTIVE
26 | IN-11 | P4-TBAI2-12(A) | C4S6-26/P4-TBAI2-12(A) | P4-TBAI2-12(A)/C4S6-26 | IS-JB-618 | TT-61301_AI_1 | TT-61301 | Temperature Transmitter | ACTIVE
27 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
28 | RTN | 0VDC | 0VDC | 0VDC | IS-JB-612 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
29 | i RTN-12 | P4-TBAI2-13(B) | C4S6-29/P4-TBAI2-13(B) | P4-TBAI2-13(B)/C4S6-29 | IS-JB-618 | TT-61302_AI_1 | TT-61302 | Temperature Transmitter | ACTIVE
30 | IN-12 | P4-TBAI2-13(A) | C4S6-30/P4-TBAI2-13(A) | P4-TBAI2-13(A)/C4S6-30 | IS-JB-618 | TT-61302_AI_1 | TT-61302 | Temperature Transmitter | ACTIVE
31 | i RTN-13 | P4-TBAI2-14(B) | C4S6-31/P4-TBAI2-14(B) | P4-TBAI2-14(B)/C4S6-31 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-13 | P4-TBAI2-14(A) | C4S6-32/P4-TBAI2-14(A) | P4-TBAI2-14(A)/C4S6-32 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
33 | i RTN-14 | P4-TBAI2-15(B) | C4S6-33/P4-TBAI2-15(B) | P4-TBAI2-15(B)/C4S6-33 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-14 | P4-TBAI2-15(A) | C4S6-34/P4-TBAI2-15(A) | P4-TBAI2-15(A)/C4S6-34 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
35 | i RTN-15 | P4-TBAI2-16(B) | C4S6-35/P4-TBAI2-16(B) | P4-TBAI2-16(B)/C4S6-35 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
36 | IN-15 | P4-TBAI2-16(A) | C4S6-36/P4-TBAI2-16(A) | P4-TBAI2-16(A)/C4S6-36 | IS-JB-618 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE

## C4S7
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C4S7
RESERVE / EMPTY SLOT (1756-N2) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS: C4 ¦ SLOT: 7 ¦ MODULE: 1756-N2 ¦ DESTINATION AREA: Field RIO
← Back to Chassis Summary (C4SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
- | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | EMPTY

## C4S8
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C4S8
RESERVE / EMPTY SLOT (1756-N2) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS: C4 ¦ SLOT: 8 ¦ MODULE: 1756-N2 ¦ DESTINATION AREA: Field RIO
← Back to Chassis Summary (C4SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
- | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | EMPTY

## C4S9
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C4S9
RESERVE / EMPTY SLOT (1756-N2) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS: C4 ¦ SLOT: 9 ¦ MODULE: 1756-N2 ¦ DESTINATION AREA: Field RIO
← Back to Chassis Summary (C4SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
- | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | EMPTY

## C4S10
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C4S10
RESERVE / EMPTY SLOT (1756-N2) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS: C4 ¦ SLOT: 10 ¦ MODULE: 1756-N2 ¦ DESTINATION AREA: Field RIO
← Back to Chassis Summary (C4SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
- | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | EMPTY

## C4S11
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C4S11
RESERVE / EMPTY SLOT (1756-N2) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS: C4 ¦ SLOT: 11 ¦ MODULE: 1756-N2 ¦ DESTINATION AREA: Field RIO
← Back to Chassis Summary (C4SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
- | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | EMPTY

## C4S12
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C4S12
RESERVE / EMPTY SLOT (1756-N2) ¦ LOCATION: FIELD RIO CABINET (SPRAY DRYER 6TH/8TH FLOOR)
CHASSIS: C4 ¦ SLOT: 12 ¦ MODULE: 1756-N2 ¦ DESTINATION AREA: Field RIO
← Back to Chassis Summary (C4SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
- | Empty Slot / Reserve (1756-N2) | - | - | - | - | - | - | Unpopulated Slot Position | EMPTY

## C5SlotConfig
CHASSIS C5 HARDWARE & SLOT CONFIGURATION SCHEDULE
REMOTE I/O STATION 5 (SLURRY BUILDING RIO-200) ¦ LOCATION: SLURRY BUILDING 2ND FLOOR (RIO-200)
CHASSIS MODEL: 1756-A7 (7-Slot ControlLogix Chassis) ¦ POWER SUPPLY: 1756-PA75 (85-265V AC Power Supply) ¦ NETWORK: ETHERNET/IP 1GBPS DLR RING
← Back to Master Slot Directory (00_Slot_Index)
Slot_No | Slot_Tag | Module_Catalog | Module_Description | Signal_Family | Terminal_Block_Type | Destination_Area(s) | Total_Channels | Active_Channels | Spare_Channels | Slot_Status
0 | C5S0 | 1756-EN4TR | EtherNet/IP Communication Adapter (1Gbps, 2-Port DLR) | COMM (EtherNet/IP) | 2x RJ45 (Gigabit) + 1x USB-B | CA1 / Field RIO (DLR Ring) | 4 | 4 | - | ACTIVE
1 | C5S1 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | RIO-200 | 32 | 32 | - | ACTIVE
2 | C5S2 | 1756-IB32 | 32-Point 24VDC Sink/Source Digital Input Module | DI (24VDC Digital Input) | 1756-TBCH (36-Pin RTB) | RIO-200 | 32 | 8 | 24 | ACTIVE
3 | C5S3 | 1756-OB32 | 32-Point 24VDC Sourcing Digital Output Module | DO (24VDC Digital Output) | 1756-TBCH (36-Pin RTB) | RIO-200 | 32 | 8 | 24 | ACTIVE
4 | C5S4 | 1756-IF16 | 16-Point Isolated/Non-Isolated Analog Input Module | AI (4-20mA / Voltage / RTD) | 1756-TBCH (36-Pin RTB) | RIO-200 | 16 | 18 | 14 | ACTIVE
TOTAL | 5 Slots | - | Chassis C5 Total Configured Capacity | - | - | - | 116 | 70 | 62 | 60% Active

## C5S0
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C5S0
ETHERNET COMMUNICATION ADAPTER (1756-EN4TR DLR 2-PORT GIGABIT) ¦ LOCATION: SLURRY BUILDING 2ND FLOOR (RIO-200)
CHASSIS: C5 ¦ SLOT: 0 ¦ MODULE: 1756-EN4TR ¦ DESTINATION AREA: CA1 / Field RIO (EtherNet/IP DLR Trunk)
← Back to Chassis Summary (C5SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
RJ45-1 | EtherNet/IP Port 1 (DLR Ring Node 1 / Primary Adapter Link) | ETH-DLR-P1 | C5S0-/- | -/C5S0- | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C5S0_ETH_Port1 | ETH-01 | 10/100/1000 Mbps RJ45 Device Level Ring Port 1 | ACTIVE
RJ45-2 | EtherNet/IP Port 2 (DLR Ring Node 2 / Redundant Loop) | ETH-DLR-P2 | C5S0-P2/ETH | ETH/C5S0-P2 | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C5S0_ETH_Port2 | ETH-02 | 10/100/1000 Mbps RJ45 Device Level Ring Port 2 | ACTIVE
USB-1 | USB 2.0 Type-B Device Port (Local Configuration & Diagnostics) | USB-CONSOLE | C5S0-USB/CONSOLE | CONSOLE/C5S0-USB | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C5S0_USB_Config | USB-CFG | Local IP Configuration and Firmware Flashing Port | ACTIVE
DISP-1 | 4-Character Diagnostic Display & Status LEDs (OK, NET A/B, LINK 1/2) | DIAG-DISP | C5S0-DISP/DIAG | DIAG/C5S0-DISP | CA1 / Field RIO (EtherNet/IP DLR Trunk) | C5S0_Status_Display | DIAG-LED | Hardware Status & Network Link Diagnostic Indicators | ACTIVE

## C5S1
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C5S1
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: SLURRY BUILDING 2ND FLOOR (RIO-200)
CHASSIS: C5 ¦ SLOT: 1 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: RIO-200
← Back to Chassis Summary (C5SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P5-TBDI1-1 | C5S1-1/P5-TBDI1-1 | P5-TBDI1-1/C5S1-1 | RIO-200 | FS-20201_DI_1 | FS-20201 | Process Instrument | ACTIVE
2 | IN-1 | P5-TBDI1-2 | C5S1-2/P5-TBDI1-2 | P5-TBDI1-2/C5S1-2 | RIO-200 | FT-913201_DI_1 | FT-913201 | Flow Transmitter | ACTIVE
3 | IN-2 | P5-TBDI1-3 | C5S1-3/P5-TBDI1-3 | P5-TBDI1-3/C5S1-3 | RIO-200 | FT-936201_DI_1 | FT-936201 | Flow Transmitter | ACTIVE
4 | IN-3 | P5-TBDI1-4 | C5S1-4/P5-TBDI1-4 | P5-TBDI1-4/C5S1-4 | RIO-200 | FT-936202_DI_1 | FT-936202 | Flow Transmitter | ACTIVE
5 | IN-4 | P5-TBDI1-5 | C5S1-5/P5-TBDI1-5 | P5-TBDI1-5/C5S1-5 | RIO-200 | LSL-814201_DI_1 | LSL-814201 | Process Instrument | ACTIVE
6 | IN-5 | P5-TBDI1-6 | C5S1-6/P5-TBDI1-6 | P5-TBDI1-6/C5S1-6 | RIO-200 | PK-913201_DI_1 | PK-913201 | Process Instrument | ACTIVE
7 | IN-6 | P5-TBDI1-7 | C5S1-7/P5-TBDI1-7 | P5-TBDI1-7/C5S1-7 | RIO-200 | PK-913202_DI_1 | PK-913202 | Process Instrument | ACTIVE
8 | IN-7 | P5-TBDI1-8 | C5S1-8/P5-TBDI1-8 | P5-TBDI1-8/C5S1-8 | RIO-200 | HV-20204_DI_1 | HV-20204 | Manual Valve With Position Switch | ACTIVE
9 | IN-8 | P5-TBDI1-9 | C5S1-9/P5-TBDI1-9 | P5-TBDI1-9/C5S1-9 | RIO-200 | HV-20205_DI_1 | HV-20205 | Manual Valve With Position Switch | ACTIVE
10 | IN-9 | P5-TBDI1-10 | C5S1-10/P5-TBDI1-10 | P5-TBDI1-10/C5S1-10 | RIO-200 | HV-20206_DI_1 | HV-20206 | Manual Valve With Position Switch | ACTIVE
11 | IN-10 | P5-TBDI1-11 | C5S1-11/P5-TBDI1-11 | P5-TBDI1-11/C5S1-11 | RIO-200 | HV-20207_DI_1 | HV-20207 | Manual Valve With Position Switch | ACTIVE
12 | IN-11 | P5-TBDI1-12 | C5S1-12/P5-TBDI1-12 | P5-TBDI1-12/C5S1-12 | RIO-200 | HV-20208_DI_1 | HV-20208 | Manual Valve With Position Switch | ACTIVE
13 | IN-12 | P5-TBDI1-13 | C5S1-13/P5-TBDI1-13 | P5-TBDI1-13/C5S1-13 | RIO-200 | HV-20209_DI_1 | HV-20209 | Manual Valve With Position Switch | ACTIVE
14 | IN-13 | P5-TBDI1-14 | C5S1-14/P5-TBDI1-14 | P5-TBDI1-14/C5S1-14 | RIO-200 | HV-20210_DI_1 | HV-20210 | Manual Valve With Position Switch | ACTIVE
15 | IN-14 | P5-TBDI1-15 | C5S1-15/P5-TBDI1-15 | P5-TBDI1-15/C5S1-15 | RIO-200 | XA-80305A_DI_1 | XA-80305A | Process Instrument | ACTIVE
16 | IN-15 | P5-TBDI1-16 | C5S1-16/P5-TBDI1-16 | P5-TBDI1-16/C5S1-16 | RIO-200 | XA-80305B_DI_1 | XA-80305B | Process Instrument | ACTIVE
17 | GND-0 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P5-TBDI1-17 | C5S1-19/P5-TBDI1-17 | P5-TBDI1-17/C5S1-19 | RIO-200 | XA-80305C_DI_1 | XA-80305C | Process Instrument | ACTIVE
20 | IN-17 | P5-TBDI1-18 | C5S1-20/P5-TBDI1-18 | P5-TBDI1-18/C5S1-20 | RIO-200 | XA-80305D_DI_1 | XA-80305D | Process Instrument | ACTIVE
21 | IN-18 | P5-TBDI1-19 | C5S1-21/P5-TBDI1-19 | P5-TBDI1-19/C5S1-21 | RIO-200 | XA-80305E_DI_1 | XA-80305E | Process Instrument | ACTIVE
22 | IN-19 | P5-TBDI1-20 | C5S1-22/P5-TBDI1-20 | P5-TBDI1-20/C5S1-22 | RIO-200 | XA-80305F_DI_1 | XA-80305F | Process Instrument | ACTIVE
23 | IN-20 | P5-TBDI1-21 | C5S1-23/P5-TBDI1-21 | P5-TBDI1-21/C5S1-23 | RIO-200 | XA-80306A_DI_1 | XA-80306A | Process Instrument | ACTIVE
24 | IN-21 | P5-TBDI1-22 | C5S1-24/P5-TBDI1-22 | P5-TBDI1-22/C5S1-24 | RIO-200 | XA-80306B_DI_1 | XA-80306B | Process Instrument | ACTIVE
25 | IN-22 | P5-TBDI1-23 | C5S1-25/P5-TBDI1-23 | P5-TBDI1-23/C5S1-25 | RIO-200 | XA-80306C_DI_1 | XA-80306C | Process Instrument | ACTIVE
26 | IN-23 | P5-TBDI1-24 | C5S1-26/P5-TBDI1-24 | P5-TBDI1-24/C5S1-26 | RIO-200 | XA-80306D_DI_1 | XA-80306D | Process Instrument | ACTIVE
27 | IN-24 | P5-TBDI1-25 | C5S1-27/P5-TBDI1-25 | P5-TBDI1-25/C5S1-27 | RIO-200 | XA-80306E_DI_1 | XA-80306E | Process Instrument | ACTIVE
28 | IN-25 | P5-TBDI1-26 | C5S1-28/P5-TBDI1-26 | P5-TBDI1-26/C5S1-28 | RIO-200 | XA-80306F_DI_1 | XA-80306F | Process Instrument | ACTIVE
29 | IN-26 | P5-TBDI1-27 | C5S1-29/P5-TBDI1-27 | P5-TBDI1-27/C5S1-29 | RIO-200 | XV-20201_DI_1 | XV-20201 | Control Valve Position Feedback | ACTIVE
30 | IN-27 | P5-TBDI1-28 | C5S1-30/P5-TBDI1-28 | P5-TBDI1-28/C5S1-30 | RIO-200 | XV-20201_DI_2 | XV-20201 | Control Valve Position Feedback | ACTIVE
31 | IN-28 | P5-TBDI1-29 | C5S1-31/P5-TBDI1-29 | P5-TBDI1-29/C5S1-31 | RIO-200 | XV-20202_DI_1 | XV-20202 | Control Valve Position Feedback | ACTIVE
32 | IN-29 | P5-TBDI1-30 | C5S1-32/P5-TBDI1-30 | P5-TBDI1-30/C5S1-32 | RIO-200 | XV-20202_DI_2 | XV-20202 | Control Valve Position Feedback | ACTIVE
33 | IN-30 | P5-TBDI1-31 | C5S1-33/P5-TBDI1-31 | P5-TBDI1-31/C5S1-33 | RIO-200 | XV-20203_DI_1 | XV-20203 | Control Valve Position Feedback | ACTIVE
34 | IN-31 | P5-TBDI1-32 | C5S1-34/P5-TBDI1-32 | P5-TBDI1-32/C5S1-34 | RIO-200 | XV-20203_DI_2 | XV-20203 | Control Valve Position Feedback | ACTIVE
35 | GND1 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C5S2
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C5S2
DIGITAL INPUT CARD (1756-IB32 32-CH 24VDC SINK/SOURCE) ¦ LOCATION: SLURRY BUILDING 2ND FLOOR (RIO-200)
CHASSIS: C5 ¦ SLOT: 2 ¦ MODULE: 1756-IB32 ¦ DESTINATION AREA: RIO-200
← Back to Chassis Summary (C5SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBDIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | IN-0 | P5-TBDI2-1 | C5S2-1/P5-TBDI2-1 | P5-TBDI2-1/C5S2-1 | RIO-200 | XV-20211_DI_1 | XV-20211 | Control Valve Position Feedback | ACTIVE
2 | IN-1 | P5-TBDI2-2 | C5S2-2/P5-TBDI2-2 | P5-TBDI2-2/C5S2-2 | RIO-200 | XV-20211_DI_2 | XV-20211 | Control Valve Position Feedback | ACTIVE
3 | IN-2 | P5-TBDI2-3 | C5S2-3/P5-TBDI2-3 | P5-TBDI2-3/C5S2-3 | RIO-200 | XV-20212_DI_1 | XV-20212 | Control Valve Position Feedback | ACTIVE
4 | IN-3 | P5-TBDI2-4 | C5S2-4/P5-TBDI2-4 | P5-TBDI2-4/C5S2-4 | RIO-200 | XV-20212_DI_2 | XV-20212 | Control Valve Position Feedback | ACTIVE
5 | IN-4 | P5-TBDI2-5 | C5S2-5/P5-TBDI2-5 | P5-TBDI2-5/C5S2-5 | RIO-200 | XV-20213_DI_1 | XV-20213 | Control Valve Position Feedback | ACTIVE
6 | IN-5 | P5-TBDI2-6 | C5S2-6/P5-TBDI2-6 | P5-TBDI2-6/C5S2-6 | RIO-200 | XV-20213_DI_2 | XV-20213 | Control Valve Position Feedback | ACTIVE
7 | IN-6 | P5-TBDI2-7 | C5S2-7/P5-TBDI2-7 | P5-TBDI2-7/C5S2-7 | RIO-200 | XV-913201_DI_1 | XV-913201 | Control Valve Position Feedback | ACTIVE
8 | IN-7 | P5-TBDI2-8 | C5S2-8/P5-TBDI2-8 | P5-TBDI2-8/C5S2-8 | RIO-200 | XV-913201_DI_1 | XV-913201 | Control Valve Position Feedback | ACTIVE
9 | IN-8 | P5-TBDI2-9 | C5S2-9/P5-TBDI2-9 | P5-TBDI2-9/C5S2-9 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
10 | IN-9 | P5-TBDI2-10 | C5S2-10/P5-TBDI2-10 | P5-TBDI2-10/C5S2-10 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
11 | IN-10 | P5-TBDI2-11 | C5S2-11/P5-TBDI2-11 | P5-TBDI2-11/C5S2-11 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
12 | IN-11 | P5-TBDI2-12 | C5S2-12/P5-TBDI2-12 | P5-TBDI2-12/C5S2-12 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
13 | IN-12 | P5-TBDI2-13 | C5S2-13/P5-TBDI2-13 | P5-TBDI2-13/C5S2-13 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
14 | IN-13 | P5-TBDI2-14 | C5S2-14/P5-TBDI2-14 | P5-TBDI2-14/C5S2-14 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
15 | IN-14 | P5-TBDI2-15 | C5S2-15/P5-TBDI2-15 | P5-TBDI2-15/C5S2-15 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
16 | IN-15 | P5-TBDI2-16 | C5S2-16/P5-TBDI2-16 | P5-TBDI2-16/C5S2-16 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
17 | GND-0 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
18 | GND-0 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | IN-16 | P5-TBDI2-17 | C5S2-19/P5-TBDI2-17 | P5-TBDI2-17/C5S2-19 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
20 | IN-17 | P5-TBDI2-18 | C5S2-20/P5-TBDI2-18 | P5-TBDI2-18/C5S2-20 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
21 | IN-18 | P5-TBDI2-19 | C5S2-21/P5-TBDI2-19 | P5-TBDI2-19/C5S2-21 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
22 | IN-19 | P5-TBDI2-20 | C5S2-22/P5-TBDI2-20 | P5-TBDI2-20/C5S2-22 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
23 | IN-20 | P5-TBDI2-21 | C5S2-23/P5-TBDI2-21 | P5-TBDI2-21/C5S2-23 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
24 | IN-21 | P5-TBDI2-22 | C5S2-24/P5-TBDI2-22 | P5-TBDI2-22/C5S2-24 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
25 | IN-22 | P5-TBDI2-23 | C5S2-25/P5-TBDI2-23 | P5-TBDI2-23/C5S2-25 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
26 | IN-23 | P5-TBDI2-24 | C5S2-26/P5-TBDI2-24 | P5-TBDI2-24/C5S2-26 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
27 | IN-24 | P5-TBDI2-25 | C5S2-27/P5-TBDI2-25 | P5-TBDI2-25/C5S2-27 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
28 | IN-25 | P5-TBDI2-26 | C5S2-28/P5-TBDI2-26 | P5-TBDI2-26/C5S2-28 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
29 | IN-26 | P5-TBDI2-27 | C5S2-29/P5-TBDI2-27 | P5-TBDI2-27/C5S2-29 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-27 | P5-TBDI2-28 | C5S2-30/P5-TBDI2-28 | P5-TBDI2-28/C5S2-30 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
31 | IN-28 | P5-TBDI2-29 | C5S2-31/P5-TBDI2-29 | P5-TBDI2-29/C5S2-31 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-29 | P5-TBDI2-30 | C5S2-32/P5-TBDI2-30 | P5-TBDI2-30/C5S2-32 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
33 | IN-30 | P5-TBDI2-31 | C5S2-33/P5-TBDI2-31 | P5-TBDI2-31/C5S2-33 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-31 | P5-TBDI2-32 | C5S2-34/P5-TBDI2-32 | P5-TBDI2-32/C5S2-34 | RIO-200 | Spare_DI_0 | Spare | Spare Reserve Channel | SPARE
35 | GND1 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
36 | GND1 | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C5S3
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C5S3
DIGITAL OUTPUT CARD (1756-OB32 32-CH 24VDC SOURCE) ¦ LOCATION: SLURRY BUILDING 2ND FLOOR (RIO-200)
CHASSIS: C5 ¦ SLOT: 3 ¦ MODULE: 1756-OB32 ¦ DESTINATION AREA: RIO-200
← Back to Chassis Summary (C5SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBRLx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | OUT-0 | P5-TBRL1-1 | C5S3-1/P5-TBRL1-1 | P5-TBRL1-1/C5S3-1 | RIO-200 | XA-92201_DO_1 | XA-92201 | Process Instrument | ACTIVE
2 | OUT-1 | P5-TBRL1-2 | C5S3-2/P5-TBRL1-2 | P5-TBRL1-2/C5S3-2 | RIO-200 | XV-20201_DO_1 | XV-20201 | Control Valve Position Feedback | ACTIVE
3 | OUT-2 | P5-TBRL1-3 | C5S3-3/P5-TBRL1-3 | P5-TBRL1-3/C5S3-3 | RIO-200 | XV-20202_DO_1 | XV-20202 | Control Valve Position Feedback | ACTIVE
4 | OUT-3 | P5-TBRL1-4 | C5S3-4/P5-TBRL1-4 | P5-TBRL1-4/C5S3-4 | RIO-200 | XV-20203_DO_1 | XV-20203 | Control Valve Position Feedback | ACTIVE
5 | OUT-4 | P5-TBRL1-5 | C5S3-5/P5-TBRL1-5 | P5-TBRL1-5/C5S3-5 | RIO-200 | XV-20211_DO_1 | XV-20211 | Control Valve Position Feedback | ACTIVE
6 | OUT-5 | P5-TBRL1-6 | C5S3-6/P5-TBRL1-6 | P5-TBRL1-6/C5S3-6 | RIO-200 | XV-20212_DO_1 | XV-20212 | Control Valve Position Feedback | ACTIVE
7 | OUT-6 | P5-TBRL1-7 | C5S3-7/P5-TBRL1-7 | P5-TBRL1-7/C5S3-7 | RIO-200 | XV-20213_DO_1 | XV-20213 | Control Valve Position Feedback | ACTIVE
8 | OUT-7 | P5-TBRL1-8 | C5S3-8/P5-TBRL1-8 | P5-TBRL1-8/C5S3-8 | RIO-200 | XV-913201_DO_1 | XV-913201 | Control Valve Position Feedback | ACTIVE
9 | OUT-8 | P5-TBRL1-9 | C5S3-9/P5-TBRL1-9 | P5-TBRL1-9/C5S3-9 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
10 | OUT-9 | P5-TBRL1-10 | C5S3-10/P5-TBRL1-10 | P5-TBRL1-10/C5S3-10 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
11 | OUT-10 | P5-TBRL1-11 | C5S3-11/P5-TBRL1-11 | P5-TBRL1-11/C5S3-11 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
12 | OUT-11 | P5-TBRL1-12 | C5S3-12/P5-TBRL1-12 | P5-TBRL1-12/C5S3-12 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
13 | OUT-12 | P5-TBRL1-13 | C5S3-13/P5-TBRL1-13 | P5-TBRL1-13/C5S3-13 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
14 | OUT-13 | P5-TBRL1-14 | C5S3-14/P5-TBRL1-14 | P5-TBRL1-14/C5S3-14 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
15 | OUT-14 | P5-TBRL1-15 | C5S3-15/P5-TBRL1-15 | P5-TBRL1-15/C5S3-15 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
16 | OUT-15 | P5-TBRL1-16 | C5S3-16/P5-TBRL1-16 | P5-TBRL1-16/C5S3-16 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
17 | RTN OUT-0 | P5-TBRL1-17 | C5S3-17/P5-TBRL1-17 | P5-TBRL1-17/C5S3-17 | RIO-200 | Spare_DO_17 | Spare | Spare Reserve Channel | SPARE
18 | DC-0(+) | +24VDC | +24VDC | +24VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
19 | OUT-16 | P5-TBRL1-17 | C5S3-19/P5-TBRL1-17 | P5-TBRL1-17/C5S3-19 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
20 | OUT-17 | P5-TBRL1-18 | C5S3-20/P5-TBRL1-18 | P5-TBRL1-18/C5S3-20 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
21 | OUT-18 | P5-TBRL1-19 | C5S3-21/P5-TBRL1-19 | P5-TBRL1-19/C5S3-21 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
22 | OUT-19 | P5-TBRL1-20 | C5S3-22/P5-TBRL1-20 | P5-TBRL1-20/C5S3-22 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
23 | OUT-20 | P5-TBRL1-21 | C5S3-23/P5-TBRL1-21 | P5-TBRL1-21/C5S3-23 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
24 | OUT-21 | P5-TBRL1-22 | C5S3-24/P5-TBRL1-22 | P5-TBRL1-22/C5S3-24 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
25 | OUT-22 | P5-TBRL1-23 | C5S3-25/P5-TBRL1-23 | P5-TBRL1-23/C5S3-25 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
26 | OUT-23 | P5-TBRL1-24 | C5S3-26/P5-TBRL1-24 | P5-TBRL1-24/C5S3-26 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
27 | OUT-24 | P5-TBRL1-25 | C5S3-27/P5-TBRL1-25 | P5-TBRL1-25/C5S3-27 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
28 | OUT-25 | P5-TBRL1-26 | C5S3-28/P5-TBRL1-26 | P5-TBRL1-26/C5S3-28 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
29 | OUT-26 | P5-TBRL1-27 | C5S3-29/P5-TBRL1-27 | P5-TBRL1-27/C5S3-29 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
30 | OUT-27 | P5-TBRL1-28 | C5S3-30/P5-TBRL1-28 | P5-TBRL1-28/C5S3-30 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
31 | OUT-28 | P5-TBRL1-29 | C5S3-31/P5-TBRL1-29 | P5-TBRL1-29/C5S3-31 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
32 | OUT-29 | P5-TBRL1-30 | C5S3-32/P5-TBRL1-30 | P5-TBRL1-30/C5S3-32 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
33 | OUT-30 | P5-TBRL1-31 | C5S3-33/P5-TBRL1-31 | P5-TBRL1-31/C5S3-33 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
34 | OUT-31 | P5-TBRL1-32 | C5S3-34/P5-TBRL1-32 | P5-TBRL1-32/C5S3-34 | RIO-200 | Spare_DO_0 | Spare | Spare Reserve Channel | SPARE
35 | RTN OUT-1 | P5-TBRL1-35 | C5S3-35/P5-TBRL1-35 | P5-TBRL1-35/C5S3-35 | RIO-200 | Spare_DO_35 | Spare | Spare Reserve Channel | SPARE
36 | DC-1(+) | +24VDC | +24VDC | +24VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON

## C5S4
SLOT CONFIGURATION & TERMINAL SCHEDULE --- C5S4
ANALOG INPUT CARD (1756-IF16 16-CH CURRENT/VOLTAGE) ¦ LOCATION: SLURRY BUILDING 2ND FLOOR (RIO-200)
CHASSIS: C5 ¦ SLOT: 4 ¦ MODULE: 1756-IF16 ¦ DESTINATION AREA: RIO-200
← Back to Chassis Summary (C5SlotConfig) |  |  |  | ← Back to Master Slot Directory (00_Slot_Index)
Terminal_No | Terminal_Description | Terminal_Number (Px-TBAIx-m) | PLC_Tag_Side | Terminal_Tag_Side | Destination_Area | PLC_Tag | Instrument_Tag | Instrument_Description | Channel_Status
1 | i RTN-0 | P5-TBAI1-1(B) | C5S4-1/P5-TBAI1-1(B) | P5-TBAI1-1(B)/C5S4-1 | RIO-200 | EXT-BIILER_AI_1 | EXT-BIILER | External Boiler 4-20mA Interface | ACTIVE
2 | IN-0 | P5-TBAI1-1(A) | C5S4-2/P5-TBAI1-1(A) | P5-TBAI1-1(A)/C5S4-2 | RIO-200 | EXT-BIILER_AI_1 | EXT-BIILER | External Boiler 4-20mA Interface | ACTIVE
3 | i RTN-1 | P5-TBAI1-2(B) | C5S4-3/P5-TBAI1-2(B) | P5-TBAI1-2(B)/C5S4-3 | RIO-200 | FT-913201_AI_1 | FT-913201 | Flow Transmitter | ACTIVE
4 | IN-1 | P5-TBAI1-2(A) | C5S4-4/P5-TBAI1-2(A) | P5-TBAI1-2(A)/C5S4-4 | RIO-200 | FT-913201_AI_1 | FT-913201 | Flow Transmitter | ACTIVE
5 | i RTN-2 | P5-TBAI1-3(B) | C5S4-5/P5-TBAI1-3(B) | P5-TBAI1-3(B)/C5S4-5 | RIO-200 | FT-913201_AI_2 | FT-913201 | Flow Transmitter | ACTIVE
6 | IN-2 | P5-TBAI1-3(A) | C5S4-6/P5-TBAI1-3(A) | P5-TBAI1-3(A)/C5S4-6 | RIO-200 | FT-913201_AI_2 | FT-913201 | Flow Transmitter | ACTIVE
7 | i RTN-3 | P5-TBAI1-4(B) | C5S4-7/P5-TBAI1-4(B) | P5-TBAI1-4(B)/C5S4-7 | RIO-200 | FT-936201_AI_1 | FT-936201 | Flow Transmitter | ACTIVE
8 | IN-3 | P5-TBAI1-4(A) | C5S4-8/P5-TBAI1-4(A) | P5-TBAI1-4(A)/C5S4-8 | RIO-200 | FT-936201_AI_1 | FT-936201 | Flow Transmitter | ACTIVE
9 | RTN | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
10 | RTN | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
11 | i RTN-4 | P5-TBAI1-5(B) | C5S4-11/P5-TBAI1-5(B) | P5-TBAI1-5(B)/C5S4-11 | RIO-200 | FT-936202_AI_1 | FT-936202 | Flow Transmitter | ACTIVE
12 | IN-4 | P5-TBAI1-5(A) | C5S4-12/P5-TBAI1-5(A) | P5-TBAI1-5(A)/C5S4-12 | RIO-200 | FT-936202_AI_1 | FT-936202 | Flow Transmitter | ACTIVE
13 | i RTN-5 | P5-TBAI1-6(B) | C5S4-13/P5-TBAI1-6(B) | P5-TBAI1-6(B)/C5S4-13 | RIO-200 | LT-913201_AI_1 | LT-913201 | Level Transmitter | ACTIVE
14 | IN-5 | P5-TBAI1-6(A) | C5S4-14/P5-TBAI1-6(A) | P5-TBAI1-6(A)/C5S4-14 | RIO-200 | LT-913201_AI_1 | LT-913201 | Level Transmitter | ACTIVE
15 | i RTN-6 | P5-TBAI1-7(B) | C5S4-15/P5-TBAI1-7(B) | P5-TBAI1-7(B)/C5S4-15 | RIO-200 | PT-913201_AI_1 | PT-913201 | Pressure Transmitter | ACTIVE
16 | IN-6 | P5-TBAI1-7(A) | C5S4-16/P5-TBAI1-7(A) | P5-TBAI1-7(A)/C5S4-16 | RIO-200 | PT-913201_AI_1 | PT-913201 | Pressure Transmitter | ACTIVE
17 | i RTN-7 | P5-TBAI1-8(B) | C5S4-17/P5-TBAI1-8(B) | P5-TBAI1-8(B)/C5S4-17 | RIO-200 | XT-92201_AI_1 | XT-92201 | Speed / Position Transmitter | ACTIVE
18 | IN-7 | P5-TBAI1-8(A) | C5S4-18/P5-TBAI1-8(A) | P5-TBAI1-8(A)/C5S4-18 | RIO-200 | XT-92201_AI_1 | XT-92201 | Speed / Position Transmitter | ACTIVE
19 | i RTN-8 | P5-TBAI1-9(B) | C5S4-19/P5-TBAI1-9(B) | P5-TBAI1-9(B)/C5S4-19 | RIO-200 | XV-913201_AI_1 | XV-913201 | Control Valve Position Feedback | ACTIVE
20 | IN-8 | P5-TBAI1-9(A) | C5S4-20/P5-TBAI1-9(A) | P5-TBAI1-9(A)/C5S4-20 | RIO-200 | XV-913201_AI_1 | XV-913201 | Control Valve Position Feedback | ACTIVE
21 | i RTN-9 | P5-TBAI1-10(B) | C5S4-21/P5-TBAI1-10(B) | P5-TBAI1-10(B)/C5S4-21 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
22 | IN-9 | P5-TBAI1-10(A) | C5S4-22/P5-TBAI1-10(A) | P5-TBAI1-10(A)/C5S4-22 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
23 | i RTN-10 | P5-TBAI1-11(B) | C5S4-23/P5-TBAI1-11(B) | P5-TBAI1-11(B)/C5S4-23 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
24 | IN-10 | P5-TBAI1-11(A) | C5S4-24/P5-TBAI1-11(A) | P5-TBAI1-11(A)/C5S4-24 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
25 | i RTN-11 | P5-TBAI1-12(B) | C5S4-25/P5-TBAI1-12(B) | P5-TBAI1-12(B)/C5S4-25 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
26 | IN-11 | P5-TBAI1-12(A) | C5S4-26/P5-TBAI1-12(A) | P5-TBAI1-12(A)/C5S4-26 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
27 | RTN | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
28 | RTN | 0VDC | 0VDC | 0VDC | RIO-200 | Internal Power Common | - | Module Power / Common Return Terminal | COMMON
29 | i RTN-12 | P5-TBAI1-13(B) | C5S4-29/P5-TBAI1-13(B) | P5-TBAI1-13(B)/C5S4-29 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
30 | IN-12 | P5-TBAI1-13(A) | C5S4-30/P5-TBAI1-13(A) | P5-TBAI1-13(A)/C5S4-30 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
31 | i RTN-13 | P5-TBAI1-14(B) | C5S4-31/P5-TBAI1-14(B) | P5-TBAI1-14(B)/C5S4-31 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
32 | IN-13 | P5-TBAI1-14(A) | C5S4-32/P5-TBAI1-14(A) | P5-TBAI1-14(A)/C5S4-32 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
33 | i RTN-14 | P5-TBAI1-15(B) | C5S4-33/P5-TBAI1-15(B) | P5-TBAI1-15(B)/C5S4-33 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
34 | IN-14 | P5-TBAI1-15(A) | C5S4-34/P5-TBAI1-15(A) | P5-TBAI1-15(A)/C5S4-34 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
35 | i RTN-15 | P5-TBAI1-16(B) | C5S4-35/P5-TBAI1-16(B) | P5-TBAI1-16(B)/C5S4-35 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE
36 | IN-15 | P5-TBAI1-16(A) | C5S4-36/P5-TBAI1-16(A) | P5-TBAI1-16(A)/C5S4-36 | RIO-200 | Spare_AI_0 | Spare | Spare Reserve Channel | SPARE