## DIDO_Loopback_Report
AUTOMATED DI/DO CLOSED-LOOP CROSS-WIRING VERIFICATION REPORT
Project: SPRINT 18K Spray Dryer ¦ Target: MCP-01 (C1, C2, C3, C4) ¦ Test Method: Dry Contact Relay Loopback to DI Terminal
TOTAL TESTED 256 LOOPS |  | PASSED LOOPS 256 (100.0%) |  | FAILED LOOPS 0 (0.0%) |  | AVG LATENCY 31.4 ms |  | OVERALL VERDICT ACCEPTED (PASS)
Loop # | DO Slot & Pin | Interposing Relay Coil Tag | Relay Dry Contact | Temp Loopback Wire Ref | Paired DI Terminal Block | DI Slot & Pin | Switching Latency | Loop State Transition | Verdict
LPB-001 | C1S8 - Pin 1 | TBRL-1 (A1/A2) | TBRL-1 (11/14) | JMP-LPB-001 | TBDI-1 (Pin 1) | C1S4 - Pin 1 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-002 | C1S8 - Pin 2 | TBRL-2 (A1/A2) | TBRL-2 (11/14) | JMP-LPB-002 | TBDI-2 (Pin 2) | C1S4 - Pin 2 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-003 | C1S8 - Pin 3 | TBRL-3 (A1/A2) | TBRL-3 (11/14) | JMP-LPB-003 | TBDI-3 (Pin 3) | C1S4 - Pin 3 | 22 ms | 0 -> 1 -> 0 | PASS
LPB-004 | C1S8 - Pin 4 | TBRL-4 (A1/A2) | TBRL-4 (11/14) | JMP-LPB-004 | TBDI-4 (Pin 4) | C1S4 - Pin 4 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-005 | C1S8 - Pin 5 | TBRL-5 (A1/A2) | TBRL-5 (11/14) | JMP-LPB-005 | TBDI-5 (Pin 5) | C1S4 - Pin 5 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-006 | C1S8 - Pin 6 | TBRL-6 (A1/A2) | TBRL-6 (11/14) | JMP-LPB-006 | TBDI-6 (Pin 6) | C1S4 - Pin 6 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-007 | C1S8 - Pin 7 | TBRL-7 (A1/A2) | TBRL-7 (11/14) | JMP-LPB-007 | TBDI-7 (Pin 7) | C1S4 - Pin 7 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-008 | C1S8 - Pin 8 | TBRL-8 (A1/A2) | TBRL-8 (11/14) | JMP-LPB-008 | TBDI-8 (Pin 8) | C1S4 - Pin 8 | 26 ms | 0 -> 1 -> 0 | PASS
LPB-009 | C1S8 - Pin 9 | TBRL-9 (A1/A2) | TBRL-9 (11/14) | JMP-LPB-009 | TBDI-9 (Pin 9) | C1S4 - Pin 9 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-010 | C1S8 - Pin 10 | TBRL-10 (A1/A2) | TBRL-10 (11/14) | JMP-LPB-010 | TBDI-10 (Pin 10) | C1S4 - Pin 10 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-011 | C1S8 - Pin 11 | TBRL-11 (A1/A2) | TBRL-11 (11/14) | JMP-LPB-011 | TBDI-11 (Pin 11) | C1S4 - Pin 11 | 43 ms | 0 -> 1 -> 0 | PASS
LPB-012 | C1S8 - Pin 12 | TBRL-12 (A1/A2) | TBRL-12 (11/14) | JMP-LPB-012 | TBDI-12 (Pin 12) | C1S4 - Pin 12 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-013 | C1S8 - Pin 13 | TBRL-13 (A1/A2) | TBRL-13 (11/14) | JMP-LPB-013 | TBDI-13 (Pin 13) | C1S4 - Pin 13 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-014 | C1S8 - Pin 14 | TBRL-14 (A1/A2) | TBRL-14 (11/14) | JMP-LPB-014 | TBDI-14 (Pin 14) | C1S4 - Pin 14 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-015 | C1S8 - Pin 15 | TBRL-15 (A1/A2) | TBRL-15 (11/14) | JMP-LPB-015 | TBDI-15 (Pin 15) | C1S4 - Pin 15 | 40 ms | 0 -> 1 -> 0 | PASS
LPB-016 | C1S8 - Pin 16 | TBRL-16 (A1/A2) | TBRL-16 (11/14) | JMP-LPB-016 | TBDI-16 (Pin 16) | C1S4 - Pin 16 | 35 ms | 0 -> 1 -> 0 | PASS
LPB-017 | C1S8 - Pin 19 | TBRL-17 (A1/A2) | TBRL-17 (11/14) | JMP-LPB-017 | TBDI-17 (Pin 19) | C1S4 - Pin 19 | 23 ms | 0 -> 1 -> 0 | PASS
LPB-018 | C1S8 - Pin 20 | TBRL-18 (A1/A2) | TBRL-18 (11/14) | JMP-LPB-018 | TBDI-18 (Pin 20) | C1S4 - Pin 20 | 22 ms | 0 -> 1 -> 0 | PASS
LPB-019 | C1S8 - Pin 21 | TBRL-19 (A1/A2) | TBRL-19 (11/14) | JMP-LPB-019 | TBDI-19 (Pin 21) | C1S4 - Pin 21 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-020 | C1S8 - Pin 22 | TBRL-20 (A1/A2) | TBRL-20 (11/14) | JMP-LPB-020 | TBDI-20 (Pin 22) | C1S4 - Pin 22 | 28 ms | 0 -> 1 -> 0 | PASS
LPB-021 | C1S8 - Pin 23 | TBRL-21 (A1/A2) | TBRL-21 (11/14) | JMP-LPB-021 | TBDI-21 (Pin 23) | C1S4 - Pin 23 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-022 | C1S8 - Pin 24 | TBRL-22 (A1/A2) | TBRL-22 (11/14) | JMP-LPB-022 | TBDI-22 (Pin 24) | C1S4 - Pin 24 | 38 ms | 0 -> 1 -> 0 | PASS
LPB-023 | C1S8 - Pin 25 | TBRL-23 (A1/A2) | TBRL-23 (11/14) | JMP-LPB-023 | TBDI-23 (Pin 25) | C1S4 - Pin 25 | 41 ms | 0 -> 1 -> 0 | PASS
LPB-024 | C1S8 - Pin 26 | TBRL-24 (A1/A2) | TBRL-24 (11/14) | JMP-LPB-024 | TBDI-24 (Pin 26) | C1S4 - Pin 26 | 22 ms | 0 -> 1 -> 0 | PASS
LPB-025 | C1S8 - Pin 27 | TBRL-25 (A1/A2) | TBRL-25 (11/14) | JMP-LPB-025 | TBDI-25 (Pin 27) | C1S4 - Pin 27 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-026 | C1S8 - Pin 28 | TBRL-26 (A1/A2) | TBRL-26 (11/14) | JMP-LPB-026 | TBDI-26 (Pin 28) | C1S4 - Pin 28 | 28 ms | 0 -> 1 -> 0 | PASS
LPB-027 | C1S8 - Pin 29 | TBRL-27 (A1/A2) | TBRL-27 (11/14) | JMP-LPB-027 | TBDI-27 (Pin 29) | C1S4 - Pin 29 | 44 ms | 0 -> 1 -> 0 | PASS
LPB-028 | C1S8 - Pin 30 | TBRL-28 (A1/A2) | TBRL-28 (11/14) | JMP-LPB-028 | TBDI-28 (Pin 30) | C1S4 - Pin 30 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-029 | C1S8 - Pin 31 | TBRL-29 (A1/A2) | TBRL-29 (11/14) | JMP-LPB-029 | TBDI-29 (Pin 31) | C1S4 - Pin 31 | 44 ms | 0 -> 1 -> 0 | PASS
LPB-030 | C1S8 - Pin 32 | TBRL-30 (A1/A2) | TBRL-30 (11/14) | JMP-LPB-030 | TBDI-30 (Pin 32) | C1S4 - Pin 32 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-031 | C1S8 - Pin 33 | TBRL-31 (A1/A2) | TBRL-31 (11/14) | JMP-LPB-031 | TBDI-31 (Pin 33) | C1S4 - Pin 33 | 35 ms | 0 -> 1 -> 0 | PASS
LPB-032 | C1S8 - Pin 34 | TBRL-32 (A1/A2) | TBRL-32 (11/14) | JMP-LPB-032 | TBDI-32 (Pin 34) | C1S4 - Pin 34 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-033 | C1S9 - Pin 1 | TBRL-33 (A1/A2) | TBRL-33 (11/14) | JMP-LPB-033 | TBDI-33 (Pin 1) | C1S5 - Pin 1 | 36 ms | 0 -> 1 -> 0 | PASS
LPB-034 | C1S9 - Pin 2 | TBRL-34 (A1/A2) | TBRL-34 (11/14) | JMP-LPB-034 | TBDI-34 (Pin 2) | C1S5 - Pin 2 | 40 ms | 0 -> 1 -> 0 | PASS
LPB-035 | C1S9 - Pin 3 | TBRL-35 (A1/A2) | TBRL-35 (11/14) | JMP-LPB-035 | TBDI-35 (Pin 3) | C1S5 - Pin 3 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-036 | C1S9 - Pin 4 | TBRL-36 (A1/A2) | TBRL-36 (11/14) | JMP-LPB-036 | TBDI-36 (Pin 4) | C1S5 - Pin 4 | 22 ms | 0 -> 1 -> 0 | PASS
LPB-037 | C1S9 - Pin 5 | TBRL-37 (A1/A2) | TBRL-37 (11/14) | JMP-LPB-037 | TBDI-37 (Pin 5) | C1S5 - Pin 5 | 27 ms | 0 -> 1 -> 0 | PASS
LPB-038 | C1S9 - Pin 6 | TBRL-38 (A1/A2) | TBRL-38 (11/14) | JMP-LPB-038 | TBDI-38 (Pin 6) | C1S5 - Pin 6 | 44 ms | 0 -> 1 -> 0 | PASS
LPB-039 | C1S9 - Pin 7 | TBRL-39 (A1/A2) | TBRL-39 (11/14) | JMP-LPB-039 | TBDI-39 (Pin 7) | C1S5 - Pin 7 | 35 ms | 0 -> 1 -> 0 | PASS
LPB-040 | C1S9 - Pin 8 | TBRL-40 (A1/A2) | TBRL-40 (11/14) | JMP-LPB-040 | TBDI-40 (Pin 8) | C1S5 - Pin 8 | 32 ms | 0 -> 1 -> 0 | PASS
LPB-041 | C1S9 - Pin 9 | TBRL-41 (A1/A2) | TBRL-41 (11/14) | JMP-LPB-041 | TBDI-41 (Pin 9) | C1S5 - Pin 9 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-042 | C1S9 - Pin 10 | TBRL-42 (A1/A2) | TBRL-42 (11/14) | JMP-LPB-042 | TBDI-42 (Pin 10) | C1S5 - Pin 10 | 26 ms | 0 -> 1 -> 0 | PASS
LPB-043 | C1S9 - Pin 11 | TBRL-43 (A1/A2) | TBRL-43 (11/14) | JMP-LPB-043 | TBDI-43 (Pin 11) | C1S5 - Pin 11 | 28 ms | 0 -> 1 -> 0 | PASS
LPB-044 | C1S9 - Pin 12 | TBRL-44 (A1/A2) | TBRL-44 (11/14) | JMP-LPB-044 | TBDI-44 (Pin 12) | C1S5 - Pin 12 | 32 ms | 0 -> 1 -> 0 | PASS
LPB-045 | C1S9 - Pin 13 | TBRL-45 (A1/A2) | TBRL-45 (11/14) | JMP-LPB-045 | TBDI-45 (Pin 13) | C1S5 - Pin 13 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-046 | C1S9 - Pin 14 | TBRL-46 (A1/A2) | TBRL-46 (11/14) | JMP-LPB-046 | TBDI-46 (Pin 14) | C1S5 - Pin 14 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-047 | C1S9 - Pin 15 | TBRL-47 (A1/A2) | TBRL-47 (11/14) | JMP-LPB-047 | TBDI-47 (Pin 15) | C1S5 - Pin 15 | 34 ms | 0 -> 1 -> 0 | PASS
LPB-048 | C1S9 - Pin 16 | TBRL-48 (A1/A2) | TBRL-48 (11/14) | JMP-LPB-048 | TBDI-48 (Pin 16) | C1S5 - Pin 16 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-049 | C1S9 - Pin 19 | TBRL-49 (A1/A2) | TBRL-49 (11/14) | JMP-LPB-049 | TBDI-49 (Pin 19) | C1S5 - Pin 19 | 33 ms | 0 -> 1 -> 0 | PASS
LPB-050 | C1S9 - Pin 20 | TBRL-50 (A1/A2) | TBRL-50 (11/14) | JMP-LPB-050 | TBDI-50 (Pin 20) | C1S5 - Pin 20 | 33 ms | 0 -> 1 -> 0 | PASS
LPB-051 | C1S9 - Pin 21 | TBRL-51 (A1/A2) | TBRL-51 (11/14) | JMP-LPB-051 | TBDI-51 (Pin 21) | C1S5 - Pin 21 | 41 ms | 0 -> 1 -> 0 | PASS
LPB-052 | C1S9 - Pin 22 | TBRL-52 (A1/A2) | TBRL-52 (11/14) | JMP-LPB-052 | TBDI-52 (Pin 22) | C1S5 - Pin 22 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-053 | C1S9 - Pin 23 | TBRL-53 (A1/A2) | TBRL-53 (11/14) | JMP-LPB-053 | TBDI-53 (Pin 23) | C1S5 - Pin 23 | 23 ms | 0 -> 1 -> 0 | PASS
LPB-054 | C1S9 - Pin 24 | TBRL-54 (A1/A2) | TBRL-54 (11/14) | JMP-LPB-054 | TBDI-54 (Pin 24) | C1S5 - Pin 24 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-055 | C1S9 - Pin 25 | TBRL-55 (A1/A2) | TBRL-55 (11/14) | JMP-LPB-055 | TBDI-55 (Pin 25) | C1S5 - Pin 25 | 36 ms | 0 -> 1 -> 0 | PASS
LPB-056 | C1S9 - Pin 26 | TBRL-56 (A1/A2) | TBRL-56 (11/14) | JMP-LPB-056 | TBDI-56 (Pin 26) | C1S5 - Pin 26 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-057 | C1S9 - Pin 27 | TBRL-57 (A1/A2) | TBRL-57 (11/14) | JMP-LPB-057 | TBDI-57 (Pin 27) | C1S5 - Pin 27 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-058 | C1S9 - Pin 28 | TBRL-58 (A1/A2) | TBRL-58 (11/14) | JMP-LPB-058 | TBDI-58 (Pin 28) | C1S5 - Pin 28 | 34 ms | 0 -> 1 -> 0 | PASS
LPB-059 | C1S9 - Pin 29 | TBRL-59 (A1/A2) | TBRL-59 (11/14) | JMP-LPB-059 | TBDI-59 (Pin 29) | C1S5 - Pin 29 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-060 | C1S9 - Pin 30 | TBRL-60 (A1/A2) | TBRL-60 (11/14) | JMP-LPB-060 | TBDI-60 (Pin 30) | C1S5 - Pin 30 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-061 | C1S9 - Pin 31 | TBRL-61 (A1/A2) | TBRL-61 (11/14) | JMP-LPB-061 | TBDI-61 (Pin 31) | C1S5 - Pin 31 | 31 ms | 0 -> 1 -> 0 | PASS
LPB-062 | C1S9 - Pin 32 | TBRL-62 (A1/A2) | TBRL-62 (11/14) | JMP-LPB-062 | TBDI-62 (Pin 32) | C1S5 - Pin 32 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-063 | C1S9 - Pin 33 | TBRL-63 (A1/A2) | TBRL-63 (11/14) | JMP-LPB-063 | TBDI-63 (Pin 33) | C1S5 - Pin 33 | 41 ms | 0 -> 1 -> 0 | PASS
LPB-064 | C1S9 - Pin 34 | TBRL-64 (A1/A2) | TBRL-64 (11/14) | JMP-LPB-064 | TBDI-64 (Pin 34) | C1S5 - Pin 34 | 33 ms | 0 -> 1 -> 0 | PASS
LPB-065 | C2S6 - Pin 1 | TBRL-65 (A1/A2) | TBRL-65 (11/14) | JMP-LPB-065 | TBDI-65 (Pin 1) | C1S6 - Pin 1 | 40 ms | 0 -> 1 -> 0 | PASS
LPB-066 | C2S6 - Pin 2 | TBRL-66 (A1/A2) | TBRL-66 (11/14) | JMP-LPB-066 | TBDI-66 (Pin 2) | C1S6 - Pin 2 | 28 ms | 0 -> 1 -> 0 | PASS
LPB-067 | C2S6 - Pin 3 | TBRL-67 (A1/A2) | TBRL-67 (11/14) | JMP-LPB-067 | TBDI-67 (Pin 3) | C1S6 - Pin 3 | 44 ms | 0 -> 1 -> 0 | PASS
LPB-068 | C2S6 - Pin 4 | TBRL-68 (A1/A2) | TBRL-68 (11/14) | JMP-LPB-068 | TBDI-68 (Pin 4) | C1S6 - Pin 4 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-069 | C2S6 - Pin 5 | TBRL-69 (A1/A2) | TBRL-69 (11/14) | JMP-LPB-069 | TBDI-69 (Pin 5) | C1S6 - Pin 5 | 23 ms | 0 -> 1 -> 0 | PASS
LPB-070 | C2S6 - Pin 6 | TBRL-70 (A1/A2) | TBRL-70 (11/14) | JMP-LPB-070 | TBDI-70 (Pin 6) | C1S6 - Pin 6 | 43 ms | 0 -> 1 -> 0 | PASS
LPB-071 | C2S6 - Pin 7 | TBRL-71 (A1/A2) | TBRL-71 (11/14) | JMP-LPB-071 | TBDI-71 (Pin 7) | C1S6 - Pin 7 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-072 | C2S6 - Pin 8 | TBRL-72 (A1/A2) | TBRL-72 (11/14) | JMP-LPB-072 | TBDI-72 (Pin 8) | C1S6 - Pin 8 | 31 ms | 0 -> 1 -> 0 | PASS
LPB-073 | C2S6 - Pin 9 | TBRL-73 (A1/A2) | TBRL-73 (11/14) | JMP-LPB-073 | TBDI-73 (Pin 9) | C1S6 - Pin 9 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-074 | C2S6 - Pin 10 | TBRL-74 (A1/A2) | TBRL-74 (11/14) | JMP-LPB-074 | TBDI-74 (Pin 10) | C1S6 - Pin 10 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-075 | C2S6 - Pin 11 | TBRL-75 (A1/A2) | TBRL-75 (11/14) | JMP-LPB-075 | TBDI-75 (Pin 11) | C1S6 - Pin 11 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-076 | C2S6 - Pin 12 | TBRL-76 (A1/A2) | TBRL-76 (11/14) | JMP-LPB-076 | TBDI-76 (Pin 12) | C1S6 - Pin 12 | 34 ms | 0 -> 1 -> 0 | PASS
LPB-077 | C2S6 - Pin 13 | TBRL-77 (A1/A2) | TBRL-77 (11/14) | JMP-LPB-077 | TBDI-77 (Pin 13) | C1S6 - Pin 13 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-078 | C2S6 - Pin 14 | TBRL-78 (A1/A2) | TBRL-78 (11/14) | JMP-LPB-078 | TBDI-78 (Pin 14) | C1S6 - Pin 14 | 36 ms | 0 -> 1 -> 0 | PASS
LPB-079 | C2S6 - Pin 15 | TBRL-79 (A1/A2) | TBRL-79 (11/14) | JMP-LPB-079 | TBDI-79 (Pin 15) | C1S6 - Pin 15 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-080 | C2S6 - Pin 16 | TBRL-80 (A1/A2) | TBRL-80 (11/14) | JMP-LPB-080 | TBDI-80 (Pin 16) | C1S6 - Pin 16 | 33 ms | 0 -> 1 -> 0 | PASS
LPB-081 | C2S6 - Pin 19 | TBRL-81 (A1/A2) | TBRL-81 (11/14) | JMP-LPB-081 | TBDI-81 (Pin 19) | C1S6 - Pin 19 | 27 ms | 0 -> 1 -> 0 | PASS
LPB-082 | C2S6 - Pin 20 | TBRL-82 (A1/A2) | TBRL-82 (11/14) | JMP-LPB-082 | TBDI-82 (Pin 20) | C1S6 - Pin 20 | 33 ms | 0 -> 1 -> 0 | PASS
LPB-083 | C2S6 - Pin 21 | TBRL-83 (A1/A2) | TBRL-83 (11/14) | JMP-LPB-083 | TBDI-83 (Pin 21) | C1S6 - Pin 21 | 33 ms | 0 -> 1 -> 0 | PASS
LPB-084 | C2S6 - Pin 22 | TBRL-84 (A1/A2) | TBRL-84 (11/14) | JMP-LPB-084 | TBDI-84 (Pin 22) | C1S6 - Pin 22 | 28 ms | 0 -> 1 -> 0 | PASS
LPB-085 | C2S6 - Pin 23 | TBRL-85 (A1/A2) | TBRL-85 (11/14) | JMP-LPB-085 | TBDI-85 (Pin 23) | C1S6 - Pin 23 | 43 ms | 0 -> 1 -> 0 | PASS
LPB-086 | C2S6 - Pin 24 | TBRL-86 (A1/A2) | TBRL-86 (11/14) | JMP-LPB-086 | TBDI-86 (Pin 24) | C1S6 - Pin 24 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-087 | C2S6 - Pin 25 | TBRL-87 (A1/A2) | TBRL-87 (11/14) | JMP-LPB-087 | TBDI-87 (Pin 25) | C1S6 - Pin 25 | 44 ms | 0 -> 1 -> 0 | PASS
LPB-088 | C2S6 - Pin 26 | TBRL-88 (A1/A2) | TBRL-88 (11/14) | JMP-LPB-088 | TBDI-88 (Pin 26) | C1S6 - Pin 26 | 43 ms | 0 -> 1 -> 0 | PASS
LPB-089 | C2S6 - Pin 27 | TBRL-89 (A1/A2) | TBRL-89 (11/14) | JMP-LPB-089 | TBDI-89 (Pin 27) | C1S6 - Pin 27 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-090 | C2S6 - Pin 28 | TBRL-90 (A1/A2) | TBRL-90 (11/14) | JMP-LPB-090 | TBDI-90 (Pin 28) | C1S6 - Pin 28 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-091 | C2S6 - Pin 29 | TBRL-91 (A1/A2) | TBRL-91 (11/14) | JMP-LPB-091 | TBDI-91 (Pin 29) | C1S6 - Pin 29 | 41 ms | 0 -> 1 -> 0 | PASS
LPB-092 | C2S6 - Pin 30 | TBRL-92 (A1/A2) | TBRL-92 (11/14) | JMP-LPB-092 | TBDI-92 (Pin 30) | C1S6 - Pin 30 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-093 | C2S6 - Pin 31 | TBRL-93 (A1/A2) | TBRL-93 (11/14) | JMP-LPB-093 | TBDI-93 (Pin 31) | C1S6 - Pin 31 | 27 ms | 0 -> 1 -> 0 | PASS
LPB-094 | C2S6 - Pin 32 | TBRL-94 (A1/A2) | TBRL-94 (11/14) | JMP-LPB-094 | TBDI-94 (Pin 32) | C1S6 - Pin 32 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-095 | C2S6 - Pin 33 | TBRL-95 (A1/A2) | TBRL-95 (11/14) | JMP-LPB-095 | TBDI-95 (Pin 33) | C1S6 - Pin 33 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-096 | C2S6 - Pin 34 | TBRL-96 (A1/A2) | TBRL-96 (11/14) | JMP-LPB-096 | TBDI-96 (Pin 34) | C1S6 - Pin 34 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-097 | C2S7 - Pin 1 | TBRL-97 (A1/A2) | TBRL-97 (11/14) | JMP-LPB-097 | TBDI-97 (Pin 1) | C1S7 - Pin 1 | 27 ms | 0 -> 1 -> 0 | PASS
LPB-098 | C2S7 - Pin 2 | TBRL-98 (A1/A2) | TBRL-98 (11/14) | JMP-LPB-098 | TBDI-98 (Pin 2) | C1S7 - Pin 2 | 36 ms | 0 -> 1 -> 0 | PASS
LPB-099 | C2S7 - Pin 3 | TBRL-99 (A1/A2) | TBRL-99 (11/14) | JMP-LPB-099 | TBDI-99 (Pin 3) | C1S7 - Pin 3 | 34 ms | 0 -> 1 -> 0 | PASS
LPB-100 | C2S7 - Pin 4 | TBRL-100 (A1/A2) | TBRL-100 (11/14) | JMP-LPB-100 | TBDI-100 (Pin 4) | C1S7 - Pin 4 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-101 | C2S7 - Pin 5 | TBRL-101 (A1/A2) | TBRL-101 (11/14) | JMP-LPB-101 | TBDI-101 (Pin 5) | C1S7 - Pin 5 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-102 | C2S7 - Pin 6 | TBRL-102 (A1/A2) | TBRL-102 (11/14) | JMP-LPB-102 | TBDI-102 (Pin 6) | C1S7 - Pin 6 | 44 ms | 0 -> 1 -> 0 | PASS
LPB-103 | C2S7 - Pin 7 | TBRL-103 (A1/A2) | TBRL-103 (11/14) | JMP-LPB-103 | TBDI-103 (Pin 7) | C1S7 - Pin 7 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-104 | C2S7 - Pin 8 | TBRL-104 (A1/A2) | TBRL-104 (11/14) | JMP-LPB-104 | TBDI-104 (Pin 8) | C1S7 - Pin 8 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-105 | C2S7 - Pin 9 | TBRL-105 (A1/A2) | TBRL-105 (11/14) | JMP-LPB-105 | TBDI-105 (Pin 9) | C1S7 - Pin 9 | 43 ms | 0 -> 1 -> 0 | PASS
LPB-106 | C2S7 - Pin 10 | TBRL-106 (A1/A2) | TBRL-106 (11/14) | JMP-LPB-106 | TBDI-106 (Pin 10) | C1S7 - Pin 10 | 32 ms | 0 -> 1 -> 0 | PASS
LPB-107 | C2S7 - Pin 11 | TBRL-107 (A1/A2) | TBRL-107 (11/14) | JMP-LPB-107 | TBDI-107 (Pin 11) | C1S7 - Pin 11 | 23 ms | 0 -> 1 -> 0 | PASS
LPB-108 | C2S7 - Pin 12 | TBRL-108 (A1/A2) | TBRL-108 (11/14) | JMP-LPB-108 | TBDI-108 (Pin 12) | C1S7 - Pin 12 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-109 | C2S7 - Pin 13 | TBRL-109 (A1/A2) | TBRL-109 (11/14) | JMP-LPB-109 | TBDI-109 (Pin 13) | C1S7 - Pin 13 | 23 ms | 0 -> 1 -> 0 | PASS
LPB-110 | C2S7 - Pin 14 | TBRL-110 (A1/A2) | TBRL-110 (11/14) | JMP-LPB-110 | TBDI-110 (Pin 14) | C1S7 - Pin 14 | 32 ms | 0 -> 1 -> 0 | PASS
LPB-111 | C2S7 - Pin 15 | TBRL-111 (A1/A2) | TBRL-111 (11/14) | JMP-LPB-111 | TBDI-111 (Pin 15) | C1S7 - Pin 15 | 34 ms | 0 -> 1 -> 0 | PASS
LPB-112 | C2S7 - Pin 16 | TBRL-112 (A1/A2) | TBRL-112 (11/14) | JMP-LPB-112 | TBDI-112 (Pin 16) | C1S7 - Pin 16 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-113 | C2S7 - Pin 19 | TBRL-113 (A1/A2) | TBRL-113 (11/14) | JMP-LPB-113 | TBDI-113 (Pin 19) | C1S7 - Pin 19 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-114 | C2S7 - Pin 20 | TBRL-114 (A1/A2) | TBRL-114 (11/14) | JMP-LPB-114 | TBDI-114 (Pin 20) | C1S7 - Pin 20 | 28 ms | 0 -> 1 -> 0 | PASS
LPB-115 | C2S7 - Pin 21 | TBRL-115 (A1/A2) | TBRL-115 (11/14) | JMP-LPB-115 | TBDI-115 (Pin 21) | C1S7 - Pin 21 | 40 ms | 0 -> 1 -> 0 | PASS
LPB-116 | C2S7 - Pin 22 | TBRL-116 (A1/A2) | TBRL-116 (11/14) | JMP-LPB-116 | TBDI-116 (Pin 22) | C1S7 - Pin 22 | 44 ms | 0 -> 1 -> 0 | PASS
LPB-117 | C2S7 - Pin 23 | TBRL-117 (A1/A2) | TBRL-117 (11/14) | JMP-LPB-117 | TBDI-117 (Pin 23) | C1S7 - Pin 23 | 32 ms | 0 -> 1 -> 0 | PASS
LPB-118 | C2S7 - Pin 24 | TBRL-118 (A1/A2) | TBRL-118 (11/14) | JMP-LPB-118 | TBDI-118 (Pin 24) | C1S7 - Pin 24 | 28 ms | 0 -> 1 -> 0 | PASS
LPB-119 | C2S7 - Pin 25 | TBRL-119 (A1/A2) | TBRL-119 (11/14) | JMP-LPB-119 | TBDI-119 (Pin 25) | C1S7 - Pin 25 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-120 | C2S7 - Pin 26 | TBRL-120 (A1/A2) | TBRL-120 (11/14) | JMP-LPB-120 | TBDI-120 (Pin 26) | C1S7 - Pin 26 | 37 ms | 0 -> 1 -> 0 | PASS
LPB-121 | C2S7 - Pin 27 | TBRL-121 (A1/A2) | TBRL-121 (11/14) | JMP-LPB-121 | TBDI-121 (Pin 27) | C1S7 - Pin 27 | 34 ms | 0 -> 1 -> 0 | PASS
LPB-122 | C2S7 - Pin 28 | TBRL-122 (A1/A2) | TBRL-122 (11/14) | JMP-LPB-122 | TBDI-122 (Pin 28) | C1S7 - Pin 28 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-123 | C2S7 - Pin 29 | TBRL-123 (A1/A2) | TBRL-123 (11/14) | JMP-LPB-123 | TBDI-123 (Pin 29) | C1S7 - Pin 29 | 36 ms | 0 -> 1 -> 0 | PASS
LPB-124 | C2S7 - Pin 30 | TBRL-124 (A1/A2) | TBRL-124 (11/14) | JMP-LPB-124 | TBDI-124 (Pin 30) | C1S7 - Pin 30 | 26 ms | 0 -> 1 -> 0 | PASS
LPB-125 | C2S7 - Pin 31 | TBRL-125 (A1/A2) | TBRL-125 (11/14) | JMP-LPB-125 | TBDI-125 (Pin 31) | C1S7 - Pin 31 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-126 | C2S7 - Pin 32 | TBRL-126 (A1/A2) | TBRL-126 (11/14) | JMP-LPB-126 | TBDI-126 (Pin 32) | C1S7 - Pin 32 | 26 ms | 0 -> 1 -> 0 | PASS
LPB-127 | C2S7 - Pin 33 | TBRL-127 (A1/A2) | TBRL-127 (11/14) | JMP-LPB-127 | TBDI-127 (Pin 33) | C1S7 - Pin 33 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-128 | C2S7 - Pin 34 | TBRL-128 (A1/A2) | TBRL-128 (11/14) | JMP-LPB-128 | TBDI-128 (Pin 34) | C1S7 - Pin 34 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-129 | C2S8 - Pin 1 | TBRL-129 (A1/A2) | TBRL-129 (11/14) | JMP-LPB-129 | TBDI-129 (Pin 1) | C2S1 - Pin 1 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-130 | C2S8 - Pin 2 | TBRL-130 (A1/A2) | TBRL-130 (11/14) | JMP-LPB-130 | TBDI-130 (Pin 2) | C2S1 - Pin 2 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-131 | C2S8 - Pin 3 | TBRL-131 (A1/A2) | TBRL-131 (11/14) | JMP-LPB-131 | TBDI-131 (Pin 3) | C2S1 - Pin 3 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-132 | C2S8 - Pin 4 | TBRL-132 (A1/A2) | TBRL-132 (11/14) | JMP-LPB-132 | TBDI-132 (Pin 4) | C2S1 - Pin 4 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-133 | C2S8 - Pin 5 | TBRL-133 (A1/A2) | TBRL-133 (11/14) | JMP-LPB-133 | TBDI-133 (Pin 5) | C2S1 - Pin 5 | 40 ms | 0 -> 1 -> 0 | PASS
LPB-134 | C2S8 - Pin 6 | TBRL-134 (A1/A2) | TBRL-134 (11/14) | JMP-LPB-134 | TBDI-134 (Pin 6) | C2S1 - Pin 6 | 35 ms | 0 -> 1 -> 0 | PASS
LPB-135 | C2S8 - Pin 7 | TBRL-135 (A1/A2) | TBRL-135 (11/14) | JMP-LPB-135 | TBDI-135 (Pin 7) | C2S1 - Pin 7 | 40 ms | 0 -> 1 -> 0 | PASS
LPB-136 | C2S8 - Pin 8 | TBRL-136 (A1/A2) | TBRL-136 (11/14) | JMP-LPB-136 | TBDI-136 (Pin 8) | C2S1 - Pin 8 | 34 ms | 0 -> 1 -> 0 | PASS
LPB-137 | C2S8 - Pin 9 | TBRL-137 (A1/A2) | TBRL-137 (11/14) | JMP-LPB-137 | TBDI-137 (Pin 9) | C2S1 - Pin 9 | 33 ms | 0 -> 1 -> 0 | PASS
LPB-138 | C2S8 - Pin 10 | TBRL-138 (A1/A2) | TBRL-138 (11/14) | JMP-LPB-138 | TBDI-138 (Pin 10) | C2S1 - Pin 10 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-139 | C2S8 - Pin 11 | TBRL-139 (A1/A2) | TBRL-139 (11/14) | JMP-LPB-139 | TBDI-139 (Pin 11) | C2S1 - Pin 11 | 26 ms | 0 -> 1 -> 0 | PASS
LPB-140 | C2S8 - Pin 12 | TBRL-140 (A1/A2) | TBRL-140 (11/14) | JMP-LPB-140 | TBDI-140 (Pin 12) | C2S1 - Pin 12 | 38 ms | 0 -> 1 -> 0 | PASS
LPB-141 | C2S8 - Pin 13 | TBRL-141 (A1/A2) | TBRL-141 (11/14) | JMP-LPB-141 | TBDI-141 (Pin 13) | C2S1 - Pin 13 | 37 ms | 0 -> 1 -> 0 | PASS
LPB-142 | C2S8 - Pin 14 | TBRL-142 (A1/A2) | TBRL-142 (11/14) | JMP-LPB-142 | TBDI-142 (Pin 14) | C2S1 - Pin 14 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-143 | C2S8 - Pin 15 | TBRL-143 (A1/A2) | TBRL-143 (11/14) | JMP-LPB-143 | TBDI-143 (Pin 15) | C2S1 - Pin 15 | 23 ms | 0 -> 1 -> 0 | PASS
LPB-144 | C2S8 - Pin 16 | TBRL-144 (A1/A2) | TBRL-144 (11/14) | JMP-LPB-144 | TBDI-144 (Pin 16) | C2S1 - Pin 16 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-145 | C2S8 - Pin 19 | TBRL-145 (A1/A2) | TBRL-145 (11/14) | JMP-LPB-145 | TBDI-145 (Pin 19) | C2S1 - Pin 19 | 26 ms | 0 -> 1 -> 0 | PASS
LPB-146 | C2S8 - Pin 20 | TBRL-146 (A1/A2) | TBRL-146 (11/14) | JMP-LPB-146 | TBDI-146 (Pin 20) | C2S1 - Pin 20 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-147 | C2S8 - Pin 21 | TBRL-147 (A1/A2) | TBRL-147 (11/14) | JMP-LPB-147 | TBDI-147 (Pin 21) | C2S1 - Pin 21 | 27 ms | 0 -> 1 -> 0 | PASS
LPB-148 | C2S8 - Pin 22 | TBRL-148 (A1/A2) | TBRL-148 (11/14) | JMP-LPB-148 | TBDI-148 (Pin 22) | C2S1 - Pin 22 | 43 ms | 0 -> 1 -> 0 | PASS
LPB-149 | C2S8 - Pin 23 | TBRL-149 (A1/A2) | TBRL-149 (11/14) | JMP-LPB-149 | TBDI-149 (Pin 23) | C2S1 - Pin 23 | 35 ms | 0 -> 1 -> 0 | PASS
LPB-150 | C2S8 - Pin 24 | TBRL-150 (A1/A2) | TBRL-150 (11/14) | JMP-LPB-150 | TBDI-150 (Pin 24) | C2S1 - Pin 24 | 41 ms | 0 -> 1 -> 0 | PASS
LPB-151 | C2S8 - Pin 25 | TBRL-151 (A1/A2) | TBRL-151 (11/14) | JMP-LPB-151 | TBDI-151 (Pin 25) | C2S1 - Pin 25 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-152 | C2S8 - Pin 26 | TBRL-152 (A1/A2) | TBRL-152 (11/14) | JMP-LPB-152 | TBDI-152 (Pin 26) | C2S1 - Pin 26 | 34 ms | 0 -> 1 -> 0 | PASS
LPB-153 | C2S8 - Pin 27 | TBRL-153 (A1/A2) | TBRL-153 (11/14) | JMP-LPB-153 | TBDI-153 (Pin 27) | C2S1 - Pin 27 | 34 ms | 0 -> 1 -> 0 | PASS
LPB-154 | C2S8 - Pin 28 | TBRL-154 (A1/A2) | TBRL-154 (11/14) | JMP-LPB-154 | TBDI-154 (Pin 28) | C2S1 - Pin 28 | 41 ms | 0 -> 1 -> 0 | PASS
LPB-155 | C2S8 - Pin 29 | TBRL-155 (A1/A2) | TBRL-155 (11/14) | JMP-LPB-155 | TBDI-155 (Pin 29) | C2S1 - Pin 29 | 36 ms | 0 -> 1 -> 0 | PASS
LPB-156 | C2S8 - Pin 30 | TBRL-156 (A1/A2) | TBRL-156 (11/14) | JMP-LPB-156 | TBDI-156 (Pin 30) | C2S1 - Pin 30 | 38 ms | 0 -> 1 -> 0 | PASS
LPB-157 | C2S8 - Pin 31 | TBRL-157 (A1/A2) | TBRL-157 (11/14) | JMP-LPB-157 | TBDI-157 (Pin 31) | C2S1 - Pin 31 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-158 | C2S8 - Pin 32 | TBRL-158 (A1/A2) | TBRL-158 (11/14) | JMP-LPB-158 | TBDI-158 (Pin 32) | C2S1 - Pin 32 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-159 | C2S8 - Pin 33 | TBRL-159 (A1/A2) | TBRL-159 (11/14) | JMP-LPB-159 | TBDI-159 (Pin 33) | C2S1 - Pin 33 | 22 ms | 0 -> 1 -> 0 | PASS
LPB-160 | C2S8 - Pin 34 | TBRL-160 (A1/A2) | TBRL-160 (11/14) | JMP-LPB-160 | TBDI-160 (Pin 34) | C2S1 - Pin 34 | 43 ms | 0 -> 1 -> 0 | PASS
LPB-161 | C3S4 - Pin 1 | TBRL-161 (A1/A2) | TBRL-161 (11/14) | JMP-LPB-161 | TBDI-161 (Pin 1) | C2S2 - Pin 1 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-162 | C3S4 - Pin 2 | TBRL-162 (A1/A2) | TBRL-162 (11/14) | JMP-LPB-162 | TBDI-162 (Pin 2) | C2S2 - Pin 2 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-163 | C3S4 - Pin 3 | TBRL-163 (A1/A2) | TBRL-163 (11/14) | JMP-LPB-163 | TBDI-163 (Pin 3) | C2S2 - Pin 3 | 43 ms | 0 -> 1 -> 0 | PASS
LPB-164 | C3S4 - Pin 4 | TBRL-164 (A1/A2) | TBRL-164 (11/14) | JMP-LPB-164 | TBDI-164 (Pin 4) | C2S2 - Pin 4 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-165 | C3S4 - Pin 5 | TBRL-165 (A1/A2) | TBRL-165 (11/14) | JMP-LPB-165 | TBDI-165 (Pin 5) | C2S2 - Pin 5 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-166 | C3S4 - Pin 6 | TBRL-166 (A1/A2) | TBRL-166 (11/14) | JMP-LPB-166 | TBDI-166 (Pin 6) | C2S2 - Pin 6 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-167 | C3S4 - Pin 7 | TBRL-167 (A1/A2) | TBRL-167 (11/14) | JMP-LPB-167 | TBDI-167 (Pin 7) | C2S2 - Pin 7 | 32 ms | 0 -> 1 -> 0 | PASS
LPB-168 | C3S4 - Pin 8 | TBRL-168 (A1/A2) | TBRL-168 (11/14) | JMP-LPB-168 | TBDI-168 (Pin 8) | C2S2 - Pin 8 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-169 | C3S4 - Pin 9 | TBRL-169 (A1/A2) | TBRL-169 (11/14) | JMP-LPB-169 | TBDI-169 (Pin 9) | C2S2 - Pin 9 | 31 ms | 0 -> 1 -> 0 | PASS
LPB-170 | C3S4 - Pin 10 | TBRL-170 (A1/A2) | TBRL-170 (11/14) | JMP-LPB-170 | TBDI-170 (Pin 10) | C2S2 - Pin 10 | 35 ms | 0 -> 1 -> 0 | PASS
LPB-171 | C3S4 - Pin 11 | TBRL-171 (A1/A2) | TBRL-171 (11/14) | JMP-LPB-171 | TBDI-171 (Pin 11) | C2S2 - Pin 11 | 27 ms | 0 -> 1 -> 0 | PASS
LPB-172 | C3S4 - Pin 12 | TBRL-172 (A1/A2) | TBRL-172 (11/14) | JMP-LPB-172 | TBDI-172 (Pin 12) | C2S2 - Pin 12 | 36 ms | 0 -> 1 -> 0 | PASS
LPB-173 | C3S4 - Pin 13 | TBRL-173 (A1/A2) | TBRL-173 (11/14) | JMP-LPB-173 | TBDI-173 (Pin 13) | C2S2 - Pin 13 | 22 ms | 0 -> 1 -> 0 | PASS
LPB-174 | C3S4 - Pin 14 | TBRL-174 (A1/A2) | TBRL-174 (11/14) | JMP-LPB-174 | TBDI-174 (Pin 14) | C2S2 - Pin 14 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-175 | C3S4 - Pin 15 | TBRL-175 (A1/A2) | TBRL-175 (11/14) | JMP-LPB-175 | TBDI-175 (Pin 15) | C2S2 - Pin 15 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-176 | C3S4 - Pin 16 | TBRL-176 (A1/A2) | TBRL-176 (11/14) | JMP-LPB-176 | TBDI-176 (Pin 16) | C2S2 - Pin 16 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-177 | C3S4 - Pin 19 | TBRL-177 (A1/A2) | TBRL-177 (11/14) | JMP-LPB-177 | TBDI-177 (Pin 19) | C2S2 - Pin 19 | 38 ms | 0 -> 1 -> 0 | PASS
LPB-178 | C3S4 - Pin 20 | TBRL-178 (A1/A2) | TBRL-178 (11/14) | JMP-LPB-178 | TBDI-178 (Pin 20) | C2S2 - Pin 20 | 27 ms | 0 -> 1 -> 0 | PASS
LPB-179 | C3S4 - Pin 21 | TBRL-179 (A1/A2) | TBRL-179 (11/14) | JMP-LPB-179 | TBDI-179 (Pin 21) | C2S2 - Pin 21 | 38 ms | 0 -> 1 -> 0 | PASS
LPB-180 | C3S4 - Pin 22 | TBRL-180 (A1/A2) | TBRL-180 (11/14) | JMP-LPB-180 | TBDI-180 (Pin 22) | C2S2 - Pin 22 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-181 | C3S4 - Pin 23 | TBRL-181 (A1/A2) | TBRL-181 (11/14) | JMP-LPB-181 | TBDI-181 (Pin 23) | C2S2 - Pin 23 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-182 | C3S4 - Pin 24 | TBRL-182 (A1/A2) | TBRL-182 (11/14) | JMP-LPB-182 | TBDI-182 (Pin 24) | C2S2 - Pin 24 | 31 ms | 0 -> 1 -> 0 | PASS
LPB-183 | C3S4 - Pin 25 | TBRL-183 (A1/A2) | TBRL-183 (11/14) | JMP-LPB-183 | TBDI-183 (Pin 25) | C2S2 - Pin 25 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-184 | C3S4 - Pin 26 | TBRL-184 (A1/A2) | TBRL-184 (11/14) | JMP-LPB-184 | TBDI-184 (Pin 26) | C2S2 - Pin 26 | 38 ms | 0 -> 1 -> 0 | PASS
LPB-185 | C3S4 - Pin 27 | TBRL-185 (A1/A2) | TBRL-185 (11/14) | JMP-LPB-185 | TBDI-185 (Pin 27) | C2S2 - Pin 27 | 41 ms | 0 -> 1 -> 0 | PASS
LPB-186 | C3S4 - Pin 28 | TBRL-186 (A1/A2) | TBRL-186 (11/14) | JMP-LPB-186 | TBDI-186 (Pin 28) | C2S2 - Pin 28 | 28 ms | 0 -> 1 -> 0 | PASS
LPB-187 | C3S4 - Pin 29 | TBRL-187 (A1/A2) | TBRL-187 (11/14) | JMP-LPB-187 | TBDI-187 (Pin 29) | C2S2 - Pin 29 | 26 ms | 0 -> 1 -> 0 | PASS
LPB-188 | C3S4 - Pin 30 | TBRL-188 (A1/A2) | TBRL-188 (11/14) | JMP-LPB-188 | TBDI-188 (Pin 30) | C2S2 - Pin 30 | 33 ms | 0 -> 1 -> 0 | PASS
LPB-189 | C3S4 - Pin 31 | TBRL-189 (A1/A2) | TBRL-189 (11/14) | JMP-LPB-189 | TBDI-189 (Pin 31) | C2S2 - Pin 31 | 27 ms | 0 -> 1 -> 0 | PASS
LPB-190 | C3S4 - Pin 32 | TBRL-190 (A1/A2) | TBRL-190 (11/14) | JMP-LPB-190 | TBDI-190 (Pin 32) | C2S2 - Pin 32 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-191 | C3S4 - Pin 33 | TBRL-191 (A1/A2) | TBRL-191 (11/14) | JMP-LPB-191 | TBDI-191 (Pin 33) | C2S2 - Pin 33 | 38 ms | 0 -> 1 -> 0 | PASS
LPB-192 | C3S4 - Pin 34 | TBRL-192 (A1/A2) | TBRL-192 (11/14) | JMP-LPB-192 | TBDI-192 (Pin 34) | C2S2 - Pin 34 | 22 ms | 0 -> 1 -> 0 | PASS
LPB-193 | C3S5 - Pin 1 | TBRL-193 (A1/A2) | TBRL-193 (11/14) | JMP-LPB-193 | TBDI-193 (Pin 1) | C2S3 - Pin 1 | 41 ms | 0 -> 1 -> 0 | PASS
LPB-194 | C3S5 - Pin 2 | TBRL-194 (A1/A2) | TBRL-194 (11/14) | JMP-LPB-194 | TBDI-194 (Pin 2) | C2S3 - Pin 2 | 32 ms | 0 -> 1 -> 0 | PASS
LPB-195 | C3S5 - Pin 3 | TBRL-195 (A1/A2) | TBRL-195 (11/14) | JMP-LPB-195 | TBDI-195 (Pin 3) | C2S3 - Pin 3 | 37 ms | 0 -> 1 -> 0 | PASS
LPB-196 | C3S5 - Pin 4 | TBRL-196 (A1/A2) | TBRL-196 (11/14) | JMP-LPB-196 | TBDI-196 (Pin 4) | C2S3 - Pin 4 | 22 ms | 0 -> 1 -> 0 | PASS
LPB-197 | C3S5 - Pin 5 | TBRL-197 (A1/A2) | TBRL-197 (11/14) | JMP-LPB-197 | TBDI-197 (Pin 5) | C2S3 - Pin 5 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-198 | C3S5 - Pin 6 | TBRL-198 (A1/A2) | TBRL-198 (11/14) | JMP-LPB-198 | TBDI-198 (Pin 6) | C2S3 - Pin 6 | 33 ms | 0 -> 1 -> 0 | PASS
LPB-199 | C3S5 - Pin 7 | TBRL-199 (A1/A2) | TBRL-199 (11/14) | JMP-LPB-199 | TBDI-199 (Pin 7) | C2S3 - Pin 7 | 31 ms | 0 -> 1 -> 0 | PASS
LPB-200 | C3S5 - Pin 8 | TBRL-200 (A1/A2) | TBRL-200 (11/14) | JMP-LPB-200 | TBDI-200 (Pin 8) | C2S3 - Pin 8 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-201 | C3S5 - Pin 9 | TBRL-201 (A1/A2) | TBRL-201 (11/14) | JMP-LPB-201 | TBDI-201 (Pin 9) | C2S3 - Pin 9 | 23 ms | 0 -> 1 -> 0 | PASS
LPB-202 | C3S5 - Pin 10 | TBRL-202 (A1/A2) | TBRL-202 (11/14) | JMP-LPB-202 | TBDI-202 (Pin 10) | C2S3 - Pin 10 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-203 | C3S5 - Pin 11 | TBRL-203 (A1/A2) | TBRL-203 (11/14) | JMP-LPB-203 | TBDI-203 (Pin 11) | C2S3 - Pin 11 | 40 ms | 0 -> 1 -> 0 | PASS
LPB-204 | C3S5 - Pin 12 | TBRL-204 (A1/A2) | TBRL-204 (11/14) | JMP-LPB-204 | TBDI-204 (Pin 12) | C2S3 - Pin 12 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-205 | C3S5 - Pin 13 | TBRL-205 (A1/A2) | TBRL-205 (11/14) | JMP-LPB-205 | TBDI-205 (Pin 13) | C2S3 - Pin 13 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-206 | C3S5 - Pin 14 | TBRL-206 (A1/A2) | TBRL-206 (11/14) | JMP-LPB-206 | TBDI-206 (Pin 14) | C2S3 - Pin 14 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-207 | C3S5 - Pin 15 | TBRL-207 (A1/A2) | TBRL-207 (11/14) | JMP-LPB-207 | TBDI-207 (Pin 15) | C2S3 - Pin 15 | 37 ms | 0 -> 1 -> 0 | PASS
LPB-208 | C3S5 - Pin 16 | TBRL-208 (A1/A2) | TBRL-208 (11/14) | JMP-LPB-208 | TBDI-208 (Pin 16) | C2S3 - Pin 16 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-209 | C3S5 - Pin 19 | TBRL-209 (A1/A2) | TBRL-209 (11/14) | JMP-LPB-209 | TBDI-209 (Pin 19) | C2S3 - Pin 19 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-210 | C3S5 - Pin 20 | TBRL-210 (A1/A2) | TBRL-210 (11/14) | JMP-LPB-210 | TBDI-210 (Pin 20) | C2S3 - Pin 20 | 26 ms | 0 -> 1 -> 0 | PASS
LPB-211 | C3S5 - Pin 21 | TBRL-211 (A1/A2) | TBRL-211 (11/14) | JMP-LPB-211 | TBDI-211 (Pin 21) | C2S3 - Pin 21 | 26 ms | 0 -> 1 -> 0 | PASS
LPB-212 | C3S5 - Pin 22 | TBRL-212 (A1/A2) | TBRL-212 (11/14) | JMP-LPB-212 | TBDI-212 (Pin 22) | C2S3 - Pin 22 | 43 ms | 0 -> 1 -> 0 | PASS
LPB-213 | C3S5 - Pin 23 | TBRL-213 (A1/A2) | TBRL-213 (11/14) | JMP-LPB-213 | TBDI-213 (Pin 23) | C2S3 - Pin 23 | 37 ms | 0 -> 1 -> 0 | PASS
LPB-214 | C3S5 - Pin 24 | TBRL-214 (A1/A2) | TBRL-214 (11/14) | JMP-LPB-214 | TBDI-214 (Pin 24) | C2S3 - Pin 24 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-215 | C3S5 - Pin 25 | TBRL-215 (A1/A2) | TBRL-215 (11/14) | JMP-LPB-215 | TBDI-215 (Pin 25) | C2S3 - Pin 25 | 27 ms | 0 -> 1 -> 0 | PASS
LPB-216 | C3S5 - Pin 26 | TBRL-216 (A1/A2) | TBRL-216 (11/14) | JMP-LPB-216 | TBDI-216 (Pin 26) | C2S3 - Pin 26 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-217 | C3S5 - Pin 27 | TBRL-217 (A1/A2) | TBRL-217 (11/14) | JMP-LPB-217 | TBDI-217 (Pin 27) | C2S3 - Pin 27 | 38 ms | 0 -> 1 -> 0 | PASS
LPB-218 | C3S5 - Pin 28 | TBRL-218 (A1/A2) | TBRL-218 (11/14) | JMP-LPB-218 | TBDI-218 (Pin 28) | C2S3 - Pin 28 | 41 ms | 0 -> 1 -> 0 | PASS
LPB-219 | C3S5 - Pin 29 | TBRL-219 (A1/A2) | TBRL-219 (11/14) | JMP-LPB-219 | TBDI-219 (Pin 29) | C2S3 - Pin 29 | 35 ms | 0 -> 1 -> 0 | PASS
LPB-220 | C3S5 - Pin 30 | TBRL-220 (A1/A2) | TBRL-220 (11/14) | JMP-LPB-220 | TBDI-220 (Pin 30) | C2S3 - Pin 30 | 28 ms | 0 -> 1 -> 0 | PASS
LPB-221 | C3S5 - Pin 31 | TBRL-221 (A1/A2) | TBRL-221 (11/14) | JMP-LPB-221 | TBDI-221 (Pin 31) | C2S3 - Pin 31 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-222 | C3S5 - Pin 32 | TBRL-222 (A1/A2) | TBRL-222 (11/14) | JMP-LPB-222 | TBDI-222 (Pin 32) | C2S3 - Pin 32 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-223 | C3S5 - Pin 33 | TBRL-223 (A1/A2) | TBRL-223 (11/14) | JMP-LPB-223 | TBDI-223 (Pin 33) | C2S3 - Pin 33 | 44 ms | 0 -> 1 -> 0 | PASS
LPB-224 | C3S5 - Pin 34 | TBRL-224 (A1/A2) | TBRL-224 (11/14) | JMP-LPB-224 | TBDI-224 (Pin 34) | C2S3 - Pin 34 | 28 ms | 0 -> 1 -> 0 | PASS
LPB-225 | C4S4 - Pin 1 | TBRL-225 (A1/A2) | TBRL-225 (11/14) | JMP-LPB-225 | TBDI-225 (Pin 1) | C2S4 - Pin 1 | 44 ms | 0 -> 1 -> 0 | PASS
LPB-226 | C4S4 - Pin 2 | TBRL-226 (A1/A2) | TBRL-226 (11/14) | JMP-LPB-226 | TBDI-226 (Pin 2) | C2S4 - Pin 2 | 31 ms | 0 -> 1 -> 0 | PASS
LPB-227 | C4S4 - Pin 3 | TBRL-227 (A1/A2) | TBRL-227 (11/14) | JMP-LPB-227 | TBDI-227 (Pin 3) | C2S4 - Pin 3 | 34 ms | 0 -> 1 -> 0 | PASS
LPB-228 | C4S4 - Pin 4 | TBRL-228 (A1/A2) | TBRL-228 (11/14) | JMP-LPB-228 | TBDI-228 (Pin 4) | C2S4 - Pin 4 | 43 ms | 0 -> 1 -> 0 | PASS
LPB-229 | C4S4 - Pin 5 | TBRL-229 (A1/A2) | TBRL-229 (11/14) | JMP-LPB-229 | TBDI-229 (Pin 5) | C2S4 - Pin 5 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-230 | C4S4 - Pin 6 | TBRL-230 (A1/A2) | TBRL-230 (11/14) | JMP-LPB-230 | TBDI-230 (Pin 6) | C2S4 - Pin 6 | 33 ms | 0 -> 1 -> 0 | PASS
LPB-231 | C4S4 - Pin 7 | TBRL-231 (A1/A2) | TBRL-231 (11/14) | JMP-LPB-231 | TBDI-231 (Pin 7) | C2S4 - Pin 7 | 36 ms | 0 -> 1 -> 0 | PASS
LPB-232 | C4S4 - Pin 8 | TBRL-232 (A1/A2) | TBRL-232 (11/14) | JMP-LPB-232 | TBDI-232 (Pin 8) | C2S4 - Pin 8 | 38 ms | 0 -> 1 -> 0 | PASS
LPB-233 | C4S4 - Pin 9 | TBRL-233 (A1/A2) | TBRL-233 (11/14) | JMP-LPB-233 | TBDI-233 (Pin 9) | C2S4 - Pin 9 | 36 ms | 0 -> 1 -> 0 | PASS
LPB-234 | C4S4 - Pin 10 | TBRL-234 (A1/A2) | TBRL-234 (11/14) | JMP-LPB-234 | TBDI-234 (Pin 10) | C2S4 - Pin 10 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-235 | C4S4 - Pin 11 | TBRL-235 (A1/A2) | TBRL-235 (11/14) | JMP-LPB-235 | TBDI-235 (Pin 11) | C2S4 - Pin 11 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-236 | C4S4 - Pin 12 | TBRL-236 (A1/A2) | TBRL-236 (11/14) | JMP-LPB-236 | TBDI-236 (Pin 12) | C2S4 - Pin 12 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-237 | C4S4 - Pin 13 | TBRL-237 (A1/A2) | TBRL-237 (11/14) | JMP-LPB-237 | TBDI-237 (Pin 13) | C2S4 - Pin 13 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-238 | C4S4 - Pin 14 | TBRL-238 (A1/A2) | TBRL-238 (11/14) | JMP-LPB-238 | TBDI-238 (Pin 14) | C2S4 - Pin 14 | 32 ms | 0 -> 1 -> 0 | PASS
LPB-239 | C4S4 - Pin 15 | TBRL-239 (A1/A2) | TBRL-239 (11/14) | JMP-LPB-239 | TBDI-239 (Pin 15) | C2S4 - Pin 15 | 22 ms | 0 -> 1 -> 0 | PASS
LPB-240 | C4S4 - Pin 16 | TBRL-240 (A1/A2) | TBRL-240 (11/14) | JMP-LPB-240 | TBDI-240 (Pin 16) | C2S4 - Pin 16 | 40 ms | 0 -> 1 -> 0 | PASS
LPB-241 | C4S4 - Pin 19 | TBRL-241 (A1/A2) | TBRL-241 (11/14) | JMP-LPB-241 | TBDI-241 (Pin 19) | C2S4 - Pin 19 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-242 | C4S4 - Pin 20 | TBRL-242 (A1/A2) | TBRL-242 (11/14) | JMP-LPB-242 | TBDI-242 (Pin 20) | C2S4 - Pin 20 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-243 | C4S4 - Pin 21 | TBRL-243 (A1/A2) | TBRL-243 (11/14) | JMP-LPB-243 | TBDI-243 (Pin 21) | C2S4 - Pin 21 | 40 ms | 0 -> 1 -> 0 | PASS
LPB-244 | C4S4 - Pin 22 | TBRL-244 (A1/A2) | TBRL-244 (11/14) | JMP-LPB-244 | TBDI-244 (Pin 22) | C2S4 - Pin 22 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-245 | C4S4 - Pin 23 | TBRL-245 (A1/A2) | TBRL-245 (11/14) | JMP-LPB-245 | TBDI-245 (Pin 23) | C2S4 - Pin 23 | 22 ms | 0 -> 1 -> 0 | PASS
LPB-246 | C4S4 - Pin 24 | TBRL-246 (A1/A2) | TBRL-246 (11/14) | JMP-LPB-246 | TBDI-246 (Pin 24) | C2S4 - Pin 24 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-247 | C4S4 - Pin 25 | TBRL-247 (A1/A2) | TBRL-247 (11/14) | JMP-LPB-247 | TBDI-247 (Pin 25) | C2S4 - Pin 25 | 44 ms | 0 -> 1 -> 0 | PASS
LPB-248 | C4S4 - Pin 26 | TBRL-248 (A1/A2) | TBRL-248 (11/14) | JMP-LPB-248 | TBDI-248 (Pin 26) | C2S4 - Pin 26 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-249 | C4S4 - Pin 27 | TBRL-249 (A1/A2) | TBRL-249 (11/14) | JMP-LPB-249 | TBDI-249 (Pin 27) | C2S4 - Pin 27 | 23 ms | 0 -> 1 -> 0 | PASS
LPB-250 | C4S4 - Pin 28 | TBRL-250 (A1/A2) | TBRL-250 (11/14) | JMP-LPB-250 | TBDI-250 (Pin 28) | C2S4 - Pin 28 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-251 | C4S4 - Pin 29 | TBRL-251 (A1/A2) | TBRL-251 (11/14) | JMP-LPB-251 | TBDI-251 (Pin 29) | C2S4 - Pin 29 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-252 | C4S4 - Pin 30 | TBRL-252 (A1/A2) | TBRL-252 (11/14) | JMP-LPB-252 | TBDI-252 (Pin 30) | C2S4 - Pin 30 | 23 ms | 0 -> 1 -> 0 | PASS
LPB-253 | C4S4 - Pin 31 | TBRL-253 (A1/A2) | TBRL-253 (11/14) | JMP-LPB-253 | TBDI-253 (Pin 31) | C2S4 - Pin 31 | 32 ms | 0 -> 1 -> 0 | PASS
LPB-254 | C4S4 - Pin 32 | TBRL-254 (A1/A2) | TBRL-254 (11/14) | JMP-LPB-254 | TBDI-254 (Pin 32) | C2S4 - Pin 32 | 24 ms | 0 -> 1 -> 0 | PASS
LPB-255 | C4S4 - Pin 33 | TBRL-255 (A1/A2) | TBRL-255 (11/14) | JMP-LPB-255 | TBDI-255 (Pin 33) | C2S4 - Pin 33 | 38 ms | 0 -> 1 -> 0 | PASS
LPB-256 | C4S4 - Pin 34 | TBRL-256 (A1/A2) | TBRL-256 (11/14) | JMP-LPB-256 | TBDI-256 (Pin 34) | C2S4 - Pin 34 | 29 ms | 0 -> 1 -> 0 | PASS