## C1_Executive_Summary
CHASSIS C1 DI/DO FACTORY ACCEPTANCE TEST (FAT) MASTER REPORT
Project: SPRINT 18K Spray Dryer ¦ Target: MCP-01 Chassis C1 ¦ Document: KAL-FAT-TR-C1-2608 ¦ Rev 1.0
TOTAL CHANNELS |  | PASSED CHANNELS |  | FAILED CHANNELS |  | AVG SWITCH LATENCY
192 |  | 192 (100%) |  | 0 (0.0%) |  | 28.9 ms
64 DO + 128 DI Channels |  | Zero Faults Detected |  | 100% Signal Integrity |  | Standard Spec: < 200 ms
1. CHASSIS C1 HARDWARE CONFIGURATION & TEST COVERAGE
Slot # | Module Model | Description / Function | Channel Count | Field Destination | FAT Test Methodology | Test Status | Verdict
C1S0 | 1756-L950TPSXT | ControlLogix 5580 Master Processor (20MB) | 1x CPU | Central Area (CA1) | Firmware v34, memory & CPU diagnostics | 100% Verified | PASS
C1S1 | 1756-EN4TR | EtherNet/IP 1Gbps DLR Supervisor Port | 2x DLR Ports | DLR Ring & Cisco 9300 | Ring break recovery test (<3ms) | 100% Verified | PASS
C1S2 | 1756-EN4TR | EtherNet/IP 1Gbps Plant Network Uplink | 2x Ports | Plant Core Backbone | VLAN tagging & HSRP ping test | 100% Verified | PASS
C1S3 | 1756-EN4TR | EtherNet/IP 1Gbps SCADA Communication | 2x Ports | FactoryTalk View SE Server | SCADA poll rate & packet latency check | 100% Verified | PASS
C1S4 | 1756-IB32 | 24VDC Digital Input Module (DI Group 1) | 32 Channels | CA1, JB-401 (TBDI1) | Closed-Loop Cross-Wiring from C1S8 Relays | 32/32 Tested | PASS
C1S5 | 1756-IB32 | 24VDC Digital Input Module (DI Group 2) | 32 Channels | JB-401 (TBDI2) | Closed-Loop Cross-Wiring from C1S9 Relays | 32/32 Tested | PASS
C1S6 | 1756-IB32 | 24VDC Digital Input Module (DI Group 3) | 32 Channels | JB-401, JB-601 (TBDI3) | Direct 24VDC Dry Contact Simulation | 32/32 Tested | PASS
C1S7 | 1756-IB32 | 24VDC Digital Input Module (DI Group 4) | 32 Channels | JB-601 (TBDI4) | Direct 24VDC Dry Contact Simulation | 32/32 Tested | PASS
C1S8 | 1756-OB32 | 24VDC Digital Output Module (DO Group 1) | 32 Channels | Relays P1-TBRL1 (1-32) | Force DO -> Relay A1 -> NO 11/14 -> C1S4 | 32/32 Tested | PASS
C1S9 | 1756-OB32 | 24VDC Digital Output Module (DO Group 2) | 32 Channels | Relays P1-TBRL2 (1-32) | Force DO -> Relay A1 -> NO 11/14 -> C1S5 | 32/32 Tested | PASS
C1S10 | 1756-IF16 | Analog Input 4-20mA (Slurry & Spray Feed) | 16 Channels | JB-401 (TBAI1) | Differential 5-Point Calibration (Fluke 789) | 16/16 Tested | PASS
C1S11 | 1756-IF16 | Analog Input 4-20mA (Burner & Chamber Temp) | 16 Channels | JB-601 (TBAI2) | Differential 5-Point Calibration (Fluke 789) | 16/16 Tested | PASS
C1S12 | 1756-N2 | Unpopulated Slot Position | - | Spare Slot | Slot Cover Installed | N/A | PASS

## C1_DIDO_Loopback_Test
CHASSIS C1 — DI/DO CLOSED-LOOP CROSS-WIRING VERIFICATION (64 LOOPS)
Verification: C1S8 DO -> P1-TBRL1 Relay -> C1S4 DI (Loops 1-32) ¦ C1S9 DO -> P1-TBRL2 Relay -> C1S5 DI (Loops 33-64)
Loop # | DO Slot & Pin | Interposing Relay Coil | Relay Contact NO | Temp Jumper Wire | Target DI Terminal | DI Slot & Pin | Switch Latency | Logic State Transition | Verdict
C1-LPB-001 | C1S8.1 | P1-TBRL-1 (A1/A2) | P1-TBRL-1 (11/14) | TMP-JMP-001 | P1-TBDI-1 (Pin 1) | C1S4.1 | 40 ms | 0 -> 1 -> 0 | PASS
C1-LPB-002 | C1S8.2 | P1-TBRL-2 (A1/A2) | P1-TBRL-2 (11/14) | TMP-JMP-002 | P1-TBDI-2 (Pin 2) | C1S4.2 | 28 ms | 0 -> 1 -> 0 | PASS
C1-LPB-003 | C1S8.3 | P1-TBRL-3 (A1/A2) | P1-TBRL-3 (11/14) | TMP-JMP-003 | P1-TBDI-3 (Pin 3) | C1S4.3 | 39 ms | 0 -> 1 -> 0 | PASS
C1-LPB-004 | C1S8.4 | P1-TBRL-4 (A1/A2) | P1-TBRL-4 (11/14) | TMP-JMP-004 | P1-TBDI-4 (Pin 4) | C1S4.4 | 33 ms | 0 -> 1 -> 0 | PASS
C1-LPB-005 | C1S8.5 | P1-TBRL-5 (A1/A2) | P1-TBRL-5 (11/14) | TMP-JMP-005 | P1-TBDI-5 (Pin 5) | C1S4.5 | 36 ms | 0 -> 1 -> 0 | PASS
C1-LPB-006 | C1S8.6 | P1-TBRL-6 (A1/A2) | P1-TBRL-6 (11/14) | TMP-JMP-006 | P1-TBDI-6 (Pin 6) | C1S4.6 | 23 ms | 0 -> 1 -> 0 | PASS
C1-LPB-007 | C1S8.7 | P1-TBRL-7 (A1/A2) | P1-TBRL-7 (11/14) | TMP-JMP-007 | P1-TBDI-7 (Pin 7) | C1S4.7 | 38 ms | 0 -> 1 -> 0 | PASS
C1-LPB-008 | C1S8.8 | P1-TBRL-8 (A1/A2) | P1-TBRL-8 (11/14) | TMP-JMP-008 | P1-TBDI-8 (Pin 8) | C1S4.8 | 28 ms | 0 -> 1 -> 0 | PASS
C1-LPB-009 | C1S8.9 | P1-TBRL-9 (A1/A2) | P1-TBRL-9 (11/14) | TMP-JMP-009 | P1-TBDI-9 (Pin 9) | C1S4.9 | 41 ms | 0 -> 1 -> 0 | PASS
C1-LPB-010 | C1S8.10 | P1-TBRL-10 (A1/A2) | P1-TBRL-10 (11/14) | TMP-JMP-010 | P1-TBDI-10 (Pin 10) | C1S4.10 | 29 ms | 0 -> 1 -> 0 | PASS
C1-LPB-011 | C1S8.11 | P1-TBRL-11 (A1/A2) | P1-TBRL-11 (11/14) | TMP-JMP-011 | P1-TBDI-11 (Pin 11) | C1S4.11 | 31 ms | 0 -> 1 -> 0 | PASS
C1-LPB-012 | C1S8.12 | P1-TBRL-12 (A1/A2) | P1-TBRL-12 (11/14) | TMP-JMP-012 | P1-TBDI-12 (Pin 12) | C1S4.12 | 37 ms | 0 -> 1 -> 0 | PASS
C1-LPB-013 | C1S8.13 | P1-TBRL-13 (A1/A2) | P1-TBRL-13 (11/14) | TMP-JMP-013 | P1-TBDI-13 (Pin 13) | C1S4.13 | 28 ms | 0 -> 1 -> 0 | PASS
C1-LPB-014 | C1S8.14 | P1-TBRL-14 (A1/A2) | P1-TBRL-14 (11/14) | TMP-JMP-014 | P1-TBDI-14 (Pin 14) | C1S4.14 | 32 ms | 0 -> 1 -> 0 | PASS
C1-LPB-015 | C1S8.15 | P1-TBRL-15 (A1/A2) | P1-TBRL-15 (11/14) | TMP-JMP-015 | P1-TBDI-15 (Pin 15) | C1S4.15 | 36 ms | 0 -> 1 -> 0 | PASS
C1-LPB-016 | C1S8.16 | P1-TBRL-16 (A1/A2) | P1-TBRL-16 (11/14) | TMP-JMP-016 | P1-TBDI-16 (Pin 16) | C1S4.16 | 24 ms | 0 -> 1 -> 0 | PASS
C1-LPB-017 | C1S8.19 | P1-TBRL-17 (A1/A2) | P1-TBRL-17 (11/14) | TMP-JMP-017 | P1-TBDI-17 (Pin 19) | C1S4.19 | 30 ms | 0 -> 1 -> 0 | PASS
C1-LPB-018 | C1S8.20 | P1-TBRL-18 (A1/A2) | P1-TBRL-18 (11/14) | TMP-JMP-018 | P1-TBDI-18 (Pin 20) | C1S4.20 | 28 ms | 0 -> 1 -> 0 | PASS
C1-LPB-019 | C1S8.21 | P1-TBRL-19 (A1/A2) | P1-TBRL-19 (11/14) | TMP-JMP-019 | P1-TBDI-19 (Pin 21) | C1S4.21 | 27 ms | 0 -> 1 -> 0 | PASS
C1-LPB-020 | C1S8.22 | P1-TBRL-20 (A1/A2) | P1-TBRL-20 (11/14) | TMP-JMP-020 | P1-TBDI-20 (Pin 22) | C1S4.22 | 24 ms | 0 -> 1 -> 0 | PASS
C1-LPB-021 | C1S8.23 | P1-TBRL-21 (A1/A2) | P1-TBRL-21 (11/14) | TMP-JMP-021 | P1-TBDI-21 (Pin 23) | C1S4.23 | 36 ms | 0 -> 1 -> 0 | PASS
C1-LPB-022 | C1S8.24 | P1-TBRL-22 (A1/A2) | P1-TBRL-22 (11/14) | TMP-JMP-022 | P1-TBDI-22 (Pin 24) | C1S4.24 | 39 ms | 0 -> 1 -> 0 | PASS
C1-LPB-023 | C1S8.25 | P1-TBRL-23 (A1/A2) | P1-TBRL-23 (11/14) | TMP-JMP-023 | P1-TBDI-23 (Pin 25) | C1S4.25 | 33 ms | 0 -> 1 -> 0 | PASS
C1-LPB-024 | C1S8.26 | P1-TBRL-24 (A1/A2) | P1-TBRL-24 (11/14) | TMP-JMP-024 | P1-TBDI-24 (Pin 26) | C1S4.26 | 28 ms | 0 -> 1 -> 0 | PASS
C1-LPB-025 | C1S8.27 | P1-TBRL-25 (A1/A2) | P1-TBRL-25 (11/14) | TMP-JMP-025 | P1-TBDI-25 (Pin 27) | C1S4.27 | 37 ms | 0 -> 1 -> 0 | PASS
C1-LPB-026 | C1S8.28 | P1-TBRL-26 (A1/A2) | P1-TBRL-26 (11/14) | TMP-JMP-026 | P1-TBDI-26 (Pin 28) | C1S4.28 | 32 ms | 0 -> 1 -> 0 | PASS
C1-LPB-027 | C1S8.29 | P1-TBRL-27 (A1/A2) | P1-TBRL-27 (11/14) | TMP-JMP-027 | P1-TBDI-27 (Pin 29) | C1S4.29 | 29 ms | 0 -> 1 -> 0 | PASS
C1-LPB-028 | C1S8.30 | P1-TBRL-28 (A1/A2) | P1-TBRL-28 (11/14) | TMP-JMP-028 | P1-TBDI-28 (Pin 30) | C1S4.30 | 42 ms | 0 -> 1 -> 0 | PASS
C1-LPB-029 | C1S8.31 | P1-TBRL-29 (A1/A2) | P1-TBRL-29 (11/14) | TMP-JMP-029 | P1-TBDI-29 (Pin 31) | C1S4.31 | 34 ms | 0 -> 1 -> 0 | PASS
C1-LPB-030 | C1S8.32 | P1-TBRL-30 (A1/A2) | P1-TBRL-30 (11/14) | TMP-JMP-030 | P1-TBDI-30 (Pin 32) | C1S4.32 | 35 ms | 0 -> 1 -> 0 | PASS
C1-LPB-031 | C1S8.33 | P1-TBRL-31 (A1/A2) | P1-TBRL-31 (11/14) | TMP-JMP-031 | P1-TBDI-31 (Pin 33) | C1S4.33 | 28 ms | 0 -> 1 -> 0 | PASS
C1-LPB-032 | C1S8.34 | P1-TBRL-32 (A1/A2) | P1-TBRL-32 (11/14) | TMP-JMP-032 | P1-TBDI-32 (Pin 34) | C1S4.34 | 24 ms | 0 -> 1 -> 0 | PASS
C1-LPB-033 | C1S9.1 | P1-TBRL-33 (A1/A2) | P1-TBRL-33 (11/14) | TMP-JMP-033 | P1-TBDI-33 (Pin 1) | C1S5.1 | 35 ms | 0 -> 1 -> 0 | PASS
C1-LPB-034 | C1S9.2 | P1-TBRL-34 (A1/A2) | P1-TBRL-34 (11/14) | TMP-JMP-034 | P1-TBDI-34 (Pin 2) | C1S5.2 | 36 ms | 0 -> 1 -> 0 | PASS
C1-LPB-035 | C1S9.3 | P1-TBRL-35 (A1/A2) | P1-TBRL-35 (11/14) | TMP-JMP-035 | P1-TBDI-35 (Pin 3) | C1S5.3 | 31 ms | 0 -> 1 -> 0 | PASS
C1-LPB-036 | C1S9.4 | P1-TBRL-36 (A1/A2) | P1-TBRL-36 (11/14) | TMP-JMP-036 | P1-TBDI-36 (Pin 4) | C1S5.4 | 28 ms | 0 -> 1 -> 0 | PASS
C1-LPB-037 | C1S9.5 | P1-TBRL-37 (A1/A2) | P1-TBRL-37 (11/14) | TMP-JMP-037 | P1-TBDI-37 (Pin 5) | C1S5.5 | 25 ms | 0 -> 1 -> 0 | PASS
C1-LPB-038 | C1S9.6 | P1-TBRL-38 (A1/A2) | P1-TBRL-38 (11/14) | TMP-JMP-038 | P1-TBDI-38 (Pin 6) | C1S5.6 | 42 ms | 0 -> 1 -> 0 | PASS
C1-LPB-039 | C1S9.7 | P1-TBRL-39 (A1/A2) | P1-TBRL-39 (11/14) | TMP-JMP-039 | P1-TBDI-39 (Pin 7) | C1S5.7 | 41 ms | 0 -> 1 -> 0 | PASS
C1-LPB-040 | C1S9.8 | P1-TBRL-40 (A1/A2) | P1-TBRL-40 (11/14) | TMP-JMP-040 | P1-TBDI-40 (Pin 8) | C1S5.8 | 32 ms | 0 -> 1 -> 0 | PASS
C1-LPB-041 | C1S9.9 | P1-TBRL-41 (A1/A2) | P1-TBRL-41 (11/14) | TMP-JMP-041 | P1-TBDI-41 (Pin 9) | C1S5.9 | 30 ms | 0 -> 1 -> 0 | PASS
C1-LPB-042 | C1S9.10 | P1-TBRL-42 (A1/A2) | P1-TBRL-42 (11/14) | TMP-JMP-042 | P1-TBDI-42 (Pin 10) | C1S5.10 | 34 ms | 0 -> 1 -> 0 | PASS
C1-LPB-043 | C1S9.11 | P1-TBRL-43 (A1/A2) | P1-TBRL-43 (11/14) | TMP-JMP-043 | P1-TBDI-43 (Pin 11) | C1S5.11 | 34 ms | 0 -> 1 -> 0 | PASS
C1-LPB-044 | C1S9.12 | P1-TBRL-44 (A1/A2) | P1-TBRL-44 (11/14) | TMP-JMP-044 | P1-TBDI-44 (Pin 12) | C1S5.12 | 29 ms | 0 -> 1 -> 0 | PASS
C1-LPB-045 | C1S9.13 | P1-TBRL-45 (A1/A2) | P1-TBRL-45 (11/14) | TMP-JMP-045 | P1-TBDI-45 (Pin 13) | C1S5.13 | 35 ms | 0 -> 1 -> 0 | PASS
C1-LPB-046 | C1S9.14 | P1-TBRL-46 (A1/A2) | P1-TBRL-46 (11/14) | TMP-JMP-046 | P1-TBDI-46 (Pin 14) | C1S5.14 | 24 ms | 0 -> 1 -> 0 | PASS
C1-LPB-047 | C1S9.15 | P1-TBRL-47 (A1/A2) | P1-TBRL-47 (11/14) | TMP-JMP-047 | P1-TBDI-47 (Pin 15) | C1S5.15 | 34 ms | 0 -> 1 -> 0 | PASS
C1-LPB-048 | C1S9.16 | P1-TBRL-48 (A1/A2) | P1-TBRL-48 (11/14) | TMP-JMP-048 | P1-TBDI-48 (Pin 16) | C1S5.16 | 35 ms | 0 -> 1 -> 0 | PASS
C1-LPB-049 | C1S9.19 | P1-TBRL-49 (A1/A2) | P1-TBRL-49 (11/14) | TMP-JMP-049 | P1-TBDI-49 (Pin 19) | C1S5.19 | 22 ms | 0 -> 1 -> 0 | PASS
C1-LPB-050 | C1S9.20 | P1-TBRL-50 (A1/A2) | P1-TBRL-50 (11/14) | TMP-JMP-050 | P1-TBDI-50 (Pin 20) | C1S5.20 | 36 ms | 0 -> 1 -> 0 | PASS
C1-LPB-051 | C1S9.21 | P1-TBRL-51 (A1/A2) | P1-TBRL-51 (11/14) | TMP-JMP-051 | P1-TBDI-51 (Pin 21) | C1S5.21 | 28 ms | 0 -> 1 -> 0 | PASS
C1-LPB-052 | C1S9.22 | P1-TBRL-52 (A1/A2) | P1-TBRL-52 (11/14) | TMP-JMP-052 | P1-TBDI-52 (Pin 22) | C1S5.22 | 39 ms | 0 -> 1 -> 0 | PASS
C1-LPB-053 | C1S9.23 | P1-TBRL-53 (A1/A2) | P1-TBRL-53 (11/14) | TMP-JMP-053 | P1-TBDI-53 (Pin 23) | C1S5.23 | 25 ms | 0 -> 1 -> 0 | PASS
C1-LPB-054 | C1S9.24 | P1-TBRL-54 (A1/A2) | P1-TBRL-54 (11/14) | TMP-JMP-054 | P1-TBDI-54 (Pin 24) | C1S5.24 | 33 ms | 0 -> 1 -> 0 | PASS
C1-LPB-055 | C1S9.25 | P1-TBRL-55 (A1/A2) | P1-TBRL-55 (11/14) | TMP-JMP-055 | P1-TBDI-55 (Pin 25) | C1S5.25 | 22 ms | 0 -> 1 -> 0 | PASS
C1-LPB-056 | C1S9.26 | P1-TBRL-56 (A1/A2) | P1-TBRL-56 (11/14) | TMP-JMP-056 | P1-TBDI-56 (Pin 26) | C1S5.26 | 33 ms | 0 -> 1 -> 0 | PASS
C1-LPB-057 | C1S9.27 | P1-TBRL-57 (A1/A2) | P1-TBRL-57 (11/14) | TMP-JMP-057 | P1-TBDI-57 (Pin 27) | C1S5.27 | 33 ms | 0 -> 1 -> 0 | PASS
C1-LPB-058 | C1S9.28 | P1-TBRL-58 (A1/A2) | P1-TBRL-58 (11/14) | TMP-JMP-058 | P1-TBDI-58 (Pin 28) | C1S5.28 | 22 ms | 0 -> 1 -> 0 | PASS
C1-LPB-059 | C1S9.29 | P1-TBRL-59 (A1/A2) | P1-TBRL-59 (11/14) | TMP-JMP-059 | P1-TBDI-59 (Pin 29) | C1S5.29 | 30 ms | 0 -> 1 -> 0 | PASS
C1-LPB-060 | C1S9.30 | P1-TBRL-60 (A1/A2) | P1-TBRL-60 (11/14) | TMP-JMP-060 | P1-TBDI-60 (Pin 30) | C1S5.30 | 40 ms | 0 -> 1 -> 0 | PASS
C1-LPB-061 | C1S9.31 | P1-TBRL-61 (A1/A2) | P1-TBRL-61 (11/14) | TMP-JMP-061 | P1-TBDI-61 (Pin 31) | C1S5.31 | 26 ms | 0 -> 1 -> 0 | PASS
C1-LPB-062 | C1S9.32 | P1-TBRL-62 (A1/A2) | P1-TBRL-62 (11/14) | TMP-JMP-062 | P1-TBDI-62 (Pin 32) | C1S5.32 | 23 ms | 0 -> 1 -> 0 | PASS
C1-LPB-063 | C1S9.33 | P1-TBRL-63 (A1/A2) | P1-TBRL-63 (11/14) | TMP-JMP-063 | P1-TBDI-63 (Pin 33) | C1S5.33 | 35 ms | 0 -> 1 -> 0 | PASS
C1-LPB-064 | C1S9.34 | P1-TBRL-64 (A1/A2) | P1-TBRL-64 (11/14) | TMP-JMP-064 | P1-TBDI-64 (Pin 34) | C1S5.34 | 27 ms | 0 -> 1 -> 0 | PASS

## C1_DI_Direct_Simulation
CHASSIS C1 — DIGITAL INPUT DIRECT DRY CONTACT SIMULATION (64 CHANNELS)
Testing C1S6 DI (Channels 1-32) & C1S7 DI (Channels 33-64) via TB-24VDC Toggle Simulation Jig
Test # | DI Slot & Pin | Target Terminal Tag | Power Source Rail | Simulation Method | Signal Transition | Response Time | PLC Tag Address | Verdict
C1-DIS-001 | C1S6.1 | P1-TBDI-65 (Pin 1) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 20 ms | Local:1:I.Data[0] | PASS
C1-DIS-002 | C1S6.2 | P1-TBDI-66 (Pin 2) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 14 ms | Local:1:I.Data[1] | PASS
C1-DIS-003 | C1S6.3 | P1-TBDI-67 (Pin 3) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 16 ms | Local:1:I.Data[2] | PASS
C1-DIS-004 | C1S6.4 | P1-TBDI-68 (Pin 4) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 24 ms | Local:1:I.Data[3] | PASS
C1-DIS-005 | C1S6.5 | P1-TBDI-69 (Pin 5) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 23 ms | Local:1:I.Data[4] | PASS
C1-DIS-006 | C1S6.6 | P1-TBDI-70 (Pin 6) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 27 ms | Local:1:I.Data[5] | PASS
C1-DIS-007 | C1S6.7 | P1-TBDI-71 (Pin 7) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 17 ms | Local:1:I.Data[6] | PASS
C1-DIS-008 | C1S6.8 | P1-TBDI-72 (Pin 8) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 27 ms | Local:1:I.Data[7] | PASS
C1-DIS-009 | C1S6.9 | P1-TBDI-73 (Pin 9) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 28 ms | Local:1:I.Data[8] | PASS
C1-DIS-010 | C1S6.10 | P1-TBDI-74 (Pin 10) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 21 ms | Local:1:I.Data[9] | PASS
C1-DIS-011 | C1S6.11 | P1-TBDI-75 (Pin 11) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 17 ms | Local:1:I.Data[10] | PASS
C1-DIS-012 | C1S6.12 | P1-TBDI-76 (Pin 12) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 28 ms | Local:1:I.Data[11] | PASS
C1-DIS-013 | C1S6.13 | P1-TBDI-77 (Pin 13) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 12 ms | Local:1:I.Data[12] | PASS
C1-DIS-014 | C1S6.14 | P1-TBDI-78 (Pin 14) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 14 ms | Local:1:I.Data[13] | PASS
C1-DIS-015 | C1S6.15 | P1-TBDI-79 (Pin 15) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 14 ms | Local:1:I.Data[14] | PASS
C1-DIS-016 | C1S6.16 | P1-TBDI-80 (Pin 16) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 13 ms | Local:1:I.Data[15] | PASS
C1-DIS-017 | C1S6.19 | P1-TBDI-81 (Pin 19) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 23 ms | Local:1:I.Data[16] | PASS
C1-DIS-018 | C1S6.20 | P1-TBDI-82 (Pin 20) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 26 ms | Local:1:I.Data[17] | PASS
C1-DIS-019 | C1S6.21 | P1-TBDI-83 (Pin 21) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 15 ms | Local:1:I.Data[18] | PASS
C1-DIS-020 | C1S6.22 | P1-TBDI-84 (Pin 22) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 26 ms | Local:1:I.Data[19] | PASS
C1-DIS-021 | C1S6.23 | P1-TBDI-85 (Pin 23) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 16 ms | Local:1:I.Data[20] | PASS
C1-DIS-022 | C1S6.24 | P1-TBDI-86 (Pin 24) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 17 ms | Local:1:I.Data[21] | PASS
C1-DIS-023 | C1S6.25 | P1-TBDI-87 (Pin 25) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 18 ms | Local:1:I.Data[22] | PASS
C1-DIS-024 | C1S6.26 | P1-TBDI-88 (Pin 26) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 26 ms | Local:1:I.Data[23] | PASS
C1-DIS-025 | C1S6.27 | P1-TBDI-89 (Pin 27) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 16 ms | Local:1:I.Data[24] | PASS
C1-DIS-026 | C1S6.28 | P1-TBDI-90 (Pin 28) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 14 ms | Local:1:I.Data[25] | PASS
C1-DIS-027 | C1S6.29 | P1-TBDI-91 (Pin 29) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 16 ms | Local:1:I.Data[26] | PASS
C1-DIS-028 | C1S6.30 | P1-TBDI-92 (Pin 30) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 21 ms | Local:1:I.Data[27] | PASS
C1-DIS-029 | C1S6.31 | P1-TBDI-93 (Pin 31) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 22 ms | Local:1:I.Data[28] | PASS
C1-DIS-030 | C1S6.32 | P1-TBDI-94 (Pin 32) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 24 ms | Local:1:I.Data[29] | PASS
C1-DIS-031 | C1S6.33 | P1-TBDI-95 (Pin 33) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 14 ms | Local:1:I.Data[30] | PASS
C1-DIS-032 | C1S6.34 | P1-TBDI-96 (Pin 34) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 13 ms | Local:1:I.Data[31] | PASS
C1-DIS-033 | C1S7.1 | P1-TBDI-97 (Pin 1) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 23 ms | Local:2:I.Data[0] | PASS
C1-DIS-034 | C1S7.2 | P1-TBDI-98 (Pin 2) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 26 ms | Local:2:I.Data[1] | PASS
C1-DIS-035 | C1S7.3 | P1-TBDI-99 (Pin 3) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 13 ms | Local:2:I.Data[2] | PASS
C1-DIS-036 | C1S7.4 | P1-TBDI-100 (Pin 4) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 18 ms | Local:2:I.Data[3] | PASS
C1-DIS-037 | C1S7.5 | P1-TBDI-101 (Pin 5) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 20 ms | Local:2:I.Data[4] | PASS
C1-DIS-038 | C1S7.6 | P1-TBDI-102 (Pin 6) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 22 ms | Local:2:I.Data[5] | PASS
C1-DIS-039 | C1S7.7 | P1-TBDI-103 (Pin 7) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 14 ms | Local:2:I.Data[6] | PASS
C1-DIS-040 | C1S7.8 | P1-TBDI-104 (Pin 8) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 20 ms | Local:2:I.Data[7] | PASS
C1-DIS-041 | C1S7.9 | P1-TBDI-105 (Pin 9) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 16 ms | Local:2:I.Data[8] | PASS
C1-DIS-042 | C1S7.10 | P1-TBDI-106 (Pin 10) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 20 ms | Local:2:I.Data[9] | PASS
C1-DIS-043 | C1S7.11 | P1-TBDI-107 (Pin 11) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 26 ms | Local:2:I.Data[10] | PASS
C1-DIS-044 | C1S7.12 | P1-TBDI-108 (Pin 12) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 18 ms | Local:2:I.Data[11] | PASS
C1-DIS-045 | C1S7.13 | P1-TBDI-109 (Pin 13) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 25 ms | Local:2:I.Data[12] | PASS
C1-DIS-046 | C1S7.14 | P1-TBDI-110 (Pin 14) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 15 ms | Local:2:I.Data[13] | PASS
C1-DIS-047 | C1S7.15 | P1-TBDI-111 (Pin 15) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 28 ms | Local:2:I.Data[14] | PASS
C1-DIS-048 | C1S7.16 | P1-TBDI-112 (Pin 16) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 22 ms | Local:2:I.Data[15] | PASS
C1-DIS-049 | C1S7.19 | P1-TBDI-113 (Pin 19) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 19 ms | Local:2:I.Data[16] | PASS
C1-DIS-050 | C1S7.20 | P1-TBDI-114 (Pin 20) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 15 ms | Local:2:I.Data[17] | PASS
C1-DIS-051 | C1S7.21 | P1-TBDI-115 (Pin 21) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 20 ms | Local:2:I.Data[18] | PASS
C1-DIS-052 | C1S7.22 | P1-TBDI-116 (Pin 22) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 17 ms | Local:2:I.Data[19] | PASS
C1-DIS-053 | C1S7.23 | P1-TBDI-117 (Pin 23) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 12 ms | Local:2:I.Data[20] | PASS
C1-DIS-054 | C1S7.24 | P1-TBDI-118 (Pin 24) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 12 ms | Local:2:I.Data[21] | PASS
C1-DIS-055 | C1S7.25 | P1-TBDI-119 (Pin 25) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 24 ms | Local:2:I.Data[22] | PASS
C1-DIS-056 | C1S7.26 | P1-TBDI-120 (Pin 26) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 26 ms | Local:2:I.Data[23] | PASS
C1-DIS-057 | C1S7.27 | P1-TBDI-121 (Pin 27) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 13 ms | Local:2:I.Data[24] | PASS
C1-DIS-058 | C1S7.28 | P1-TBDI-122 (Pin 28) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 22 ms | Local:2:I.Data[25] | PASS
C1-DIS-059 | C1S7.29 | P1-TBDI-123 (Pin 29) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 19 ms | Local:2:I.Data[26] | PASS
C1-DIS-060 | C1S7.30 | P1-TBDI-124 (Pin 30) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 20 ms | Local:2:I.Data[27] | PASS
C1-DIS-061 | C1S7.31 | P1-TBDI-125 (Pin 31) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 27 ms | Local:2:I.Data[28] | PASS
C1-DIS-062 | C1S7.32 | P1-TBDI-126 (Pin 32) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 18 ms | Local:2:I.Data[29] | PASS
C1-DIS-063 | C1S7.33 | P1-TBDI-127 (Pin 33) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 22 ms | Local:2:I.Data[30] | PASS
C1-DIS-064 | C1S7.34 | P1-TBDI-128 (Pin 34) | TB-24VDC (Rail 1) | 16-CH Toggle Switch Box | 0 -> 1 -> 0 | 22 ms | Local:2:I.Data[31] | PASS

## Sign_Off_Certificate
CHASSIS C1 DI/DO FAT ACCEPTANCE & ENDORSEMENT CERTIFICATE
Project Name: | Ingredion Thailand — SPRINT 18K TPA Spray Dryer Plant (Kalasin)
Target Control System: | Rockwell Automation ControlLogix 5580 — Chassis C1 (Main CPU & Core I/O)
Test Scope: | 100% Verification of 64 DO Channels (C1S8, C1S9) & 128 DI Channels (C1S4, C1S5, C1S6, C1S7)
Test Standards: | IEC 62381 / ISA-RP60.8 / NFPA 79 Electrical Safety Standards
Testing Venue: | xDev Engineering Workshop, Assembly & Integration Testing Bay 1
Test Date: | 08-October-2026
Overall Pass Rate: | 192 / 192 Channels Tested (100.0% PASS Rate ¦ 0 Open Category A Defects)
Final Verdict: | CHASSIS C1 DI/DO WIRING & HARDWARE OFFICIALLY ACCEPTED FOR COMMISSIONING
REPRESENTATIVE ENDORSEMENTS:
____________________________________ |  | ____________________________________ | ____________________________________
Client Lead Representative |  | Lead Automation Integrator | Quality & Safety Officer
Ingredion (Thailand) Co., Ltd. |  | Kalasin Engineering Co., Ltd. | xDev Workshop Integration Center
Project Engineering Manager |  | Senior Automation Engineer | QA/QC Compliance Lead
Date: _____ / _____ / 2026 |  | Date: _____ / _____ / 2026 | Date: _____ / _____ / 2026