## FAT_Schedule_C1_C4
FAT 1-DAY AGENDA & TIMETABLE — FOCUS ON CHASSIS C1, C2, C3, C4
Project: SPRINT 18K Spray Dryer ¦ Target: MCP-01 (C1, C2, C3, C4) ¦ Ref: KAL-FAT-AGN-2608-C1C4
Item | Time Window | Duration | Milestone / Agenda Item | Key Activities (Focus on Chassis C1–C4) | Lead Role | Location / Bay
1 | 09:00 - 09:15 | 15 min | Client Arrival & Welcome | Client reception, visitor badge, safety induction, ESD protection check before entering MCP-01 bay. | Safety Lead / Host | Lobby / Conf Room A
2 | 09:15 - 09:30 | 15 min | Detail on FAT (Kick-off Briefing) | 15-Min Kick-off on C1-C4: 4-Chassis DLR ring architecture, test boundary, acceptance criteria, Cat A vs B punch rules. | Project Manager / Lead Automation | Main Conference Room
3 | 09:30 - 10:45 | 75 min | Station 1: C1 & C2 Core Audit | C1 Master CPU (Slot 0: 1756-L950TPSXT), Cisco 9300 HSRP & DLR ring break test (<3ms), C1 & C2 DI loop toggle (1756-IB32) & DO relay forcing (1756-OB32 -> TBRL -> TB-0VDC). | Lead PLC Eng / Client Inspector | Test Bay 1 (MCP-01: C1/C2)
4 | 10:45 - 12:00 | 75 min | Station 2: C1 & C2 Analog Loops | C1 (C1S10-S11) & C2 (C2S9-S12) 4-20mA calibration audit (Fluke 789 5-point test), verify differential loops (IN-x / i RTN-x) on 1756-IF16, zero crosstalk check. | Instrumentation Lead / Client Rep | Test Bay 1 (MCP-01: C1/C2)
5 | 12:00 - 13:00 | 60 min | Lunch Break & Informal Discussion | Executive hot luncheon served in private dining room. Mid-day review of morning C1/C2 test logs. | All Participants | Executive Dining Lounge
6 | 13:00 - 14:15 | 75 min | Station 3: C3 (AO) & C4 (P&F IS Barrier) | Chassis C3 modulating valve AO (1756-OF8: 4-20mA) simulation; Chassis C4 dedicated Hazardous Area RIO with Pepperl+Fuchs K-System Zener barrier audit & wire break alarm. | Instrumentation & IS Lead / Client | Test Bay 2 (MCP-01: C3/C4)
7 | 14:15 - 15:00 | 45 min | Station 4: SCADA & Safety Interlocks | FactoryTalk View SE SCADA integration for C1-C4 tags, faceplates & alarms. Process safety trips: Chamber high-temp trip, burner lockout & Master E-Stop de-energization (<50ms). | SCADA Lead / Process Eng | SCADA Control Station
8 | 15:00 - 15:30 | 30 min | Coffee Break & Data Consolidation | Afternoon coffee break, pastries and refreshments. Engineering team consolidates completed C1-C4 test sheets into preliminary Punch List. | All Participants (Eng team consolidates) | Hospitality Lounge / Office
9 | 15:30 - 16:30 | 60 min | Summary Meeting & Comments | Presentation of C1-C4 test results & 100% pass rate. Detailed review of Client Comments. Categorize Punch List (Cat A vs B), assign action owners & due dates. | PM, Lead Engineers & Client Team | Main Conference Room
10 | 16:30 - 17:00 | 30 min | FAT Sign-off & Departure | Formal signing of FAT Certificate of Acceptance for MCP-01 (C1-C4). Review packing protection, dispatch plan & SAT alignment. Departure. | Signatories & Directors | Main Conference Room

## C1_C4_Scope_Matrix
CHASSIS C1, C2, C3, C4 HARDWARE & TESTING SCOPE MATRIX
Chassis | Slot Range | Module Types | Channel Count | Primary Field Destinations | Testing Method | Acceptance Standard
C1 (Master) | S0: 1756-L950TPSXT S1-S3: 1756-EN4TR | CPU (20MB) + 3x 1Gbps COMM | 1x CPU Core 3x Network Links | Central Area (CA1), DLR Supervisor, Cisco 9300 | CPU power-up, DLR ring break test (<3ms), HSRP switch failover, memory health check. | 100% Green status, 0 packet drop
C1 (Local I/O) | S4-S7: 1756-IB32 S8-S9: 1756-OB32 S10-S11: 1756-IF16 | 4x DI (32-pt) 2x DO (32-pt) 2x AI (16-pt) | 128 DI, 64 DO, 32 AI Channels | CA1, JB-401, JB-601 | Toggle DI contacts via TB-24VDC; force DO to TBRL relays; 5-point AI calibration with Fluke 789. | DI/DO 100% bit toggle, AI error <0.5% FS
C2 (Process) | S0: 1756-EN4TR S1-S5: 1756-IB32 | 1x DLR COMM 5x DI (32-pt) | 160 DI Channels | JB-402, JB-602, JB-607 | Simulate dry contacts from field pumps, valves and limit switches; verify Studio 5000 bit status. | DI transition verified, LED on
C2 (Process) | S6-S8: 1756-OB32 S9-S12: 1756-IF16 | 3x DO (32-pt) 4x AI (16-pt) | 96 DO Channels 64 AI Channels | JB-402, JB-602, JB-607, CA1 | Force DO bits to interposing relays; inject 4-20mA to differential inputs (IN-x & i RTN-x). | Relay contacts closed, AI error <0.5% FS
C3 (Extended) | S0: 1756-EN4TR S1-S3: 1756-IB32 S4-S5: 1756-OB32 | 1x DLR COMM 3x DI (32-pt) 2x DO (32-pt) | 96 DI Channels 64 DO Channels | JB-606, JB-612, JB-618 | Simulate bag filter differential pressure switches, rotary valve limits, and pulse jet outputs. | Pulse jet timing verified, DI/DO ok
C3 (Extended) | S6-S9: 1756-IF16 S12: 1756-OF8 | 4x AI (16-pt) 1x AO (8-pt) | 64 AI Channels 8 AO Channels | JB-607, JB-608, JB-612, JB-618 | AI temperature/pressure calibration; force AO modulating setpoints (4-20mA) to control valves. | AO current output error <0.5% FS
C4 (IS Barrier) | S0: 1756-EN4TR S1-S3: 1756-IB32 | 1x DLR COMM 3x IS-DI (32-pt) | 96 IS DI Channels | IS-JB-603, 608, IS-JB-612, 618 | Namur proximity switch simulation through Pepperl+Fuchs K-System Zener / Galvanic barriers. | P&F barrier healthy, DI bit toggle ok
C4 (IS Barrier) | S4: 1756-OB32 S5-S6: 1756-IF16 | 1x IS-DO (32-pt) 2x IS-AI (16-pt) | 32 IS DO Channels 32 IS AI Channels | IS-JB-603, 608, IS-JB-612, 618 | P&F DO isolator solenoid drive; P&F AI barrier transparency test & wire-break fault detection. | Line Fault Detection (LFD) alarms ok

## Punch_List_C1_C4
FAT PUNCH LIST & ACTION TRACKING LOG — CHASSIS C1, C2, C3, C4
Item # | Category | Target Chassis / Slot | Defect / Observation Description | Proposed Corrective Action | Responsible Owner | Target Due Date | Status | Client Sign-off
P-01 | Cat B | MCP-01 / C1 | Slight paint scuff mark on bottom left door frame from transit. | Touch-up paint using OEM Tamco RAL 7035 aerosol. | Mechanical Lead | Before Dispatch | Open
P-02 | Cat B | C3S12 (AO) | Terminal label on AO TB-402-1 requires bolder text. | Replace ferrule label sleeve with high-contrast heat-shrink. | Wiring Lead | Same Day (17:00) | Closed | VERIFIED
P-03 | Cat A | C1-C4 Overall | No Category A critical issues identified during Pre-FAT audit. | Maintain zero Category A status through final sign-off. | Lead Automation | N/A | N/A

## Attendee_Register
FAT ATTENDEE & PARTICIPANT REGISTER (MCP-01: C1–C4)
No. | Full Name | Organization / Company | Role / Job Title | Contact Phone / Email | Sign-in Signature
1 | Client Project Manager | Ingredion (Thailand) Co., Ltd. | Project Engineering Manager | pm@ingredion.com
2 | Client Lead Automation / E&I | Ingredion (Thailand) Co., Ltd. | Lead Instrumentation & Control Eng | ei.lead@ingredion.com
3 | Client Plant Operations Lead | Ingredion (Thailand) Co., Ltd. | Spray Dryer Process Specialist | ops@ingredion.com
4 | Lead System Integrator | Kalasin Engineering Co., Ltd. | Project Automation Manager | +66 81-xxx-xxxx
5 | Lead PLC / SCADA Engineer | Kalasin Engineering Co., Ltd. | Senior Automation Engineer (C1-C4) | +66 89-xxx-xxxx
6 | Electrical & Wiring Lead | Kalasin Engineering Co., Ltd. | MCP-01 Hardware Integration Lead | +66 86-xxx-xxxx
7 | QA/QC & Safety Officer | xDev Workshop Integration Center | QA/QC Compliance Lead | +66 84-xxx-xxxx

## DIDO_Loopback_Simulation
AUTOMATED DI/DO CLOSED-LOOP CROSS-WIRING SIMULATION (SAMPLE LOG)
Objective: Verify wiring from PLC DO to Relay Coil (A1/A2), Relay Contacts (11/14), and DI Input Terminals
Loop # | DO Slot & Pin | Interposing Relay Coil Tag | Relay Dry Contact | Temp Loopback Wire Ref | Paired DI Terminal Block | DI Slot & Pin | Switching Latency | Loop State Transition | Verdict
LPB-001 | C1S8 - Pin 1 | TBRL-1 (A1/A2) | TBRL-1 (11/14) | JMP-LPB-001 | TBDI-1 (Pin 1) | C1S4 - Pin 1 | 30 ms | 0 -> 1 -> 0 | PASS
LPB-002 | C1S8 - Pin 2 | TBRL-2 (A1/A2) | TBRL-2 (11/14) | JMP-LPB-002 | TBDI-2 (Pin 2) | C1S4 - Pin 2 | 43 ms | 0 -> 1 -> 0 | PASS
LPB-003 | C1S8 - Pin 3 | TBRL-3 (A1/A2) | TBRL-3 (11/14) | JMP-LPB-003 | TBDI-3 (Pin 3) | C1S4 - Pin 3 | 37 ms | 0 -> 1 -> 0 | PASS
LPB-004 | C1S8 - Pin 4 | TBRL-4 (A1/A2) | TBRL-4 (11/14) | JMP-LPB-004 | TBDI-4 (Pin 4) | C1S4 - Pin 4 | 28 ms | 0 -> 1 -> 0 | PASS
LPB-005 | C1S8 - Pin 5 | TBRL-5 (A1/A2) | TBRL-5 (11/14) | JMP-LPB-005 | TBDI-5 (Pin 5) | C1S4 - Pin 5 | 39 ms | 0 -> 1 -> 0 | PASS
LPB-006 | C1S8 - Pin 6 | TBRL-6 (A1/A2) | TBRL-6 (11/14) | JMP-LPB-006 | TBDI-6 (Pin 6) | C1S4 - Pin 6 | 26 ms | 0 -> 1 -> 0 | PASS
LPB-007 | C1S8 - Pin 7 | TBRL-7 (A1/A2) | TBRL-7 (11/14) | JMP-LPB-007 | TBDI-7 (Pin 7) | C1S4 - Pin 7 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-008 | C1S8 - Pin 8 | TBRL-8 (A1/A2) | TBRL-8 (11/14) | JMP-LPB-008 | TBDI-8 (Pin 8) | C1S4 - Pin 8 | 40 ms | 0 -> 1 -> 0 | PASS
LPB-009 | C1S8 - Pin 9 | TBRL-9 (A1/A2) | TBRL-9 (11/14) | JMP-LPB-009 | TBDI-9 (Pin 9) | C1S4 - Pin 9 | 40 ms | 0 -> 1 -> 0 | PASS
LPB-010 | C1S8 - Pin 10 | TBRL-10 (A1/A2) | TBRL-10 (11/14) | JMP-LPB-010 | TBDI-10 (Pin 10) | C1S4 - Pin 10 | 37 ms | 0 -> 1 -> 0 | PASS
LPB-011 | C1S8 - Pin 11 | TBRL-11 (A1/A2) | TBRL-11 (11/14) | JMP-LPB-011 | TBDI-11 (Pin 11) | C1S4 - Pin 11 | 29 ms | 0 -> 1 -> 0 | PASS
LPB-012 | C1S8 - Pin 12 | TBRL-12 (A1/A2) | TBRL-12 (11/14) | JMP-LPB-012 | TBDI-12 (Pin 12) | C1S4 - Pin 12 | 37 ms | 0 -> 1 -> 0 | PASS
LPB-013 | C1S8 - Pin 13 | TBRL-13 (A1/A2) | TBRL-13 (11/14) | JMP-LPB-013 | TBDI-13 (Pin 13) | C1S4 - Pin 13 | 35 ms | 0 -> 1 -> 0 | PASS
LPB-014 | C1S8 - Pin 14 | TBRL-14 (A1/A2) | TBRL-14 (11/14) | JMP-LPB-014 | TBDI-14 (Pin 14) | C1S4 - Pin 14 | 28 ms | 0 -> 1 -> 0 | PASS
LPB-015 | C1S8 - Pin 15 | TBRL-15 (A1/A2) | TBRL-15 (11/14) | JMP-LPB-015 | TBDI-15 (Pin 15) | C1S4 - Pin 15 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-016 | C1S8 - Pin 16 | TBRL-16 (A1/A2) | TBRL-16 (11/14) | JMP-LPB-016 | TBDI-16 (Pin 16) | C1S4 - Pin 16 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-017 | C1S8 - Pin 19 | TBRL-17 (A1/A2) | TBRL-17 (11/14) | JMP-LPB-017 | TBDI-17 (Pin 19) | C1S4 - Pin 19 | 43 ms | 0 -> 1 -> 0 | PASS
LPB-018 | C1S8 - Pin 20 | TBRL-18 (A1/A2) | TBRL-18 (11/14) | JMP-LPB-018 | TBDI-18 (Pin 20) | C1S4 - Pin 20 | 35 ms | 0 -> 1 -> 0 | PASS
LPB-019 | C1S8 - Pin 21 | TBRL-19 (A1/A2) | TBRL-19 (11/14) | JMP-LPB-019 | TBDI-19 (Pin 21) | C1S4 - Pin 21 | 33 ms | 0 -> 1 -> 0 | PASS
LPB-020 | C1S8 - Pin 22 | TBRL-20 (A1/A2) | TBRL-20 (11/14) | JMP-LPB-020 | TBDI-20 (Pin 22) | C1S4 - Pin 22 | 35 ms | 0 -> 1 -> 0 | PASS
LPB-021 | C1S8 - Pin 23 | TBRL-21 (A1/A2) | TBRL-21 (11/14) | JMP-LPB-021 | TBDI-21 (Pin 23) | C1S4 - Pin 23 | 35 ms | 0 -> 1 -> 0 | PASS
LPB-022 | C1S8 - Pin 24 | TBRL-22 (A1/A2) | TBRL-22 (11/14) | JMP-LPB-022 | TBDI-22 (Pin 24) | C1S4 - Pin 24 | 36 ms | 0 -> 1 -> 0 | PASS
LPB-023 | C1S8 - Pin 25 | TBRL-23 (A1/A2) | TBRL-23 (11/14) | JMP-LPB-023 | TBDI-23 (Pin 25) | C1S4 - Pin 25 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-024 | C1S8 - Pin 26 | TBRL-24 (A1/A2) | TBRL-24 (11/14) | JMP-LPB-024 | TBDI-24 (Pin 26) | C1S4 - Pin 26 | 23 ms | 0 -> 1 -> 0 | PASS
LPB-025 | C1S8 - Pin 27 | TBRL-25 (A1/A2) | TBRL-25 (11/14) | JMP-LPB-025 | TBDI-25 (Pin 27) | C1S4 - Pin 27 | 43 ms | 0 -> 1 -> 0 | PASS
LPB-026 | C1S8 - Pin 28 | TBRL-26 (A1/A2) | TBRL-26 (11/14) | JMP-LPB-026 | TBDI-26 (Pin 28) | C1S4 - Pin 28 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-027 | C1S8 - Pin 29 | TBRL-27 (A1/A2) | TBRL-27 (11/14) | JMP-LPB-027 | TBDI-27 (Pin 29) | C1S4 - Pin 29 | 42 ms | 0 -> 1 -> 0 | PASS
LPB-028 | C1S8 - Pin 30 | TBRL-28 (A1/A2) | TBRL-28 (11/14) | JMP-LPB-028 | TBDI-28 (Pin 30) | C1S4 - Pin 30 | 25 ms | 0 -> 1 -> 0 | PASS
LPB-029 | C1S8 - Pin 31 | TBRL-29 (A1/A2) | TBRL-29 (11/14) | JMP-LPB-029 | TBDI-29 (Pin 31) | C1S4 - Pin 31 | 23 ms | 0 -> 1 -> 0 | PASS
LPB-030 | C1S8 - Pin 32 | TBRL-30 (A1/A2) | TBRL-30 (11/14) | JMP-LPB-030 | TBDI-30 (Pin 32) | C1S4 - Pin 32 | 34 ms | 0 -> 1 -> 0 | PASS
LPB-031 | C1S8 - Pin 33 | TBRL-31 (A1/A2) | TBRL-31 (11/14) | JMP-LPB-031 | TBDI-31 (Pin 33) | C1S4 - Pin 33 | 45 ms | 0 -> 1 -> 0 | PASS
LPB-032 | C1S8 - Pin 34 | TBRL-32 (A1/A2) | TBRL-32 (11/14) | JMP-LPB-032 | TBDI-32 (Pin 34) | C1S4 - Pin 34 | 32 ms | 0 -> 1 -> 0 | PASS